## Daily Dashboard
Month :-July 2025
Month | 2025-07-01
Date | 2025-07-22
Operation Year | 2026
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
2025-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 40.7027 | 39.3337 | -3.363%
| E_Grid MTD(MWh) | 895.4584 | 914.4089 | 2.116%
| E_Grid YTD (MWh) | 6253.2193 | 5220.7918 | -16.51%
2 | CUF Daily(%) | 14.47% | 13.98% | -3.363%
| CUF MTD(%) | 14.47% | 14.78% | 2.116%
| CUF YTD(%) | 19.67% | 16.43% | -16.51%
3 | PR_Daily (%) | 75.06% | 74.02% | -1.383%
| PR_MTD (%) | 75.06% | 74.48% | -0.7758%
| PR_YTD (%) | 72.67% | 68.84% | -5.271%
4 | POA Daily (KWh/m2) | 4.6269 | 4.534 | -2.009%
| POA MTD(KWh/m2) | 101.7925 | 104.7595 | 2.915%
| POA YTD(KWh/m2) | 735.8255 | 647.092 | -12.06%
5 | PA Daily | 99.5% | 99.5% | -0.001488%
| PA MTD | 99.5% | 99.97% | 0.4731%
| PA YTD | 99.5% | 98.9% | -0.6071%
6 | GA Daily | 98.55% | 100% | 1.471%
| GA MTD | 98.55% | 98.73% | 0.185%
| GA YTD | 98.55% | 95.82% | -2.768%
7 | TA Daily | 99.5% | 98.63% | -0.875%
| TA MTD | 99.5% | 98.71% | -0.7908%
| TA YTD | 99.5% | 97.99% | -1.516%

## CMS_Data
Daily
Tagname | Date | Target | Actual | Difference
E Grid Target | 4586000% | 40.7027 | 39.3337 | 1.369
Shadding | 4586000% | 0 | 0 | 0
Soiling | 4586000% | 0 | 0 | 0
IAM | 4586000% | 0 | 0 | 0
Bifacial Gain | 4586000% | 0 | 0 | 0
Temperature | 4586000% | 0 | 0 | 0
Mismatch | 4586000% | 0 | 0 | 0
DC Ohmic | 4586000% | 0 | 0 | 0
AC Ohmic | 4586000% | 0 | 0 | 0
Inverter Conversion | 4586000% | 0 | 0 | 0
MPPT Mismatch | 4586000% | 0 | 0 | 0
Clipping Loss | 4586000% | 0 | 0 | 0
Curtailment Order | 4586000% | 0 | 0 | 0
Reactive Power | 4586000% | 0 | 0 | 0
Plant Uptime | 4586000% | 99.5 | 99.4985 | -0.0014802 | -0.00060246
Grid Uptime | 4586000% | 98.55 | 100 | 1.45 | 0.59019
Tracker Uptime | 4586000% | 99.5 | 98.6294 | -0.87061 | -0.070873
Tracker Gain | 4586000% | 0 | 0 | 0
Dc Unbalanced Load | 4586000% | 0 | 0 | 0
Measured | 4586000% | 39.3337 | 39.3337 | 39.3337
Repowering Delay | 4586000% | 0 | 0 | 0
Capacity Shortfall | 4586000% | 0 | 0 | 0
PR | 4586000% | 0 | -0.032716 | -0.032716
POA | 4586000% | 4.6269 | 4.534 | -0.092933 | -0.81752

## Annual KPI
Till Date | 2025-07-22 | 2025-07-01
ES Solar Private Limited Performance Summary-YTD
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target TA (%) | Measured TA (%)
2026 | 113 | 735.8255 | 647.092 | 6253.2193 | 5220.7918 | 72.51% | 68.84% | 19.67% | 16.43% | 98.55% | 95.82% | 99.5% | 98.9% | 99.5% | 97.99%
ES Solar Private Limited Performance Summary-Monthwise
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target TA (%) | Measured TA (%)
2025-04-01 | 30 | 228.5601 | 203.5885 | 1903.6714 | 1666.8495 | 71.07% | 69.86% | 22.56% | 19.75% | 98.55% | 98.18% | 99.5% | 100% | 99.5% | 96.4%
2025-05-01 | 31 | 465.5149 | 185.2855 | 3935.3547 | 1419.166 | 72.13% | 65.35% | 45.13% | 16.28% | 98.55% | 93.99% | 99.5% | 96.06% | 99.5% | 98.43%
2025-06-01 | 30 | 634.033 | 153.4585 | 5357.7609 | 1220.3674 | 72.1% | 67.85% | 63.49% | 14.46% | 98.55% | 93.23% | 99.5% | 99.94% | 99.5% | 98.6%
2025-07-01 | 31 | 735.8255 | 104.7595 | 6253.2193 | 914.4089 | 72.51% | 74.48% | 71.71% | 10.49% | 98.55% | 98.73% | 99.5% | 99.97% | 99.5% | 98.71%
2025-08-01 | 31 | 735.8255 | 0 | 6253.2193 | 0 | 72.51% |  | 71.71% | 0% | 98.55% |  | 99.5% |  | 99.5%
2025-09-01 | 30 | 735.8255 | 0 | 6253.2193 | 0 | 72.51% |  | 74.1% | 0% | 98.55% |  | 99.5% |  | 99.5%
2025-10-01 | 31 | 735.8255 | 0 | 6253.2193 | 0 | 72.51% |  | 71.71% | 0% | 98.55% |  | 99.5% |  | 99.5%
2025-11-01 | 30 | 735.8255 | 0 | 6253.2193 | 0 | 72.51% |  | 74.1% | 0% | 98.55% |  | 99.5% |  | 99.5%
2025-12-01 | 31 | 735.8255 | 0 | 6253.2193 | 0 | 72.51% |  | 71.71% | 0% | 98.55% |  | 99.5% |  | 99.5%
2026-01-01 | 31 | 735.8255 | 0 | 6253.2193 | 0 | 72.51% |  | 71.71% | 0% | 98.55% |  | 99.5% |  | 99.5%
2026-02-01 | 28 | 735.8255 | 0 | 6253.2193 | 0 | 72.51% |  | 79.4% | 0% | 98.55% |  | 99.5% |  | 99.5%
2026-03-01 | 31 | 735.8255 | 0 | 6253.2193 | 0 | 72.51% |  | 71.71% | 0% | 98.55% |  | 99.5% |  | 99.5%
Formulas:
Days = DAY(EOMONTH([Year],0))

## Monthly KPI
Till Date | 2025-07-22
ES Solar Private Limited Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target TA (%) | Measured TA (%)
2025-07-01 | 22 | 101.7925 | 104.7595 | 895.4584 | 914.4089 | 75.06% | 74.48% | 14.47% | 14.78% | 98.55% | 98.73% | 99.5% | 99.97% | 99.5% | 98.71%
Start Date | 2025-07-16
End Date | 2025-07-22
ES Solar Private Limited Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target TA (%) | Measured TA (%)
2025-07-01 | 7 | 32.3885 | 35.419 | 284.9186 | 305.8844 | 75.06% | 73.69% | 14.47% | 15.54% | 98.55% | 97.92% | 99.5% | 99.93% | 99.5% | 98.56%
Formulas:
Days = [Days, row below]-6

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 12.0667 | 0 |  | 6.201 |  | 23 | 47 | 3 | 7 | 100% |  |  | 97.93% |  | 95.41% |  |  |  | 50008 |  |  |  | 11.72 | 7.7166 | 74138.7097 | 81.98% | 26.36% | 99.5% | 98.55% | [9 empty] | 11.72
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 11.7333 | 0 |  | 6.4635 |  | 23 | 47 | 3 | 7 | 100% |  |  | 100% |  | 95.38% | 70.54% |  | 19% | 53648 | 53632.9 | 194.7 | 53438.2 | 11.72 | 7.7166 | 74138.7097 | 81.98% | 26.36% | 99.5% | 98.55% | [9 empty] | 11.72
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 11.75 | 0 |  | 6.759 |  | 23 | 45.64 | 7.9 | 10 | 100% |  |  | 100% |  | 95.43% | 70.24% |  | 19.78% | 55860 | 55857.4 | 213.8 | 55643.6 | 11.72 | 7.7166 | 74138.7097 | 81.98% | 26.36% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 11.8833 | 0 |  | 6.522 |  | 23 | 46.3 | 6 | 11 | 100% |  |  | 100% |  | 95.42% | 70.27% |  | 19.1% | 53934 | 53905.6 | 192.1 | 53713.5 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 11.85 | 0 |  | 7.825 |  | 23 | 46.3 | 6 | 11 | 100% |  |  | 100% |  | 95.42% | 70.01% |  | 22.82% | 64439 | 64404 | 202.8 | 64201.2 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 11.7 | 0 |  | 4.134 |  | 23 | 35 | 8 | 13 | 100% |  |  | 100% |  | 95.44% | 73.37% |  | 12.64% | 35802 | 35748.2 | 200 | 35548.2 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 11.8667 | 0 |  | 7.965 |  | 23 | 47 | 8 | 15 | 100% |  |  | 100% |  | 95.44% | 70.21% |  | 23.3% | 65783 | 65766.1 | 221.4 | 65544.7 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 11.9 | 0 |  | 6.87 |  | 23 | 47 | 8 | 15 | 100% |  |  | 100% |  | 95.42% | 70.98% |  | 20.32% | 57610 | 57350.3 | 198.8 | 57151.5 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 11.8667 | 0 |  | 7.45 |  | 23 | 47 | 6 | 11 | 100% |  |  | 100% |  | 95.44% | 70.41% |  | 21.86% | 61698 | 61665.7 | 185.6 | 61480.1 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 11.9833 | 0 |  | 7.269 |  | 23 | 47 | 4.9 | 16 | 100% |  |  | 100% |  | 95.43% | 69.62% |  | 21.09% | 59545 | 59510.7 | 200.4 | 59310.3 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 11.9333 | 0 |  | 6.297 |  | 23 | 44 | 6 | 9 | 100% |  |  | 100% |  | 95.41% | 71.29% |  | 18.71% | 52822 | 52786.6 | 171.4 | 52615.2 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 12.0667 | 0 |  | 6.438 |  | 23 | 44 | 5 | 9 | 100% |  |  | 98.62% |  | 95.47% | 69.64% |  | 18.68% | 52783 | 52809.4 | 266 | 52543.4 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 11.9167 | 0 |  | 6.28 |  | 23 | 44 | 5 | 9 | 100% |  |  | 81.96% |  | 95.4% | 70.01% |  | 18.32% | 51777 | 51671.1 | 143.3 | 51527.8 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 11.8333 | 0 |  | 7.4885 |  | 23 | 44 | 5 | 9 | 100% |  |  | 98.59% |  | 95.36% | 69.75% |  | 21.76% | 61509 | 61487.1 | 272.9 | 61214.2 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 11.95 | 0 |  | 7.4275 |  | 23 | 44 | 8 | 11 | 100% |  |  | 100% |  | 95.43% | 70.81% |  | 21.91% | 61789 | 61777.5 | 140.1 | 61637.4 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 12.0667 | 0 |  | 7.1675 |  | 23 | 44 | 8 | 11 | 100% |  |  | 100% |  | 95.43% | 69.96% |  | 20.89% | 58986 | 58958.4 | 192.1 | 58766.3 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 12.0833 | 0 |  | 7.622 |  | 23 | 48.8 | 4.7 | 11 | 100% |  |  | 100% |  | 95.43% | 70.08% |  | 22.26% | 62850 | 62809 | 209.8 | 62599.2 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 12.2167 | 0 |  | 7.5395 |  | 23 | 49.6 | 4.7 | 11 | 100% |  |  | 100% |  | 95.47% | 68.81% |  | 21.62% | 61059 | 60998.2 | 192.9 | 60805.3 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 12.1 | 0 |  | 6.3755 |  | 23 | 48 | 4.7 | 11 | 100% |  |  | 100% |  | 95.44% | 71.55% |  | 19.01% | 53729 | 53649.8 | 185.4 | 53464.4 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 12.1667 | 0 |  | 6.973 |  | 23 | 48 | 4.7 | 11 | 100% |  |  | 100% |  | 95.45% | 71.91% |  | 20.89% | 59011 | 58950.5 | 180.7 | 58769.8 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 10.7 | 0 |  | 4.6045 |  | 23 | 39 | 6 | 16 | 100% |  |  | 100% |  | 94.87% | 71.01% |  | 13.62% | 38584 | 38520.5 | 200.3 | 38320.2 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 12.1167 | 0 |  | 6.566 |  | 23 | 47 | 7 | 21 | 100% |  |  | 100% |  | 95.52% | 70.02% |  | 19.16% | 54154 | 54079.3 | 193.4 | 53885.9 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 12.25 | 0 |  | 7.733 |  | 23 | 47.8 | 6 | 10 | 100% |  |  | 100% |  | 95.48% | 69.72% |  | 22.46% | 63391 | 63367.3 | 180.2 | 63187.1 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 12.0333 | 0 |  | 7.39 |  | 23 | 47.8 | 6 | 10 | 100% |  |  | 100% |  | 98.55% | 70.5% |  | 21.71% | 61251 | 61242.9 | 181.9 | 61061 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 12.1 | 0 |  | 6.935 |  | 23 | 46 | 5 | 11 | 100% |  |  | 92.01% |  | 98.58% | 60.57% |  | 17.5% | 49439 | 49427 | 195.5 | 49231.5 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 12.0667 | 0 |  | 6.7005 |  | 23 | 50 | 6 | 14 | 100% |  |  | 100% |  | 98.57% | 69.45% |  | 19.39% | 54702 | 54630.4 | 93.1 | 54537.3 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 11.9833 | 0 |  | 6.522 |  | 23 | 48 | 6 | 14 | 100% |  |  | 97.22% |  | 98.56% | 70.83% |  | 19.25% | 54437 | 54419.7 | 276.8 | 54142.9 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 11.1667 | 0 |  | 5.754 |  | 23 | 51 | 7.9 | 22 | 100% |  |  | 87.01% |  | 98.44% | 69.61% |  | 16.69% | 47182 | 47129.6 | 183.6 | 46946 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 12.3333 | 0 |  | 7.193 |  | 24 | 47 | 1.7 | 7 | 100% |  |  | 100% |  | 98.58% | 68.57% |  | 20.55% | 58030 | 58002.5 | 197.5 | 57805 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 11 | 0 |  | 4.786 |  | 23 | 42 | 1.7 | 7 | 100% |  |  | 95.45% |  | 98.47% | 73.17% |  | 14.59% | 41311 | 41236 | 196.2 | 41039.8 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 12.3167 | 0 |  | 7.4605 |  | 24 | 48 | 1.7 | 7 | 100% |  |  | 98.65% |  | 98.01% | 69.19% |  | 21.51% | 60717 | 60690.9 | 195.1 | 60495.8 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 12.2333 | 0 |  | 6.364 |  | 23 | 44 | 1.7 | 13 | 100% |  |  | 100% |  | 98.01% | 69.67% |  | 18.47% | 52297 | 52134.6 | 169.7 | 51964.9 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 12.4 | 0 |  | 7.9365 |  | 24 | 48 | 1.7 | 13 | 100% |  |  | 95.83% |  | 98.02% | 68.1% |  | 22.52% | 63373 | 63522.7 | 183.1 | 63339.6 | 11.72 | 7.6187 | 63455.7137 | 71.07% | 22.56% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 12.35 | 0 |  | 7.3975 |  | 24 | 48 | 5 | 8 | 100% |  |  | 100% |  | 98.02% | 69.09% |  | 21.3% | 60169 | 60099.8 | 195.4 | 59904.4 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 12.1333 | 0 |  | 7.258 |  | 24 | 48 | 4 | 7 | 100% |  |  | 100% |  | 98.59% | 69.62% |  | 21.05% | 59459 | 59411.3 | 188.6 | 59222.7 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 12.3667 | 0 |  | 7.848 |  | 24 | 48.7 | 4.7 | 7 | 100% |  |  | 100% |  | 98.59% | 69.61% |  | 22.76% | 64273 | 64193.8 | 170.1 | 64023.7 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 12.4333 | 0 |  | 8.324 |  | 24 | 49 | 2 | 4 | 100% |  |  | 100% |  | 98.6% | 68.25% |  | 23.67% | 66804 | 66766.9 | 186.9 | 66580 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 12.4667 | 0 |  | 8.169 |  | 24 | 53 | 2 | 7 | 100% |  |  | 98.93% |  | 96.78% | 67.3% |  | 22.91% | 64581 | 64601.4 | 171.2 | 64430.2 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 12.1333 | 0 |  | 7.439 |  | 24 | 48 | 3 | 5 | 98.98% |  |  | 100% |  | 98.59% | 70.12% |  | 21.73% | 61433 | 61329.9 | 199.1 | 61130.8 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 12.4167 | 0 |  | 8.61 |  | 24 | 50 | 5 | 7 | 100% |  |  | 100% |  | 98.59% | 68.37% |  | 24.53% | 69499 | 69167.1 | 170.5 | 68996.6 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 12.4833 | 0 |  | 7.948 |  | 24 | 49 | 5 | 9 | 100% |  |  | 100% |  | 98.6% | 69.12% |  | 22.89% | 64558 | 64581.7 | 197.2 | 64384.5 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 12.4833 | 0 |  | 7.536 |  | 24 | 48 | 5 | 7 | 100% |  |  | 98.13% |  | 98.59% | 69.31% |  | 21.76% | 61406 | 61387.8 | 170.5 | 61217.3 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 12.3667 | 0 |  | 6.463 |  | 24 | 46 | 5 | 7 | 100% |  |  | 100% |  | 98.58% | 70.78% |  | 19.06% | 53872 | 53814.3 | 204.6 | 53609.7 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 12.1167 | 0 |  | 6.073 |  | 23 | 46 | 5 | 8 | 100% |  |  | 100% |  | 98.55% | 71.38% |  | 18.06% | 51067 | 50952.3 | 143.8 | 50808.5 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 11.9 | 0 |  | 5.75 |  | 23 | 44 | 6 | 9 | 100% |  |  | 100% |  | 98.53% | 71.52% |  | 17.14% | 48796 | 48400 | 200 | 48200 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 11.8667 | 0 |  | 6.262 |  | 23 | 44 | 6 | 9 | 100% |  |  | 57.87% |  | 98.55% | 54.35% |  | 14.18% | 39449 | 39885.8 | 0 | 39885.8 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 11.5167 | 0 |  | 6.549 |  | 23 | 43 | 5 | 11 | 100% |  |  | 100% |  | 98.49% | 70.66% |  | 19.28% | 54465 | 54423.8 | 189 | 54234.8 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 11.1167 | 0 |  | 4.469 |  | 23 | 43 | 7 | 11 | 100% |  |  | 100% |  | 98.59% | 74.78% |  | 13.93% | 39471 | 39404.9 | 235.2 | 39169.7 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 12.5 | 0 |  | 6.637 |  | 23 | 45 | 5 | 7 | 100% |  |  | 97.6% |  | 98.6% | 69.4% |  | 19.19% | 54066 | 54164.6 | 178.8 | 53985.8 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 12.2167 | 0 |  | 6.887 |  | 23 | 46.6 | 2.4 | 6 | 100% |  |  | 93.32% |  | 98.56% | 66.48% |  | 19.08% | 53945 | 53878.2 | 221.1 | 53657.1 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 12.5 | 0 |  | 5.192 |  | 23 | 40 | 5 | 10 | 100% |  |  | 100% |  | 98.6% | 73.46% |  | 15.89% | 44734 | 44791.8 | 88.9 | 44702.9 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 12.45 | 0 |  | 4.719 |  | 23 | 42 | 5 | 7 | 100% |  |  | 68.01% |  | 98.17% | 48.82% |  | 9.6% | 27131 | 27050.9 | 49.2 | 27001.7 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 12.4167 | 0 |  | 4.529 |  | 23 | 38 | 5 | 10 | 100% |  |  | 100% |  | 98.3% | 73.53% |  | 13.88% | 39277 | 39209.6 | 179.8 | 39029.8 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 9.5667 | 0 |  | 3.194 |  | 23 | 36 | 2 | 6 | 100% |  |  | 87.98% |  | 97.57% | 66.59% |  | 8.862% | 25034 | 25007.1 | 80.9 | 24926.2 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 10.7 | 0 |  | 5.785 |  | 23 | 44 | 2 | 7 | 96.62% |  |  | 96.57% |  | 98.3% | 67.7% |  | 16.32% | 46154 | 46085.9 | 187.5 | 45898.4 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 12.6167 | 0 |  | 5.835 |  | 23 | 44 | 2 | 7 | 99.59% |  |  | 100% |  | 98.48% | 72.86% |  | 17.71% | 50090 | 50024 | 196.9 | 49827.1 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 12.6167 | 0 |  | 3.245 |  | 23 | 31 | 2 | 8 | 100% |  |  | 100% |  | 98.61% | 78.82% |  | 10.66% | 30174 | 30122.9 | 146.9 | 29976 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 12.6833 | 0 |  | 4.46 |  | 23 | 36 | 2 | 8 | 100% |  |  | 100% |  | 98.61% | 73.13% |  | 13.59% | 38413 | 38410.6 | 186.8 | 38223.8 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 12.4167 | 0 |  | 3.038 |  | 23 | 33 | 2 | 6 | 100% |  |  | 93.15% |  | 98.58% | 72.35% |  | 9.159% | 26020 | 25957.7 | 196.5 | 25761.2 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 11.6333 | 0 |  | 2.875 |  | 23 | 33 | 2 | 6 | 100% |  |  | 94.7% |  | 98.47% | 76.38% |  | 9.149% | 25975 | 25931.6 | 196.2 | 25735.4 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 12.4833 | 0 |  | 4.76 |  | 23 | 32 | 2.5 | 5 | 100% |  |  | 35.11% |  | 98.59% | 29.1% |  | 5.772% | 16427 | 16436.9 | 201.7 | 16235.2 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 12.25 | 0 |  | 3.23 |  | 23 | 32 | 2.5 | 5 | 56.42% |  |  | 100% |  | 98.6% | 26.93% |  | 3.624% | 10359 | 10299.1 | 105.4 | 10193.7 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 12.4333 | 0 |  | 6.501 |  | 23 | 37 | 2 | 6 | 34.5% |  |  | 100% |  | 98.61% | 25.62% |  | 6.94% | 19773 | 19626.8 | 104.6 | 19522.2 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 12.75 | 0 |  | 8.303 |  | 23 | 44 | 3 | 7 | 91.61% |  |  | 92.29% |  | 98.6% | 60.31% |  | 20.87% | 58786 | 58820.8 | 130 | 58690.8 | 11.72 | 7.6437 | 65538.1719 | 73.16% | 23.3% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 12.75 | 0 |  | 7.675 |  | 24 | 41 | 3 | 7 | 100% |  |  | 100% |  | 98.6% | 71.33% |  | 22.81% | 64395 | 64322.5 | 160.8 | 64161.7 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 12.7 | 0 |  | 6.404 |  | 23 | 41 | 3 | 8 | 99.59% |  |  | 94.23% |  | 98.59% | 68.99% |  | 18.41% | 51969 | 51964.7 | 181.2 | 51783.5 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 12.7167 | 0 |  | 7.0525 |  | 24 | 42 | 2 | 7 | 100% |  |  | 94.23% |  | 98.6% | 64.02% |  | 18.81% | 53096 | 53089.4 | 176.5 | 52912.9 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 12.55 | 0 |  | 7.8515 |  | 23 | 39 | 2 | 7 | 100% |  |  | 100% |  | 98.58% | 67.89% |  | 22.21% | 62632 | 62627.4 | 155.4 | 62472 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 12.5667 | 0 |  | 3.362 |  | 22 | 36 | 3 | 6 | 100% |  |  | 100% |  | 98.59% | 77.16% |  | 10.81% | 30612 | 30584 | 181.4 | 30402.6 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 12.55 | 0 |  | 6.9025 |  | 23 | 39 | 2 | 5 | 100% |  |  | 74.63% |  | 98.6% | 49.11% |  | 14.12% | 39908 | 39909.4 | 182.3 | 39727.1 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 12.7167 | 0 |  | 5.718 |  | 22 | 40 | 3 | 6 | 100% |  |  | 98.69% |  | 98.6% | 70.72% |  | 16.85% | 47632 | 47586.5 | 191.9 | 47394.6 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 12.65 | 0 |  | 6.038 |  | 24 | 39 | 2 | 5 | 100% |  |  | 100% |  | 98.6% | 72.04% |  | 18.12% | 51189 | 51165.1 | 183.1 | 50982 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 12.0167 | 0 |  | 2.193 |  | 23 | 29 | 8 | 11 | 100% |  |  | 100% |  | 98.62% | 78.14% |  | 7.14% | 20411 | 20307.4 | 223.7 | 20083.7 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 12.6333 | 0 |  | 1.3805 |  | 23 | 26 | 9 | 13 | 100% |  |  | 100% |  | 98.61% | 82.92% |  | 4.77% | 13737 | 13610.7 | 195 | 13415.7 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 11.65 | 0 |  | 3.055 |  | 23 | 31 | 8 | 11 | 100% |  |  | 97.85% |  | 98.61% | 77.21% |  | 9.829% | 27888 | 27841.2 | 195.3 | 27645.9 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 11.8333 | 0 |  | 4.709 |  | 23 | 42 | 6 | 11 | 100% |  |  | 98.73% |  | 98.6% | 75.74% |  | 14.86% | 42025 | 41990.2 | 189.6 | 41800.6 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 12.65 | 0 |  | 3.98 |  | 23 | 41 | 3 | 5 | 100% |  |  | 76.28% |  | 98.6% | 57.48% |  | 9.532% | 27064 | 27067.9 | 256.8 | 26811.1 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 12.7333 | 0 |  | 4.615 |  | 23 | 41 | 3 | 6 | 100% |  |  | 100% |  | 98.62% | 72.8% |  | 14% | 39588 | 39511.4 | 138.1 | 39373.3 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 12.3 | 0 |  | 3.305 |  | 23 | 32 | 3 | 7 | 100% |  |  | 79.54% |  | 98.57% | 45.79% |  | 6.305% | 17934 | 17929.3 | 193.5 | 17735.8 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 11.9167 | 0 |  | 3.659 |  | 23 | 33 | 4 | 9 | 100% |  |  | 88.53% |  | 98.55% | 63.46% |  | 9.675% | 27484 | 27394.2 | 181.2 | 27213 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 12.8333 | 0 |  | 7.0995 |  | 23 | 40 | 5 | 10 | 100% |  |  | 100% |  | 98.62% | 72.42% |  | 21.42% | 60514 | 60456.2 | 202 | 60254.2 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 12.7167 | 0 |  | 5.8425 |  | 23 | 38 | 5 | 10 | 99.77% |  |  | 77.98% |  | 98.6% | 59.25% |  | 14.42% | 40682 | 40765.6 | 196.1 | 40569.5 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 12.5333 | 0 |  | 5.323 |  | 23 | 40 | 5 | 9 | 100% |  |  | 17.55% |  | 98.59% | 6.366% |  | 1.412% | 4149 | 4164.4 | 192.7 | 3971.7 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 12.6 | 0 |  | 5.635 |  | 23 | 40 | 5 | 9 | 98.95% |  |  | 100% |  | 98.61% | 72.92% |  | 17.12% | 48444 | 48365.7 | 205.9 | 48159.8 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 12.6167 | 0 |  | 7.485 |  | 23 | 40 | 5 | 9 | 100% |  |  | 100% |  | 98.61% | 72.71% |  | 22.68% | 64022 | 63968.1 | 187 | 63781.1 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 12.6667 | 0 |  | 6.933 |  | 23 | 40 | 5 | 12 | 99.84% |  |  | 100% |  | 98.6% | 72.46% |  | 20.93% | 59104 | 59059.9 | 185.5 | 58874.4 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 12.55 | 0 |  | 4.8875 |  | 23 | 35.5 | 6 | 11 | 100% |  |  | 100% |  | 98.59% | 75.67% |  | 15.41% | 43601 | 43532.4 | 185.4 | 43347 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 12.4167 | 0 |  | 4.114 |  | 23 | 35 | 6 | 11 | 100% |  |  | 100% |  | 98.59% | 79.37% |  | 13.61% | 38480 | 38474.7 | 203.6 | 38271.1 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 12.5667 | 0 |  | 4.826 |  | 23 | 36 | 4 | 8 | 100% |  |  | 98.54% |  | 98.61% | 74.19% |  | 14.92% | 42248 | 42164.8 | 204.2 | 41960.6 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 0 |  | 3.728 |  | 23 | 33.5 | 4 | 8 | 100% |  |  | 100% |  | 98.62% | 78.96% |  | 12.27% | 34650 | 34657.4 | 157.7 | 34499.7 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 12.7667 | 0 |  | 6.3665 |  | 24 | 39 | 4 | 8 | 100% |  |  | 100% |  | 98.63% | 72.4% |  | 19.2% | 54258 | 54219.8 | 201.7 | 54018.1 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 12.8 | 0 |  | 5.745 |  | 24 | 39 | 4 | 9 | 100% |  |  | 100% |  | 98.63% | 73.52% |  | 17.6% | 49754 | 49697.5 | 192.2 | 49505.3 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 12.65 | 0 |  | 4.0375 |  | 23 | 32 | 5 | 9 | 100% |  |  | 100% |  | 98.61% | 76.48% |  | 12.87% | 36426 | 36402.2 | 212.8 | 36189.4 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 11.6 | 0 |  | 3.536 |  | 23 | 33 | 4 | 9 | 100% |  |  | 100% |  | 98.52% | 79.75% |  | 11.75% | 33217 | 33181.6 | 131.6 | 33050 | 11.72 | 5.6173 | 47413.5389 | 72.02% | 16.86% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 12.3 | 0 |  | 2.9095 |  | 23 | 30 | 4 | 10 | 100% |  |  | 92.68% |  | 98.59% | 68.39% |  | 8.291% | 23498 | 23489.5 | 169.7 | 23319.8 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 12.4833 | 0 |  | 1.8685 |  | 23 | 27.8 | 4 | 7 | 100% |  |  | 100% |  | 101.2% | 84.42% |  | 6.573% | 18730 | 18675 | 187.1 | 18487.9 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 12.4 | 0 |  | 2.936 |  | 23 | 31 | 4 | 8 | 100% |  |  | 100% |  | 98.6% | 82.37% |  | 10.08% | 28582 | 28521.8 | 179.5 | 28342.3 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 12.4667 | 0 |  | 5.243 |  | 23 | 36 | 4.7 | 8 | 100% |  |  | 100% |  | 98.6% | 75.02% |  | 16.39% | 46331 | 46278.5 | 181.4 | 46097.1 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 12.6833 | 0 |  | 5.5305 |  | 23 | 35 | 5 | 10 | 100% |  |  | 100% |  | 98.61% | 75.47% |  | 17.39% | 49145 | 49077 | 156.1 | 48920.9 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 12.4167 | 0 |  | 5.7975 |  | 23 | 36.5 | 5 | 10 | 100% |  |  | 100% |  | 98.61% | 74.94% |  | 18.1% | 51112 | 51094.4 | 174.6 | 50919.8 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | 12.5167 | 0 |  | 2.2005 |  | 23 | 29 | 4 | 6 | 100% |  |  | 100% |  | 98.62% | 84.03% |  | 7.704% | 21891 | 21847.4 | 176.3 | 21671.1 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | 12.5 | 0 |  | 3.3835 |  | 23 | 31 | 4 | 8 | 100% |  |  | 100% |  | 98.61% | 80.21% |  | 11.31% | 32028 | 31986.7 | 179.2 | 31807.5 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | 12.3167 | 0 |  | 3.7805 |  | 23 | 32 | 3 | 7 | 100% |  |  | 100% |  | 98.6% | 78.71% |  | 12.4% | 35111 | 35052.4 | 179.6 | 34872.8 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | 12.7833 | 0 |  | 5.3525 |  | 23 | 36 | 2 | 5 | 100% |  |  | 100% |  | 98.63% | 75.09% |  | 16.75% | 47305 | 47280.1 | 173.1 | 47107 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | 12.55 | 0 |  | 6.159 |  | 24 | 39 | 2 | 6 | 100% |  |  | 100% |  | 98.61% | 72.91% |  | 18.71% | 52773 | 52805.1 | 179.6 | 52625.5 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | 12.7333 | 0 |  | 6.594 |  | 24 | 39 | 3 | 6 | 100% |  |  | 100% |  | 98.63% | 71.2% |  | 19.56% | 55062 | 55041.4 | 17.8 | 55023.6 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | 12.7167 | 0 |  | 6.1085 |  | 24 | 38 | 3 | 6 | 100% |  |  | 100% |  | 98.62% | 73.04% |  | 18.59% | 52510 | 52500.9 | 208.3 | 52292.6 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | 12.75 | 0 |  | 6.761 |  | 24 | 37 | 3 | 7 | 100% |  |  | 100% |  | 98.63% | 71.06% |  | 20.02% | 56530 | 56483.8 | 175.7 | 56308.1 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | 12.7 | 0 |  | 4.716 |  | 24 | 36 | 3 | 7 | 99.86% |  |  | 93.96% |  | 98.63% | 73.69% |  | 14.48% | 40981 | 40901 | 172.5 | 40728.5 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | 12.3167 | 0 |  | 5.516 |  | 24 | 38 | 2 | 5 | 100% |  |  | 100% |  | 98.58% | 74.58% |  | 17.14% | 48410 | 48389.6 | 174.5 | 48215.1 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | 12.5 | 0 |  | 4.893 |  | 23 | 37 | 2 | 6 | 100% |  |  | 100% |  | 98.61% | 76.56% |  | 15.61% | 44148 | 44081.3 | 177.5 | 43903.8 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | 11.0167 | 0 |  | 4.381 |  | 23 | 38 | 2 | 7 | 100% |  |  | 100% |  | 98.42% | 76.16% |  | 13.9% | 39367 | 39304.8 | 200.5 | 39104.3 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | 12.5 | 0 |  | 3.866 |  | 23 | 33 | 2 | 5 | 100% |  |  | 86.8% |  | 98.61% | 66.69% |  | 10.74% | 30465 | 30411 | 193.7 | 30217.3 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | 12.4833 | 0 |  | 6.682 |  | 23 | 41 | 2 | 5 | 100% |  |  | 98.66% |  | 98.62% | 71.75% |  | 19.98% | 56333 | 56376.7 | 184.2 | 56192.5 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | 11.0333 | 0 |  | 5.547 |  | 23 | 39 | 2 | 5.8 | 100% |  |  | 100% |  | 98.42% | 75.25% |  | 17.39% | 49163 | 49085 | 167.3 | 48917.7 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | 12.6667 | 0 |  | 4.534 |  | 23 | 34 | 2.8 | 7 | 99.5% |  |  | 100% |  | 98.63% | 74.02% |  | 13.98% | 39592 | 39507.8 | 174.1 | 39333.7 | 11.72 | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.6269 | 40702.6541 | 75.06% | 14.47% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.7714 | 42082.4051 | 75.25% | 14.96% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.505 | 47057.0461 | 72.94% | 16.73% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.6456 | 50360.9111 | 76.11% | 17.9% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 5.6271 | 49196.0027 | 74.6% | 17.49% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 5.3205 | 48291.2846 | 77.44% | 17.17% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 6.0176 | 54155.2263 | 76.79% | 19.25% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 6.9011 | 57320.0267 | 70.87% | 20.38% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 7.7166 | 67607.7984 | 74.76% | 24.04% | 99.5% | 98.55% | [9 empty] | 11.72
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Raw Data
[7 empty] | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Plant DC Capcity (MW) | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | IC1_Inv1 | IC1_Inv2 | IC1_Inv3 | IC1_Inv4 | IC2_Inv1 | IC2_Inv2 | 33 kV Outgoinng Export Reading | 33 kV Outgoinng Import Reading | GHI(Wh/m2) | POA1(Wh/m2) | POA2(Wh/m2) | Avg. POA Lost (W/m2) | Avg. Ambient Temp (POA>20W/m2) | Avg. Module Temp (POA>20W/m2) | Avg. Wind Speed (m/s) | Max. Wind Speed (m/s) | Rain Fall (mm) | Inverters Generation ( kWh) | Export (kWh) | Import (kWh) | Net Export (kWh) | Avg. POA without Exclusion (W/m2)2 | Net Avg. POA with Exclusion (W/m2) | Operating Hours | Remarks
2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 11.72 | 0.25903 | 0.76181 | 8514 | 8550 | 7600 | 8095 | 8639 | 8610 | 127293.966 | 549.7648 | 0 | 6201 | 6201 | 85 | 23 | 47 | 3 | 7 | 0 | 50008 | #REF! | #REF! | #REF! | 6201 | 6116 | 12.0667
2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 11.72 | 0.26944 | 0.75833 | 9055 | 9136 | 8210 | 8664 | 9336 | 9247 | 127347.5989 | 549.9595 | 0 | 6473 | 6454 | 0 | 23 | 47 | 3 | 7 | 0 | 53648 | 53632.9 | 194.7 | 53438.2 | 6463.5 | 6463.5 | 11.7333
2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 11.72 | 0.27431 | 0.76389 | 9390 | 9589 | 8520 | 8991 | 9722 | 9648 | 127403.4563 | 550.1733 | 0 | 6804 | 6714 | 0 | 23 | 45.64 | 7.9 | 10 | 0 | 55860 | 55857.4 | 213.8 | 55643.6 | 6759 | 6759 | 11.75
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 11.72 | 0.26667 | 0.76181 | 8982 | 9261 | 8262 | 8656 | 9501 | 9272 | 127457.3619 | 550.3654 | 0 | 6522 | 6522 | 0 | 23 | 46.3 | 6 | 11 | 0 | 53934 | 53905.6 | 192.1 | 53713.5 | 6522 | 6522 | 11.8833
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 11.72 | 0.26875 | 0.7625 | 10545 | 10967 | 9938 | 10470 | 11401 | 11118 | 127521.7659 | 550.5682 | 0 | 7848 | 7802 | 0 | 23 | 46.3 | 6 | 11 | 0 | 64439 | 64404 | 202.8 | 64201.2 | 7825 | 7825 | 11.85
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 11.72 | 0.27639 | 0.76389 | 5999 | 6096 | 5489 | 5687 | 6255 | 6276 | 127557.5141 | 550.7682 | 0 | 4148 | 4120 | 0 | 23 | 35 | 8 | 13 | 0 | 35802 | 35748.2 | 200 | 35548.2 | 4134 | 4134 | 11.7
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 11.72 | 0.27014 | 0.76458 | 10910 | 11202 | 10011 | 10521 | 11635 | 11504 | 127623.2802 | 550.9896 | 0 | 7974 | 7956 | 0 | 23 | 47 | 8 | 15 | 0 | 65783 | 65766.1 | 221.4 | 65544.7 | 7965 | 7965 | 11.8667
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 11.72 | 0.26597 | 0.76181 | 9795 | 9732 | 8715 | 9190 | 10105 | 10073 | 127680.6305 | 551.1884 | 0 | 6891 | 6849 | 0 | 23 | 47 | 8 | 15 | 0 | 57610 | 57350.3 | 198.8 | 57151.5 | 6870 | 6870 | 11.9
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 11.72 | 0.27014 | 0.76458 | 10268 | 10616 | 9296 | 9928 | 10811 | 10779 | 127742.2962 | 551.374 | 0 | 7489 | 7411 | 0 | 23 | 47 | 6 | 11 | 0 | 61698 | 61665.7 | 185.6 | 61480.1 | 7450 | 7450 | 11.8667
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 11.72 | 0.26389 | 0.76319 | 9984 | 10079 | 8999 | 9597 | 10425 | 10461 | 127801.8069 | 551.5744 | 0 | 7329 | 7209 | 0 | 23 | 47 | 4.9 | 16 | 0 | 59545 | 59510.7 | 200.4 | 59310.3 | 7269 | 7269 | 11.9833
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 11.72 | 0.26389 | 0.76111 | 8819 | 8973 | 8046 | 8590 | 9142 | 9252 | 127854.5935 | 551.7458 | 0 | 6339 | 6255 | 0 | 23 | 44 | 6 | 9 | 0 | 52822 | 52786.6 | 171.4 | 52615.2 | 6297 | 6297 | 11.9333
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 11.72 | 0.26528 | 0.76806 | 8825 | 8978 | 8139 | 8563 | 9167 | 9111 | 127907.4029 | 552.0118 | 0 | 6485 | 6391 | 138 | 23 | 44 | 5 | 9 | 0 | 52783 | 52809.4 | 266 | 52543.4 | 6438 | 6300 | 12.0667
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 11.72 | 0.26389 | 0.76042 | 8642 | 8802 | 7961 | 8366 | 8966 | 9040 | 127959.074 | 552.1551 | 0 | 6319 | 6241 | 0 | 23 | 44 | 5 | 9 | 8 | 51777 | 51671.1 | 143.3 | 51527.8 | 6280 | 6280 | 11.9167
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 11.72 | 0.2625 | 0.75556 | 10114 | 10308 | 9423 | 9977 | 10898 | 10789 | 128020.5611 | 552.428 | 0 | 7505 | 7472 | 154 | 23 | 44 | 5 | 9 | 0 | 61509 | 61487.1 | 272.9 | 61214.2 | 7488.5 | 7334.5 | 11.8333
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 11.72 | 0.26528 | 0.76319 | 10296 | 10494 | 9384 | 9961 | 10794 | 10860 | 128082.3386 | 552.5681 | 0 | 7440 | 7415 | 0 | 23 | 44 | 8 | 11 | 0 | 61789 | 61777.5 | 140.1 | 61637.4 | 7427.5 | 7427.5 | 11.95
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 11.72 | 0.26111 | 0.76389 | 9772 | 10123 | 8941 | 9477 | 10300 | 10373 | 128141.297 | 552.7602 | 0 | 7177 | 7158 | 0 | 23 | 44 | 8 | 11 | 0 | 58986 | 58958.4 | 192.1 | 58766.3 | 7167.5 | 7167.5 | 12.0667
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 11.72 | 0.26042 | 0.76389 | 10593 | 10781 | 9579 | 10079 | 10855 | 10963 | 128204.106 | 552.97 | 0 | 7668 | 7576 | 0 | 23 | 48.8 | 4.7 | 11 | 0 | 62850 | 62809 | 209.8 | 62599.2 | 7622 | 7622 | 12.0833
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 11.72 | 0.25903 | 0.76806 | 10265 | 10442 | 9257 | 9763 | 10618 | 10714 | 128265.1042 | 553.1629 | 0 | 7536 | 7543 | 0 | 23 | 49.6 | 4.7 | 11 | 0 | 61059 | 60998.2 | 192.9 | 60805.3 | 7539.5 | 7539.5 | 12.2167
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 11.72 | 0.26042 | 0.76458 | 8976 | 9134 | 8180 | 8643 | 9442 | 9354 | 128318.754 | 553.3483 | 0 | 6351 | 6400 | 0 | 23 | 48 | 4.7 | 11 | 0 | 53729 | 53649.8 | 185.4 | 53464.4 | 6375.5 | 6375.5 | 12.1
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 11.72 | 0.25833 | 0.76528 | 9880 | 10032 | 8905 | 9439 | 10426 | 10329 | 128377.7045 | 553.529 | 0 | 6973 | 6973 | 0 | 23 | 48 | 4.7 | 11 | 0 | 59011 | 58950.5 | 180.7 | 58769.8 | 6973 | 6973 | 12.1667
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 11.72 | 0.2625 | 0.70833 | 6398 | 6537 | 5828 | 6170 | 6874 | 6777 | 128416.225 | 553.7293 | 0 | 4631 | 4578 | 0 | 23 | 39 | 6 | 16 | 0 | 38584 | 38520.5 | 200.3 | 38320.2 | 4604.5 | 4604.5 | 10.7
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 11.72 | 0.26806 | 0.77292 | 9081 | 9266 | 8037 | 8680 | 9572 | 9518 | 128470.3043 | 553.9227 | 0 | 6566 | 6566 | 0 | 23 | 47 | 7 | 21 | 0 | 54154 | 54079.3 | 193.4 | 53885.9 | 6566 | 6566 | 12.1167
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 11.72 | 0.25833 | 0.76875 | 10575 | 10734 | 9282 | 10224 | 11344 | 11232 | 128533.6716 | 554.1029 | 0 | 7733 | 7733 | 0 | 23 | 47.8 | 6 | 10 | 0 | 63391 | 63367.3 | 180.2 | 63187.1 | 7733 | 7733 | 12.25
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 11.72 | 0.25556 | 0.75694 | 10217 | 10347 | 9055 | 9872 | 10900 | 10860 | 128594.9145 | 554.2848 | 0 | 7390 | 7390 | 0 | 23 | 47.8 | 6 | 10 | 0 | 61251 | 61242.9 | 181.9 | 61061 | 7390 | 7390 | 12.0333
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 11.72 | 0.26389 | 0.76806 | 8225 | 8602 | 7611 | 7945 | 8590 | 8466 | 128644.3415 | 554.4803 | 0 | 6935 | 6935 | 941 | 23 | 46 | 5 | 11 | 0 | 49439 | 49427 | 195.5 | 49231.5 | 6935 | 5994 | 12.1
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 11.72 | 0.26042 | 0.76319 | 9186 | 9198 | 8081 | 8764 | 9711 | 9762 | 128698.9719 | 554.5734 | 0 | 6657 | 6744 | 0 | 23 | 50 | 6 | 14 | 0 | 54702 | 54630.4 | 93.1 | 54537.3 | 6700.5 | 6700.5 | 12.0667
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 11.72 | 0.26111 | 0.76042 | 9060 | 9448 | 8069 | 8718 | 9569 | 9573 | 128753.3916 | 554.8502 | 0 | 6654 | 6390 | 50 | 23 | 48 | 6 | 14 | 0 | 54437 | 54419.7 | 276.8 | 54142.9 | 6522 | 6472 | 11.9833
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 11.72 | 0.25556 | 0.72083 | 7852 | 8144 | 6953 | 7559 | 8367 | 8307 | 128800.5212 | 555.0338 | 0 | 5754 | 5754 | 35 | 23 | 51 | 7.9 | 22 | 0 | 47182 | 47129.6 | 183.6 | 46946 | 5754 | 5719 | 11.1667
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 11.72 | 0.25347 | 0.76736 | 9772 | 9884 | 8388 | 9430 | 10193 | 10363 | 128858.5237 | 555.2313 | 0 | 7150 | 7236 | 0 | 24 | 47 | 1.7 | 7 | 5 | 58030 | 58002.5 | 197.5 | 57805 | 7193 | 7193 | 12.3333
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 11.72 | 0.27083 | 0.72917 | 7027 | 6909 | 6065 | 6629 | 7333 | 7348 | 128899.7597 | 555.4275 | 0 | 4748 | 4824 | 0 | 23 | 42 | 1.7 | 7 | 5 | 41311 | 41236 | 196.2 | 41039.8 | 4786 | 4786 | 11
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 11.72 | 0.25208 | 0.76528 | 10194 | 10352 | 8736 | 9904 | 10716 | 10815 | 128960.4506 | 555.6226 | 0 | 7477 | 7444 | 22 | 24 | 48 | 1.7 | 7 | 5 | 60717 | 60690.9 | 195.1 | 60495.8 | 7460.5 | 7438.5 | 12.3167
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 11.72 | 0.25556 | 0.76528 | 8769 | 8872 | 7577 | 8526 | 9216 | 9337 | 129012.5852 | 555.7923 | 0 | 6364 | 6364 | 0 | 23 | 44 | 1.7 | 13 | 4 | 52297 | 52134.6 | 169.7 | 51964.9 | 6364 | 6364 | 12.2333
2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 11.72 | 0.25278 | 0.76944 | 10635 | 10738 | 9073 | 10400 | 11159 | 11368 | 129076.1079 | 555.9754 | 0 | 7939 | 7934 | 50 | 24 | 48 | 1.7 | 13 | 0 | 63373 | 63522.7 | 183.1 | 63339.6 | 7936.5 | 7886.5 | 12.4
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 11.72 | 0.25486 | 0.76944 | 9992 | 10244 | 8857 | 9880 | 10529 | 10667 | 129136.2077 | 556.1708 | 0 | 7419 | 7376 | 0 | 24 | 48 | 5 | 8 | 0 | 60169 | 60099.8 | 195.4 | 59904.4 | 7397.5 | 7397.5 | 12.35
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 11.72 | 0.26319 | 0.76875 | 9930 | 10194 | 8721 | 9683 | 10388 | 10543 | 129195.619 | 556.3594 | 0 | 7258 | 7258 | 0 | 24 | 48 | 4 | 7 | 0 | 59459 | 59411.3 | 188.6 | 59222.7 | 7258 | 7258 | 12.1333
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 11.72 | 0.25417 | 0.76944 | 10699 | 11261 | 9288 | 10408 | 11344 | 11273 | 129259.8128 | 556.5295 | 0 | 7848 | 7848 | 0 | 24 | 48.7 | 4.7 | 7 | 0 | 64273 | 64193.8 | 170.1 | 64023.7 | 7848 | 7848 | 12.3667
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 11.72 | 0.25417 | 0.77222 | 11263 | 11550 | 9651 | 10909 | 11650 | 11781 | 129326.5797 | 556.7164 | 0 | 8324 | 8324 | 0 | 24 | 49 | 2 | 4 | 0 | 66804 | 66766.9 | 186.9 | 66580 | 8324 | 8324 | 12.4333
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 11.72 | 0.25208 | 0.77153 | 10888 | 11026 | 9360 | 10513 | 11387 | 11407 | 129391.1811 | 556.8876 | 0 | 8169 | 8169 | 65 | 24 | 53 | 2 | 7 | 0 | 64581 | 64601.4 | 171.2 | 64430.2 | 8169 | 8104 | 12.4667
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 11.72 | 0.26389 | 0.76944 | 10307 | 10487 | 8989 | 9958 | 10915 | 10777 | 129452.511 | 557.0867 | 0 | 7439 | 7439 | 0 | 24 | 48 | 3 | 5 | 0 | 61433 | 61329.9 | 199.1 | 61130.8 | 7439 | 7439 | 12.1333
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 11.72 | 0.25208 | 0.76944 | 11808 | 11770 | 9992 | 11218 | 12367 | 12344 | 129521.6781 | 557.2572 | 0 | 8610 | 8610 | 0 | 24 | 50 | 5 | 7 | 0 | 69499 | 69167.1 | 170.5 | 68996.6 | 8610 | 8610 | 12.4167
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 11.72 | 0.25208 | 0.77222 | 10860 | 11005 | 9393 | 10431 | 11458 | 11411 | 129586.2598 | 557.4544 | 0 | 7948 | 7948 | 0 | 24 | 49 | 5 | 9 | 0 | 64558 | 64581.7 | 197.2 | 64384.5 | 7948 | 7948 | 12.4833
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 11.72 | 0.25 | 0.77014 | 10288 | 10661 | 8847 | 9858 | 10826 | 10926 | 129647.6476 | 557.6249 | 0 | 7536 | 7536 | 100 | 24 | 48 | 5 | 7 | 0 | 61406 | 61387.8 | 170.5 | 61217.3 | 7536 | 7436 | 12.4833
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 11.72 | 0.25208 | 0.76736 | 9129 | 9182 | 7890 | 8689 | 9571 | 9411 | 129701.4619 | 557.8295 | 0 | 6463 | 6463 | 0 | 24 | 46 | 5 | 7 | 0 | 53872 | 53814.3 | 204.6 | 53609.7 | 6463 | 6463 | 12.3667
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 11.72 | 0.25208 | 0.75694 | 8570 | 8791 | 7523 | 8321 | 8917 | 8945 | 129752.4142 | 557.9733 | 0 | 6073 | 6073 | 0 | 23 | 46 | 5 | 8 | 0 | 51067 | 50952.3 | 143.8 | 50808.5 | 6073 | 6073 | 12.1167
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 11.72 | 0.25417 | 0.75 | 8287 | 8048 | 7109 | 7943 | 8628 | 8781 | 129800.8142 | 558.1733 | 0 | 5750 | 5750 | 0 | 23 | 44 | 6 | 9 | 0 | 48796 | 48400 | 200 | 48200 | 5750 | 5750 | 11.9
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 11.72 | 0.26042 | 0.75486 | 6606 | 6860 | 5804 | 6367 | 6985 | 6827 | 129840.7 | 558.1642 | 0 | 6262 | 6262 | 1400 | 23 | 44 | 6 | 9 | 0 | 39449 | 39885.8 | 0 | 39885.8 | 6262 | 4862 | 11.8667
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 11.72 | 0.25486 | 0.73472 | 9103 | 9463 | 7964 | 8886 | 9577 | 9472 | 129895.1238 | 558.3532 | 0 | 6549 | 6549 | 0 | 23 | 43 | 5 | 11 | 0 | 54465 | 54423.8 | 189 | 54234.8 | 6549 | 6549 | 11.5167
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 11.72 | 0.30625 | 0.76944 | 6599 | 6916 | 5895 | 6258 | 6911 | 6892 | 129934.5287 | 558.5884 | 0 | 4469 | 4469 | 0 | 23 | 43 | 7 | 11 | 0 | 39471 | 39404.9 | 235.2 | 39169.7 | 4469 | 4469 | 11.1167
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 11.72 | 0.25139 | 0.77222 | 9024 | 9310 | 7986 | 8648 | 9616 | 9482 | 129988.6933 | 558.7672 | 0 | 6637 | 6637 | 257 | 23 | 45 | 5 | 7 | 0 | 54066 | 54164.6 | 178.8 | 53985.8 | 6637 | 6380 | 12.5
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 11.72 | 0.25139 | 0.76042 | 9089 | 9207 | 7914 | 8761 | 9520 | 9454 | 130042.5715 | 558.9883 | 0 | 6887 | 6887 | 457 | 23 | 46.6 | 2.4 | 6 | 0 | 53945 | 53878.2 | 221.1 | 53657.1 | 6887 | 6430 | 12.2167
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 11.72 | 0.25208 | 0.77292 | 7538 | 7716 | 6616 | 7163 | 7831 | 7870 | 130087.3633 | 559.0772 | 0 | 5192 | 5192 | 0 | 23 | 40 | 5 | 10 | 0 | 44734 | 44791.8 | 88.9 | 44702.9 | 5192 | 5192 | 12.5
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 11.72 | 0.25208 | 0.77083 | 4542 | 4783 | 4152 | 4357 | 4672 | 4625 | 130114.4142 | 559.1264 | 0 | 4719 | 4719 | 1551 | 23 | 42 | 5 | 7 | 0 | 27131 | 27050.9 | 49.2 | 27001.7 | 4719 | 3168 | 12.45
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 11.72 | 0.24792 | 0.76528 | 6667 | 6679 | 5769 | 6318 | 6880 | 6964 | 130153.6238 | 559.3062 | 0 | 4529 | 4529 | 0 | 23 | 38 | 5 | 10 | 0 | 39277 | 39209.6 | 179.8 | 39029.8 | 4529 | 4529 | 12.4167
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 11.72 | 0.29444 | 0.69306 | 4247 | 4330 | 3801 | 3965 | 4354 | 4337 | 130178.6309 | 559.3871 | 0 | 3177 | 3211 | 460 | 23 | 36 | 2 | 6 | 0 | 25034 | 25007.1 | 80.9 | 24926.2 | 3194 | 2734 | 9.5667
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 11.72 | 0.27986 | 0.72569 | 7662 | 8183 | 5863 | 7757 | 8361 | 8328 | 130224.7168 | 559.5746 | 0 | 5757 | 5813 | 211 | 23 | 44 | 2 | 7 | 0 | 46154 | 46085.9 | 187.5 | 45898.4 | 5785 | 5574 | 10.7
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 11.72 | 0.25208 | 0.77778 | 8611 | 8431 | 7020 | 8158 | 8758 | 9112 | 130274.7408 | 559.7715 | 0 | 5835 | 5835 | 0 | 23 | 44 | 2 | 7 | 0 | 50090 | 50024 | 196.9 | 49827.1 | 5835 | 5835 | 12.6167
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 11.72 | 0.25208 | 0.77778 | 5128 | 5224 | 4605 | 4775 | 5161 | 5281 | 130304.8637 | 559.9184 | 0 | 3245 | 3245 | 0 | 23 | 31 | 2 | 8 | 0 | 30174 | 30122.9 | 146.9 | 29976 | 3245 | 3245 | 12.6167
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 11.72 | 0.24861 | 0.77708 | 6491 | 6815 | 5851 | 6141 | 6436 | 6679 | 130343.2743 | 560.1052 | 0 | 4460 | 4460 | 0 | 23 | 36 | 2 | 8 | 0 | 38413 | 38410.6 | 186.8 | 38223.8 | 4460 | 4460 | 12.6833
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 11.72 | 0.25 | 0.76736 | 4388 | 4589 | 4022 | 4116 | 4470 | 4435 | 130369.232 | 560.3017 | 0 | 3038 | 3038 | 175 | 23 | 33 | 2 | 6 | 0 | 26020 | 25957.7 | 196.5 | 25761.2 | 3038 | 2863 | 12.4167
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 11.72 | 0.24514 | 0.72986 | 4397 | 4466 | 3908 | 4107 | 4569 | 4528 | 130395.1636 | 560.4979 | 0 | 2875 | 2875 | 72 | 23 | 33 | 2 | 6 | 0 | 25975 | 25931.6 | 196.2 | 25735.4 | 2875 | 2803 | 11.6333
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 11.72 | 0.25 | 0.77014 | 2720 | 2762 | 2385 | 2693 | 2957 | 2910 | 130411.6005 | 560.6996 | 0 | 4760 | 4760 | 2803 | 23 | 32 | 2.5 | 5 | 0 | 16427 | 16436.9 | 201.7 | 16235.2 | 4760 | 1957 | 12.4833
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 11.72 | 0.26389 | 0.77431 | 0 | 0 | 0 | 0 | 5112 | 5247 | 130421.8996 | 560.805 | 0 | 3230 | 3230 | 0 | 23 | 32 | 2.5 | 5 | 0 | 10359 | 10299.1 | 105.4 | 10193.7 | 3230 | 3230 | 12.25
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 11.72 | 0.25833 | 0.77639 | 0 | 0 | 0 | 0 | 9886 | 9887 | 130441.5264 | 560.9096 | 0 | 6501 | 6501 | 0 | 23 | 37 | 2 | 6 | 0 | 19773 | 19626.8 | 104.6 | 19522.2 | 6501 | 6501 | 12.4333
2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 11.72 | 0.24444 | 0.77569 | 9800 | 9837 | 8337 | 9409 | 10797 | 10606 | 130500.3472 | 561.0396 | 0 | 8303 | 8303 | 0 | 23 | 44 | 3 | 7 | 0 | 58786 | 58820.8 | 130 | 58690.8 | 8303 | 8303 | 12.75
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 11.72 | 0.24236 | 0.77361 | 10792 | 10969 | 9393 | 10427 | 11444 | 11370 | 130564.6697 | 561.2004 | 0 | 7674 | 7676 | 0 | 24 | 41 | 3 | 7 | 0 | 64395 | 64322.5 | 160.8 | 64161.7 | 7675 | 7675 | 12.75
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 11.72 | 0.24167 | 0.77083 | 8316 | 8792 | 7648 | 8519 | 9291 | 9403 | 130616.6344 | 561.3816 | 0 | 6392 | 6416 | 174 | 23 | 41 | 3 | 8 | 0 | 51969 | 51964.7 | 181.2 | 51783.5 | 6404 | 6230 | 12.7
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 11.72 | 0.24375 | 0.77361 | 8872 | 9166 | 7861 | 8631 | 9342 | 9224 | 130669.7238 | 561.5581 | 0 | 7152 | 6953 | 656 | 24 | 42 | 2 | 7 | 0 | 53096 | 53089.4 | 176.5 | 52912.9 | 7052.5 | 6396.5 | 12.7167
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 11.72 | 0.24514 | 18:26 | 10445 | 10516 | 9034 | 10191 | 11346 | 11100 | 130732.3512 | 561.7135 | 0 | 7830 | 7873 | 623 | 23 | 39 | 2 | 7 | 0 | 62632 | 62627.4 | 155.4 | 62472 | 7851.5 | 7228.5 | 12.55
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 11.72 | 0.24792 | 18:31 | 5185 | 5348 | 4659 | 4884 | 5228 | 5308 | 130762.9352 | 561.8949 | 0 | 3373 | 3351 | 0 | 22 | 36 | 3 | 6 | 0 | 30612 | 30584 | 181.4 | 30402.6 | 3362 | 3362 | 12.5667
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 11.72 | 0.25069 | 18:34 | 6600 | 6907 | 5887 | 6560 | 7079 | 6875 | 130802.8446 | 562.0772 | 0 | 6905 | 6900 | 2084 | 23 | 39 | 2 | 5 | 0 | 39908 | 39909.4 | 182.3 | 39727.1 | 6902.5 | 4818.5 | 12.55
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 11.72 | 0.24583 | 18:37 | 8053 | 8215 | 7044 | 7651 | 8327 | 8342 | 130850.4311 | 562.2691 | 0 | 5708 | 5728 | 49 | 22 | 40 | 3 | 6 | 0 | 47632 | 47586.5 | 191.9 | 47394.6 | 5718 | 5669 | 12.7167
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 11.72 | 0.24722 | 18:35 | 8633 | 8807 | 7414 | 8239 | 9097 | 8999 | 130901.5962 | 562.4522 | 0 | 6019 | 6057 | 0 | 24 | 39 | 2 | 5 | 0 | 51189 | 51165.1 | 183.1 | 50982 | 6038 | 6038 | 12.65
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 11.72 | 0.27847 | 18:42 | 3488 | 3587 | 3118 | 3243 | 3464 | 3511 | 130921.9036 | 562.6759 | 0 | 2178 | 2208 | 0 | 23 | 29 | 8 | 11 | 0 | 20411 | 20307.4 | 223.7 | 20083.7 | 2193 | 2193 | 12.0167
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 11.72 | 0.25139 | 18:40 | 2353 | 2362 | 2106 | 2174 | 2350 | 2392 | 130935.5143 | 562.8709 | 0 | 1384 | 1377 | 0 | 23 | 26 | 9 | 13 | 0 | 13737 | 13610.7 | 195 | 13415.7 | 1380.5 | 1380.5 | 12.6333
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 11.72 | 0.29167 | 18:39 | 4727 | 4836 | 4257 | 4424 | 4784 | 4860 | 130963.3555 | 563.0662 | 0 | 3055 | 3055 | 0 | 23 | 31 | 8 | 11 | 0 | 27888 | 27841.2 | 195.3 | 27645.9 | 3055 | 3055 | 11.65
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 11.72 | 0.28125 | 18:35 | 7084 | 7338 | 6307 | 6693 | 7282 | 7321 | 131005.3457 | 563.2558 | 0 | 4709 | 4709 | 50 | 23 | 42 | 6 | 11 | 0 | 42025 | 41990.2 | 189.6 | 41800.6 | 4709 | 4659 | 11.8333
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 11.72 | 0.24861 | 18:37 | 4570 | 4735 | 4070 | 4309 | 4679 | 4701 | 131032.4136 | 563.5126 | 0 | 4165 | 3795 | 1097 | 23 | 41 | 3 | 5 | 0 | 27064 | 27067.9 | 256.8 | 26811.1 | 3980 | 2883 | 12.65
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 11.72 | 0.25208 | 18:47 | 6666 | 6951 | 5888 | 6330 | 6844 | 6909 | 131071.925 | 563.6507 | 0 | 4615 | 4615 | 0 | 23 | 41 | 3 | 6 | 0 | 39588 | 39511.4 | 138.1 | 39373.3 | 4615 | 4615 | 12.7333
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 11.72 | 0.25 | 18:18 | 3056 | 3084 | 2725 | 2865 | 3121 | 3083 | 131089.8543 | 563.8442 | 0 | 3305 | 3305 | 1253 | 23 | 32 | 3 | 7 | 0 | 17934 | 17929.3 | 193.5 | 17735.8 | 3305 | 2052 | 12.3
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 11.72 | 0.25764 | 18:06 | 4645 | 4734 | 4157 | 4425 | 4739 | 4784 | 131117.2485 | 564.0254 | 0 | 3659 | 3659 | 618 | 23 | 33 | 4 | 9 | 0 | 27484 | 27394.2 | 181.2 | 27213 | 3659 | 3041 | 11.9167
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 11.72 | 0.24861 | 18:48 | 10194 | 10275 | 8827 | 9758 | 10751 | 10709 | 131177.7047 | 564.2274 | 0 | 7144 | 7055 | 0 | 23 | 40 | 5 | 10 | 0 | 60514 | 60456.2 | 202 | 60254.2 | 7099.5 | 7099.5 | 12.8333
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 11.72 | 0.24444 | 18:35 | 6874 | 6990 | 6089 | 6634 | 7255 | 6840 | 131218.4703 | 564.4235 | 0 | 5835 | 5850 | 1123 | 23 | 38 | 5 | 10 | 0 | 40682 | 40765.6 | 196.1 | 40569.5 | 5842.5 | 4719.5 | 12.7167
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 11.72 | 0.24861 | 18:30 | 689 | 673 | 599 | 682 | 746 | 760 | 131222.6347 | 564.6162 | 0 | 5323 | 5323 | 4833 | 23 | 40 | 5 | 9 | 0 | 4149 | 4164.4 | 192.7 | 3971.7 | 5323 | 490 | 12.5333
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 11.72 | 0.25139 | 18:38 | 7548 | 8679 | 7363 | 7892 | 8458 | 8504 | 131271.0004 | 564.8221 | 0 | 5635 | 5635 | 0 | 23 | 40 | 5 | 9 | 0 | 48444 | 48365.7 | 205.9 | 48159.8 | 5635 | 5635 | 12.6
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 11.72 | 0.25069 | 18:38 | 10663 | 11293 | 9597 | 10359 | 11119 | 10991 | 131334.9685 | 565.0091 | 0 | 7485 | 7485 | 0 | 23 | 40 | 5 | 9 | 0 | 64022 | 63968.1 | 187 | 63781.1 | 7485 | 7485 | 12.6167
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 11.72 | 0.24653 | 18:35 | 9675 | 10497 | 8941 | 9548 | 10142 | 10301 | 131394.0284 | 565.1946 | 0 | 6933 | 6933 | 0 | 23 | 40 | 5 | 12 | 0 | 59104 | 59059.9 | 185.5 | 58874.4 | 6933 | 6933 | 12.6667
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 11.72 | 0.24792 | 18:30 | 7336 | 7546 | 6625 | 7011 | 7477 | 7606 | 131437.5608 | 565.38 | 0 | 4910 | 4865 | 0 | 23 | 35.5 | 6 | 11 | 0 | 43601 | 43532.4 | 185.4 | 43347 | 4887.5 | 4887.5 | 12.55
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 11.72 | 0.25347 | 18:30 | 6483 | 6778 | 5859 | 6142 | 6572 | 6646 | 131476.0355 | 565.5836 | 0 | 4114 | 4114 | 0 | 23 | 35 | 6 | 11 | 0 | 38480 | 38474.7 | 203.6 | 38271.1 | 4114 | 4114 | 12.4167
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 11.72 | 0.25417 | 18:40 | 7173 | 7290 | 6365 | 6760 | 7350 | 7310 | 131518.2003 | 565.7878 | 0 | 4854 | 4798 | 0 | 23 | 36 | 4 | 8 | 0 | 42248 | 42164.8 | 204.2 | 41960.6 | 4826 | 4826 | 12.5667
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 11.72 | 0.25694 | 18:45 | 5881 | 6003 | 5235 | 5531 | 5952 | 6048 | 131552.8577 | 565.9455 | 0 | 3733 | 3723 | 0 | 23 | 33.5 | 4 | 8 | 0 | 34650 | 34657.4 | 157.7 | 34499.7 | 3728 | 3728 | 12.5833
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 11.72 | 0.25139 | 18:48 | 9192 | 9439 | 7982 | 8754 | 9446 | 9445 | 131607.0775 | 566.1472 | 0 | 6419 | 6314 | 0 | 24 | 39 | 4 | 8 | 0 | 54258 | 54219.8 | 201.7 | 54018.1 | 6366.5 | 6366.5 | 12.7667
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 11.72 | 0.25139 | 18:50 | 8424 | 8524 | 7414 | 7990 | 8708 | 8694 | 131656.775 | 566.3394 | 0 | 5742 | 5748 | 0 | 24 | 39 | 4 | 9 | 0 | 49754 | 49697.5 | 192.2 | 49505.3 | 5745 | 5745 | 12.8
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 11.72 | 0.24931 | 18:38 | 6164 | 6282 | 5521 | 5882 | 6218 | 6359 | 131693.1772 | 566.5522 | 0 | 4065 | 4010 | 0 | 23 | 32 | 5 | 9 | 0 | 36426 | 36402.2 | 212.8 | 36189.4 | 4037.5 | 4037.5 | 12.65
2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 11.72 | 0.26111 | 17:52 | 5421 | 5775 | 5104 | 5334 | 5719 | 5864 | 131726.3588 | 566.6838 | 0 | 3544 | 3528 | 0 | 23 | 33 | 4 | 9 | 0 | 33217 | 33181.6 | 131.6 | 33050 | 3536 | 3536 | 11.6
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 11.72 | 0.25833 | 18:30 | 3989 | 4130 | 3648 | 3721 | 3983 | 4027 | 131749.8483 | 566.8535 | 0 | 2923 | 2896 | 506 | 23 | 30 | 4 | 10 | 0 | 23498 | 23489.5 | 169.7 | 23319.8 | 2909.5 | 2403.5 | 12.3
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 11.72 | 0.26319 | 18:48 | 3170 | 3277 | 2894 | 2948 | 3208 | 3233 | 131768.5233 | 567.0406 | 0 | 1862 | 1875 | 0 | 23 | 27.8 | 4 | 7 | 0 | 18730 | 18675 | 187.1 | 18487.9 | 1868.5 | 1868.5 | 12.4833
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 11.72 | 0.25764 | 18:35 | 4873 | 4991 | 4406 | 4502 | 4855 | 4955 | 131797.0451 | 567.2201 | 0 | 2941 | 2931 | 0 | 23 | 31 | 4 | 8 | 0 | 28582 | 28521.8 | 179.5 | 28342.3 | 2936 | 2936 | 12.4
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 11.72 | 0.25347 | 18:33 | 7804 | 7958 | 7034 | 7349 | 8022 | 8164 | 131843.3236 | 567.4015 | 0 | 5254 | 5232 | 0 | 23 | 36 | 4.7 | 8 | 0 | 46331 | 46278.5 | 181.4 | 46097.1 | 5243 | 5243 | 12.4667
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 11.72 | 0.24931 | 18:40 | 8113 | 8539 | 7492 | 7853 | 8493 | 8655 | 131892.4006 | 567.5576 | 0 | 5536 | 5525 | 0 | 23 | 35 | 5 | 10 | 0 | 49145 | 49077 | 156.1 | 48920.9 | 5530.5 | 5530.5 | 12.6833
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 11.72 | 0.26042 | 18:40 | 8647 | 8894 | 7737 | 8141 | 8827 | 8866 | 131943.495 | 567.7322 | 0 | 5840 | 5755 | 0 | 23 | 36.5 | 5 | 10 | 0 | 51112 | 51094.4 | 174.6 | 50919.8 | 5797.5 | 5797.5 | 12.4167
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 11.72 | 0.25972 | 18:45 | 3732 | 3830 | 3398 | 3438 | 3702 | 3791 | 131965.3424 | 567.9085 | 0 | 2200 | 2201 | 0 | 23 | 29 | 4 | 6 | 0 | 21891 | 21847.4 | 176.3 | 21671.1 | 2200.5 | 2200.5 | 12.5167
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 11.72 | 0.25833 | 18:42 | 5478 | 5576 | 4900 | 5073 | 5422 | 5579 | 131997.3291 | 568.0877 | 0 | 3411 | 3356 | 0 | 23 | 31 | 4 | 8 | 0 | 32028 | 31986.7 | 179.2 | 31807.5 | 3383.5 | 3383.5 | 12.5
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 11.72 | 0.25903 | 18:32 | 6013 | 6047 | 5330 | 5629 | 5965 | 6127 | 132032.3815 | 568.2673 | 0 | 3799 | 3762 | 0 | 23 | 32 | 3 | 7 | 0 | 35111 | 35052.4 | 179.6 | 34872.8 | 3780.5 | 3780.5 | 12.3167
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 11.72 | 0.25417 | 18:53 | 8009 | 8107 | 7093 | 7605 | 8216 | 8275 | 132079.6616 | 568.4404 | 0 | 5343 | 5362 | 0 | 23 | 36 | 2 | 5 | 0 | 47305 | 47280.1 | 173.1 | 47107 | 5352.5 | 5352.5 | 12.7833
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 11.72 | 0.25486 | 18:40 | 8881 | 8919 | 7786 | 8452 | 9361 | 9374 | 132132.4667 | 568.62 | 0 | 6075 | 6243 | 0 | 24 | 39 | 2 | 6 | 0 | 52773 | 52805.1 | 179.6 | 52625.5 | 6159 | 6159 | 12.55
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 11.72 | 0.25417 | 18:50 | 9247 | 9347 | 8118 | 8901 | 9723 | 9726 | 132187.5081 | 568.6378 | 0 | 6621 | 6567 | 0 | 24 | 39 | 3 | 6 | 0 | 55062 | 55041.4 | 17.8 | 55023.6 | 6594 | 6594 | 12.7333
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 11.72 | 0.25208 | 18:46 | 8883 | 9026 | 7836 | 8441 | 9121 | 9203 | 132240.009 | 568.8461 | 0 | 6142 | 6075 | 0 | 24 | 38 | 3 | 6 | 0 | 52510 | 52500.9 | 208.3 | 52292.6 | 6108.5 | 6108.5 | 12.7167
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 11.72 | 0.25208 | 18:48 | 9526 | 9633 | 8376 | 9122 | 9826 | 10047 | 132296.4928 | 569.0218 | 0 | 6744 | 6778 | 0 | 24 | 37 | 3 | 7 | 0 | 56530 | 56483.8 | 175.7 | 56308.1 | 6761 | 6761 | 12.75
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 11.72 | 0.25764 | 18:53 | 6868 | 7127 | 6151 | 6629 | 7008 | 7198 | 132337.3938 | 569.1943 | 0 | 4757 | 4675 | 114 | 24 | 36 | 3 | 7 | 0 | 40981 | 40901 | 172.5 | 40728.5 | 4716 | 4602 | 12.7
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 11.72 | 0.25347 | 18:24 | 8126 | 8353 | 7397 | 7802 | 8305 | 8427 | 132385.7834 | 569.3688 | 0 | 5546 | 5486 | 0 | 24 | 38 | 2 | 5 | 0 | 48410 | 48389.6 | 174.5 | 48215.1 | 5516 | 5516 | 12.3167
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 11.72 | 0.25833 | 18:42 | 7486 | 7530 | 6719 | 7033 | 7660 | 7720 | 132429.8647 | 569.5463 | 0 | 4893 | 4893 | 0 | 23 | 37 | 2 | 6 | 0 | 44148 | 44081.3 | 177.5 | 43903.8 | 4893 | 4893 | 12.5
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 11.72 | 0.25694 | 17:11 | 6643 | 6768 | 6008 | 6266 | 6842 | 6840 | 132469.1695 | 569.7468 | 0 | 4381 | 4381 | 0 | 23 | 38 | 2 | 7 | 0 | 39367 | 39304.8 | 200.5 | 39104.3 | 4381 | 4381 | 11.0167
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 11.72 | 0.25694 | 18:40 | 5134 | 5019 | 4488 | 4780 | 5503 | 5541 | 132499.5805 | 569.9405 | 0 | 3827 | 3905 | 516 | 23 | 33 | 2 | 5 | 0 | 30465 | 30411 | 193.7 | 30217.3 | 3866 | 3350 | 12.5
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 11.72 | 0.25972 | 18:43 | 9429 | 9739 | 8458 | 9083 | 9794 | 9830 | 132555.9572 | 570.1247 | 0 | 6677 | 6687 | 125 | 23 | 41 | 2 | 5 | 0 | 56333 | 56376.7 | 184.2 | 56192.5 | 6682 | 6615 | 12.4833
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 11.72 | 0.25625 | 17:11 | 8343 | 8483 | 7412 | 7908 | 8463 | 8554 | 132605.0422 | 570.292 | 0 | 5545 | 5549 | 0 | 23 | 39 | 2 | 5.8 | 0 | 49163 | 49085 | 167.3 | 48917.7 | 5547 | 6615 | 11.0333
2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 11.72 | 0.25694 | 18:50 | 6202 | 6936 | 5970 | 6496 | 6896 | 7092 | 132644.55 | 570.4661 | 0 | 4534 | 4534 | 0 | 23 | 34 | 2.8 | 7 | 0 | 39592 | 39507.8 | 174.1 | 39333.7 | 4534 | 6615 | 12.6667
Formulas:
Days = DAY(EOMONTH(Raw_Data[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | Bugt Capacity | CC*Bugt | Capacity | 11.72
1 | April | 4 | 2022-04-01 | 2022 | FY23 | 30 | 187.8683 | 228.5601 |  | 23.0578 |  | 1844.1036 | 11.72 | 68.84% | 7.6187 | 0 | 0 | 0 | 61.4701 | 0 | 0 | 21.85% | [7 empty] | 99.5% | 98.55% | 99.5%
2 | May | 5 | 2022-05-01 | 2022 | FY23 | 31 | 194.1311 | 236.9548 |  | 24.8039 |  | 1900.095 | 11.72 | 68.42% | 7.6437 | 0 | 0 | 0 | 61.2934 | 0 | 0 | 21.79% | [7 empty] | 99.5% | 98.55% | 99.5%
3 | June | 6 | 2022-06-01 | 2022 | FY23 | 30 | 144.3275 | 168.5181 |  | 20.9133 |  | 1378.1107 | 11.72 | 69.78% | 5.6173 | 0 | 0 | 0 | 45.937 | 0 | 0 | 16.33% | [7 empty] | 99.5% | 98.55% | 99.5%
4 | July | 7 | 2022-07-01 | 2022 | FY23 | 31 | 124.8107 | 143.4349 |  | 20.3913 |  | 1181.2377 | 11.72 | 70.27% | 4.6269 | 0 | 0 | 0 | 38.1044 | 0 | 0 | 13.55% | [7 empty] | 99.5% | 98.55% | 99.5%
5 | August | 8 | 2022-08-01 | 2022 | FY23 | 31 | 129.0323 | 147.9127 |  | 19.6866 |  | 1220.9736 | 11.72 | 70.43% | 4.7714 | 0 | 0 | 0 | 39.3862 | 0 | 0 | 14% | [7 empty] | 99.5% | 98.55% | 99.5%
6 | September | 9 | 2022-09-01 | 2022 | FY23 | 30 | 138.8604 | 165.1488 |  | 18.9303 |  | 1365.4675 | 11.72 | 70.55% | 5.505 | 0 | 0 | 0 | 45.5156 | 0 | 0 | 16.18% | [7 empty] | 99.5% | 98.55% | 99.5%
7 | October | 10 | 2022-10-01 | 2022 | FY23 | 31 | 144.2789 | 175.0139 |  | 19.6606 |  | 1449.4546 | 11.72 | 70.67% | 5.6456 | 0 | 0 | 0 | 46.7566 | 0 | 0 | 16.62% | [7 empty] | 99.5% | 98.55% | 99.5%
8 | November | 11 | 2022-11-01 | 2022 | FY23 | 30 | 136.8868 | 168.812 |  | 17.558 |  | 1413.3311 | 11.72 | 71.44% | 5.6271 | 0 | 0 | 0 | 47.111 | 0 | 0 | 16.75% | [7 empty] | 99.5% | 98.55% | 99.5%
9 | December | 12 | 2022-12-01 | 2022 | FY23 | 31 | 132.7428 | 164.9346 |  | 17.1964 |  | 1388.0447 | 11.72 | 71.81% | 5.3205 | 0 | 0 | 0 | 44.7756 | 0 | 0 | 15.92% | [7 empty] | 99.5% | 98.55% | 99.5%
10 | January | 1 | 2023-01-01 | 2023 | FY23 | 31 | 147.1786 | 186.5454 |  | 17.4299 |  | 1560.5343 | 11.72 | 71.38% | 6.0176 | 0 | 0 | 0 | 50.3398 | 0 | 0 | 17.9% | [7 empty] | 99.5% | 98.55% | 99.5%
11 | February | 2 | 2023-02-01 | 2023 | FY23 | 28 | 153.8357 | 193.2304 |  | 17.7717 |  | 1599.367 | 11.72 | 70.62% | 6.9011 | 0 | 0 | 0 | 57.1203 | 0 | 0 | 20.31% | [7 empty] | 99.5% | 98.55% | 99.5%
12 | March | 3 | 2023-03-01 | 2023 | FY23 | 31 | 191.2409 | 239.2148 |  | 22.1564 |  | 1945.2493 | 11.72 | 69.38% | 7.7166 | 0 | 0 | 0 | 62.75 | 0 | 0 | 22.31% | [7 empty] | 99.5% | 98.55% | 99.5%
13 | April | 4 | 2023-04-01 | 2023 | FY24 | 30 | 187.8683 | 228.5601 |  | 23.0578 |  | 1780 | 11.72 | 66.45% | 7.6187 | 0 | 0 | 0 | 59.3333 | 0 | 0 | 21.09% | [7 empty] | 99.5% | 98.55% | 99.5%
14 | May | 5 | 2023-05-01 | 2023 | FY24 | 31 | 194.1311 | 236.9548 |  | 24.8039 |  | 1900 | 11.72 | 68.42% | 7.6437 | 0 | 0 | 0 | 61.2903 | 0 | 0 | 21.79% | [7 empty] | 99.5% | 98.55% | 99.5%
15 | June | 6 | 2023-06-01 | 2023 | FY24 | 30 | 144.3275 | 168.5181 |  | 20.9133 |  | 1330 | 11.72 | 67.34% | 5.6173 | 0 | 0 | 0 | 44.3333 | 0 | 0 | 15.76% | [7 empty] | 99.5% | 98.55% | 99.5%
16 | July | 7 | 2023-07-01 | 2023 | FY24 | 31 | 124.8107 | 143.4349 |  | 20.3913 |  | 1180 | 11.72 | 70.19% | 4.6269 | 0 | 0 | 0 | 38.0645 | 0 | 0 | 13.53% | [7 empty] | 99.5% | 98.55% | 99.5%
17 | August | 8 | 2023-08-01 | 2025 | FY24 | 31 | 129.0323 | 147.9127 |  | 19.6866 |  | 1220 | 11.72 | 70.38% | 4.7714 | 0 | 0 | 0 | 39.3548 | 0 | 0 | 13.99% | [7 empty] | 99.5% | 98.55% | 99.5%
18 | September | 9 | 2023-09-01 | 2025 | FY24 | 30 | 138.8604 | 165.1488 |  | 18.9303 |  | 1320 | 11.72 | 68.2% | 5.505 | 0 | 0 | 0 | 44 | 0 | 0 | 15.64% | [7 empty] | 99.5% | 98.55% | 99.5%
19 | October | 10 | 2023-10-01 | 2025 | FY24 | 31 | 144.2789 | 175.0139 |  | 19.6606 |  | 1720 | 11.72 | 83.85% | 5.6456 | 0 | 0 | 0 | 55.4839 | 0 | 0 | 19.73% | [7 empty] | 99.5% | 98.55% | 99.5%
20 | November | 11 | 2023-11-01 | 2025 | FY24 | 30 | 136.8868 | 168.812 |  | 17.558 |  | 1630 | 11.72 | 82.39% | 5.6271 | 0 | 0 | 0 | 54.3333 | 0 | 0 | 19.32% | [7 empty] | 99.5% | 98.55% | 99.5%
21 | December | 12 | 2023-12-01 | 2025 | FY24 | 31 | 132.7428 | 164.9346 |  | 17.1964 |  | 1650 | 11.72 | 85.36% | 5.3205 | 0 | 0 | 0 | 53.2258 | 0 | 0 | 18.92% | [7 empty] | 99.5% | 98.55% | 99.5%
22 | January | 1 | 2024-01-01 | 2025 | FY24 | 31 | 147.1786 | 186.5454 |  | 17.4299 |  | 1860 | 11.72 | 85.07% | 6.0176 | 0 | 0 | 0 | 60 | 0 | 0 | 21.33% | [7 empty] | 99.5% | 98.55% | 99.5%
23 | February | 2 | 2024-02-01 | 2025 | FY24 | 29 | 153.8357 | 193.2304 |  | 17.7717 |  | 1780 | 11.72 | 78.6% | 6.6631 | 0 | 0 | 0 | 61.3793 | 0 | 0 | 21.82% | [7 empty] | 99.5% | 98.55% | 99.5%
24 | March | 3 | 2024-03-01 | 2025 | FY24 | 31 | 191.2409 | 239.2148 |  | 22.1564 |  | 2310 | 11.72 | 82.39% | 7.7166 | 0 | 0 | 0 | 74.5161 | 0 | 0 | 26.49% | [7 empty] | 99.5% | 98.55% | 99.5%
25 | April | 4 | 2024-04-01 | 2025 | FY25 | 30 | 187.8683 | 228.5601 |  | 23.0578 |  | 1769 | 11.72 | 66.04% | 7.6187 | 0 | 0 | 0 | 58.9667 | 0 | 0 | 20.96% | [7 empty] | 99.5% | 98.55% | 99.5%
26 | May | 5 | 2024-05-01 | 2026 | FY25 | 31 | 194.1311 | 236.9548 |  | 24.8039 |  | 1888 | 11.72 | 67.98% | 7.6437 | 0 | 0 | 0 | 60.9032 | 0 | 0 | 21.65% | [7 empty] | 99.5% | 98.55% | 99.5%
27 | June | 6 | 2024-06-01 | 2026 | FY25 | 30 | 144.3275 | 168.5181 |  | 20.9133 |  | 1321.8 | 11.72 | 66.93% | 5.6173 | 0 | 0 | 0 | 44.06 | 0 | 0 | 15.66% | [7 empty] | 99.5% | 98.55% | 99.5%
28 | July | 7 | 2024-07-01 | 2026 | FY25 | 31 | 124.8107 | 143.4349 |  | 20.3913 |  | 1172.6 | 11.72 | 69.75% | 4.6269 | 0 | 0 | 23.1498 | 37.8258 | 0 | 222.4161 | 13.45% | [7 empty] | 99.5% | 98.55% | 99.5%
29 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 | 129.0323 | 147.9127 |  | 19.6866 |  | 1212.3 | 11.72 | 69.93% | 4.7714 | 0 | 0 | 0 | 39.1065 | 0 | 0 | 13.9% | [7 empty] | 99.5% | 98.55% | 99.5%
30 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 | 138.8604 | 165.1488 |  | 18.9303 |  | 1311.9 | 11.72 | 67.78% | 5.505 | 0 | 0 | 0 | 43.73 | 0 | 0 | 15.55% | [7 empty] | 99.5% | 98.55% | 99.5%
31 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 | 144.2789 | 175.0139 |  | 19.6606 |  | 1712 | 11.72 | 83.46% | 5.6456 | 0 | 0 | 0 | 55.2258 | 0 | 0 | 19.63% | [7 empty] | 99.5% | 98.55% | 99.5%
32 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 | 136.8868 | 168.812 |  | 17.558 |  | 1618.4 | 11.72 | 81.8% | 5.6271 | 0 | 0 | 0 | 53.9467 | 0 | 0 | 19.18% | [7 empty] | 99.5% | 98.55% | 99.5%
33 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 | 132.7428 | 164.9346 |  | 17.1964 |  | 1641.6 | 11.72 | 84.92% | 5.3205 | 0 | 0 | 23.1498 | 52.9548 | 0 | 222.4161 | 18.83% | [7 empty] | 99.5% | 98.55% | 99.5%
34 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 | 147.1786 | 186.5454 |  | 17.4299 |  | 1841 | 11.72 | 84.21% | 6.0176 | 0 | 0 | 0 | 59.3871 | 0 | 0 | 21.11% | [7 empty] | 99.5% | 98.55% | 99.5%
35 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 | 153.8357 | 193.2304 |  | 17.7717 |  | 1760 | 11.72 | 77.72% | 6.9011 | 0 | 0 | 0 | 62.8571 | 0 | 0 | 22.35% | [7 empty] | 99.5% | 98.55% | 99.5%
36 | March | 3 | 2025-03-01 | 2025 | FY25 | 31 | 191.2409 | 239.2148 |  | 22.1564 |  | 2298.3 | 11.72 | 81.98% | 7.7166 | 3 | 23.1498 | 23.1498 | 74.1387 | 222.4161 | 222.4161 | 26.36% | 26.36% | 26.36% | 11.72 | 11.72 |  |  |  | 99.5% | 98.55% | 99.5%
37 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 | 187.8683 | 228.5601 |  | 23.0578 |  | 1903.6714 | 11.72 | 71.07% | 7.6187 | 30 | 228.5601 | 228.5601 | 63.4557 | 1903.6714 | 1903.6714 | 22.56% | 22.56% | 22.56% | 11.72 | 11.72 |  |  |  | 99.5% | 98.55% | 99.5%
38 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 | 194.1311 | 236.9548 |  | 24.8039 |  | 2031.6833 | 11.72 | 73.16% | 7.6437 | 31 | 236.9548 | 465.5149 | 65.5382 | 2031.6833 | 3935.3547 | 23.3% | 23.3% | 22.94% | 11.72 | 11.72 |  |  |  | 99.5% | 98.55% | 99.5%
39 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 | 144.3275 | 168.5181 |  | 20.9133 |  | 1422.4062 | 11.72 | 72.02% | 5.6173 | 30 | 168.5181 | 634.033 | 47.4135 | 1422.4062 | 5357.7609 | 16.86% | 16.86% | 20.93% | 11.72 | 11.72 |  |  |  | 99.5% | 98.55% | 99.5%
40 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 | 124.8107 | 143.4349 |  | 20.3913 |  | 1261.7823 | 11.72 | 75.06% | 4.6269 | 22 | 101.7925 | 735.8255 | 40.7027 | 895.4584 | 6253.2193 | 14.47% | 14.47% | 19.67% | 11.72 | 11.72 |  |  |  | 99.5% | 98.55% | 99.5%
41 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 | 129.0323 | 147.9127 |  | 19.6866 |  | 1304.5546 | 11.72 | 75.25% | 4.7714 | 0 | 0 | 735.8255 | 42.0824 | 0 | 6253.2193 | 14.96% |  | 19.67% |  | 11.72 |  |  |  | 99.5% | 98.55% | 99.5%
42 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 | 138.8604 | 165.1488 |  | 18.9303 |  | 1411.7114 | 11.72 | 72.94% | 5.505 | 0 | 0 | 735.8255 | 47.057 | 0 | 6253.2193 | 16.73% |  | 19.67% |  | 11.72 |  |  |  | 99.5% | 98.55% | 99.5%
43 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 | 144.2789 | 175.0139 |  | 19.6606 |  | 1561.1882 | 11.72 | 76.11% | 5.6456 | 0 | 0 | 735.8255 | 50.3609 | 0 | 6253.2193 | 17.9% |  | 19.67% |  | 11.72 |  |  |  | 99.5% | 98.55% | 99.5%
44 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 | 136.8868 | 168.812 |  | 17.558 |  | 1475.8801 | 11.72 | 74.6% | 5.6271 | 0 | 0 | 735.8255 | 49.196 | 0 | 6253.2193 | 17.49% |  | 19.67% |  | 11.72 |  |  |  | 99.5% | 98.55% | 99.5%
45 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 | 132.7428 | 164.9346 |  | 17.1964 |  | 1497.0298 | 11.72 | 77.44% | 5.3205 | 0 | 0 | 735.8255 | 48.2913 | 0 | 6253.2193 | 17.17% |  | 19.67% |  | 11.72 |  |  |  | 99.5% | 98.55% | 99.5%
46 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 | 147.1786 | 186.5454 |  | 17.4299 |  | 1678.812 | 11.72 | 76.79% | 6.0176 | 0 | 0 | 735.8255 | 54.1552 | 0 | 6253.2193 | 19.25% |  | 19.67% |  | 11.72 |  |  |  | 99.5% | 98.55% | 99.5%
47 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 | 153.8357 | 193.2304 |  | 17.7717 |  | 1604.9607 | 11.72 | 70.87% | 6.9011 | 0 | 0 | 735.8255 | 57.32 | 0 | 6253.2193 | 20.38% |  | 19.67% |  | 11.72 |  |  |  | 99.5% | 98.55% | 99.5%
48 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 | 191.2409 | 239.2148 |  | 22.1564 |  | 2095.8418 | 11.72 | 74.76% | 7.7166 | 0 | 0 | 735.8255 | 67.6078 | 0 | 6253.2193 | 24.04% |  | 19.67% |  | 11.72 |  |  |  | 99.5% | 98.55% | 99.5%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## Inv_SY
[9 empty] | 1987.725 | 2031.205 | 1806.68 | 1844.725 | 2020.105 | 2020
Finacial Year | Start Month | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Plant DC Capcity (MW) | IC1_Inv1 | IC1_Inv2 | IC1_Inv3 | IC1_Inv4 | IC2_Inv1 | IC2_Inv2 | Avg. SY | Max. SY
2025 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 11.72 | 4.2833 | 4.2093 | 4.2066 | 4.3882 | 4.2765 | 4.2624 | 4.271 | 4.3882
2025 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 11.72 | 4.5555 | 4.4978 | 4.5442 | 4.6966 | 4.6215 | 4.5777 | 4.5822 | 4.6966
2025 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 11.72 | 4.724 | 4.7208 | 4.7158 | 4.8739 | 4.8126 | 4.7762 | 4.7706 | 4.8739
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 11.72 | 4.5187 | 4.5594 | 4.573 | 4.6923 | 4.7032 | 4.5901 | 4.6061 | 4.7032
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 11.72 | 5.3051 | 5.3993 | 5.5007 | 5.6756 | 5.6438 | 5.504 | 5.5047 | 5.6756
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 11.72 | 3.018 | 3.0012 | 3.0382 | 3.0828 | 3.0964 | 3.1069 | 3.0573 | 3.1069
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 11.72 | 5.4887 | 5.515 | 5.5411 | 5.7033 | 5.7596 | 5.695 | 5.6171 | 5.7596
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 11.72 | 4.9277 | 4.7912 | 4.8238 | 4.9818 | 5.0022 | 4.9866 | 4.9189 | 5.0022
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 11.72 | 5.1657 | 5.2265 | 5.1453 | 5.3818 | 5.3517 | 5.3361 | 5.2679 | 5.3818
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 11.72 | 5.0228 | 4.9621 | 4.981 | 5.2024 | 5.1606 | 5.1787 | 5.0846 | 5.2024
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 11.72 | 4.4367 | 4.4176 | 4.4535 | 4.6565 | 4.5255 | 4.5802 | 4.5117 | 4.6565
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 11.72 | 4.4397 | 4.42 | 4.5049 | 4.6419 | 4.5379 | 4.5104 | 4.5091 | 4.6419
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 11.72 | 4.3477 | 4.3334 | 4.4064 | 4.5351 | 4.4384 | 4.4752 | 4.4227 | 4.5351
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 11.72 | 5.0882 | 5.0748 | 5.2156 | 5.4084 | 5.3948 | 5.3411 | 5.2538 | 5.4084
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 11.72 | 5.1798 | 5.1664 | 5.1941 | 5.3997 | 5.3433 | 5.3762 | 5.2766 | 5.3997
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 11.72 | 4.9162 | 4.9837 | 4.9489 | 5.1374 | 5.0987 | 5.1351 | 5.0367 | 5.1374
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 11.72 | 5.3292 | 5.3077 | 5.302 | 5.4637 | 5.3735 | 5.4272 | 5.3672 | 5.4637
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 11.72 | 5.1642 | 5.1408 | 5.1238 | 5.2924 | 5.2562 | 5.304 | 5.2135 | 5.304
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 11.72 | 4.5157 | 4.4968 | 4.5276 | 4.6853 | 4.674 | 4.6307 | 4.5884 | 4.6853
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 11.72 | 4.9705 | 4.9389 | 4.9289 | 5.1168 | 5.1611 | 5.1134 | 5.0383 | 5.1611
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 11.72 | 3.2188 | 3.2183 | 3.2258 | 3.3447 | 3.4028 | 3.355 | 3.2942 | 3.4028
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 11.72 | 4.5685 | 4.5618 | 4.4485 | 4.7053 | 4.7384 | 4.7119 | 4.6224 | 4.7384
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 11.72 | 5.3202 | 5.2845 | 5.1376 | 5.5423 | 5.6155 | 5.5604 | 5.4101 | 5.6155
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 11.72 | 5.14 | 5.094 | 5.012 | 5.3515 | 5.3958 | 5.3762 | 5.2282 | 5.3958
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 11.72 | 4.1379 | 4.2349 | 4.2127 | 4.3069 | 4.2523 | 4.1911 | 4.2226 | 4.3069
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 11.72 | 4.6214 | 4.5283 | 4.4728 | 4.7508 | 4.8072 | 4.8327 | 4.6689 | 4.8327
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 11.72 | 4.558 | 4.6514 | 4.4662 | 4.7259 | 4.7369 | 4.7391 | 4.6463 | 4.7391
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 11.72 | 3.9502 | 4.0094 | 3.8485 | 4.0976 | 4.1419 | 4.1124 | 4.0267 | 4.1419
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 11.72 | 4.9162 | 4.8661 | 4.6428 | 5.1119 | 5.0458 | 5.1302 | 4.9521 | 5.1302
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 11.72 | 3.5352 | 3.4014 | 3.357 | 3.5935 | 3.63 | 3.6376 | 3.5258 | 3.6376
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 11.72 | 5.1285 | 5.0965 | 4.8354 | 5.3688 | 5.3047 | 5.354 | 5.1813 | 5.3688
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 11.72 | 4.4116 | 4.3679 | 4.1939 | 4.6218 | 4.5621 | 4.6223 | 4.4633 | 4.6223
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 11.72 | 5.3503 | 5.2865 | 5.0219 | 5.6377 | 5.524 | 5.6277 | 5.408 | 5.6377
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 11.72 | 5.0269 | 5.0433 | 4.9024 | 5.3558 | 5.2121 | 5.2807 | 5.1369 | 5.3558
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 11.72 | 4.9957 | 5.0187 | 4.8271 | 5.249 | 5.1423 | 5.2193 | 5.0753 | 5.249
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 11.72 | 5.3825 | 5.544 | 5.1409 | 5.642 | 5.6155 | 5.5807 | 5.4843 | 5.642
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 11.72 | 5.6663 | 5.6863 | 5.3418 | 5.9136 | 5.767 | 5.8322 | 5.7012 | 5.9136
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 11.72 | 5.4776 | 5.4283 | 5.1808 | 5.699 | 5.6368 | 5.647 | 5.5116 | 5.699
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 11.72 | 5.1853 | 5.1629 | 4.9754 | 5.3981 | 5.4032 | 5.3351 | 5.2434 | 5.4032
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 11.72 | 5.9405 | 5.7946 | 5.5306 | 6.0811 | 6.122 | 6.1109 | 5.9299 | 6.122
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 11.72 | 5.4635 | 5.418 | 5.199 | 5.6545 | 5.672 | 5.649 | 5.5093 | 5.672
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 11.72 | 5.1758 | 5.2486 | 4.8968 | 5.3439 | 5.3591 | 5.4089 | 5.2389 | 5.4089
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 11.72 | 4.5927 | 4.5205 | 4.3671 | 4.7102 | 4.7379 | 4.6589 | 4.5979 | 4.7379
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 11.72 | 4.3115 | 4.328 | 4.164 | 4.5107 | 4.4141 | 4.4282 | 4.3594 | 4.5107
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 11.72 | 4.1691 | 3.9622 | 3.9348 | 4.3058 | 4.2711 | 4.347 | 4.165 | 4.347
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 11.72 | 3.3234 | 3.3773 | 3.2125 | 3.4515 | 3.4577 | 3.3797 | 3.367 | 3.4577
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 11.72 | 4.5796 | 4.6588 | 4.4081 | 4.817 | 4.7408 | 4.6891 | 4.6489 | 4.817
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 11.72 | 3.3199 | 3.4049 | 3.2629 | 3.3924 | 3.4211 | 3.4119 | 3.3688 | 3.4211
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 11.72 | 4.5399 | 4.5835 | 4.4203 | 4.688 | 4.7601 | 4.6941 | 4.6143 | 4.7601
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 11.72 | 4.5726 | 4.5328 | 4.3804 | 4.7492 | 4.7126 | 4.6802 | 4.6046 | 4.7492
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 11.72 | 3.7923 | 3.7987 | 3.662 | 3.883 | 3.8765 | 3.896 | 3.8181 | 3.896
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 11.72 | 2.285 | 2.3548 | 2.2981 | 2.3619 | 2.3128 | 2.2896 | 2.317 | 2.3619
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 11.72 | 3.3541 | 3.2882 | 3.1931 | 3.4249 | 3.4058 | 3.4475 | 3.3523 | 3.4475
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 11.72 | 2.1366 | 2.1317 | 2.1039 | 2.1494 | 2.1553 | 2.147 | 2.1373 | 2.1553
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 11.72 | 3.8547 | 4.0286 | 3.2452 | 4.205 | 4.1389 | 4.1228 | 3.9325 | 4.205
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 11.72 | 4.3321 | 4.1507 | 3.8856 | 4.4223 | 4.3354 | 4.5109 | 4.2728 | 4.5109
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 11.72 | 2.5798 | 2.5719 | 2.5489 | 2.5885 | 2.5548 | 2.6144 | 2.5764 | 2.6144
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 11.72 | 3.2655 | 3.3552 | 3.2385 | 3.329 | 3.186 | 3.3064 | 3.2801 | 3.3552
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 11.72 | 2.2075 | 2.2593 | 2.2262 | 2.2312 | 2.2128 | 2.1955 | 2.2221 | 2.2593
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 11.72 | 2.2121 | 2.1987 | 2.1631 | 2.2263 | 2.2618 | 2.2416 | 2.2173 | 2.2618
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 11.72 | 1.3684 | 1.3598 | 1.3201 | 1.4598 | 1.4638 | 1.4406 | 1.4021 | 1.4638
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 11.72 | 0 | 0 | 0 | 0 | 2.5306 | 2.5975 | 2.564 | 2.5975
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 11.72 | 0 | 0 | 0 | 0 | 4.8938 | 4.8946 | 4.8942 | 4.8946
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 11.72 | 4.9303 | 4.8429 | 4.6145 | 5.1005 | 5.3448 | 5.2505 | 5.0139 | 5.3448
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 11.72 | 5.4293 | 5.4002 | 5.199 | 5.6523 | 5.6651 | 5.6287 | 5.4958 | 5.6651
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 11.72 | 4.1837 | 4.3285 | 4.2332 | 4.618 | 4.5993 | 4.655 | 4.4363 | 4.655
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 11.72 | 4.4634 | 4.5126 | 4.3511 | 4.6787 | 4.6245 | 4.5663 | 4.5328 | 4.6787
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 11.72 | 5.2548 | 5.1772 | 5.0003 | 5.5244 | 5.6165 | 5.495 | 5.3447 | 5.6165
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 11.72 | 2.6085 | 2.6329 | 2.5788 | 2.6475 | 2.588 | 2.6277 | 2.6139 | 2.6475
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 11.72 | 3.3204 | 3.4004 | 3.2585 | 3.5561 | 3.5043 | 3.4035 | 3.4072 | 3.5561
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 11.72 | 4.0514 | 4.0444 | 3.8989 | 4.1475 | 4.1221 | 4.1297 | 4.0656 | 4.1475
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 11.72 | 4.3432 | 4.3358 | 4.1037 | 4.4662 | 4.5032 | 4.455 | 4.3678 | 4.5032
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 11.72 | 1.7548 | 1.7659 | 1.7258 | 1.758 | 1.7148 | 1.7381 | 1.7429 | 1.7659
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 11.72 | 1.1838 | 1.1629 | 1.1657 | 1.1785 | 1.1633 | 1.1842 | 1.173 | 1.1842
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 11.72 | 2.3781 | 2.3809 | 2.3563 | 2.3982 | 2.3682 | 2.4059 | 2.3813 | 2.4059
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 11.72 | 3.5639 | 3.6126 | 3.4909 | 3.6282 | 3.6048 | 3.6243 | 3.5874 | 3.6282
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 11.72 | 2.2991 | 2.3311 | 2.2528 | 2.3358 | 2.3162 | 2.3272 | 2.3104 | 2.3358
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 11.72 | 3.3536 | 3.4221 | 3.259 | 3.4314 | 3.3879 | 3.4203 | 3.3791 | 3.4314
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 11.72 | 1.5374 | 1.5183 | 1.5083 | 1.5531 | 1.545 | 1.5262 | 1.5314 | 1.5531
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 11.72 | 2.3368 | 2.3306 | 2.3009 | 2.3987 | 2.3459 | 2.3683 | 2.3469 | 2.3987
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 11.72 | 5.1285 | 5.0586 | 4.8858 | 5.2897 | 5.322 | 5.3015 | 5.1643 | 5.322
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 11.72 | 3.4582 | 3.4413 | 3.3703 | 3.5962 | 3.5914 | 3.3861 | 3.4739 | 3.5962
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 11.72 | 0.34663 | 0.33133 | 0.33155 | 0.3697 | 0.36929 | 0.37624 | 0.35412 | 0.37624
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 11.72 | 3.7973 | 4.2728 | 4.0754 | 4.2781 | 4.1869 | 4.2099 | 4.1368 | 4.2781
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 11.72 | 5.3644 | 5.5598 | 5.312 | 5.6155 | 5.5042 | 5.4411 | 5.4661 | 5.6155
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 11.72 | 4.8674 | 5.1679 | 4.9489 | 5.1758 | 5.0205 | 5.0995 | 5.0467 | 5.1758
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 11.72 | 3.6907 | 3.715 | 3.6669 | 3.8006 | 3.7013 | 3.7653 | 3.7233 | 3.8006
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 11.72 | 3.2615 | 3.3369 | 3.243 | 3.3295 | 3.2533 | 3.2901 | 3.2857 | 3.3369
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 11.72 | 3.6086 | 3.589 | 3.523 | 3.6645 | 3.6384 | 3.6188 | 3.6071 | 3.6645
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 11.72 | 2.9587 | 2.9554 | 2.8976 | 2.9983 | 2.9464 | 2.9941 | 2.9584 | 2.9983
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 11.72 | 4.6244 | 4.647 | 4.418 | 4.7454 | 4.676 | 4.6757 | 4.6311 | 4.7454
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 11.72 | 4.238 | 4.1965 | 4.1037 | 4.3313 | 4.3107 | 4.304 | 4.2473 | 4.3313
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 11.72 | 3.101 | 3.0927 | 3.0559 | 3.1886 | 3.0781 | 3.148 | 3.1107 | 3.1886
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 11.72 | 2.7272 | 2.8431 | 2.8251 | 2.8915 | 2.831 | 2.903 | 2.8368 | 2.903
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 11.72 | 2.0068 | 2.0333 | 2.0192 | 2.0171 | 1.9717 | 1.9936 | 2.0069 | 2.0333
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 11.72 | 1.5948 | 1.6133 | 1.6018 | 1.5981 | 1.588 | 1.6005 | 1.5994 | 1.6133
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 11.72 | 2.4515 | 2.4572 | 2.4387 | 2.4405 | 2.4033 | 2.453 | 2.4407 | 2.4572
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 11.72 | 3.9261 | 3.9179 | 3.8933 | 3.9838 | 3.9711 | 4.0416 | 3.9556 | 4.0416
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 11.72 | 4.0816 | 4.2039 | 4.1468 | 4.257 | 4.2042 | 4.2847 | 4.1964 | 4.2847
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 11.72 | 4.3502 | 4.3787 | 4.2824 | 4.4131 | 4.3696 | 4.3891 | 4.3639 | 4.4131
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 11.72 | 1.8775 | 1.8856 | 1.8808 | 1.8637 | 1.8326 | 1.8767 | 1.8695 | 1.8856
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 11.72 | 2.7559 | 2.7452 | 2.7122 | 2.75 | 2.684 | 2.7619 | 2.7349 | 2.7619
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 11.72 | 3.0251 | 2.9771 | 2.9502 | 3.0514 | 2.9528 | 3.0332 | 2.9983 | 3.0514
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 11.72 | 4.0292 | 3.9912 | 3.926 | 4.1226 | 4.0671 | 4.0965 | 4.0388 | 4.1226
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 11.72 | 4.4679 | 4.391 | 4.3096 | 4.5817 | 4.6339 | 4.6406 | 4.5041 | 4.6406
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 11.72 | 4.6521 | 4.6017 | 4.4933 | 4.8251 | 4.8131 | 4.8149 | 4.7 | 4.8251
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 11.72 | 4.4689 | 4.4437 | 4.3372 | 4.5757 | 4.5151 | 4.5559 | 4.4828 | 4.5757
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 11.72 | 4.7924 | 4.7425 | 4.6361 | 4.9449 | 4.8641 | 4.9738 | 4.8256 | 4.9738
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 11.72 | 3.4552 | 3.5088 | 3.4046 | 3.5935 | 3.4691 | 3.5634 | 3.4991 | 3.5935
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 11.72 | 4.0881 | 4.1123 | 4.0943 | 4.2294 | 4.1112 | 4.1718 | 4.1345 | 4.2294
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 11.72 | 3.7661 | 3.7072 | 3.719 | 3.8125 | 3.7919 | 3.8218 | 3.7697 | 3.8218
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 11.72 | 3.342 | 3.332 | 3.3254 | 3.3967 | 3.387 | 3.3861 | 3.3615 | 3.3967
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 11.72 | 2.5829 | 2.4709 | 2.4841 | 2.5912 | 2.7241 | 2.7431 | 2.5994 | 2.7431
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 11.72 | 4.7436 | 4.7947 | 4.6815 | 4.9238 | 4.8483 | 4.8663 | 4.8097 | 4.9238
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 11.72 | 4.1973 | 4.1763 | 4.1026 | 4.2868 | 4.1894 | 4.2347 | 4.1978 | 4.2868
2026 | 2025 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 11.72 | 3.1201 | 3.4147 | 3.3044 | 3.5214 | 3.4137 | 3.5109 | 3.3809 | 3.5214
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Inv_SY_Dev
Finacial Year | Start Month | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Plant DC Capcity (MW) | IC1_Inv1 WRT Avg. | IC1_Inv2 wrt Avg. | IC1_Inv3 wrt Avg. | IC1_Inv4 wrt Avg. | IC2_Inv1 wrt Avg. | IC2_Inv2 wrt Avg. | IC1_Inv1 wrt Max. | IC1_Inv2 wrt Max. | IC1_Inv3 wrt Max. | IC1_Inv4 wrt Max. | IC2_Inv1 wrt Max. | IC2_Inv2 wrt Max.
FY2024-25 | 4 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | 2025-03-29 | 11.72 | 0.2866% | -1.445% | -1.509% | 2.743% | 0.1279% | -0.2031% | 0% | 2.743% | -4.138% | 0% | -2.545% | -2.867%
2025 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | 2025-03-30 | 11.72 | -0.5844% | -1.842% | -0.8291% | 2.497% | 0.8577% | -0.09854% | 0% | 2.497% | -3.245% | 0% | -1.599% | -2.532%
2025 | 2025 | 2025 | Year_3 | Year_3 | Mar-25 | 31 | 2025-03-31 | 11.72 | -0.9763% | -1.042% | -1.147% | 2.166% | 0.8815% | 0.1188% | 0% | 2.166% | -3.243% | 0% | -1.257% | -2.004%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-01 | 11.72 | -1.897% | -1.015% | -0.7185% | 1.871% | 2.108% | -0.3479% | 0% | 2.108% | -2.768% | -0.2322% | 0% | -2.405%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-02 | 11.72 | -3.627% | -1.916% | -0.07327% | 3.105% | 2.526% | -0.01399% | 0% | 3.105% | -3.082% | 0% | -0.5616% | -3.025%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-03 | 11.72 | -1.283% | -1.834% | -0.6242% | 0.8371% | 1.28% | 1.625% | 0% | 1.625% | -2.213% | -0.7752% | -0.3398% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-04 | 11.72 | -2.286% | -1.819% | -1.353% | 1.534% | 2.537% | 1.387% | 0% | 2.537% | -3.794% | -0.9777% | 0% | -1.121%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-05 | 11.72 | 0.1799% | -2.595% | -1.934% | 1.278% | 1.694% | 1.377% | 0% | 1.694% | -3.567% | -0.4087% | 0% | -0.3115%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-06 | 11.72 | -1.939% | -0.7861% | -2.326% | 2.163% | 1.592% | 1.296% | 0% | 2.163% | -4.394% | 0% | -0.5598% | -0.849%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-07 | 11.72 | -1.215% | -2.41% | -2.038% | 2.317% | 1.495% | 1.851% | 0% | 2.317% | -4.257% | 0% | -0.8031% | -0.4553%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-08 | 11.72 | -1.661% | -2.086% | -1.29% | 3.211% | 0.3068% | 1.519% | 0% | 3.211% | -4.361% | 0% | -2.814% | -1.639%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-09 | 11.72 | -1.539% | -1.976% | -0.09317% | 2.944% | 0.6372% | 0.02765% | 0% | 2.944% | -2.95% | 0% | -2.24% | -2.833%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-10 | 11.72 | -1.696% | -2.019% | -0.3681% | 2.541% | 0.3545% | 1.188% | 0% | 2.541% | -2.837% | 0% | -2.132% | -1.32%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-11 | 11.72 | -3.152% | -3.407% | -0.7267% | 2.942% | 2.683% | 1.661% | 0% | 2.942% | -3.564% | 0% | -0.2519% | -1.244%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-12 | 11.72 | -1.834% | -2.088% | -1.564% | 2.334% | 1.264% | 1.889% | 0% | 2.334% | -3.809% | 0% | -1.045% | -0.4349%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-13 | 11.72 | -2.392% | -1.051% | -1.743% | 1.999% | 1.232% | 1.955% | 0% | 1.999% | -3.669% | 0% | -0.7515% | -0.04287%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-14 | 11.72 | -0.7081% | -1.109% | -1.215% | 1.797% | 0.1168% | 1.118% | 0% | 1.797% | -2.959% | 0% | -1.651% | -0.6673%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-15 | 11.72 | -0.9465% | -1.395% | -1.722% | 1.512% | 0.8175% | 1.734% | 0% | 1.734% | -3.397% | -0.2182% | -0.9012% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-16 | 11.72 | -1.583% | -1.995% | -1.323% | 2.112% | 1.867% | 0.9226% | 0% | 2.112% | -3.364% | 0% | -0.2398% | -1.164%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-17 | 11.72 | -1.345% | -1.971% | -2.17% | 1.558% | 2.438% | 1.491% | 0% | 2.438% | -4.499% | -0.8596% | 0% | -0.9252%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-18 | 11.72 | -2.291% | -2.305% | -2.076% | 1.532% | 3.296% | 1.844% | 0% | 3.296% | -5.201% | -1.708% | 0% | -1.406%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-19 | 11.72 | -1.165% | -1.311% | -3.762% | 1.794% | 2.509% | 1.936% | 0% | 2.509% | -6.118% | -0.6977% | 0% | -0.559%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-20 | 11.72 | -1.662% | -2.321% | -5.037% | 2.444% | 3.798% | 2.778% | 0% | 3.798% | -8.511% | -1.305% | 0% | -0.9822%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-21 | 11.72 | -1.687% | -2.567% | -4.137% | 2.357% | 3.204% | 2.831% | 0% | 3.204% | -7.113% | -0.8207% | 0% | -0.3618%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-22 | 11.72 | -2.006% | 0.2913% | -0.235% | 1.995% | 0.7017% | -0.7468% | 0% | 1.995% | -2.187% | 0% | -1.268% | -2.688%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-23 | 11.72 | -1.018% | -3.01% | -4.199% | 1.756% | 2.962% | 3.508% | 0% | 3.508% | -7.446% | -1.693% | -0.5276% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-24 | 11.72 | -1.9% | 0.1114% | -3.875% | 1.714% | 1.951% | 1.999% | 0% | 1.999% | -5.759% | -0.2786% | -0.04698% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-25 | 11.72 | -1.898% | -0.428% | -4.425% | 1.762% | 2.861% | 2.128% | 0% | 2.861% | -7.083% | -1.068% | 0% | -0.7119%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-26 | 11.72 | -0.7264% | -1.738% | -6.247% | 3.225% | 1.891% | 3.595% | 0% | 3.595% | -9.501% | -0.3572% | -1.646% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-27 | 11.72 | 0.2668% | -3.527% | -4.788% | 1.92% | 2.956% | 3.172% | 0% | 3.172% | -7.715% | -1.213% | -0.2093% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-28 | 11.72 | -1.02% | -1.637% | -6.676% | 3.619% | 2.381% | 3.332% | 0% | 3.619% | -9.936% | 0% | -1.195% | -0.2768%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-29 | 11.72 | -1.158% | -2.138% | -6.035% | 3.553% | 2.215% | 3.563% | 0% | 3.563% | -9.268% | -0.009738% | -1.301% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Apr-25 | 30 | 2025-04-30 | 11.72 | -1.067% | -2.247% | -7.14% | 4.247% | 2.144% | 4.062% | 0% | 4.247% | -10.92% | 0% | -2.017% | -0.1769%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-01 | 11.72 | -2.141% | -1.821% | -4.565% | 4.262% | 1.465% | 2.8% | 0% | 4.262% | -8.466% | 0% | -2.683% | -1.403%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-02 | 11.72 | -1.57% | -1.116% | -4.891% | 3.422% | 1.319% | 2.836% | 0% | 3.422% | -8.038% | 0% | -2.033% | -0.5661%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-03 | 11.72 | -1.855% | 1.089% | -6.261% | 2.876% | 2.393% | 1.758% | 0% | 2.876% | -8.882% | 0% | -0.4694% | -1.087%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-04 | 11.72 | -0.6126% | -0.2618% | -6.303% | 3.726% | 1.155% | 2.297% | 0% | 3.726% | -9.669% | 0% | -2.479% | -1.377%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-05 | 11.72 | -0.6163% | -1.511% | -6.002% | 3.4% | 2.272% | 2.457% | 0% | 3.4% | -9.093% | 0% | -1.09% | -0.9111%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-06 | 11.72 | -1.107% | -1.534% | -5.11% | 2.951% | 3.048% | 1.751% | 0% | 3.048% | -7.917% | -0.0942% | 0% | -1.259%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-07 | 11.72 | 0.1775% | -2.282% | -6.734% | 2.55% | 3.238% | 3.052% | 0% | 3.238% | -9.66% | -0.667% | 0% | -0.1808%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-08 | 11.72 | -0.8314% | -1.659% | -5.632% | 2.635% | 2.952% | 2.535% | 0% | 2.952% | -8.338% | -0.3082% | 0% | -0.405%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-09 | 11.72 | -1.204% | 0.1862% | -6.529% | 2.005% | 2.296% | 3.246% | 0% | 3.246% | -9.467% | -1.202% | -0.9204% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-10 | 11.72 | -0.1128% | -1.684% | -5.019% | 2.443% | 3.045% | 1.327% | 0% | 3.045% | -7.825% | -0.5843% | 0% | -1.667%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-11 | 11.72 | -1.1% | -0.7212% | -4.483% | 3.47% | 1.255% | 1.578% | 0% | 3.47% | -7.686% | 0% | -2.141% | -1.829%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-12 | 11.72 | 0.09816% | -4.87% | -5.526% | 3.38% | 2.547% | 4.37% | 0% | 4.37% | -9.482% | -0.9487% | -1.748% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-13 | 11.72 | -1.296% | 0.3054% | -4.589% | 2.508% | 2.694% | 0.3766% | 0% | 2.694% | -7.092% | -0.1816% | 0% | -2.257%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-14 | 11.72 | -1.491% | 0.2131% | -5.18% | 3.615% | 1.978% | 0.8648% | 0% | 3.615% | -8.489% | 0% | -1.581% | -2.655%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-15 | 11.72 | -1.453% | 1.07% | -3.145% | 0.6988% | 1.552% | 1.278% | 0% | 1.552% | -4.625% | -0.8399% | 0% | -0.2697%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-16 | 11.72 | -1.613% | -0.6677% | -4.205% | 1.596% | 3.161% | 1.729% | 0% | 3.161% | -7.14% | -1.516% | 0% | -1.388%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-17 | 11.72 | -0.6964% | -1.56% | -4.869% | 3.14% | 2.345% | 1.641% | 0% | 3.14% | -7.766% | 0% | -0.7705% | -1.453%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-18 | 11.72 | -0.676% | -0.5069% | -4.089% | 1.699% | 1.531% | 2.042% | 0% | 2.042% | -6.008% | -0.3356% | -0.5007% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-19 | 11.72 | -1.381% | 1.629% | -0.8151% | 1.935% | -0.1844% | -1.183% | 0% | 1.935% | -2.698% | 0% | -2.08% | -3.06%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-20 | 11.72 | 0.05416% | -1.911% | -4.747% | 2.167% | 1.596% | 2.841% | 0% | 2.841% | -7.378% | -0.6562% | -1.211% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-21 | 11.72 | -0.03327% | -0.2613% | -1.566% | 0.5637% | 0.8426% | 0.4541% | 0% | 0.8426% | -2.388% | -0.2766% | 0% | -0.3853%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-22 | 11.72 | -1.98% | 2.444% | -17.48% | 6.928% | 5.248% | 4.838% | 0% | 6.928% | -22.83% | 0% | -1.571% | -1.955%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-23 | 11.72 | 1.387% | -2.858% | -9.063% | 3.499% | 1.464% | 5.571% | 0% | 5.571% | -13.86% | -1.963% | -3.89% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-24 | 11.72 | 0.1345% | -0.1745% | -1.067% | 0.4694% | -0.8365% | 1.474% | 0% | 1.474% | -2.505% | -0.9905% | -2.277% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-25 | 11.72 | -0.4438% | 2.288% | -1.267% | 1.489% | -2.87% | 0.8029% | 0% | 2.288% | -3.476% | -0.7809% | -5.042% | -1.452%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-26 | 11.72 | -0.6542% | 1.673% | 0.1844% | 0.4114% | -0.4198% | -1.194% | 0% | 1.673% | -1.464% | -1.24% | -2.058% | -2.82%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-27 | 11.72 | -0.2337% | -0.8372% | -2.443% | 0.4099% | 2.007% | 1.097% | 0% | 2.007% | -4.363% | -1.566% | 0% | -0.8922%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-28 | 11.72 | -2.402% | -3.017% | -5.847% | 4.119% | 4.401% | 2.747% | 0% | 4.401% | -9.816% | -0.2697% | 0% | -1.584%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-29 | 11.72 | -100% | -100% | -100% | -100% | -1.306% | 1.306% | 0% | 1.306% | -100% | -100% | -2.578% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-30 | 11.72 | -100% | -100% | -100% | -100% | -0.007656% | 0.007656% | 0% | 0.007656% | -100% | -100% | -0.01531% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | May-25 | 31 | 2025-05-31 | 11.72 | -1.668% | -3.41% | -7.965% | 1.727% | 6.599% | 4.718% | 0% | 6.599% | -13.66% | -4.57% | 0% | -1.764%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-01 | 11.72 | -1.209% | -1.738% | -5.399% | 2.849% | 3.08% | 2.419% | 0% | 3.08% | -8.226% | -0.2245% | 0% | -0.6415%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-02 | 11.72 | -5.694% | -2.43% | -4.578% | 4.097% | 3.674% | 4.93% | 0% | 4.93% | -9.061% | -0.7931% | -1.196% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-03 | 11.72 | -1.531% | -0.4453% | -4.009% | 3.22% | 2.024% | 0.7404% | 0% | 3.22% | -7.003% | 0% | -1.159% | -2.403%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-04 | 11.72 | -1.683% | -3.134% | -6.443% | 3.362% | 5.086% | 2.813% | 0% | 5.086% | -10.97% | -1.64% | 0% | -2.163%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-05 | 11.72 | -0.2065% | 0.7273% | -1.345% | 1.287% | -0.9918% | 0.5285% | 0% | 1.287% | -2.598% | 0% | -2.25% | -0.7489%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-06 | 11.72 | -2.548% | -0.1978% | -4.365% | 4.37% | 2.85% | -0.1092% | 0% | 4.37% | -8.369% | 0% | -1.457% | -4.292%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-07 | 11.72 | -0.3513% | -0.5227% | -4.102% | 2.013% | 1.388% | 1.575% | 0% | 2.013% | -5.995% | 0% | -0.6133% | -0.4291%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-08 | 11.72 | -0.5653% | -0.7326% | -6.049% | 2.253% | 3.1% | 1.994% | 0% | 3.1% | -8.873% | -0.8213% | 0% | -1.072%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-09 | 11.72 | 0.681% | 1.322% | -0.9801% | 0.8655% | -1.614% | -0.2743% | 0% | 1.322% | -2.272% | -0.4508% | -2.898% | -1.576%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-10 | 11.72 | 0.9141% | -0.8683% | -0.6282% | 0.4648% | -0.83% | 0.9476% | 0% | 0.9476% | -1.561% | -0.4782% | -1.761% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-11 | 11.72 | -0.1327% | -0.01688% | -1.05% | 0.7112% | -0.5485% | 1.037% | 0% | 1.037% | -2.065% | -0.3222% | -1.569% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-12 | 11.72 | -0.6569% | 0.7023% | -2.69% | 1.136% | 0.4829% | 1.026% | 0% | 1.136% | -3.783% | 0% | -0.6455% | -0.1082%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-13 | 11.72 | -0.4878% | 0.898% | -2.494% | 1.102% | 0.2526% | 0.7292% | 0% | 1.102% | -3.558% | 0% | -0.8405% | -0.3691%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-14 | 11.72 | -0.7539% | 1.274% | -3.553% | 1.549% | 0.2629% | 1.22% | 0% | 1.549% | -5.024% | 0% | -1.267% | -0.3237%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-15 | 11.72 | 0.395% | -0.8539% | -1.508% | 1.416% | 0.8869% | -0.3363% | 0% | 1.416% | -2.884% | 0% | -0.522% | -1.728%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-16 | 11.72 | -0.4282% | -0.6926% | -1.959% | 2.209% | -0.0415% | 0.9129% | 0% | 2.209% | -4.078% | 0% | -2.202% | -1.268%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-17 | 11.72 | -0.6942% | -2.048% | -5.394% | 2.427% | 3.053% | 2.656% | 0% | 3.053% | -8.197% | -0.6074% | 0% | -0.3855%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-18 | 11.72 | -0.4519% | -0.9389% | -2.984% | 3.52% | 3.382% | -2.527% | 0% | 3.52% | -6.282% | 0% | -0.1335% | -5.841%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-19 | 11.72 | -2.116% | -6.436% | -6.375% | 4.4% | 4.283% | 6.245% | 0% | 6.245% | -11.88% | -1.737% | -1.847% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-20 | 11.72 | -8.206% | 3.29% | -1.482% | 3.418% | 1.212% | 1.768% | 0% | 3.418% | -4.738% | 0% | -2.133% | -1.595%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-21 | 11.72 | -1.861% | 1.713% | -2.821% | 2.732% | 0.6957% | -0.4584% | 0% | 2.732% | -5.405% | 0% | -1.982% | -3.105%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-22 | 11.72 | -3.553% | 2.402% | -1.938% | 2.56% | -0.5178% | 1.047% | 0% | 2.56% | -4.385% | 0% | -3.001% | -1.475%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-23 | 11.72 | -0.8771% | -0.2221% | -1.514% | 2.075% | -0.5912% | 1.129% | 0% | 2.075% | -3.516% | 0% | -2.612% | -0.9267%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-24 | 11.72 | -0.7365% | 1.559% | -1.301% | 1.332% | -0.9867% | 0.1333% | 0% | 1.559% | -2.816% | -0.223% | -2.506% | -1.404%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-25 | 11.72 | 0.04372% | -0.5009% | -2.33% | 1.592% | 0.8692% | 0.3255% | 0% | 1.592% | -3.86% | 0% | -0.7116% | -1.247%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-26 | 11.72 | 0.009044% | -0.1015% | -2.056% | 1.348% | -0.406% | 1.206% | 0% | 1.348% | -3.359% | 0% | -1.731% | -0.1407%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-27 | 11.72 | -0.145% | 0.3433% | -4.6% | 2.469% | 0.9695% | 0.964% | 0% | 2.469% | -6.899% | 0% | -1.463% | -1.468%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-28 | 11.72 | -0.2198% | -1.197% | -3.383% | 1.976% | 1.491% | 1.333% | 0% | 1.976% | -5.255% | 0% | -0.4757% | -0.6305%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-29 | 11.72 | -0.3113% | -0.5777% | -1.763% | 2.502% | -1.05% | 1.199% | 0% | 2.502% | -4.161% | 0% | -3.465% | -1.271%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jun-25 | 30 | 2025-06-30 | 11.72 | -3.863% | 0.2226% | -0.4143% | 1.927% | -0.2039% | 2.332% | 0% | 2.332% | -2.683% | -0.3955% | -2.478% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-01 | 11.72 | -0.005911% | 1.312% | 0.6098% | 0.5066% | -1.757% | -0.6662% | 0% | 1.312% | -0.6936% | -0.7954% | -3.029% | -1.953%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-02 | 11.72 | -0.2899% | 0.8692% | 0.1506% | -0.08471% | -0.7121% | 0.06689% | 0% | 0.8692% | -0.7125% | -0.9457% | -1.568% | -0.7954%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-03 | 11.72 | 0.4443% | 0.6744% | -0.08095% | -0.009463% | -1.531% | 0.5026% | 0% | 0.6744% | -0.7502% | -0.6792% | -2.19% | -0.1706%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-04 | 11.72 | -0.7465% | -0.9544% | -1.575% | 0.7121% | 0.3907% | 2.173% | 0% | 2.173% | -3.668% | -1.43% | -1.744% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-05 | 11.72 | -2.736% | 0.1798% | -1.18% | 1.445% | 0.1876% | 2.104% | 0% | 2.104% | -3.217% | -0.6453% | -1.877% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-06 | 11.72 | -0.3129% | 0.3398% | -1.866% | 1.129% | 0.1311% | 0.5787% | 0% | 1.129% | -2.961% | 0% | -0.9868% | -0.5442%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-07 | 11.72 | 0.43% | 0.861% | 0.6052% | -0.3098% | -1.974% | 0.3877% | 0% | 0.861% | -0.2536% | -1.161% | -2.811% | -0.4692%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-08 | 11.72 | 0.77% | 0.377% | -0.83% | 0.5538% | -1.859% | 0.9881% | 0% | 0.9881% | -1.8% | -0.4301% | -2.819% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-09 | 11.72 | 0.8935% | -0.708% | -1.605% | 1.772% | -1.516% | 1.164% | 0% | 1.772% | -3.318% | 0% | -3.231% | -0.5976%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-10 | 11.72 | -0.2364% | -1.177% | -2.793% | 2.075% | 0.7017% | 1.43% | 0% | 2.075% | -4.768% | 0% | -1.345% | -0.6314%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-11 | 11.72 | -0.8036% | -2.512% | -4.319% | 1.723% | 2.882% | 3.03% | 0% | 3.03% | -7.133% | -1.269% | -0.1439% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-12 | 11.72 | -1.021% | -2.092% | -4.398% | 2.661% | 2.406% | 2.443% | 0% | 2.661% | -6.876% | 0% | -0.2486% | -0.2126%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-13 | 11.72 | -0.3088% | -0.8723% | -3.247% | 2.074% | 0.7214% | 1.632% | 0% | 2.074% | -5.213% | 0% | -1.325% | -0.4329%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-14 | 11.72 | -0.6885% | -1.723% | -3.927% | 2.472% | 0.7971% | 3.07% | 0% | 3.07% | -6.788% | -0.5801% | -2.205% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-15 | 11.72 | -1.254% | 0.2762% | -2.701% | 2.698% | -0.8563% | 1.837% | 0% | 2.698% | -5.257% | 0% | -3.461% | -0.8383%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-16 | 11.72 | -1.122% | -0.536% | -0.9735% | 2.294% | -0.5642% | 0.9018% | 0% | 2.294% | -3.194% | 0% | -2.794% | -1.361%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-17 | 11.72 | -0.09602% | -1.66% | -1.346% | 1.134% | 0.5875% | 1.381% | 0% | 1.381% | -2.69% | -0.2431% | -0.7824% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-18 | 11.72 | -0.5811% | -0.8785% | -1.074% | 1.046% | 0.7559% | 0.7316% | 0% | 1.046% | -2.098% | 0% | -0.2873% | -0.3113%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-19 | 11.72 | -0.6358% | -4.941% | -4.434% | -0.3157% | 4.799% | 5.528% | 0% | 5.528% | -9.44% | -5.537% | -0.691% | 0%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-20 | 11.72 | -1.374% | -0.312% | -2.665% | 2.372% | 0.8018% | 1.178% | 0% | 2.372% | -4.92% | 0% | -1.534% | -1.166%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-21 | 11.72 | -0.01368% | -0.5121% | -2.27% | 2.12% | -0.2013% | 0.8771% | 0% | 2.12% | -4.298% | 0% | -2.273% | -1.217%
2026 | 2025 | 2025 | Year_3 | Year_3 | Jul-25 | 31 | 2025-07-22 | 11.72 | -7.712% | 1.001% | -2.262% | 4.156% | 0.9705% | 3.846% | 0% | 4.156% | -6.162% | 0% | -3.059% | -0.2982%
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Plant BD
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affceted Equipment | DC Capacity Affceted (kW) | Plant Equivalent Weightage | Affected Equipmenet Location | Fault Catrgory | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgemnet Time | Work Start time on Fault | Work Completiuon time on fualt | Acknowdlegemnet time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(Wh/m2) | Approxuimate Energy Loss (KWh) | PTW No. | Job Card No.
1 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-19 |  |  |  | IC2_Inv2 | 2020 | 0.1725 | IC2_Inv2 | Inverter | Pu communication |  | 0.29931 | 0.30417 | 0.30486 | 0.32014 | 0.11667 | 0.13333 | 0.5 | 0.5 | replaced 40A fuse | Close | 0.086248 | 89 | 147.3779
2 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | IC2_Inv2 | 2020 | 0.1725 | IC2_Inv2 | Inverter | Pu communication |  | 0.26389 | 0.27431 | 0.27639 | 0.29375 | 0.25 | 0.3 | 0.71667 | 0.71667 | replaced 40A fuse | Close | 0.12362 | 50 | 73.8898
3 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | IC1_Inv3 | 1806.68 | 0.15428 | IC1_Inv3 | Inverter | Reduced Run |  | 0.53264 | 0.53819 | 0.53889 | 0.55208 | 0.13333 | 0.15 | 0.46667 | 0.46667 | kept half load | Close | 0.071997 | 281 | 371.4074
4 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | IC1_Inv3 | 1806.68 | 0.15428 | IC1_Inv3 | Inverter | Reduced Run |  | 0.55208 | 0.55208 | 0.55278 | 0.625 | 0 | 0.016667 | 1.75 | 1.75 | resolved | Close | 0.26999 | 1472 | 1945.5931
5 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | IC1_Inv1 | 1987.725 | 0.16974 | IC1_Inv1 | Inverter | excess temperature difference |  | 0.44097 | 0.44167 | 0.44444 | 0.44583 | 0.016667 | 0.083333 | 0.11667 | 0.11667 | Excess temperature difference | Close | 0.019803 | 102 | 148.3267
6 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | IC1_Inv3 | 1806.68 | 0.15428 | IC1_Inv3 | Inverter | excess temperature difference |  | 0.57361 | 0.58333 | 0.58542 | 0.5875 | 0.23333 | 0.28333 | 0.33333 | 0.33333 | Excess temperature difference | Close | 0.051426 | 253 | 334.3988
7 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | IC1_Inv1 | 1987.725 | 0.16974 | IC1_Inv1 | Inverter | icr-01 isolated for repowering work purpose |  | 0.43472 | 0.43472 | 0.43542 | 0.77431 | 0 | 0.016667 | 8.15 | 8.15 | Client scope | open | 1.3834 | 3230 | 4697.0133
8 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | IC1_Inv2 | 2031.205 | 0.17345 | IC1_Inv2 | Inverter | icr-01 isolated for repowering work purpose |  | 0.43472 | 0.43472 | 0.43542 | 0.77431 | 0 | 0.016667 | 8.15 | 8.15 | Client scope | open | 1.4136 | 3230 | 4799.7569
9 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | IC1_Inv3 | 1806.68 | 0.15428 | IC1_Inv3 | Inverter | icr-01 isolated for repowering work purpose |  | 0.43472 | 0.43472 | 0.43542 | 0.77431 | 0 | 0.016667 | 8.15 | 8.15 | Client scope | open | 1.2574 | 3230 | 4269.2022
10 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | IC1_Inv4 | 1844.725 | 0.15753 | IC1_Inv4 | Inverter | icr-01 isolated for repowering work purpose |  | 0.43472 | 0.43472 | 0.43542 | 0.77431 | 0 | 0.016667 | 8.15 | 8.15 | Client scope | open | 1.2839 | 3230 | 4359.1029
11 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | IC1_Inv1 | 1987.725 | 0.16974 | IC1_Inv1 | Inverter | icr-01 isolated for repowering work purpose |  | 0.25833 | 0.25833 | 0.25903 | 0.77639 | 0 | 0.016667 | 12.4333 | 12.4333 | Client scope | open | 2.1104 | 3230 | 4697.0133
12 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | IC1_Inv2 | 2031.205 | 0.17345 | IC1_Inv2 | Inverter | icr-01 isolated for repowering work purpose |  | 0.25833 | 0.25833 | 0.25903 | 0.77639 | 0 | 0.016667 | 12.4333 | 12.4333 | Client scope | open | 2.1566 | 3230 | 4799.7569
13 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | IC1_Inv3 | 1806.68 | 0.15428 | IC1_Inv3 | Inverter | icr-01 isolated for repowering work purpose |  | 0.25833 | 0.25833 | 0.25903 | 0.77639 | 0 | 0.016667 | 12.4333 | 12.4333 | Client scope | open | 1.9182 | 3230 | 4269.2022
14 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | IC1_Inv4 | 1844.725 | 0.15753 | IC1_Inv4 | Inverter | icr-01 isolated for repowering work purpose |  | 0.25833 | 0.25833 | 0.25903 | 0.77639 | 0 | 0.016667 | 12.4333 | 12.4333 | Client scope | open | 1.9586 | 3230 | 4359.1029
15 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | IC1_Inv1 | 1987.725 | 0.16974 | IC1_Inv1 | Inverter | icr-01 isolated for repowering work purpose |  | 0.24444 | 0.24444 | 0.25 | 0.3125 | 0 | 0.13333 | 1.6333 | 1.6333 | Client scope | close | 0.27724 | 245 | 356.275
16 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | IC1_Inv2 | 2031.205 | 0.17345 | IC1_Inv2 | Inverter | icr-01 isolated for repowering work purpose |  | 0.24444 | 0.24444 | 0.28125 | 0.3125 | 0 | 0.88333 | 1.6333 | 1.6333 | Client scope | close | 0.28331 | 245 | 364.0683
17 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | IC1_Inv3 | 1806.68 | 0.15428 | IC1_Inv3 | Inverter | icr-01 isolated for repowering work purpose |  | 0.24444 | 0.24444 | 0.29167 | 0.3125 | 0 | 1.1333 | 1.6333 | 1.6333 | Client scope | close | 0.25199 | 245 | 323.8249
18 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | IC1_Inv4 | 1844.725 | 0.15753 | IC1_Inv4 | Inverter | icr-01 isolated for repowering work purpose |  | 0.24444 | 0.24444 | 0.30208 | 0.3125 | 0 | 1.3833 | 1.6333 | 1.6333 | Client scope | close | 0.2573 | 245 | 330.644
19 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | IC1_Inv4 | 1844.725 | 0.15753 | IC1_Inv4 | Inverter | excess temperature difference |  | 0.45625 | 0.45625 | 0.45833 | 0.47014 | 0 | 0.05 | 0.33333 | 0.33333 | Excess temperature difference | close | 0.052509 | 288 | 382.6251
20 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | IC2_Inv2 | 2020 | 0.1725 | IC2_Inv2 | Inverter | Pu communication |  | 0.54167 | 0.54167 | 0.54306 | 0.54861 | 0 | 0.033333 | 0.16667 | 0.16667 | replaced 40A fuse | close | 0.028749 | 111 | 161.4818
21 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | IC2_Inv2 | 2020 | 0.1725 | IC2_Inv2 | Inverter | DC CONTCTOR Not closing |  | 0.45833 | 0.46528 | 0.47569 | 0.49028 | 0.16667 | 0.41667 | 0.76667 | 0.76667 | Excess temperature difference | close | 0.13225 | 444 | 645.9274
22 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | IC1_Inv1 | 1987.725 | 0.16974 | IC1_Inv1 | Inverter | excess temperature difference |  | 0.44514 | 0.44583 | 0.44861 | 0.45 | 0.016667 | 0.083333 | 0.11667 | 0.11667 | Excess temperature difference | close | 0.019803 | 108 | 154.6071
23 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | IC1_Inv3 | 1806.68 | 0.15428 | IC1_Inv3 | Inverter | excess temperature difference |  | 0.49792 | 0.49861 | 0.5 | 0.50278 | 0.016667 | 0.05 | 0.11667 | 0.11667 | Excess temperature difference | close | 0.017999 | 91 | 123.4027
24 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | IC1_Inv1 | 1987.725 | 0.16974 | IC1_Inv1 | Inverter | excess temperature difference |  | 0.46667 | 0.46667 | 0.46736 | 0.47083 | 0 | 0.016667 | 0.1 | 0.1 | Excess temperature difference | close | 0.016974 |  | 0
25 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | IC1_Inv1 | 1987.725 | 0.16974 | IC1_Inv1 | Inverter | excess temperature difference |  | 0.47986 | 0.48056 | 0.48125 | 0.48333 | 0.016667 | 0.033333 | 0.083333 | 0.083333 | Excess temperature difference | close | 0.014145 |  | 0
26 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | IC1_Inv1 | 1987.725 | 0.16974 | IC1_Inv1 | Inverter | excess temperature difference |  | 0.54097 | 0.54167 | 0.54514 | 0.54514 | 0.016667 | 0.1 | 0.1 | 0.1 | Excess temperature difference | close | 0.016974 |  | 0
27 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | IC1_Inv3 | 1806.68 | 0.15428 | IC1_Inv3 | Inverter | excess temperature difference |  | 0.54097 | 0.54167 | 0.54514 | 0.54514 | 0.016667 | 0.1 | 0.1 | 0.1 | Excess temperature difference | close | 0.015428 |  | 0
28 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
29 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
30 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
31 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
32 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
33 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
34 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
35 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
36 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
37 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
38 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
39 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
40 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
41 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
42 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
43 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
44 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
45 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
46 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
47 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
48 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
49 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
50 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
51 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
52 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
53 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
54 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
55 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
56 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
57 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
58 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
59 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
60 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
61 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
62 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
63 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
64 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
65 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
66 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
67 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
68 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
69 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
70 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
71 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
72 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
73 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
74 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
75 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
76 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
77 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
78 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
79 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
80 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
81 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
82 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
83 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
84 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
85 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
86 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
87 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
88 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
89 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
90 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
91 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
92 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
93 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
94 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
95 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
96 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
97 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
98 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
99 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
100 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
101 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
102 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
103 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
104 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
105 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
106 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
107 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
108 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
109 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
110 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
111 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
112 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
113 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
114 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
115 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
116 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
117 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
118 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
119 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
120 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
121 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
122 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
123 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
124 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
125 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
126 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
127 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
128 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
129 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
130 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
131 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
132 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
133 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
134 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
135 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
136 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
137 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
138 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
139 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
140 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
141 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
142 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
143 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
144 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
145 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
146 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
147 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
148 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
149 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
150 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
151 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
152 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
153 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
154 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
155 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
156 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
157 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
158 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
159 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
160 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
161 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
162 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
163 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
164 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
165 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
166 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
167 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
168 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
169 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
170 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
171 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
172 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
173 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
174 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
175 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
176 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
177 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
178 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
179 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
180 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
181 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
182 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
183 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
184 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
185 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
186 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
187 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
188 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
189 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
190 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
191 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
192 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
193 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
194 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
195 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
196 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
197 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
198 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
199 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
200 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
201 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
202 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
203 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
204 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
205 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
206 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
207 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
208 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
209 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
210 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
211 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
212 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
213 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
214 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
215 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
216 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
217 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
218 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
219 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
220 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
221 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
222 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
223 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
224 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
225 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
226 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
227 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
228 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
229 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
230 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
231 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
232 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
233 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
234 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
235 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
236 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
237 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
238 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
239 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
240 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
241 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
242 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
243 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
244 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
245 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
246 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
247 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
248 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
249 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
250 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
251 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
252 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
253 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
254 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
255 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
256 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
257 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
258 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
259 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
260 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
261 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
262 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
263 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
264 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
265 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
266 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
267 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
268 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
269 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
270 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
271 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
272 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
273 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
274 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
275 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
276 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
277 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
278 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
279 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
280 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
281 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
282 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
283 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
284 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
285 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
286 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
287 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
288 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
289 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
290 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
291 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
292 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
293 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
294 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
295 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
296 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
297 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
298 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
299 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
300 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
301 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
302 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
303 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
304 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
305 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
306 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
307 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
308 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
309 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
310 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
311 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
312 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
313 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
314 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
315 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
316 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
317 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
318 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
319 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
320 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
321 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
322 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
323 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
324 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
325 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
326 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
327 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
328 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
329 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
330 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
331 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
332 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
333 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
334 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
335 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
336 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
337 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
338 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
339 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
340 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
341 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
342 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
343 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
344 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
345 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
346 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
347 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
348 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
349 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
350 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
351 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
352 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
353 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
354 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
355 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
356 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
357 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
358 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
359 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
360 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
361 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
362 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
363 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
364 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
365 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
366 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
367 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
368 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
369 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
370 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
371 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
372 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
373 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
374 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
375 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
376 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
377 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
378 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
379 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
380 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
381 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
382 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
383 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
384 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
385 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
386 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
387 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
388 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
389 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
390 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
391 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
392 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
393 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
394 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
395 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
396 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
397 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
398 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
399 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
400 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
401 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
402 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
403 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
404 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
405 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
406 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
407 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
408 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
409 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
410 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
411 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
412 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
413 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
414 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
415 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
416 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
417 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
418 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
419 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
420 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
421 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
422 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
423 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
424 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
425 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
426 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
427 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
428 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
429 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
430 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
431 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
432 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
433 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
434 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
435 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
436 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
437 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
438 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
439 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
440 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
441 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
442 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
443 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
444 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
445 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
446 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
447 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
448 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
449 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
450 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
451 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
452 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
453 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
454 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
455 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
456 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
457 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
458 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
459 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
460 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
461 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
462 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
463 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
464 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
465 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
466 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
467 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
468 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
469 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
470 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
471 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
472 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
473 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
474 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
475 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
476 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
477 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
478 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
479 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
480 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
481 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
482 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
483 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
484 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
485 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
486 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
487 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
488 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
489 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
490 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
491 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
492 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
493 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
494 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
495 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
496 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
497 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
498 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
499 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
500 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
501 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
502 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
503 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
504 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
505 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
506 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
507 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
508 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
509 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
510 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
511 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
512 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
513 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
514 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
515 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
516 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
517 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
518 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
519 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
520 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
521 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
522 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
523 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
524 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
525 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
526 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
527 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
528 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
529 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
530 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
531 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
532 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
533 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
534 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
535 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
536 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
537 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
538 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
539 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
540 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
541 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
542 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
543 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
544 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
545 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
546 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
547 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
548 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
549 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
550 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
551 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
552 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
553 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
554 | 1900 | 1900 | [19 empty] | 0 | 0 | 0 | 0
Formulas:
Days = DAY(EOMONTH(PA[[#This Row],[Month Year]],0))

## Tracker_BD
Sr. No. | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Date | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affected Equipment | Plant Equivalent Weightage | Angle of affected equipment | Inv Number | Gateway Number | Grid Number | MSAT Number | Table Number | Fault Category | Fault Code (As per HMI) | Breakdown Description | Fault Time | Fault Acknowledgement Time | Work Start time on Fault | Work Completion time on fault | Acknowledgement time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Avg. Target Angle during Fault Time (Radians) | Approximate Energy Loss Factor (%) | Plant Equivalent breakdown | Old equipment Serial Number | New Equipment Serial Number
1 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
2 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
3 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
4 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
5 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
6 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
7 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
8 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
9 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
10 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | required modbus cable | Open |  | 11.71% | 0.10374
11 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | required modbus cable | Open |  | 11.71% | 0.10374
12 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | required modbus cable | Open |  | 11.71% | 0.10374
13 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | required modbus cable | Open |  | 11.71% | 0.10374
14 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | required modbus cable | Open |  | 11.71% | 0.069157
15 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | required modbus cable | Open |  | 11.71% | 0.069157
16 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
17 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
18 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
19 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
20 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
21 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
22 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
23 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
24 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
25 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:28 | 6:28 |  | 0.76042 | 0 | -6.4667 | 1900-01-10 18:48 | 11.7833 | required modbus cable | Open |  | 11.71% | 0.10158
26 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:28 | 6:28 |  | 0.76042 | 0 | -6.4667 | 1900-01-10 18:48 | 11.7833 | required modbus cable | Open |  | 11.71% | 0.10158
27 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:28 | 6:28 |  | 0.76042 | 0 | -6.4667 | 1900-01-10 18:48 | 11.7833 | required modbus cable | Open |  | 11.71% | 0.10158
28 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:28 | 6:28 |  | 0.76042 | 0 | -6.4667 | 1900-01-10 18:48 | 11.7833 | required modbus cable | Open |  | 11.71% | 0.10158
29 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:28 | 6:28 |  | 0.76042 | 0 | -6.4667 | 1900-01-10 18:48 | 11.7833 | required modbus cable | Open |  | 11.71% | 0.06772
30 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-30 | 6:28 | 18:12 | 11.7333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:28 | 6:28 |  | 0.76042 | 0 | -6.4667 | 1900-01-10 18:48 | 11.7833 | required modbus cable | Open |  | 11.71% | 0.06772
31 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
32 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
33 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
34 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
35 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
36 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
37 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
38 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
39 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
40 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:35 | 6:35 |  | 0.76042 | 0 | -6.5833 | 1900-01-10 16:00 | 11.6667 | required modbus cable | Open |  | 11.71% | 0.10057
41 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:35 | 6:35 |  | 0.76042 | 0 | -6.5833 | 1900-01-10 16:00 | 11.6667 | required modbus cable | Open |  | 11.71% | 0.10057
42 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:35 | 6:35 |  | 0.76042 | 0 | -6.5833 | 1900-01-10 16:00 | 11.6667 | required modbus cable | Open |  | 11.71% | 0.10057
43 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:35 | 6:35 |  | 0.76042 | 0 | -6.5833 | 1900-01-10 16:00 | 11.6667 | required modbus cable | Open |  | 11.71% | 0.10057
44 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:35 | 6:35 |  | 0.76042 | 0 | -6.5833 | 1900-01-10 16:00 | 11.6667 | required modbus cable | Open |  | 11.71% | 0.06705
45 | 2025 | 2025 | Year_2 | Year_2 | 2024-05-01 | 31 | 2025-03-31 | 6:35 | 18:20 | 11.75 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:35 | 6:35 |  | 0.76042 | 0 | -6.5833 | 1900-01-10 16:00 | 11.6667 | required modbus cable | Open |  | 11.71% | 0.06705
46 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
47 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
48 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
49 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
50 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
51 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
52 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
53 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
54 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
55 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:24 | 6:24 |  | 0.76042 | 0 | -6.4 | 1900-01-10 20:24 | 11.85 | required modbus cable | Open |  | 11.71% | 0.10216
56 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:24 | 6:24 |  | 0.76042 | 0 | -6.4 | 1900-01-10 20:24 | 11.85 | required modbus cable | Open |  | 11.71% | 0.10216
57 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:24 | 6:24 |  | 0.76042 | 0 | -6.4 | 1900-01-10 20:24 | 11.85 | required modbus cable | Open |  | 11.71% | 0.10216
58 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:24 | 6:24 |  | 0.76042 | 0 | -6.4 | 1900-01-10 20:24 | 11.85 | required modbus cable | Open |  | 11.71% | 0.10216
59 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:24 | 6:24 |  | 0.76042 | 0 | -6.4 | 1900-01-10 20:24 | 11.85 | required modbus cable | Open |  | 11.71% | 0.068103
60 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 6:24 | 18:17 | 11.8833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:24 | 6:24 |  | 0.76042 | 0 | -6.4 | 1900-01-10 20:24 | 11.85 | required modbus cable | Open |  | 11.71% | 0.068103
61 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
62 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
63 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
64 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
65 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
66 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
67 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
68 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
69 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
70 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:27 | 6:27 |  | 0.76042 | 0 | -6.45 | 1900-01-10 19:12 | 11.8 | required modbus cable | Open |  | 11.71% | 0.10172
71 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:27 | 6:27 |  | 0.76042 | 0 | -6.45 | 1900-01-10 19:12 | 11.8 | required modbus cable | Open |  | 11.71% | 0.10172
72 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:27 | 6:27 |  | 0.76042 | 0 | -6.45 | 1900-01-10 19:12 | 11.8 | required modbus cable | Open |  | 11.71% | 0.10172
73 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:27 | 6:27 |  | 0.76042 | 0 | -6.45 | 1900-01-10 19:12 | 11.8 | required modbus cable | Open |  | 11.71% | 0.10172
74 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:27 | 6:27 |  | 0.76042 | 0 | -6.45 | 1900-01-10 19:12 | 11.8 | required modbus cable | Open |  | 11.71% | 0.067816
75 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:27 | 18:18 | 11.85 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:27 | 6:27 |  | 0.76042 | 0 | -6.45 | 1900-01-10 19:12 | 11.8 | required modbus cable | Open |  | 11.71% | 0.067816
76 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
77 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
78 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
79 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
80 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
81 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
82 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
83 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
84 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
85 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:38 | 6:38 |  | 0.76042 | 0 | -6.6333 | 1900-01-10 14:48 | 11.6167 | required modbus cable | Open |  | 11.71% | 0.10014
86 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:38 | 6:38 |  | 0.76042 | 0 | -6.6333 | 1900-01-10 14:48 | 11.6167 | required modbus cable | Open |  | 11.71% | 0.10014
87 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:38 | 6:38 |  | 0.76042 | 0 | -6.6333 | 1900-01-10 14:48 | 11.6167 | required modbus cable | Open |  | 11.71% | 0.10014
88 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:38 | 6:38 |  | 0.76042 | 0 | -6.6333 | 1900-01-10 14:48 | 11.6167 | required modbus cable | Open |  | 11.71% | 0.10014
89 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:38 | 6:38 |  | 0.76042 | 0 | -6.6333 | 1900-01-10 14:48 | 11.6167 | required modbus cable | Open |  | 11.71% | 0.066762
90 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 6:38 | 18:20 | 11.7 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:38 | 6:38 |  | 0.76042 | 0 | -6.6333 | 1900-01-10 14:48 | 11.6167 | required modbus cable | Open |  | 11.71% | 0.066762
91 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
92 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
93 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
94 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
95 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
96 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
97 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
98 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
99 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
100 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:29 | 6:29 |  | 0.76042 | 0 | -6.4833 | 1900-01-10 18:24 | 11.7667 | required modbus cable | Open |  | 11.71% | 0.10144
101 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:29 | 6:29 |  | 0.76042 | 0 | -6.4833 | 1900-01-10 18:24 | 11.7667 | required modbus cable | Open |  | 11.71% | 0.10144
102 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:29 | 6:29 |  | 0.76042 | 0 | -6.4833 | 1900-01-10 18:24 | 11.7667 | required modbus cable | Open |  | 11.71% | 0.10144
103 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:29 | 6:29 |  | 0.76042 | 0 | -6.4833 | 1900-01-10 18:24 | 11.7667 | required modbus cable | Open |  | 11.71% | 0.10144
104 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:29 | 6:29 |  | 0.76042 | 0 | -6.4833 | 1900-01-10 18:24 | 11.7667 | required modbus cable | Open |  | 11.71% | 0.067625
105 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:29 | 18:21 | 11.8667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:29 | 6:29 |  | 0.76042 | 0 | -6.4833 | 1900-01-10 18:24 | 11.7667 | required modbus cable | Open |  | 11.71% | 0.067625
106 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
107 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
108 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
109 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
110 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
111 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
112 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
113 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
114 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
115 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:23 | 6:23 |  | 0.76042 | 0 | -6.3833 | 1900-01-10 20:48 | 11.8667 | required modbus cable | Open |  | 11.71% | 0.1023
116 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:23 | 6:23 |  | 0.76042 | 0 | -6.3833 | 1900-01-10 20:48 | 11.8667 | required modbus cable | Open |  | 11.71% | 0.1023
117 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:23 | 6:23 |  | 0.76042 | 0 | -6.3833 | 1900-01-10 20:48 | 11.8667 | required modbus cable | Open |  | 11.71% | 0.1023
118 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:23 | 6:23 |  | 0.76042 | 0 | -6.3833 | 1900-01-10 20:48 | 11.8667 | required modbus cable | Open |  | 11.71% | 0.1023
119 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:23 | 6:23 |  | 0.76042 | 0 | -6.3833 | 1900-01-10 20:48 | 11.8667 | required modbus cable | Open |  | 11.71% | 0.068199
120 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:23 | 18:17 | 11.9 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:23 | 6:23 |  | 0.76042 | 0 | -6.3833 | 1900-01-10 20:48 | 11.8667 | required modbus cable | Open |  | 11.71% | 0.068199
121 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
122 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
123 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
124 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
125 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
126 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
127 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
128 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
129 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
130 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:29 | 6:29 |  | 0.76042 | 0 | -6.4833 | 1900-01-10 18:24 | 11.7667 | required modbus cable | Open |  | 11.71% | 0.10144
131 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:29 | 6:29 |  | 0.76042 | 0 | -6.4833 | 1900-01-10 18:24 | 11.7667 | required modbus cable | Open |  | 11.71% | 0.10144
132 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:29 | 6:29 |  | 0.76042 | 0 | -6.4833 | 1900-01-10 18:24 | 11.7667 | required modbus cable | Open |  | 11.71% | 0.10144
133 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:29 | 6:29 |  | 0.76042 | 0 | -6.4833 | 1900-01-10 18:24 | 11.7667 | required modbus cable | Open |  | 11.71% | 0.10144
134 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:29 | 6:29 |  | 0.76042 | 0 | -6.4833 | 1900-01-10 18:24 | 11.7667 | required modbus cable | Open |  | 11.71% | 0.067625
135 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:29 | 18:21 | 11.8667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:29 | 6:29 |  | 0.76042 | 0 | -6.4833 | 1900-01-10 18:24 | 11.7667 | required modbus cable | Open |  | 11.71% | 0.067625
136 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
137 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
138 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
139 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
140 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
141 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
142 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
143 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
144 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
145 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.10273
146 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.10273
147 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.10273
148 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.10273
149 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.068487
150 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:20 | 18:19 | 11.9833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.068487
151 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
152 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
153 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
154 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
155 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
156 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
157 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
158 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
159 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
160 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.10273
161 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.10273
162 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.10273
163 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.10273
164 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.068487
165 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 6:20 | 18:16 | 11.9333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.068487
166 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
167 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
168 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
169 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
170 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
171 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
172 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
173 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
174 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
175 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:22 | 6:22 |  | 0.76042 | 0 | -6.3667 | 1900-01-10 21:12 | 11.8833 | required modbus cable | Open |  | 11.71% | 0.10244
176 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:22 | 6:22 |  | 0.76042 | 0 | -6.3667 | 1900-01-10 21:12 | 11.8833 | required modbus cable | Open |  | 11.71% | 0.10244
177 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:22 | 6:22 |  | 0.76042 | 0 | -6.3667 | 1900-01-10 21:12 | 11.8833 | required modbus cable | Open |  | 11.71% | 0.10244
178 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:22 | 6:22 |  | 0.76042 | 0 | -6.3667 | 1900-01-10 21:12 | 11.8833 | required modbus cable | Open |  | 11.71% | 0.10244
179 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:22 | 6:22 |  | 0.76042 | 0 | -6.3667 | 1900-01-10 21:12 | 11.8833 | required modbus cable | Open |  | 11.71% | 0.068295
180 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:22 | 6:22 |  | 0.76042 | 0 | -6.3667 | 1900-01-10 21:12 | 11.8833 | required modbus cable | Open |  | 11.71% | 0.068295
181 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
182 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
183 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
184 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
185 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
186 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
187 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
188 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
189 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
190 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.10273
191 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.10273
192 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.10273
193 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.10273
194 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.068487
195 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.068487
196 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
197 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
198 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
199 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
200 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
201 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
202 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
203 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
204 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
205 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:18 | 6:18 |  | 0.76042 | 0 | -6.3 | 1900-01-10 22:48 | 11.95 | required modbus cable | Open |  | 11.71% | 0.10302
206 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:18 | 6:18 |  | 0.76042 | 0 | -6.3 | 1900-01-10 22:48 | 11.95 | required modbus cable | Open |  | 11.71% | 0.10302
207 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:18 | 6:18 |  | 0.76042 | 0 | -6.3 | 1900-01-10 22:48 | 11.95 | required modbus cable | Open |  | 11.71% | 0.10302
208 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:18 | 6:18 |  | 0.76042 | 0 | -6.3 | 1900-01-10 22:48 | 11.95 | required modbus cable | Open |  | 11.71% | 0.10302
209 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:18 | 6:18 |  | 0.76042 | 0 | -6.3 | 1900-01-10 22:48 | 11.95 | required modbus cable | Open |  | 11.71% | 0.068678
210 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:18 | 6:18 |  | 0.76042 | 0 | -6.3 | 1900-01-10 22:48 | 11.95 | required modbus cable | Open |  | 11.71% | 0.068678
211 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
212 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
213 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
214 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
215 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
216 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
217 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
218 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
219 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
220 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:22 | 6:22 |  | 0.76042 | 0 | -6.3667 | 1900-01-10 21:12 | 11.8833 | required modbus cable | Open |  | 11.71% | 0.10244
221 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:22 | 6:22 |  | 0.76042 | 0 | -6.3667 | 1900-01-10 21:12 | 11.8833 | required modbus cable | Open |  | 11.71% | 0.10244
222 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:22 | 6:22 |  | 0.76042 | 0 | -6.3667 | 1900-01-10 21:12 | 11.8833 | required modbus cable | Open |  | 11.71% | 0.10244
223 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:22 | 6:22 |  | 0.76042 | 0 | -6.3667 | 1900-01-10 21:12 | 11.8833 | required modbus cable | Open |  | 11.71% | 0.10244
224 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:22 | 6:22 |  | 0.76042 | 0 | -6.3667 | 1900-01-10 21:12 | 11.8833 | required modbus cable | Open |  | 11.71% | 0.068295
225 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:22 | 18:19 | 11.95 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:22 | 6:22 |  | 0.76042 | 0 | -6.3667 | 1900-01-10 21:12 | 11.8833 | required modbus cable | Open |  | 11.71% | 0.068295
226 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 36 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
227 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
228 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
229 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
230 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
231 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
232 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
233 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
234 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
235 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:16 | 6:16 |  | 0.76042 | 0 | -6.2667 | 1900-01-10 23:36 | 11.9833 | required modbus cable | Open |  | 11.71% | 0.1033
236 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:16 | 6:16 |  | 0.76042 | 0 | -6.2667 | 1900-01-10 23:36 | 11.9833 | required modbus cable | Open |  | 11.71% | 0.1033
237 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:16 | 6:16 |  | 0.76042 | 0 | -6.2667 | 1900-01-10 23:36 | 11.9833 | required modbus cable | Open |  | 11.71% | 0.1033
238 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:16 | 6:16 |  | 0.76042 | 0 | -6.2667 | 1900-01-10 23:36 | 11.9833 | required modbus cable | Open |  | 11.71% | 0.1033
239 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:16 | 6:16 |  | 0.76042 | 0 | -6.2667 | 1900-01-10 23:36 | 11.9833 | required modbus cable | Open |  | 11.71% | 0.06887
240 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:16 | 18:20 | 12.0667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:16 | 6:16 |  | 0.76042 | 0 | -6.2667 | 1900-01-10 23:36 | 11.9833 | required modbus cable | Open |  | 11.71% | 0.06887
241 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
242 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
243 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
244 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
245 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
246 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
247 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
248 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
249 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.10345
250 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.10345
251 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.10345
252 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.10345
253 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.068966
254 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:15 | 18:20 | 12.0833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.068966
255 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
256 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
257 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
258 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
259 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
260 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
261 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
262 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
263 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | required modbus cable | Open |  | 11.71% | 0.10374
264 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | required modbus cable | Open |  | 11.71% | 0.10374
265 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | required modbus cable | Open |  | 11.71% | 0.10374
266 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | required modbus cable | Open |  | 11.71% | 0.10374
267 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | required modbus cable | Open |  | 11.71% | 0.069157
268 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:13 | 18:26 | 12.2167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | required modbus cable | Open |  | 11.71% | 0.069157
269 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
270 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
271 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
272 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
273 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
274 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
275 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
276 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
277 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.10345
278 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.10345
279 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.10345
280 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.10345
281 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.068966
282 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 6:15 | 18:21 | 12.1 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.068966
283 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
284 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
285 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
286 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
287 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
288 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
289 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
290 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
291 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.10388
292 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.10388
293 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.10388
294 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.10388
295 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.069253
296 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:12 | 18:22 | 12.1667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.069253
297 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
298 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
299 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
300 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
301 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
302 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
303 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
304 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
305 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:18 | 6:18 |  | 0.76042 | 0 | -6.3 | 1900-01-10 22:48 | 11.95 | required modbus cable | Open |  | 11.71% | 0.10302
306 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:18 | 6:18 |  | 0.76042 | 0 | -6.3 | 1900-01-10 22:48 | 11.95 | required modbus cable | Open |  | 11.71% | 0.10302
307 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:18 | 6:18 |  | 0.76042 | 0 | -6.3 | 1900-01-10 22:48 | 11.95 | required modbus cable | Open |  | 11.71% | 0.10302
308 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:18 | 6:18 |  | 0.76042 | 0 | -6.3 | 1900-01-10 22:48 | 11.95 | required modbus cable | Open |  | 11.71% | 0.10302
309 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:18 | 6:18 |  | 0.76042 | 0 | -6.3 | 1900-01-10 22:48 | 11.95 | required modbus cable | Open |  | 11.71% | 0.068678
310 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 6:18 | 17:00 | 10.7 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:18 | 6:18 |  | 0.76042 | 0 | -6.3 | 1900-01-10 22:48 | 11.95 | required modbus cable | Open |  | 11.71% | 0.068678
311 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
312 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
313 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
314 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
315 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
316 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
317 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
318 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
319 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:26 | 6:26 |  | 0.76042 | 0 | -6.4333 | 1900-01-10 19:36 | 11.8167 | required modbus cable | Open |  | 11.71% | 0.10187
320 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:26 | 6:26 |  | 0.76042 | 0 | -6.4333 | 1900-01-10 19:36 | 11.8167 | required modbus cable | Open |  | 11.71% | 0.10187
321 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:26 | 6:26 |  | 0.76042 | 0 | -6.4333 | 1900-01-10 19:36 | 11.8167 | required modbus cable | Open |  | 11.71% | 0.10187
322 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:26 | 6:26 |  | 0.76042 | 0 | -6.4333 | 1900-01-10 19:36 | 11.8167 | required modbus cable | Open |  | 11.71% | 0.10187
323 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:26 | 6:26 |  | 0.76042 | 0 | -6.4333 | 1900-01-10 19:36 | 11.8167 | required modbus cable | Open |  | 11.71% | 0.067912
324 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:26 | 18:33 | 12.1167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:26 | 6:26 |  | 0.76042 | 0 | -6.4333 | 1900-01-10 19:36 | 11.8167 | required modbus cable | Open |  | 11.71% | 0.067912
325 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
326 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
327 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
328 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
329 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
330 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
331 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
332 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
333 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.10388
334 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.10388
335 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.10388
336 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.10388
337 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.069253
338 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:12 | 18:27 | 12.25 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.069253
339 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
340 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
341 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
342 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:08 | 6:08 |  | 0.76042 | 0 | -6.1333 | 1900-01-11 02:48 | 12.1167 | Manual tracking | Open |  | 11.71% | 0.10445
343 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
344 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
345 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
346 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
347 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
348 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
349 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
350 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
351 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
352 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:08 | 18:10 | 12.0333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:08 | 6:08 |  | 0.76042 | 0 | -6.1333 | 1900-01-11 02:48 | 12.1167 | required modbus cable | Open |  | 11.71% | 0.069636
353 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
354 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
355 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
356 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | Manual tracking | Open |  | 11.71% | 0.10273
357 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
358 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
359 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
360 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
361 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
362 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
363 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
364 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
365 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
366 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.068487
367 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
368 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
369 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
370 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | Manual tracking | Open |  | 11.71% | 0.10345
371 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
372 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
373 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
374 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
375 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
376 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
377 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
378 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
379 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
380 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 6:15 | 18:19 | 12.0667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.068966
381 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
382 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
383 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
384 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:16 | 6:16 |  | 0.76042 | 0 | -6.2667 | 1900-01-10 23:36 | 11.9833 | Manual tracking | Open |  | 11.71% | 0.1033
385 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
386 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
387 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
388 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
389 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
390 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
391 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
392 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
393 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
394 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:16 | 6:16 |  | 0.76042 | 0 | -6.2667 | 1900-01-10 23:36 | 11.9833 | required modbus cable | Open |  | 11.71% | 0.06887
395 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
396 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
397 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
398 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:08 | 6:08 |  | 0.76042 | 0 | -6.1333 | 1900-01-11 02:48 | 12.1167 | Manual tracking | Open |  | 11.71% | 0.10445
399 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
400 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
401 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
402 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
403 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
404 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
405 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
406 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
407 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
408 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:08 | 6:08 |  | 0.76042 | 0 | -6.1333 | 1900-01-11 02:48 | 12.1167 | required modbus cable | Open |  | 11.71% | 0.069636
409 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
410 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
411 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
412 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:05 | 6:05 |  | 0.76042 | 0 | -6.0833 | 1900-01-11 04:00 | 12.1667 | Manual tracking | Open |  | 11.71% | 0.10489
413 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
414 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
415 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
416 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
417 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
418 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
419 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
420 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
421 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
422 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:05 | 18:25 | 12.3333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:05 | 6:05 |  | 0.76042 | 0 | -6.0833 | 1900-01-11 04:00 | 12.1667 | required modbus cable | Open |  | 11.71% | 0.069923
423 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
424 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
425 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
426 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:30 | 6:30 |  | 0.76042 | 0 | -6.5 | 1900-01-10 18:00 | 11.75 | Manual tracking | Open |  | 11.71% | 0.10129
427 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
428 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
429 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
430 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
431 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
432 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
433 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
434 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
435 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
436 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:30 | 6:30 |  | 0.76042 | 0 | -6.5 | 1900-01-10 18:00 | 11.75 | required modbus cable | Open |  | 11.71% | 0.067529
437 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | required modbus cable | Open |  | 11.71% | 0.070115
438 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
439 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
440 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
441 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | Manual tracking | Open |  | 11.71% | 0.10517
442 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
443 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
444 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
445 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
446 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
447 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
448 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
449 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
450 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
451 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | required modbus cable | Open |  | 11.71% | 0.070115
452 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:08 | 6:08 |  | 0.76042 | 0 | -6.1333 | 1900-01-11 02:48 | 12.1167 | required modbus cable | Open |  | 11.71% | 0.069636
453 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
454 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
455 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
456 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:08 | 6:08 |  | 0.76042 | 0 | -6.1333 | 1900-01-11 02:48 | 12.1167 | Manual tracking | Open |  | 11.71% | 0.10445
457 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
458 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
459 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
460 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
461 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
462 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
463 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
464 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
465 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
466 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:08 | 18:22 | 12.2333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:08 | 6:08 |  | 0.76042 | 0 | -6.1333 | 1900-01-11 02:48 | 12.1167 | required modbus cable | Open |  | 11.71% | 0.069636
467 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:04 | 6:04 |  | 0.76042 | 0 | -6.0667 | 1900-01-11 04:24 | 12.1833 | required modbus cable | Open |  | 11.71% | 0.070019
468 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
469 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
470 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
471 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:04 | 6:04 |  | 0.76042 | 0 | -6.0667 | 1900-01-11 04:24 | 12.1833 | Manual tracking | Open |  | 11.71% | 0.10503
472 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
473 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
474 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
475 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
476 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
477 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
478 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
479 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
480 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
481 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:04 | 6:04 |  | 0.76042 | 0 | -6.0667 | 1900-01-11 04:24 | 12.1833 | required modbus cable | Open |  | 11.71% | 0.070019
482 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:07 | 6:07 |  | 0.76042 | 0 | -6.1167 | 1900-01-11 03:12 | 12.1333 | required modbus cable | Open |  | 11.71% | 0.069732
483 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
484 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
485 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
486 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:07 | 6:07 |  | 0.76042 | 0 | -6.1167 | 1900-01-11 03:12 | 12.1333 | Manual tracking | Open |  | 11.71% | 0.1046
487 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
488 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
489 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
490 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
491 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
492 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
493 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
494 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
495 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
496 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:07 | 18:28 | 12.35 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:07 | 6:07 |  | 0.76042 | 0 | -6.1167 | 1900-01-11 03:12 | 12.1333 | required modbus cable | Open |  | 11.71% | 0.069732
497 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
498 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
499 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
500 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:19 | 6:19 |  | 0.76042 | 0 | -6.3167 | 1900-01-10 22:24 | 11.9333 | Manual tracking | Open |  | 11.71% | 0.10287
501 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
502 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
503 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
504 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
505 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
506 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
507 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
508 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
509 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
510 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 6:19 | 18:27 | 12.1333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:19 | 6:19 |  | 0.76042 | 0 | -6.3167 | 1900-01-10 22:24 | 11.9333 | required modbus cable | Open |  | 11.71% | 0.068582
511 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
512 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
513 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
514 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:06 | 6:06 |  | 0.76042 | 0 | -6.1 | 1900-01-11 03:36 | 12.15 | Manual tracking | Open |  | 11.71% | 0.10474
515 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
516 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
517 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
518 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
519 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
520 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
521 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
522 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
523 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
524 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:06 | 18:28 | 12.3667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:06 | 6:06 |  | 0.76042 | 0 | -6.1 | 1900-01-11 03:36 | 12.15 | required modbus cable | Open |  | 11.71% | 0.069828
525 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
526 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
527 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
528 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:06 | 6:06 |  | 0.76042 | 0 | -6.1 | 1900-01-11 03:36 | 12.15 | Manual tracking | Open |  | 11.71% | 0.10474
529 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
530 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
531 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
532 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
533 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
534 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
535 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
536 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
537 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
538 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 6:06 | 18:32 | 12.4333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | Modbus cable issue_5meters | PCB Failure | 6:06 | 6:06 |  | 0.76042 | 0 | -6.1 | 1900-01-11 03:36 | 12.15 | required modbus cable | Open |  | 11.71% | 0.069828
539 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type5(4*42) | 0.4598% | -28 | IC2_Inv1 | G-7 | G-8 | 109 | 77 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 | 0.45833 | 0.46875 | 0 | 4.95 | 1900-01-04 04:48 | 5.2 | replaced with repaired one | Close |  | 11.71% | 0.023908
540 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type5(4*42) | 0.4598% | -28 | IC1_Inv3 | G-7 | G-8 | 100 | 33 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 | 0.47222 | 0.50694 | 0 | 5.2833 | 1900-01-05 02:48 | 6.1167 | replaced with repaired one | Close |  | 11.71% | 0.028123
541 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type5(4*42) | 0.4598% | -28 | IC1_Inv3 | G-7 | G-7 | 18 | 64 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 | 0.51389 | 0.53125 | 0 | 6.2833 | 1900-01-05 16:48 | 6.7 | replaced with repaired one | Close |  | 11.71% | 0.030805
542 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type5(4*42) | 0.4598% | -28 | IC1_Inv3 | G-1 | G-2 | 16 | 92 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 | 0.54167 | 0.57986 | 0 | 6.95 | 1900-01-06 20:48 | 7.8667 | replaced with repaired one | Close |  | 11.71% | 0.036169
543 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type5(4*42) | 0.4598% | -28 | IC2_Inv1 | G-1 | G-2 | 14 | 82 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 | 0.60278 | 0.63542 | 0 | 8.4167 | 1900-01-08 04:48 | 9.2 | replaced with repaired one | Close |  | 11.71% | 0.042299
544 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type5(4*42) | 0.4598% | -28 | IC1_Inv4 | G-1 | G-2 | 13 | 77 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 | 0.67361 | 0.69792 | 0 | 10.1167 | 1900-01-09 16:48 | 10.7 | replaced with repaired one | Close |  | 11.71% | 0.049195
545 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type5(4*42) | 0.4598% | -28 | IC2_Inv1 | G-1 | G-3 | 87 | 17 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 | 0.70833 | 0.74653 | 0 | 10.95 | 1900-01-10 20:48 | 11.8667 | replaced with repaired one | Close |  | 11.71% | 0.054559
546 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type5(4*42) | 0.4598% | -28 | IC1_Inv3 | G-1 | G-3 | 73 | 34 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 | 0.51389 | 0.53125 | 0 | 6.2833 | 1900-01-05 16:48 | 6.7 | replaced with repaired one | Close |  | 11.71% | 0.030805
547 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
548 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
549 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
550 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | Manual tracking | Open |  | 11.71% | 0.10517
551 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
552 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
553 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
554 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
555 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
556 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
557 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
558 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
559 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
560 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | required modbus cable | Open |  | 11.71% | 0
561 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
562 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
563 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
564 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | Manual tracking | Open |  | 11.71% | 0.10273
565 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
566 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
567 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
568 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
569 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
570 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
571 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
572 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
573 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
574 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 6:20 | 18:28 | 12.1333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.068487
575 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
576 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
577 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
578 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | Manual tracking | Open |  | 11.71% | 0.10517
579 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
580 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
581 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
582 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
583 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
584 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
585 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
586 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
587 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
588 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:03 | 18:28 | 12.4167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | required modbus cable | Open |  | 11.71% | 0.070115
589 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
590 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
591 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
592 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | Manual tracking | Open |  | 11.71% | 0.10517
593 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
594 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
595 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
596 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
597 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
598 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
599 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
600 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
601 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
602 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 6:03 | 18:32 | 12.4833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | required modbus cable | Open |  | 11.71% | 0.070115
603 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
604 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
605 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
606 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:00 | 6:00 |  | 0.76042 | 0 | -6 | 1900-01-11 06:00 | 12.25 | Manual tracking | Open |  | 11.71% | 0.1056
607 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
608 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
609 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
610 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
611 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
612 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
613 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
614 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
615 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
616 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:00 | 6:00 |  | 0.76042 | 0 | -6 | 1900-01-11 06:00 | 12.25 | required modbus cable | Open |  | 11.71% | 0.070402
617 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
618 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
619 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
620 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | Manual tracking | Open |  | 11.71% | 0.10517
621 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
622 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
623 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
624 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
625 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
626 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
627 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
628 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
629 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
630 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:25 | 12.3667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | required modbus cable | Open |  | 11.71% | 0.070115
631 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
632 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
633 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
634 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | Manual tracking | Open |  | 11.71% | 0.10517
635 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
636 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
637 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
638 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
639 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
640 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
641 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
642 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
643 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
644 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:03 | 18:10 | 12.1167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | required modbus cable | Open |  | 11.71% | 0.070115
645 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
646 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
647 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
648 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:06 | 6:06 |  | 0.76042 | 0 | -6.1 | 1900-01-11 03:36 | 12.15 | Manual tracking | Open |  | 11.71% | 0.10474
649 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
650 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
651 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
652 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
653 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
654 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
655 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
656 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
657 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
658 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:06 | 18:00 | 11.9 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:06 | 6:06 |  | 0.76042 | 0 | -6.1 | 1900-01-11 03:36 | 12.15 | required modbus cable | Open |  | 11.71% | 0.069828
659 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
660 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
661 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
662 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | Manual tracking | Open |  | 11.71% | 0.10345
663 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
664 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
665 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
666 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
667 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
668 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
669 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
670 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
671 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
672 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.068966
673 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
674 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
675 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
676 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:07 | 6:07 |  | 0.76042 | 0 | -6.1167 | 1900-01-11 03:12 | 12.1333 | Manual tracking | Open |  | 11.71% | 0.1046
677 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
678 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
679 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
680 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
681 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
682 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
683 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
684 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
685 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
686 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:07 | 17:38 | 11.5167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:07 | 6:07 |  | 0.76042 | 0 | -6.1167 | 1900-01-11 03:12 | 12.1333 | required modbus cable | Open |  | 11.71% | 0.069732
687 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
688 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
689 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
690 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 7:21 | 7:21 |  | 0.76042 | 0 | -7.35 | 1900-01-09 21:36 | 10.9 | Manual tracking | Open |  | 11.71% | 0.093966
691 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
692 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
693 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
694 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
695 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
696 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
697 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
698 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
699 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
700 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 7:21 | 18:28 | 11.1167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 7:21 | 7:21 |  | 0.76042 | 0 | -7.35 | 1900-01-09 21:36 | 10.9 | required modbus cable | Open |  | 11.71% | 0.062644
701 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
702 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
703 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
704 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:02 | 6:02 |  | 0.76042 | 0 | -6.0333 | 1900-01-11 05:12 | 12.2167 | Manual tracking | Open |  | 11.71% | 0.10532
705 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
706 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
707 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
708 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
709 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
710 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
711 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
712 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
713 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
714 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:02 | 6:02 |  | 0.76042 | 0 | -6.0333 | 1900-01-11 05:12 | 12.2167 | required modbus cable | Open |  | 11.71% | 0.070211
715 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
716 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
717 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
718 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:02 | 6:02 |  | 0.76042 | 0 | -6.0333 | 1900-01-11 05:12 | 12.2167 | Manual tracking | Open |  | 11.71% | 0.10532
719 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
720 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
721 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
722 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
723 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
724 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
725 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
726 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
727 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
728 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:02 | 6:02 |  | 0.76042 | 0 | -6.0333 | 1900-01-11 05:12 | 12.2167 | required modbus cable | Open |  | 11.71% | 0.070211
729 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
730 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
731 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
732 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | Manual tracking | Open |  | 11.71% | 0.10517
733 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
734 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
735 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
736 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
737 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
738 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
739 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
740 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
741 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
742 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:03 | 18:33 | 12.5 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | required modbus cable | Open |  | 11.71% | 0.070115
743 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
744 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
745 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
746 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | Manual tracking | Open |  | 11.71% | 0.10517
747 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
748 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
749 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
750 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
751 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
752 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
753 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
754 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
755 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
756 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | required modbus cable | Open |  | 11.71% | 0.070115
757 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv1 | G-1 | G-3 | 28 | 45 | Actuator | No Communication | Actuator Movemnet Blocked | 6:03 | 6:03 | 0.64583 | 0.66319 | 0 | 9.45 | 1900-01-08 20:48 | 9.8667 | Manual tracking | Open |  | 11.71% | 0.017011
758 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-7 | 70 | 46 | Actuator | No Communication | Actuator Movemnet Blocked | 6:03 | 6:03 | 0.66736 | 0.67708 | 0 | 9.9667 | 1900-01-09 04:48 | 10.2 | Manual tracking | Open |  | 11.71% | 0.017586
759 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv1 | G-1 | G-1 | 111 | 4 | Actuator | No Communication | Actuator Movemnet Blocked | 6:03 | 6:03 | 0.68056 | 0.69792 | 0 | 10.2833 | 1900-01-09 16:48 | 10.7 | Manual tracking | Open |  | 11.71% | 0.018448
760 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
761 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
762 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
763 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:57 | 5:57 |  | 0.76042 | 0 | -5.95 | 1900-01-11 07:12 | 12.3 | Manual tracking | Open |  | 11.71% | 0.10603
764 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
765 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
766 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
767 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
768 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
769 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
770 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
771 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
772 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
773 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:57 | 5:57 |  | 0.76042 | 0 | -5.95 | 1900-01-11 07:12 | 12.3 | required modbus cable | Open |  | 11.71% | 0.07069
774 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv1 | G-1 | G-3 | 28 | 45 | Actuator | No Communication | Actuator Movemnet Blocked | 5:57 | 5:57 | 0.64583 | 0.66319 | 0 | 9.55 | 1900-01-08 23:12 | 9.9667 | Manual tracking | Open |  | 11.71% | 0.017184
775 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 5:57 | 18:22 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-7 | 70 | 46 | Actuator | No Communication | Actuator Movemnet Blocked | 5:57 | 5:57 | 0.66736 | 0.67708 | 0 | 10.0667 | 1900-01-09 07:12 | 10.3 | Manual tracking | Open |  | 11.71% | 0.017759
776 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
777 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
778 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
779 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 7:04 | 7:04 |  | 0.76042 | 0 | -7.0667 | 1900-01-10 04:24 | 11.1833 | Manual tracking | Open |  | 11.71% | 0.096408
780 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
781 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
782 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
783 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
784 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
785 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
786 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
787 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
788 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
789 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure |  |  |  | 0.76042 | 0 | 0 | 1900-01-17 06:00 | 18.25 | required modbus cable | Open |  | 11.71% | 0.10489
790 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv1 | G-1 | G-3 | 28 | 45 | Actuator | No Communication | Actuator Movemnet Blocked | 7:04 | 7:04 | 0.64583 | 0.66319 | 0 | 8.4333 | 1900-01-07 20:24 | 8.85 | Manual tracking | Open |  | 11.71% | 0.015259
791 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-7 | 70 | 46 | Actuator | No Communication | Actuator Movemnet Blocked | 7:04 | 7:04 | 0.66736 | 0.67708 | 0 | 8.95 | 1900-01-08 04:24 | 9.1833 | Manual tracking | Open |  | 11.71% | 0.015833
792 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
793 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
794 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
795 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:43 | 6:43 |  | 0.76042 | 0 | -6.7167 | 1900-01-10 12:48 | 11.5333 | Manual tracking | Open |  | 11.71% | 0.099425
796 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
797 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
798 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
799 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
800 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
801 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
802 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
803 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
804 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
805 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:43 | 6:43 |  | 0.76042 | 0 | -6.7167 | 1900-01-10 12:48 | 11.5333 | required modbus cable | Open |  | 11.71% | 0.066284
806 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv3 | G-1 | G-2 | 12 | 69 | Actuator | No Communication | Actuator Movemnet Blocked | 6:43 | 6:43 | 0.64583 | 0.66319 | 0 | 8.7833 | 1900-01-08 04:48 | 9.2 | Manual tracking | Open |  | 11.71% | 0.015862
807 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
808 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
809 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
810 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | Manual tracking | Open |  | 11.71% | 0.10517
811 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
812 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
813 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
814 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
815 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
816 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
817 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
818 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
819 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
820 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | required modbus cable | Open |  | 11.71% | 0.070115
821 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv3 | G-1 | G-3 | 36 | 79 | Actuator | No Communication | Actuator Movemnet Blocked | 6:03 | 6:03 | 0.64583 | 0.66319 | 0 | 9.45 | 1900-01-08 20:48 | 9.8667 | Manual tracking | Open |  | 11.71% | 0.017011
822 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
823 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
824 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
825 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | Manual tracking | Open |  | 11.71% | 0.10517
826 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
827 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
828 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
829 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
830 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
831 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
832 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
833 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
834 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
835 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:03 | 18:40 | 12.6167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | required modbus cable | Open |  | 11.71% | 0.070115
836 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
837 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
838 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
839 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:58 | 5:58 |  | 0.76042 | 0 | -5.9667 | 1900-01-11 06:48 | 12.2833 | Manual tracking | Open |  | 11.71% | 0.10589
840 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
841 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
842 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
843 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
844 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
845 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
846 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
847 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
848 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
849 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 5:58 | 18:39 | 12.6833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:58 | 5:58 |  | 0.76042 | 0 | -5.9667 | 1900-01-11 06:48 | 12.2833 | required modbus cable | Open |  | 11.71% | 0.070594
850 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 130 | 37 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
851 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
852 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
853 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:00 | 6:00 |  | 0.76042 | 0 | -6 | 1900-01-11 06:00 | 12.25 | Manual tracking | Open |  | 11.71% | 0.1056
854 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
855 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
856 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
857 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
858 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
859 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
860 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
861 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
862 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
863 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:00 | 6:00 |  | 0.76042 | 0 | -6 | 1900-01-11 06:00 | 12.25 | required modbus cable | Open |  | 11.71% | 0.070402
864 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
865 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
866 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:53 | 5:53 |  | 0.76042 | 0 | -5.8833 | 1900-01-11 08:48 | 12.3667 | Manual tracking | Open |  | 11.71% | 0.10661
867 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
868 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
869 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
870 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
871 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
872 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
873 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
874 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
875 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
876 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:53 | 5:53 |  | 0.76042 | 0 | -5.8833 | 1900-01-11 08:48 | 12.3667 | required modbus cable | Open |  | 11.71% | 0.071073
877 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
878 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
879 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:00 | 6:00 |  | 0.76042 | 0 | -6 | 1900-01-11 06:00 | 12.25 | Manual tracking | Open |  | 11.71% | 0.1056
880 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
881 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
882 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
883 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
884 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
885 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
886 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
887 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
888 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
889 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:00 | 6:00 |  | 0.76042 | 0 | -6 | 1900-01-11 06:00 | 12.25 | required modbus cable | Open |  | 11.71% | 0.070402
890 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
891 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
892 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | Manual tracking | Open |  | 11.71% | 0.10273
893 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
894 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
895 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
896 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
897 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
898 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
899 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
900 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
901 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
902 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 6:20 | 18:35 | 12.25 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:20 | 6:20 |  | 0.76042 | 0 | -6.3333 | 1900-01-10 22:00 | 11.9167 | required modbus cable | Open |  | 11.71% | 0.068487
903 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
904 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
905 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | Manual tracking | Open |  | 11.71% | 0.10388
906 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
907 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
908 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
909 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
910 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
911 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
912 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
913 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
914 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
915 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:12 | 18:38 | 12.4333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.069253
916 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
917 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
918 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:52 | 5:52 |  | 0.76042 | 0 | -5.8667 | 1900-01-11 09:12 | 12.3833 | Manual tracking | Open |  | 11.71% | 0.10675
919 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
920 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
921 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
922 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
923 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
924 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
925 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
926 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
927 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
928 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:52 | 5:52 |  | 0.76042 | 0 | -5.8667 | 1900-01-11 09:12 | 12.3833 | required modbus cable | Open |  | 11.71% | 0.071169
929 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 5:49 | 18:34 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
930 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 5:49 | 18:34 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
931 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 5:49 | 18:34 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:49 | 5:49 |  | 0.76042 | 0 | -5.8167 | 1900-01-11 10:24 | 12.4333 | Manual tracking | Open |  | 11.71% | 0.10718
932 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 5:49 | 18:34 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
933 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 5:49 | 18:34 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
934 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 5:49 | 18:34 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
935 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 5:49 | 18:34 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
936 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 5:49 | 18:34 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
937 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 5:49 | 18:34 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
938 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 5:49 | 18:34 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
939 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 5:49 | 18:34 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
940 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 5:49 | 18:34 | 12.75 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
941 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 5:49 | 18:34 | 12.75 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:49 | 5:49 |  | 0.76042 | 0 | -5.8167 | 1900-01-11 10:24 | 12.4333 | required modbus cable | Open |  | 11.71% | 0.071456
942 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
943 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
944 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:48 | 5:48 |  | 0.76042 | 0 | -5.8 | 1900-01-11 10:48 | 12.45 | Manual tracking | Open |  | 11.71% | 0.10733
945 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
946 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
947 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
948 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
949 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
950 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
951 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
952 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
953 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
954 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:48 | 5:48 |  | 0.76042 | 0 | -5.8 | 1900-01-11 10:48 | 12.45 | required modbus cable | Open |  | 11.71% | 0.071552
955 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
956 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
957 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:51 | 5:51 |  | 0.76042 | 0 | -5.85 | 1900-01-11 09:36 | 12.4 | Manual tracking | Open |  | 11.71% | 0.1069
958 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
959 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
960 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
961 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
962 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
963 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
964 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
965 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
966 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
967 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:51 | 5:51 |  | 0.76042 | 0 | -5.85 | 1900-01-11 09:36 | 12.4 | required modbus cable | Open |  | 11.71% | 0.071264
968 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:53 | 18:26 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
969 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:53 | 18:26 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
970 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:53 | 18:26 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:53 | 5:53 |  | 0.76042 | 0 | -5.8833 | 1900-01-11 08:48 | 12.3667 | Manual tracking | Open |  | 11.71% | 0.10661
971 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:53 | 18:26 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
972 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:53 | 18:26 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
973 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:53 | 18:26 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
974 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:53 | 18:26 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
975 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:53 | 18:26 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
976 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:53 | 18:26 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
977 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:53 | 18:26 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
978 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:53 | 18:26 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
979 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:53 | 18:26 | 12.55 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
980 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:53 | 18:26 | 12.55 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:53 | 5:53 |  | 0.76042 | 0 | -5.8833 | 1900-01-11 08:48 | 12.3667 | required modbus cable | Open |  | 11.71% | 0.071073
981 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 5:57 | 18:31 | 12.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
982 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 5:57 | 18:31 | 12.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
983 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 5:57 | 18:31 | 12.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:57 | 5:57 |  | 0.76042 | 0 | -5.95 | 1900-01-11 07:12 | 12.3 | Manual tracking | Open |  | 11.71% | 0.10603
984 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 5:57 | 18:31 | 12.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
985 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 5:57 | 18:31 | 12.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
986 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 5:57 | 18:31 | 12.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
987 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 5:57 | 18:31 | 12.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
988 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 5:57 | 18:31 | 12.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
989 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 5:57 | 18:31 | 12.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
990 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 5:57 | 18:31 | 12.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
991 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 5:57 | 18:31 | 12.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
992 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 5:57 | 18:31 | 12.5667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
993 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 5:57 | 18:31 | 12.5667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:57 | 5:57 |  | 0.76042 | 0 | -5.95 | 1900-01-11 07:12 | 12.3 | required modbus cable | Open |  | 11.71% | 0.07069
994 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
995 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
996 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:01 | 6:01 |  | 0.76042 | 0 | -6.0167 | 1900-01-11 05:36 | 12.2333 | Manual tracking | Open |  | 11.71% | 0.10546
997 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
998 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
999 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1000 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1001 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1002 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1003 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1004 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1005 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1006 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:01 | 6:01 |  | 0.76042 | 0 | -6.0167 | 1900-01-11 05:36 | 12.2333 | required modbus cable | Open |  | 11.71% | 0.070307
1007 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1008 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1009 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:54 | 5:54 |  | 0.76042 | 0 | -5.9 | 1900-01-11 08:24 | 12.35 | Manual tracking | Open |  | 11.71% | 0.10647
1010 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1011 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1012 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1013 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1014 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1015 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1016 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1017 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1018 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1019 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:54 | 5:54 |  | 0.76042 | 0 | -5.9 | 1900-01-11 08:24 | 12.35 | required modbus cable | Open |  | 11.71% | 0.070977
1020 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 5:56 | 18:35 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1021 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 5:56 | 18:35 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1022 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 5:56 | 18:35 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:56 | 5:56 |  | 0.76042 | 0 | -5.9333 | 1900-01-11 07:36 | 12.3167 | Manual tracking | Open |  | 11.71% | 0.10618
1023 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 5:56 | 18:35 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1024 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 5:56 | 18:35 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1025 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 5:56 | 18:35 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1026 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 5:56 | 18:35 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1027 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 5:56 | 18:35 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1028 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 5:56 | 18:35 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1029 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 5:56 | 18:35 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1030 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 5:56 | 18:35 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1031 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 5:56 | 18:35 | 12.65 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1032 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 5:56 | 18:35 | 12.65 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:56 | 5:56 |  | 0.76042 | 0 | -5.9333 | 1900-01-11 07:36 | 12.3167 | required modbus cable | Open |  | 11.71% | 0.070785
1033 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:41 | 18:42 | 12.0167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1034 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:41 | 18:42 | 12.0167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1035 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:41 | 18:42 | 12.0167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:41 | 6:41 |  | 0.76042 | 0 | -6.6833 | 1900-01-10 13:36 | 11.5667 | Manual tracking | Open |  | 11.71% | 0.099713
1036 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:41 | 18:42 | 12.0167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1037 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:41 | 18:42 | 12.0167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1038 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:41 | 18:42 | 12.0167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1039 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:41 | 18:42 | 12.0167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1040 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:41 | 18:42 | 12.0167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1041 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:41 | 18:42 | 12.0167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1042 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:41 | 18:42 | 12.0167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1043 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:41 | 18:42 | 12.0167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1044 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:41 | 18:42 | 12.0167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1045 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:41 | 18:42 | 12.0167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:41 | 6:41 |  | 0.76042 | 0 | -6.6833 | 1900-01-10 13:36 | 11.5667 | required modbus cable | Open |  | 11.71% | 0.066475
1046 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 6:02 | 18:40 | 12.6333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1047 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 6:02 | 18:40 | 12.6333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1048 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 6:02 | 18:40 | 12.6333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:02 | 6:02 |  | 0.76042 | 0 | -6.0333 | 1900-01-11 05:12 | 12.2167 | Manual tracking | Open |  | 11.71% | 0.10532
1049 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 6:02 | 18:40 | 12.6333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1050 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 6:02 | 18:40 | 12.6333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1051 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 6:02 | 18:40 | 12.6333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1052 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 6:02 | 18:40 | 12.6333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1053 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 6:02 | 18:40 | 12.6333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1054 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 6:02 | 18:40 | 12.6333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1055 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 6:02 | 18:40 | 12.6333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1056 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 6:02 | 18:40 | 12.6333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1057 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 6:02 | 18:40 | 12.6333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1058 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 6:02 | 18:40 | 12.6333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:02 | 6:02 |  | 0.76042 | 0 | -6.0333 | 1900-01-11 05:12 | 12.2167 | required modbus cable | Open |  | 11.71% | 0.070211
1059 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1060 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1061 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 7:00 | 7:00 |  | 0.76042 | 0 | -7 | 1900-01-10 06:00 | 11.25 | Manual tracking | Open |  | 11.71% | 0.096983
1062 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1063 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1064 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1065 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1066 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1067 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1068 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1069 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1070 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1071 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 7:00 | 7:00 |  | 0.76042 | 0 | -7 | 1900-01-10 06:00 | 11.25 | required modbus cable | Open |  | 11.71% | 0.064655
1072 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1073 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1074 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:45 | 6:45 |  | 0.76042 | 0 | -6.75 | 1900-01-10 12:00 | 11.5 | Manual tracking | Open |  | 11.71% | 0.099138
1075 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1076 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1077 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1078 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1079 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1080 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1081 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1082 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1083 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1084 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:45 | 6:45 |  | 0.76042 | 0 | -6.75 | 1900-01-10 12:00 | 11.5 | required modbus cable | Open |  | 11.71% | 0.066092
1085 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1086 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1087 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:58 | 5:58 |  | 0.76042 | 0 | -5.9667 | 1900-01-11 06:48 | 12.2833 | Manual tracking | Open |  | 11.71% | 0.10589
1088 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1089 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1090 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1091 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1092 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1093 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1094 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1095 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1096 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1097 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:58 | 5:58 |  | 0.76042 | 0 | -5.9667 | 1900-01-11 06:48 | 12.2833 | required modbus cable | Open |  | 11.71% | 0.070594
1098 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1099 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1100 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | Manual tracking | Open |  | 11.71% | 0.10517
1101 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1102 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1103 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1104 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1105 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1106 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1107 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1108 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1109 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1110 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | required modbus cable | Open |  | 11.71% | 0.070115
1111 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | replaced with spare repaired one | Close |  | 11.71% | 0
1112 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv2 | G-01 | G-02 | 4 | 18 | MSAT200_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | replaced with spare repaired one | Close |  | 11.71% | 0
1113 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-07 | G-07 | 61 | 3 | MSAT200_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | replaced with spare repaired one | Close |  | 11.71% | 0
1114 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 32 | 64 | MSAT200_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | replaced with spare repaired one | Close |  | 11.71% | 0
1115 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-02 | 11 | 64 | MSAT200_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | replaced with spare repaired one | Close |  | 11.71% | 0
1116 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv2 | G-01 | G-03 | 20 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | replaced with spare repaired one | Close |  | 11.71% | 0
1117 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC2_Inv1 | G-08 | G-08 | 103 | 49 | MSAT200_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | replaced with spare repaired one | Close |  | 11.71% | 0
1118 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:03 | 18:47 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC2_Inv2 | G-08 | G-08 | 81 | 118 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | replaced with spare repaired one | Close |  | 11.71% | 0
1119 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1120 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1121 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:00 | 6:00 |  | 0.76042 | 0 | -6 | 1900-01-11 06:00 | 12.25 | Manual tracking | Open |  | 11.71% | 0.1056
1122 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1123 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1124 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1125 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1126 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1127 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1128 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1129 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1130 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1131 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:00 | 6:00 |  | 0.76042 | 0 | -6 | 1900-01-11 06:00 | 12.25 | required modbus cable | Open |  | 11.71% | 0.070402
1132 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1133 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1134 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:11 | 6:11 |  | 0.76042 | 0 | -6.1833 | 1900-01-11 01:36 | 12.0667 | Manual tracking | Open |  | 11.71% | 0.10402
1135 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1136 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1137 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1138 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1139 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1140 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1141 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1142 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1143 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1144 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:11 | 6:11 |  | 0.76042 | 0 | -6.1833 | 1900-01-11 01:36 | 12.0667 | required modbus cable | Open |  | 11.71% | 0.069349
1145 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 5:58 | 18:48 | 12.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1146 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 5:58 | 18:48 | 12.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1147 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 5:58 | 18:48 | 12.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:58 | 5:58 |  | 0.76042 | 0 | -5.9667 | 1900-01-11 06:48 | 12.2833 | Manual tracking | Open |  | 11.71% | 0.10589
1148 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 5:58 | 18:48 | 12.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1149 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 5:58 | 18:48 | 12.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1150 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 5:58 | 18:48 | 12.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1151 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 5:58 | 18:48 | 12.8333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1152 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 5:58 | 18:48 | 12.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1153 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 5:58 | 18:48 | 12.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1154 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 5:58 | 18:48 | 12.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1155 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 5:58 | 18:48 | 12.8333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1156 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 5:58 | 18:48 | 12.8333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1157 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 5:58 | 18:48 | 12.8333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:58 | 5:58 |  | 0.76042 | 0 | -5.9667 | 1900-01-11 06:48 | 12.2833 | required modbus cable | Open |  | 11.71% | 0.070594
1158 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1159 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1160 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:52 | 5:52 |  | 0.76042 | 0 | -5.8667 | 1900-01-11 09:12 | 12.3833 | Manual tracking | Open |  | 11.71% | 0.10675
1161 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1162 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1163 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1164 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1165 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1166 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1167 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1168 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1169 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1170 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:52 | 5:52 |  | 0.76042 | 0 | -5.8667 | 1900-01-11 09:12 | 12.3833 | required modbus cable | Open |  | 11.71% | 0.071169
1171 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1172 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1173 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:58 | 5:58 |  | 0.76042 | 0 | -5.9667 | 1900-01-11 06:48 | 12.2833 | Manual tracking | Open |  | 11.71% | 0.10589
1174 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1175 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1176 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1177 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1178 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1179 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1180 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1181 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1182 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1183 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:58 | 5:58 |  | 0.76042 | 0 | -5.9667 | 1900-01-11 06:48 | 12.2833 | required modbus cable | Open |  | 11.71% | 0.070594
1184 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1185 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1186 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:02 | 6:02 |  | 0.76042 | 0 | -6.0333 | 1900-01-11 05:12 | 12.2167 | Manual tracking | Open |  | 11.71% | 0.10532
1187 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1188 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1189 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1190 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1191 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1192 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1193 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1194 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1195 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1196 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 6:02 | 18:38 | 12.6 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:02 | 6:02 |  | 0.76042 | 0 | -6.0333 | 1900-01-11 05:12 | 12.2167 | required modbus cable | Open |  | 11.71% | 0.070211
1197 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 6:01 | 18:38 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1198 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 6:01 | 18:38 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1199 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 6:01 | 18:38 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:01 | 6:01 |  | 0.76042 | 0 | -6.0167 | 1900-01-11 05:36 | 12.2333 | Manual tracking | Open |  | 11.71% | 0.10546
1200 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 6:01 | 18:38 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1201 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 6:01 | 18:38 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1202 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 6:01 | 18:38 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1203 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 6:01 | 18:38 | 12.6167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1204 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 6:01 | 18:38 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1205 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 6:01 | 18:38 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1206 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 6:01 | 18:38 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1207 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 6:01 | 18:38 | 12.6167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1208 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 6:01 | 18:38 | 12.6167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1209 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 6:01 | 18:38 | 12.6167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:01 | 6:01 |  | 0.76042 | 0 | -6.0167 | 1900-01-11 05:36 | 12.2333 | required modbus cable | Open |  | 11.71% | 0.070307
1210 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1211 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1212 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:55 | 5:55 |  | 0.76042 | 0 | -5.9167 | 1900-01-11 08:00 | 12.3333 | Manual tracking | Open |  | 11.71% | 0.10632
1213 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1214 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1215 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1216 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1217 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1218 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1219 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1220 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1221 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1222 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 5:55 | 18:35 | 12.6667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:55 | 5:55 |  | 0.76042 | 0 | -5.9167 | 1900-01-11 08:00 | 12.3333 | required modbus cable | Open |  | 11.71% | 0.070881
1223 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 5:57 | 18:30 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1224 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 5:57 | 18:30 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1225 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 5:57 | 18:30 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:57 | 5:57 |  | 0.76042 | 0 | -5.95 | 1900-01-11 07:12 | 12.3 | Manual tracking | Open |  | 11.71% | 0.10603
1226 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 5:57 | 18:30 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1227 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 5:57 | 18:30 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1228 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 5:57 | 18:30 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1229 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 5:57 | 18:30 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1230 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 5:57 | 18:30 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1231 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 5:57 | 18:30 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1232 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 5:57 | 18:30 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1233 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 5:57 | 18:30 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1234 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 5:57 | 18:30 | 12.55 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1235 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 5:57 | 18:30 | 12.55 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:57 | 5:57 |  | 0.76042 | 0 | -5.95 | 1900-01-11 07:12 | 12.3 | required modbus cable | Open |  | 11.71% | 0.07069
1236 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:05 | 18:30 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1237 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:05 | 18:30 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1238 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:05 | 18:30 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:05 | 6:05 |  | 0.76042 | 0 | -6.0833 | 1900-01-11 04:00 | 12.1667 | Manual tracking | Open |  | 11.71% | 0.10489
1239 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:05 | 18:30 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1240 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:05 | 18:30 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1241 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:05 | 18:30 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1242 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:05 | 18:30 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1243 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:05 | 18:30 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1244 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:05 | 18:30 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1245 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:05 | 18:30 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1246 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:05 | 18:30 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1247 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:05 | 18:30 | 12.4167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1248 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:05 | 18:30 | 12.4167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:05 | 6:05 |  | 0.76042 | 0 | -6.0833 | 1900-01-11 04:00 | 12.1667 | required modbus cable | Open |  | 11.71% | 0.069923
1249 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1250 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1251 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:06 | 6:06 |  | 0.76042 | 0 | -6.1 | 1900-01-11 03:36 | 12.15 | Manual tracking | Open |  | 11.71% | 0.10474
1252 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1253 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1254 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1255 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1256 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1257 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1258 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1259 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1260 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1261 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:06 | 6:06 |  | 0.76042 | 0 | -6.1 | 1900-01-11 03:36 | 12.15 | required modbus cable | Open |  | 11.71% | 0.069828
1262 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:10 | 18:45 | 12.5833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1263 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:10 | 18:45 | 12.5833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1264 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:10 | 18:45 | 12.5833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:10 | 6:10 |  | 0.76042 | 0 | -6.1667 | 1900-01-11 02:00 | 12.0833 | Manual tracking | Open |  | 11.71% | 0.10417
1265 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:10 | 18:45 | 12.5833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1266 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:10 | 18:45 | 12.5833 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1267 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:10 | 18:45 | 12.5833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1268 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:10 | 18:45 | 12.5833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1269 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:10 | 18:45 | 12.5833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1270 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:10 | 18:45 | 12.5833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1271 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:10 | 18:45 | 12.5833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1272 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:10 | 18:45 | 12.5833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1273 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:10 | 18:45 | 12.5833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1274 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:10 | 18:45 | 12.5833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:10 | 6:10 |  | 0.76042 | 0 | -6.1667 | 1900-01-11 02:00 | 12.0833 | required modbus cable | Open |  | 11.71% | 0.069444
1275 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 6:02 | 18:48 | 12.7667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1276 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 6:02 | 18:48 | 12.7667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1277 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 6:02 | 18:48 | 12.7667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:02 | 6:02 |  | 0.76042 | 0 | -6.0333 | 1900-01-11 05:12 | 12.2167 | Manual tracking | Open |  | 11.71% | 0.10532
1278 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 6:02 | 18:48 | 12.7667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1279 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 6:02 | 18:48 | 12.7667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1280 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 6:02 | 18:48 | 12.7667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1281 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 6:02 | 18:48 | 12.7667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1282 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 6:02 | 18:48 | 12.7667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1283 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 6:02 | 18:48 | 12.7667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1284 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 6:02 | 18:48 | 12.7667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1285 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 6:02 | 18:48 | 12.7667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1286 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 6:02 | 18:48 | 12.7667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1287 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 6:02 | 18:48 | 12.7667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:02 | 6:02 |  | 0.76042 | 0 | -6.0333 | 1900-01-11 05:12 | 12.2167 | required modbus cable | Open |  | 11.71% | 0.070211
1288 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 6:02 | 18:50 | 12.8 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1289 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 6:02 | 18:50 | 12.8 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1290 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 6:02 | 18:50 | 12.8 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:02 | 6:02 |  | 0.76042 | 0 | -6.0333 | 1900-01-11 05:12 | 12.2167 | Manual tracking | Open |  | 11.71% | 0.10532
1291 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 6:02 | 18:50 | 12.8 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1292 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 6:02 | 18:50 | 12.8 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1293 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 6:02 | 18:50 | 12.8 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1294 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 6:02 | 18:50 | 12.8 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1295 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 6:02 | 18:50 | 12.8 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1296 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 6:02 | 18:50 | 12.8 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1297 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 6:02 | 18:50 | 12.8 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1298 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 6:02 | 18:50 | 12.8 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1299 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 6:02 | 18:50 | 12.8 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1300 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 6:02 | 18:50 | 12.8 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:02 | 6:02 |  | 0.76042 | 0 | -6.0333 | 1900-01-11 05:12 | 12.2167 | required modbus cable | Open |  | 11.71% | 0.070211
1301 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 5:59 | 18:38 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1302 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 5:59 | 18:38 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1303 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 5:59 | 18:38 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:59 | 5:59 |  | 0.76042 | 0 | -5.9833 | 1900-01-11 06:24 | 12.2667 | Manual tracking | Open |  | 11.71% | 0.10575
1304 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 5:59 | 18:38 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1305 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 5:59 | 18:38 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1306 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 5:59 | 18:38 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1307 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 5:59 | 18:38 | 12.65 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1308 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 5:59 | 18:38 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1309 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 5:59 | 18:38 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1310 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 5:59 | 18:38 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1311 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 5:59 | 18:38 | 12.65 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1312 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 5:59 | 18:38 | 12.65 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1313 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 5:59 | 18:38 | 12.65 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:59 | 5:59 |  | 0.76042 | 0 | -5.9833 | 1900-01-11 06:24 | 12.2667 | required modbus cable | Open |  | 11.71% | 0.070498
1314 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:16 | 17:52 | 11.6 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1315 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:16 | 17:52 | 11.6 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1316 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:16 | 17:52 | 11.6 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:16 | 6:16 |  | 0.76042 | 0 | -6.2667 | 1900-01-10 23:36 | 11.9833 | Manual tracking | Open |  | 11.71% | 0.1033
1317 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:16 | 17:52 | 11.6 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1318 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:16 | 17:52 | 11.6 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1319 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:16 | 17:52 | 11.6 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1320 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:16 | 17:52 | 11.6 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1321 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:16 | 17:52 | 11.6 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1322 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:16 | 17:52 | 11.6 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1323 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:16 | 17:52 | 11.6 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1324 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:16 | 17:52 | 11.6 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1325 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:16 | 17:52 | 11.6 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1326 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:16 | 17:52 | 11.6 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:16 | 6:16 |  | 0.76042 | 0 | -6.2667 | 1900-01-10 23:36 | 11.9833 | required modbus cable | Open |  | 11.71% | 0.06887
1327 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 6:12 | 18:30 | 12.3 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1328 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 6:12 | 18:30 | 12.3 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1329 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 6:12 | 18:30 | 12.3 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | Manual tracking | Open |  | 11.71% | 0.10388
1330 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 6:12 | 18:30 | 12.3 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1331 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 6:12 | 18:30 | 12.3 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1332 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 6:12 | 18:30 | 12.3 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1333 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 6:12 | 18:30 | 12.3 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1334 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 6:12 | 18:30 | 12.3 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1335 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 6:12 | 18:30 | 12.3 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1336 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 6:12 | 18:30 | 12.3 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1337 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 6:12 | 18:30 | 12.3 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1338 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 6:12 | 18:30 | 12.3 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1339 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 6:12 | 18:30 | 12.3 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.069253
1340 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:19 | 18:48 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked | 6:19 | 6:19 |  |  | 0 | -6.3167 | -6.3167 | -6.3167 | Manual tracking | Open |  | 11.71% | -0.010891
1341 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:19 | 18:48 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked | 6:19 | 6:19 |  |  | 0 | -6.3167 | -6.3167 | -6.3167 | Manual tracking | Open |  | 11.71% | -0.010891
1342 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:19 | 18:48 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:19 | 6:19 |  | 0.76042 | 0 | -6.3167 | 1900-01-10 22:24 | 11.9333 | Manual tracking | Open |  | 11.71% | 0.10287
1343 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:19 | 18:48 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked | 6:19 | 6:19 |  |  | 0 | -6.3167 | -6.3167 | -6.3167 | Manual tracking | Open |  | 11.71% | -0.010891
1344 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:19 | 18:48 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked | 6:19 | 6:19 |  |  | 0 | -6.3167 | -6.3167 | -6.3167 | Manual tracking | Open |  | 11.71% | -0.010891
1345 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:19 | 18:48 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked | 6:19 | 6:19 |  |  | 0 | -6.3167 | -6.3167 | -6.3167 | Manual tracking | Open |  | 11.71% | -0.010891
1346 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:19 | 18:48 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked | 6:19 | 6:19 |  |  | 0 | -6.3167 | -6.3167 | -6.3167 | Manual tracking | Open |  | 11.71% | -0.010891
1347 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:19 | 18:48 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure | 6:19 | 6:19 |  |  | 0 | -6.3167 | -6.3167 | -6.3167 | Manual tracking | Open |  | 11.71% | -0.054454
1348 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:19 | 18:48 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure | 6:19 | 6:19 |  |  | 0 | -6.3167 | -6.3167 | -6.3167 | Manual tracking | Open |  | 11.71% | -0.054454
1349 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:19 | 18:48 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure | 6:19 | 6:19 |  |  | 0 | -6.3167 | -6.3167 | -6.3167 | Manual tracking | Open |  | 11.71% | -0.054454
1350 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:19 | 18:48 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure | 6:19 | 6:19 |  |  | 0 | -6.3167 | -6.3167 | -6.3167 | Manual tracking | Open |  | 11.71% | -0.054454
1351 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:19 | 18:48 | 12.4833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure | 6:19 | 6:19 |  |  | 0 | -6.3167 | -6.3167 | -6.3167 | Manual tracking | Open |  | 11.71% | -0.036303
1352 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:19 | 18:48 | 12.4833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:19 | 6:19 |  | 0.76042 | 0 | -6.3167 | 1900-01-10 22:24 | 11.9333 | required modbus cable | Open |  | 11.71% | 0.068582
1353 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 6:11 | 18:35 | 12.4 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1354 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 6:11 | 18:35 | 12.4 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1355 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 6:11 | 18:35 | 12.4 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:11 | 6:11 |  | 0.76042 | 0 | -6.1833 | 1900-01-11 01:36 | 12.0667 | Manual tracking | Open |  | 11.71% | 0.10402
1356 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 6:11 | 18:35 | 12.4 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1357 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 6:11 | 18:35 | 12.4 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1358 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 6:11 | 18:35 | 12.4 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1359 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 6:11 | 18:35 | 12.4 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1360 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 6:11 | 18:35 | 12.4 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1361 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 6:11 | 18:35 | 12.4 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1362 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 6:11 | 18:35 | 12.4 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1363 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 6:11 | 18:35 | 12.4 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1364 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 6:11 | 18:35 | 12.4 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1365 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 6:11 | 18:35 | 12.4 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:11 | 6:11 |  | 0.76042 | 0 | -6.1833 | 1900-01-11 01:36 | 12.0667 | required modbus cable | Open |  | 11.71% | 0.069349
1366 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:05 | 18:33 | 12.4667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1367 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:05 | 18:33 | 12.4667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1368 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:05 | 18:33 | 12.4667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:05 | 6:05 |  | 0.76042 | 0 | -6.0833 | 1900-01-11 04:00 | 12.1667 | Manual tracking | Open |  | 11.71% | 0.10489
1369 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:05 | 18:33 | 12.4667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1370 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:05 | 18:33 | 12.4667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1371 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:05 | 18:33 | 12.4667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1372 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:05 | 18:33 | 12.4667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1373 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:05 | 18:33 | 12.4667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1374 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:05 | 18:33 | 12.4667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1375 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:05 | 18:33 | 12.4667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1376 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:05 | 18:33 | 12.4667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1377 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:05 | 18:33 | 12.4667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1378 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:05 | 18:33 | 12.4667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:05 | 6:05 |  | 0.76042 | 0 | -6.0833 | 1900-01-11 04:00 | 12.1667 | required modbus cable | Open |  | 11.71% | 0.069923
1379 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 5:59 | 18:40 | 12.6833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1380 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 5:59 | 18:40 | 12.6833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1381 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 5:59 | 18:40 | 12.6833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 5:59 | 5:59 |  | 0.76042 | 0 | -5.9833 | 1900-01-11 06:24 | 12.2667 | Manual tracking | Open |  | 11.71% | 0.10575
1382 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 5:59 | 18:40 | 12.6833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1383 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 5:59 | 18:40 | 12.6833 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1384 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 5:59 | 18:40 | 12.6833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1385 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 5:59 | 18:40 | 12.6833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1386 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 5:59 | 18:40 | 12.6833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1387 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 5:59 | 18:40 | 12.6833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1388 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 5:59 | 18:40 | 12.6833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1389 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 5:59 | 18:40 | 12.6833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1390 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 5:59 | 18:40 | 12.6833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1391 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 5:59 | 18:40 | 12.6833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 5:59 | 5:59 |  | 0.76042 | 0 | -5.9833 | 1900-01-11 06:24 | 12.2667 | required modbus cable | Open |  | 11.71% | 0.070498
1392 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:15 | 18:40 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1393 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:15 | 18:40 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1394 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:15 | 18:40 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | Manual tracking | Open |  | 11.71% | 0.10345
1395 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:15 | 18:40 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1396 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:15 | 18:40 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1397 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:15 | 18:40 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1398 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:15 | 18:40 | 12.4167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1399 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:15 | 18:40 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1400 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:15 | 18:40 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1401 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:15 | 18:40 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1402 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:15 | 18:40 | 12.4167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1403 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:15 | 18:40 | 12.4167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1404 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:15 | 18:40 | 12.4167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:15 | 6:15 |  | 0.76042 | 0 | -6.25 | 1900-01-11 | 12 | required modbus cable | Open |  | 11.71% | 0.068966
1405 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 6:14 | 18:45 | 12.5167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1406 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 6:14 | 18:45 | 12.5167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1407 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 6:14 | 18:45 | 12.5167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:14 | 6:14 |  | 0.76042 | 0 | -6.2333 | 1900-01-11 00:24 | 12.0167 | Manual tracking | Open |  | 11.71% | 0.10359
1408 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 6:14 | 18:45 | 12.5167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1409 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 6:14 | 18:45 | 12.5167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1410 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 6:14 | 18:45 | 12.5167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1411 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 6:14 | 18:45 | 12.5167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1412 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 6:14 | 18:45 | 12.5167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1413 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 6:14 | 18:45 | 12.5167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1414 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 6:14 | 18:45 | 12.5167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1415 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 6:14 | 18:45 | 12.5167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1416 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 6:14 | 18:45 | 12.5167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1417 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 6:14 | 18:45 | 12.5167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:14 | 6:14 |  | 0.76042 | 0 | -6.2333 | 1900-01-11 00:24 | 12.0167 | required modbus cable | Open |  | 11.71% | 0.069061
1418 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 6:12 | 18:42 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1419 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 6:12 | 18:42 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1420 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 6:12 | 18:42 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | Manual tracking | Open |  | 11.71% | 0.10388
1421 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 6:12 | 18:42 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1422 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 6:12 | 18:42 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1423 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 6:12 | 18:42 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1424 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 6:12 | 18:42 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1425 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 6:12 | 18:42 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1426 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 6:12 | 18:42 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1427 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 6:12 | 18:42 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1428 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 6:12 | 18:42 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1429 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 6:12 | 18:42 | 12.5 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1430 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 6:12 | 18:42 | 12.5 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.069253
1431 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 6:13 | 18:32 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1432 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 6:13 | 18:32 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1433 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 6:13 | 18:32 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | Manual tracking | Open |  | 11.71% | 0.10374
1434 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 6:13 | 18:32 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1435 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 6:13 | 18:32 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1436 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 6:13 | 18:32 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1437 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 6:13 | 18:32 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1438 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 6:13 | 18:32 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1439 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 6:13 | 18:32 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1440 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 6:13 | 18:32 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1441 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 6:13 | 18:32 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1442 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 6:13 | 18:32 | 12.3167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1443 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 6:13 | 18:32 | 12.3167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:13 | 6:13 |  | 0.76042 | 0 | -6.2167 | 1900-01-11 00:48 | 12.0333 | required modbus cable | Open |  | 11.71% | 0.069157
1444 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:06 | 18:53 | 12.7833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1445 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:06 | 18:53 | 12.7833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1446 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:06 | 18:53 | 12.7833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:06 | 6:06 |  | 0.76042 | 0 | -6.1 | 1900-01-11 03:36 | 12.15 | Manual tracking | Open |  | 11.71% | 0.10474
1447 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:06 | 18:53 | 12.7833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1448 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:06 | 18:53 | 12.7833 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1449 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:06 | 18:53 | 12.7833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1450 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:06 | 18:53 | 12.7833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1451 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:06 | 18:53 | 12.7833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1452 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:06 | 18:53 | 12.7833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1453 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:06 | 18:53 | 12.7833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1454 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:06 | 18:53 | 12.7833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1455 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:06 | 18:53 | 12.7833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1456 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-10 | 6:06 | 18:53 | 12.7833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:06 | 6:06 |  | 0.76042 | 0 | -6.1 | 1900-01-11 03:36 | 12.15 | required modbus cable | Open |  | 11.71% | 0.069828
1457 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 6:07 | 18:40 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1458 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 6:07 | 18:40 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1459 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 6:07 | 18:40 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:07 | 6:07 |  | 0.76042 | 0 | -6.1167 | 1900-01-11 03:12 | 12.1333 | Manual tracking | Open |  | 11.71% | 0.1046
1460 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 6:07 | 18:40 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1461 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 6:07 | 18:40 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1462 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 6:07 | 18:40 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1463 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 6:07 | 18:40 | 12.55 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1464 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 6:07 | 18:40 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1465 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 6:07 | 18:40 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1466 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 6:07 | 18:40 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1467 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 6:07 | 18:40 | 12.55 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1468 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 6:07 | 18:40 | 12.55 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1469 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-11 | 6:07 | 18:40 | 12.55 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:07 | 6:07 |  | 0.76042 | 0 | -6.1167 | 1900-01-11 03:12 | 12.1333 | required modbus cable | Open |  | 11.71% | 0.069732
1470 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 6:06 | 18:50 | 12.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1471 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 6:06 | 18:50 | 12.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1472 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 6:06 | 18:50 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:06 | 6:06 |  | 0.76042 | 0 | -6.1 | 1900-01-11 03:36 | 12.15 | Manual tracking | Open |  | 11.71% | 0.10474
1473 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 6:06 | 18:50 | 12.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1474 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 6:06 | 18:50 | 12.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1475 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 6:06 | 18:50 | 12.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1476 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 6:06 | 18:50 | 12.7333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1477 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 6:06 | 18:50 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1478 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 6:06 | 18:50 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1479 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 6:06 | 18:50 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1480 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 6:06 | 18:50 | 12.7333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1481 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 6:06 | 18:50 | 12.7333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1482 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-12 | 6:06 | 18:50 | 12.7333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:06 | 6:06 |  | 0.76042 | 0 | -6.1 | 1900-01-11 03:36 | 12.15 | required modbus cable | Open |  | 11.71% | 0.069828
1483 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:03 | 18:46 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1484 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:03 | 18:46 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1485 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:03 | 18:46 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | Manual tracking | Open |  | 11.71% | 0.10517
1486 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:03 | 18:46 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1487 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:03 | 18:46 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1488 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:03 | 18:46 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1489 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:03 | 18:46 | 12.7167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1490 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:03 | 18:46 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1491 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:03 | 18:46 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1492 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:03 | 18:46 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1493 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:03 | 18:46 | 12.7167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1494 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:03 | 18:46 | 12.7167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1495 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-13 | 6:03 | 18:46 | 12.7167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | required modbus cable | Open |  | 11.71% | 0.070115
1496 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 6:03 | 18:48 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1497 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 6:03 | 18:48 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1498 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 6:03 | 18:48 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | Manual tracking | Open |  | 11.71% | 0.10517
1499 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 6:03 | 18:48 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1500 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 6:03 | 18:48 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1501 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 6:03 | 18:48 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1502 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 6:03 | 18:48 | 12.75 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1503 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 6:03 | 18:48 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1504 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 6:03 | 18:48 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1505 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 6:03 | 18:48 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1506 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 6:03 | 18:48 | 12.75 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1507 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 6:03 | 18:48 | 12.75 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1508 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-14 | 6:03 | 18:48 | 12.75 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:03 | 6:03 |  | 0.76042 | 0 | -6.05 | 1900-01-11 04:48 | 12.2 | required modbus cable | Open |  | 11.71% | 0.070115
1509 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1510 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1511 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:11 | 6:11 |  | 0.76042 | 0 | -6.1833 | 1900-01-11 01:36 | 12.0667 | Manual tracking | Open |  | 11.71% | 0.10402
1512 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1513 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1514 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1515 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1516 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1517 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1518 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1519 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1520 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1521 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-15 | 6:11 | 18:53 | 12.7 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:11 | 6:11 |  | 0.76042 | 0 | -6.1833 | 1900-01-11 01:36 | 12.0667 | required modbus cable | Open |  | 11.71% | 0.069349
1522 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 6:05 | 18:24 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1523 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 6:05 | 18:24 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1524 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 6:05 | 18:24 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:05 | 6:05 |  | 0.76042 | 0 | -6.0833 | 1900-01-11 04:00 | 12.1667 | Manual tracking | Open |  | 11.71% | 0.10489
1525 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 6:05 | 18:24 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1526 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 6:05 | 18:24 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1527 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 6:05 | 18:24 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1528 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 6:05 | 18:24 | 12.3167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1529 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 6:05 | 18:24 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1530 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 6:05 | 18:24 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1531 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 6:05 | 18:24 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1532 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 6:05 | 18:24 | 12.3167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1533 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 6:05 | 18:24 | 12.3167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1534 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-16 | 6:05 | 18:24 | 12.3167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:05 | 6:05 |  | 0.76042 | 0 | -6.0833 | 1900-01-11 04:00 | 12.1667 | required modbus cable | Open |  | 11.71% | 0.069923
1535 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 6:12 | 18:42 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1536 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 6:12 | 18:42 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1537 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 6:12 | 18:42 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | Manual tracking | Open |  | 11.71% | 0.10388
1538 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 6:12 | 18:42 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1539 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 6:12 | 18:42 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1540 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 6:12 | 18:42 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1541 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 6:12 | 18:42 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1542 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 6:12 | 18:42 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1543 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 6:12 | 18:42 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1544 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 6:12 | 18:42 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1545 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 6:12 | 18:42 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1546 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 6:12 | 18:42 | 12.5 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1547 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-17 | 6:12 | 18:42 | 12.5 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:12 | 6:12 |  | 0.76042 | 0 | -6.2 | 1900-01-11 01:12 | 12.05 | required modbus cable | Open |  | 11.71% | 0.069253
1548 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 6:10 | 17:11 | 11.0167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1549 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 6:10 | 17:11 | 11.0167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1550 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 6:10 | 17:11 | 11.0167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:10 | 6:10 |  | 0.76042 | 0 | -6.1667 | 1900-01-11 02:00 | 12.0833 | Manual tracking | Open |  | 11.71% | 0.10417
1551 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 6:10 | 17:11 | 11.0167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1552 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 6:10 | 17:11 | 11.0167 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1553 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 6:10 | 17:11 | 11.0167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1554 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 6:10 | 17:11 | 11.0167 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1555 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 6:10 | 17:11 | 11.0167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1556 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 6:10 | 17:11 | 11.0167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1557 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 6:10 | 17:11 | 11.0167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1558 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 6:10 | 17:11 | 11.0167 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1559 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 6:10 | 17:11 | 11.0167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1560 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-18 | 6:10 | 17:11 | 11.0167 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:10 | 6:10 |  | 0.76042 | 0 | -6.1667 | 1900-01-11 02:00 | 12.0833 | required modbus cable | Open |  | 11.71% | 0.069444
1561 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 6:10 | 18:40 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1562 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 6:10 | 18:40 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1563 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 6:10 | 18:40 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:10 | 6:10 |  | 0.76042 | 0 | -6.1667 | 1900-01-11 02:00 | 12.0833 | Manual tracking | Open |  | 11.71% | 0.10417
1564 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 6:10 | 18:40 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1565 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 6:10 | 18:40 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1566 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 6:10 | 18:40 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1567 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 6:10 | 18:40 | 12.5 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1568 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 6:10 | 18:40 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1569 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 6:10 | 18:40 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1570 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 6:10 | 18:40 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1571 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 6:10 | 18:40 | 12.5 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1572 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 6:10 | 18:40 | 12.5 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1573 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-19 | 6:10 | 18:40 | 12.5 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:10 | 6:10 |  | 0.76042 | 0 | -6.1667 | 1900-01-11 02:00 | 12.0833 | required modbus cable | Open |  | 11.71% | 0.069444
1574 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1575 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1576 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:14 | 6:14 |  | 0.76042 | 0 | -6.2333 | 1900-01-11 00:24 | 12.0167 | Manual tracking | Open |  | 11.71% | 0.10359
1577 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1578 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1579 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1580 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1581 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1582 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1583 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1584 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1585 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1586 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:14 | 6:14 |  | 0.76042 | 0 | -6.2333 | 1900-01-11 00:24 | 12.0167 | required modbus cable | Open |  | 11.71% | 0.069061
1587 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 6:09 | 17:11 | 11.0333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1588 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 6:09 | 17:11 | 11.0333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1589 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 6:09 | 17:11 | 11.0333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:09 | 6:09 |  | 0.76042 | 0 | -6.15 | 1900-01-11 02:24 | 12.1 | Manual tracking | Open |  | 11.71% | 0.10431
1590 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 6:09 | 17:11 | 11.0333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1591 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 6:09 | 17:11 | 11.0333 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1592 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 6:09 | 17:11 | 11.0333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1593 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 6:09 | 17:11 | 11.0333 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1594 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 6:09 | 17:11 | 11.0333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1595 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 6:09 | 17:11 | 11.0333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1596 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 6:09 | 17:11 | 11.0333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1597 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 6:09 | 17:11 | 11.0333 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1598 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 6:09 | 17:11 | 11.0333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1599 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-21 | 6:09 | 17:11 | 11.0333 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:09 | 6:09 |  | 0.76042 | 0 | -6.15 | 1900-01-11 02:24 | 12.1 | required modbus cable | Open |  | 11.71% | 0.06954
1600 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 38 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1601 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv4 | G-5 | G-5 | 131 | 39 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1602 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-5 | G-4 | 133 | 26 | MSAT100_PCB | No Communication | ccu failure | 6:10 | 6:10 |  | 0.76042 | 0 | -6.1667 | 1900-01-11 02:00 | 12.0833 | Manual tracking | Open |  | 11.71% | 0.10417
1603 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-2 | 7 | 32 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1604 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | Actuator Type1(1*63) | 0.1724% | -28 | IC2_Inv2 | G-7 | G-8 | 166 | 91 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1605 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 117 | 20 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1606 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | Actuator Type1(1*63) | 0.1724% | -28 | IC1_Inv2 | G-1 | G-1 | 118 | 22 | Actuator | No Communication | Actuator Movemnet Blocked |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1607 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 45 | 8 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1608 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv4 | G-03 | G-05 | 47 | 18 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1609 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 30 | 57 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1610 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | MSAT_Type1 (5*63) | 0.8621% | -28 | IC1_Inv3 | G-01 | G-03 | 31 | 61 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1611 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 26 | 37 | MSAT100_PCB | No Communication | PCB Failure |  |  |  |  | 0 | 0 | 0 | 0 | Manual tracking | Open |  | 11.71% | 0
1612 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-22 | 6:10 | 18:50 | 12.6667 | MSAT_Type4(5*42) | 0.5747% | -28 | IC1_Inv2 | G-01 | G-03 | 27 | 42 | MSAT100_PCB | No Communication | PCB Failure | 6:10 | 6:10 |  | 0.76042 | 0 | -6.1667 | 1900-01-11 02:00 | 12.0833 | required modbus cable | Open |  | 11.71% | 0.069444
Formulas:
Days = DAY(EOMONTH(TA[[#This Row],[Month Year]],0))
Resolution Time = (TA[[#This Row],[Work Completion time on fault]]-TA[[#This Row],[Fault Time]])*24

## Grid BD
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affceted Equipment | DC Capacity Affceted (kW) | Affected Equipmenet Location | Fault Catergory | Plant Equivalent Weightage | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgemnet Time | Work Start time on Fault | Work Completiuon time on fualt | Acknowdlegemnet time | Response Time | Resolution Time | Action taken | Status | Plant Equivalent breakdown | Lost POA (Wh/m2) | Approxuimate Energy Loss (KWh) | Column1
1 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:13 | 18:17 | 12.0667 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | OCR/EFR OPERATED at 110kv kamtana | 0.69236 | 0.69236 | 0.69444 | 0.70278 | 0 | 0.05 | 0.25 | 33kv section officer | Close | 0.25 | 85 | 815.987
2 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:22 | 18:26 | 12.0667 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | Main supply failure | 0.56528 | 0.56528 | 0.56944 | 0.57222 | 0 | 0.1 | 0.16667 | 33kv section officer | Close | 0.16667 | 138 | 1148.461
3 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | Main supply failure | 0.35417 | 0.35556 | 0.35764 | 0.35972 | 0.033333 | 0.083333 | 0.13333 | 33kv section officer | Close | 0.13333 | 80 | 665.7745
4 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:20 | 18:15 | 11.9167 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | Main supply failure | 0.63472 | 0.6375 | 0.66667 | 0.71875 | 0.066667 | 0.76667 | 2.0167 | 33kv section officer | Close | 2.0167 | 84 | 699.0632
5 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:18 | 18:08 | 11.8333 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | Main supply failure | 0.48333 | 0.48333 | 0.48611 | 0.49028 | 0 | 0.066667 | 0.16667 | 33kv section officer | Close | 0.16667 | 154 | 1281.6159
6 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | LC TAKEN BY KAMtana AEE for 33kv kamtana line fault | 0.45625 | 0.45625 | 0.46181 | 0.48264 | 0 | 0.13333 | 0.63333 | 33kv section officer | Close | 0.63333 | 595 | 4951.6978
7 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:20 | 18:26 | 12.1 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | LC TAKEN BY KAMtana AEE for 33kv kamtana line fault | 0.49097 | 0.49097 | 0.49306 | 0.50486 | 0 | 0.05 | 0.33333 | 33kv section officer | Close | 0.33333 | 346 | 2879.4747
8 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:16 | 18:15 | 11.9833 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | LC taken at 33kv Manhalli JEE for 11kv line( under 33kv) fault clearance purpose | 0.49097 | 0.49097 | 0.49306 | 0.50486 | 0 | 0.05 | 0.33333 | 33kv section officer | Close | 0.33333 | 50 | 416.1091
9 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 6:08 | 17:18 | 11.1667 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | main supply failure | 0.65833 | 0.65833 | 0.66667 | 0.71875 | 0 | 0.2 | 1.45 | 33kv section officer | Close | 1.45 | 35 | 291.2763
10 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 6:30 | 17:30 | 11 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | main supply failure | 0.70833 | 0.70903 | 0.71875 | 0.72917 | 0.016667 | 0.25 | 0.5 | 33kv section officer | Close | 0.5 |  | 0
11 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:03 | 18:22 | 12.3167 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | manually tripped for gss internal work | 0.73472 | 0.73542 | 0.73611 | 0.74167 | 0.016667 | 0.033333 | 0.16667 | 33kv section officer | Close | 0.16667 | 22 | 183.088
12 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | main supply failure | 0.72222 | 0.72431 | 0.72569 | 0.73056 | 0.05 | 0.083333 | 0.2 | 33kv section officer | Close | 0.2 | 38 | 316.2429
13 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:04 | 18:28 | 12.4 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | main supply failure | 0.74514 | 0.74514 | 0.74653 | 0.75833 | 0 | 0.033333 | 0.31667 | 33kv section officer | Close | 0.31667 | 12 | 99.8662
14 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 6:03 | 18:31 | 12.4667 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | main supply failure | 0.67847 | 0.67847 | 0.67986 | 0.68403 | 0 | 0.033333 | 0.13333 | 33kv section officer | Close | 0.13333 | 65 | 556.8645
15 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 6:00 | 18:29 | 12.4833 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | main supply failure | 0.70417 | 0.70486 | 0.70694 | 0.71389 | 0.016667 | 0.066667 | 0.23333 | 33kv section officer | Close | 0.23333 | 100 | 856.7146
16 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:15 | 18:07 | 11.8667 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | Two pin insulators failure i/c 33kv manhalli line from 110kv kamtana | 0.26042 | 0.26042 | 0.28125 | 0.46875 | 0 | 0.5 | 5 | 33kv section officer | Close | 5 | 1400 | 11994.0047
17 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:02 | 18:32 | 12.5 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | OCR/EFR OPERATED at 110kv kamtana | 0.48403 | 0.48403 | 0.48958 | 0.49653 | 0 | 0.13333 | 0.3 | 33kv section officer | Close | 0.3 | 257 | 2201.7566
18 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 6:02 | 18:15 | 12.2167 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | LC taken at 110kv AEE for 5MVA TRAFO Installation at33kv kamtana station | 0.66458 | 0.66458 | 0.65972 | 0.69861 | 0 | -0.11667 | 0.81667 | 33kv section officer | Close | 0.81667 | 457 | 3915.1858
19 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 6:03 | 18:30 | 12.45 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | Two pin insulators failure i/c 33kv manhalli line from 110kv kamtana | 0.25208 | 0.25208 | 0.25208 | 0.41806 | 0 | 0 | 3.9833 | 33kv section officer | Close | 3.9833 | 1551 | 13287.6438
20 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | Two pin insulators failure i/c 33kv manhalli line from 110kv kamtana | 0.37569 | 0.37639 | 0.38542 | 0.40556 | 0.016667 | 0.23333 | 0.71667 | 33kv section officer | Close | 0.71667 | 239 | 2047.5479
21 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 7:04 | 16:38 | 9.5667 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | Two pin insulators failure i/c 33kv manhalli line from 110kv kamtana | 0.42917 | 0.42917 | 0.4375 | 0.44722 | 0 | 0.2 | 0.43333 | 33kv section officer | Close | 0.43333 | 221 | 1893.3393
22 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:43 | 17:25 | 10.7 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | Jump cut inside the gss 33kv manhalli | 0.5125 | 0.5125 | 0.51528 | 0.52778 | 0 | 0.066667 | 0.36667 | 33kv section officer | Close | 0.36667 | 211 | 1807.6678
23 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:00 | 18:25 | 12.4167 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | LC taken at 33kv Manhalli JEE for 11kv line( under 33kv) fault clearance purpose | 0.30833 | 0.30833 | 0.3125 | 0.34375 | 0 | 0.1 | 0.85 | 33kv section officer | Close | 0.85 | 175 | 1499.2506
24 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 5:53 | 17:31 | 11.6333 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | LC taken at 33kv Manhalli JEE for 11kv line( under 33kv) fault clearance purpose | 0.69444 | 0.69792 | 0.70139 | 0.72014 | 0.083333 | 0.16667 | 0.61667 | 33kv section officer | Close | 0.61667 | 72 | 616.8345
25 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:00 | 18:29 | 12.4833 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | LC taken for transoformer testing at 33kv kamtana pin insulator replacement work i/c line to 33kv manhalli purpose | 0.43333 | 0.43403 | 0.45486 | 0.77083 | 0.016667 | 0.51667 | 8.1 | 33kv section officer | Close | 8.1 | 2803 | 24013.7108
26 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 5:52 | 18:37 | 12.75 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | 10mva trafo tripped at 110 kv kamtana | 0.49722 | 0.49722 | 0.51042 | 0.53819 | 0 | 0.31667 | 0.98333 | 33kv section officer | Close | 0.98333 | 993 | 8507.1762
27 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-02 | 5:48 | 18:30 | 12.7 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | transformer testing at 110kv kamtana station | 0.68333 | 0.68403 | 0.6875 | 0.71389 | 0.016667 | 0.1 | 0.73333 | 33kv section officer | Close | 0.73333 | 174
28 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-03 | 5:51 | 18:34 | 12.7167 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | Grid failure from 220kv gss | 0.42917 | 0.42917 | 0.43403 | 0.45972 | 0 | 0.11667 | 0.73333 | 33kv section officer | Close | 0.73333 | 656
29 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-06 | 6:01 | 18:34 | 12.55 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | CT&PT Testing work purpose at Manhalli sub station hand triped | 0.56181 | 0.5625 | 0.56597 | 0.69444 | 0.016667 | 0.1 | 3.1833 | 33kv section officer | Close | 3.1833 | 2062
30 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-07 | 5:54 | 18:37 | 12.7167 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | main supply failure | 0.62292 | 0.62431 | 0.625 | 0.62986 | 0.033333 | 0.05 | 0.16667 | 33kv section officer | Close | 0.16667 | 49
31 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-11 | 7:00 | 18:39 | 11.65 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | LC taken at 33kv Manhalli JEE for 11kv line( under 33kv) fault clearance purpose | 0.42153 | 0.42153 | 0.42222 | 0.43194 | 0 | 0.016667 | 0.25 | 33kv section officer | Close | 0.25 | 50
32 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-12 | 6:45 | 18:35 | 11.8333 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | main supply failure | 0.70208 | 0.70208 | 0.70486 | 0.70833 | 0 | 0.066667 | 0.15 | 33kv section officer | Close | 0.15 | 50
33 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-13 | 5:58 | 18:37 | 12.65 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | LC taken AEE at 33kv Manhalli Gss CT oil leackage arresting purpose | 0.53194 | 0.53194 | 0.53819 | 0.65694 | 0 | 0.15 | 3 | 33kv section officer | Close | 3 | 1097
34 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-15 | 6:00 | 18:18 | 12.3 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | B phase Jump cut Near Gss 33kv manhalli. | 0.51736 | 0.51736 | 0.53125 | 0.62222 | 0 | 0.33333 | 2.5167 | 33kv section officer | Close | 2.5167 | 1253
35 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-16 | 6:11 | 18:06 | 11.9167 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | jump cut at 11o kv kamtana substation | 0.50694 | 0.50694 | 0.52083 | 0.56389 | 0 | 0.33333 | 1.3667 | 33kv section officer | Close | 1.3667 | 618
36 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | 10mva trafo tripped at 110 kv kamtana | 0.40069 | 0.40069 | 0.40278 | 0.41319 | 0 | 0.05 | 0.3 | 33kv section officer | Close | 0.3 | 216
37 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | 10mva trafo tripped at 110 kv kamtana | 0.50208 | 0.54167 | 0.56944 | 0.54167 | 0.95 | 1.6167 | 0.95 | 33kv section officer | Close | 0.95 | 570
38 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-18 | 5:52 | 18:35 | 12.7167 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | 10mva trafo tripped at 110 kv kamtana | 0.66667 | 0.66667 | 0.6875 | 0.73125 | 0 | 0.5 | 1.55 | 33kv section officer | Close | 1.55 | 337
39 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-19 | 5:58 | 18:30 | 12.5333 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | quarterly maintenance 110KV KAMTANA & Gss 33kv manhalli & replaced pin insulator polymer insplace of porcelin | 0.34028 | 0.34097 | 0.375 | 0.77083 | 0.016667 | 0.83333 | 10.3333 | 33kv section officer | Close | 10.3333 | 5160
40 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-06-25 | 6:06 | 18:40 | 12.5667 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | main supply failure | 0.42014 | 0.42014 | 0.42361 | 0.42778 | 0 | 0.083333 | 0.18333 | 33kv section officer | Close | 0.18333 | 124
41 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-07-01 | 6:12 | 18:30 | 12.3 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | Jump cut inside the gss 33kv manhalli | 0.59792 | 0.59792 | 0.60764 | 0.63542 | 0 | 0.23333 | 0.9 | 33kv section officer | Close | 0.9 | 506
42 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-07-15 | 6:11 | 18:53 | 12.7 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | low voltage detected at 110kv kamtana station | 0.71806 | 0.71944 | 0.72917 | 0.75 | 0.033333 | 0.26667 | 0.76667 | 33kv section officer | Close | 0.76667 | 114
43 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-07-19 | 6:10 | 18:40 | 12.5 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | Bird died on transmission line near GSS internal line | 0.26597 | 0.26597 | 0.29167 | 0.33472 | 0 | 0.61667 | 1.65 | 33kv section officer | Close | 1.65 | 516
44 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-02 | 30 | 2025-07-20 | 6:14 | 18:43 | 12.4833 | Grid CB | 11710.44 | Plant | Grid System | 100% | NA | Main supply failure | 0.50556 | 0.50556 | 0.50764 | 0.5125 | 0 | 0.05 | 0.16667 | 33kv section officer | Close | 0.16667 | 125
45 | 1900 | 1900
46 | 1900 | 1900
47 | 1900 | 1900
48 | 1900 | 1900
49 | 1900 | 1900
50 | 1900 | 1900
51 | 1900 | 1900
52 | 1900 | 1900
53 | 1900 | 1900
54 | 1900 | 1900
55 | 1900 | 1900
56 | 1900 | 1900
57 | 1900 | 1900
58 | 1900 | 1900
59 | 1900 | 1900
60 | 1900 | 1900
61 | 1900 | 1900
62 | 1900 | 1900
63 | 1900 | 1900
64 | 1900 | 1900
65 | 1900 | 1900
66 | 1900 | 1900
67 | 1900 | 1900
68 | 1900 | 1900
69 | 1900 | 1900
70 | 1900 | 1900
71 | 1900 | 1900
72 | 1900 | 1900
73 | 1900 | 1900
74 | 1900 | 1900
75 | 1900 | 1900
76 | 1900 | 1900
77 | 1900 | 1900
78 | 1900 | 1900
79 | 1900 | 1900
80 | 1900 | 1900
81 | 1900 | 1900
82 | 1900 | 1900
83 | 1900 | 1900
84 | 1900 | 1900
85 | 1900 | 1900
86 | 1900 | 1900
87 | 1900 | 1900
88 | 1900 | 1900
89 | 1900 | 1900
90 | 1900 | 1900
91 | 1900 | 1900
92 | 1900 | 1900
93 | 1900 | 1900
94 | 1900 | 1900
95 | 1900 | 1900
96 | 1900 | 1900
97 | 1900 | 1900
98 | 1900 | 1900
99 | 1900 | 1900
100 | 1900 | 1900
101 | 1900 | 1900
102 | 1900 | 1900
103 | 1900 | 1900
104 | 1900 | 1900
105 | 1900 | 1900
106 | 1900 | 1900
107 | 1900 | 1900
108 | 1900 | 1900
109 | 1900 | 1900
110 | 1900 | 1900
111 | 1900 | 1900
112 | 1900 | 1900
113 | 1900 | 1900
114 | 1900 | 1900
115 | 1900 | 1900
116 | 1900 | 1900
117 | 1900 | 1900
118 | 1900 | 1900
119 | 1900 | 1900
120 | 1900 | 1900
121 | 1900 | 1900
122 | 1900 | 1900
123 | 1900 | 1900
124 | 1900 | 1900
125 | 1900 | 1900
126 | 1900 | 1900
127 | 1900 | 1900
128 | 1900 | 1900
129 | 1900 | 1900
130 | 1900 | 1900
131 | 1900 | 1900
132 | 1900 | 1900
133 | 1900 | 1900
134 | 1900 | 1900
135 | 1900 | 1900
136 | 1900 | 1900
137 | 1900 | 1900
138 | 1900 | 1900
139 | 1900 | 1900
140 | 1900 | 1900
141 | 1900 | 1900
142 | 1900 | 1900
143 | 1900 | 1900
144 | 1900 | 1900
145 | 1900 | 1900
146 | 1900 | 1900
147 | 1900 | 1900
148 | 1900 | 1900
149 | 1900 | 1900
150 | 1900 | 1900
151 | 1900 | 1900
152 | 1900 | 1900
153 | 1900 | 1900
154 | 1900 | 1900
155 | 1900 | 1900
156 | 1900 | 1900
157 | 1900 | 1900
158 | 1900 | 1900
159 | 1900 | 1900
160 | 1900 | 1900
161 | 1900 | 1900
162 | 1900 | 1900
163 | 1900 | 1900
164 | 1900 | 1900
165 | 1900 | 1900
166 | 1900 | 1900
167 | 1900 | 1900
168 | 1900 | 1900
169 | 1900 | 1900
170 | 1900 | 1900
171 | 1900 | 1900
172 | 1900 | 1900
173 | 1900 | 1900
174 | 1900 | 1900
175 | 1900 | 1900
176 | 1900 | 1900
177 | 1900 | 1900
178 | 1900 | 1900
179 | 1900 | 1900
180 | 1900 | 1900
181 | 1900 | 1900
182 | 1900 | 1900
183 | 1900 | 1900
184 | 1900 | 1900
185 | 1900 | 1900
186 | 1900 | 1900
187 | 1900 | 1900
188 | 1900 | 1900
189 | 1900 | 1900
190 | 1900 | 1900
191 | 1900 | 1900
192 | 1900 | 1900
193 | 1900 | 1900
194 | 1900 | 1900
195 | 1900 | 1900
196 | 1900 | 1900
197 | 1900 | 1900
198 | 1900 | 1900
199 | 1900 | 1900
200 | 1900 | 1900
201 | 1900 | 1900
202 | 1900 | 1900
203 | 1900 | 1900
204 | 1900 | 1900
205 | 1900 | 1900
206 | 1900 | 1900
207 | 1900 | 1900
208 | 1900 | 1900
209 | 1900 | 1900
210 | 1900 | 1900
211 | 1900 | 1900
212 | 1900 | 1900
213 | 1900 | 1900
214 | 1900 | 1900
215 | 1900 | 1900
216 | 1900 | 1900
217 | 1900 | 1900
218 | 1900 | 1900
219 | 1900 | 1900
220 | 1900 | 1900
221 | 1900 | 1900
222 | 1900 | 1900
223 | 1900 | 1900
224 | 1900 | 1900
225 | 1900 | 1900
226 | 1900 | 1900
227 | 1900 | 1900
228 | 1900 | 1900
229 | 1900 | 1900
230 | 1900 | 1900
231 | 1900 | 1900
232 | 1900 | 1900
233 | 1900 | 1900
234 | 1900 | 1900
235 | 1900 | 1900
236 | 1900 | 1900
237 | 1900 | 1900
238 | 1900 | 1900
239 | 1900 | 1900
240 | 1900 | 1900
241 | 1900 | 1900
242 | 1900 | 1900
243 | 1900 | 1900
244 | 1900 | 1900
245 | 1900 | 1900
246 | 1900 | 1900
247 | 1900 | 1900
248 | 1900 | 1900
249 | 1900 | 1900
250 | 1900 | 1900
251 | 1900 | 1900
252 | 1900 | 1900
253 | 1900 | 1900
254 | 1900 | 1900
255 | 1900 | 1900
256 | 1900 | 1900
257 | 1900 | 1900
258 | 1900 | 1900
259 | 1900 | 1900
260 | 1900 | 1900
261 | 1900 | 1900
262 | 1900 | 1900
263 | 1900 | 1900
264 | 1900 | 1900
265 | 1900 | 1900
266 | 1900 | 1900
267 | 1900 | 1900
268 | 1900 | 1900
269 | 1900 | 1900
270 | 1900 | 1900
271 | 1900 | 1900
272 | 1900 | 1900
273 | 1900 | 1900
274 | 1900 | 1900
275 | 1900 | 1900
276 | 1900 | 1900
277 | 1900 | 1900
278 | 1900 | 1900
279 | 1900 | 1900
280 | 1900 | 1900
281 | 1900 | 1900
282 | 1900 | 1900
283 | 1900 | 1900
284 | 1900 | 1900
285 | 1900 | 1900
286 | 1900 | 1900
287 | 1900 | 1900
288 | 1900 | 1900
289 | 1900 | 1900
290 | 1900 | 1900
291 | 1900 | 1900
292 | 1900 | 1900
293 | 1900 | 1900
294 | 1900 | 1900
295 | 1900 | 1900
296 | 1900 | 1900
297 | 1900 | 1900
298 | 1900 | 1900
299 | 1900 | 1900
300 | 1900 | 1900
301 | 1900 | 1900
302 | 1900 | 1900
303 | 1900 | 1900
304 | 1900 | 1900
305 | 1900 | 1900
306 | 1900 | 1900
307 | 1900 | 1900
308 | 1900 | 1900
309 | 1900 | 1900
310 | 1900 | 1900
311 | 1900 | 1900
312 | 1900 | 1900
313 | 1900 | 1900
314 | 1900 | 1900
315 | 1900 | 1900
316 | 1900 | 1900
317 | 1900 | 1900
318 | 1900 | 1900
319 | 1900 | 1900
320 | 1900 | 1900
321 | 1900 | 1900
322 | 1900 | 1900
323 | 1900 | 1900
324 | 1900 | 1900
325 | 1900 | 1900
326 | 1900 | 1900
327 | 1900 | 1900
328 | 1900 | 1900
329 | 1900 | 1900
330 | 1900 | 1900
331 | 1900 | 1900
332 | 1900 | 1900
333 | 1900 | 1900
334 | 1900 | 1900
335 | 1900 | 1900
336 | 1900 | 1900
337 | 1900 | 1900
338 | 1900 | 1900
339 | 1900 | 1900
340 | 1900 | 1900
341 | 1900 | 1900
342 | 1900 | 1900
343 | 1900 | 1900
344 | 1900 | 1900
345 | 1900 | 1900
346 | 1900 | 1900
347 | 1900 | 1900
348 | 1900 | 1900
349 | 1900 | 1900
350 | 1900 | 1900
351 | 1900 | 1900
352 | 1900 | 1900
353 | 1900 | 1900
354 | 1900 | 1900
355 | 1900 | 1900
356 | 1900 | 1900
357 | 1900 | 1900
358 | 1900 | 1900
359 | 1900 | 1900
360 | 1900 | 1900
361 | 1900 | 1900
362 | 1900 | 1900
363 | 1900 | 1900
364 | 1900 | 1900
365 | 1900 | 1900
366 | 1900 | 1900
367 | 1900 | 1900
368 | 1900 | 1900
369 | 1900 | 1900
370 | 1900 | 1900
371 | 1900 | 1900
372 | 1900 | 1900
373 | 1900 | 1900
374 | 1900 | 1900
375 | 1900 | 1900
376 | 1900 | 1900
377 | 1900 | 1900
378 | 1900 | 1900
379 | 1900 | 1900
380 | 1900 | 1900
381 | 1900 | 1900
382 | 1900 | 1900
383 | 1900 | 1900
384 | 1900 | 1900
385 | 1900 | 1900
386 | 1900 | 1900
387 | 1900 | 1900
388 | 1900 | 1900
389 | 1900 | 1900
390 | 1900 | 1900
391 | 1900 | 1900
392 | 1900 | 1900
393 | 1900 | 1900
394 | 1900 | 1900
395 | 1900 | 1900
396 | 1900 | 1900
397 | 1900 | 1900
398 | 1900 | 1900
399 | 1900 | 1900
400 | 1900 | 1900
401 | 1900 | 1900
402 | 1900 | 1900
403 | 1900 | 1900
404 | 1900 | 1900
405 | 1900 | 1900
406 | 1900 | 1900
407 | 1900 | 1900
408 | 1900 | 1900
409 | 1900 | 1900
410 | 1900 | 1900
411 | 1900 | 1900
412 | 1900 | 1900
413 | 1900 | 1900
414 | 1900 | 1900
415 | 1900 | 1900
416 | 1900 | 1900
417 | 1900 | 1900
418 | 1900 | 1900
419 | 1900 | 1900
420 | 1900 | 1900
421 | 1900 | 1900
422 | 1900 | 1900
423 | 1900 | 1900
424 | 1900 | 1900
425 | 1900 | 1900
426 | 1900 | 1900
427 | 1900 | 1900
428 | 1900 | 1900
429 | 1900 | 1900
430 | 1900 | 1900
431 | 1900 | 1900
432 | 1900 | 1900
433 | 1900 | 1900
434 | 1900 | 1900
435 | 1900 | 1900
436 | 1900 | 1900
437 | 1900 | 1900
438 | 1900 | 1900
439 | 1900 | 1900
440 | 1900 | 1900
441 | 1900 | 1900
442 | 1900 | 1900
443 | 1900 | 1900
444 | 1900 | 1900
445 | 1900 | 1900
446 | 1900 | 1900
447 | 1900 | 1900
448 | 1900 | 1900
449 | 1900 | 1900
450 | 1900 | 1900
451 | 1900 | 1900
452 | 1900 | 1900
453 | 1900 | 1900
454 | 1900 | 1900
455 | 1900 | 1900
456 | 1900 | 1900
457 | 1900 | 1900
458 | 1900 | 1900
459 | 1900 | 1900
460 | 1900 | 1900
461 | 1900 | 1900
462 | 1900 | 1900
463 | 1900 | 1900
464 | 1900 | 1900
465 | 1900 | 1900
466 | 1900 | 1900
467 | 1900 | 1900
468 | 1900 | 1900
469 | 1900 | 1900
470 | 1900 | 1900
471 | 1900 | 1900
472 | 1900 | 1900
473 | 1900 | 1900
474 | 1900 | 1900
475 | 1900 | 1900
476 | 1900 | 1900
477 | 1900 | 1900
478 | 1900 | 1900
479 | 1900 | 1900
480 | 1900 | 1900
481 | 1900 | 1900
482 | 1900 | 1900
483 | 1900 | 1900
484 | 1900 | 1900
485 | 1900 | 1900
486 | 1900 | 1900
487 | 1900 | 1900
488 | 1900 | 1900
489 | 1900 | 1900
490 | 1900 | 1900
491 | 1900 | 1900
492 | 1900 | 1900
493 | 1900 | 1900
494 | 1900 | 1900
495 | 1900 | 1900
496 | 1900 | 1900
497 | 1900 | 1900
498 | 1900 | 1900
499 | 1900 | 1900
500 | 1900 | 1900
501 | 1900 | 1900
502 | 1900 | 1900
503 | 1900 | 1900
504 | 1900 | 1900
505 | 1900 | 1900
506 | 1900 | 1900
507 | 1900 | 1900
508 | 1900 | 1900
509 | 1900 | 1900
510 | 1900 | 1900
511 | 1900 | 1900
Formulas:
Days = DAY(EOMONTH(GA[[#This Row],[Month Year]],0))
Acknowdlegemnet time = (GA[[#This Row],[Acknowledgemnet Time ]]-GA[[#This Row],[Fault Time]])*24

## Mod_CL
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Cycle Number | Resources | IC1_Inv1_MC | IC1_Inv2_MC | IC1_Inv3_MC | IC1_Inv4_MC | IC2_Inv1_MC | IC2_Inv2_MC | Total Module cleaned | Morning Start Time | Morning End Time | Evening Start Time | Evening End time | Brush/MOP Replcemnet | Water Test Report | Remarks for the day | Column1 | Column2
1 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-29 | 12 | MCS |  | 3570 | 252 |  |  |  | 3822
2 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-30 | 12 | MCS | [5 empty] | 1512 | 1512
3 | 2025 | 2025 | Year_3 | Year_3 | 2025-03-01 | 31 | 2025-03-31 | 12 | MCS |  | 2898 | 1134 |  |  |  | 4032
4 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-01 | 12 | MCS |  |  |  |  | 3864 |  | 3864
5 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 12 | MCS |  |  |  |  | 2037 | 1848 | 3885
6 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-03 | 12 | MCS | [5 empty] | 3780 | 3780
7 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 12 | MCS | 1764 |  |  | 588 |  | 1848 | 4200
8 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 12 | MCS | 2310 |  | 546 | 1344 |  |  | 4200
9 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 12 | MCS | [6 empty] | 0
10 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 13 | MCS | 588 |  |  | 2100 | 126 | 1438 | 4252
11 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-08 | 13 | MCS |  |  | 3528 | 504 | 210 |  | 4242
12 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-09 | 13 | MCS | 504 | 1890 | 1029 | 588 |  |  | 4011
13 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-10 | 13 | MCS | 3444 | 588 |  |  |  |  | 4032
14 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-11 | 13 | MCS | [6 empty] | 0
15 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-12 | 13 | MCS | [6 empty] | 0
16 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-13 | 13 | MCS | [6 empty] | 0
17 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-14 | 13 | MCS | 2961 | [5 empty] | 2961
18 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-15 | 13 | MCS | 1722 |  | 588 | 1722 |  |  | 4032
19 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-16 | 13 | MCS | 420 |  | 588 |  | 1680 | 1512 | 4200
20 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-17 | 13 | MCS |  |  |  |  | 4032 |  | 4032
21 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-18 | 13 | MCS |  |  |  |  | 1848 | 2352 | 4200
22 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-19 | 13 | MCS |  |  |  | 2352 |  | 2352 | 4704
23 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-20 | 13 | MCS |  | 588 | 588 | 588 | 588 | 210 | 2562
24 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-21 | 14 | MCS |  |  | 3381 | 714 |  |  | 4095
25 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-22 | 14 | MCS | 504 | 2100 | 1176 | 378 |  |  | 4158
26 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-23 | 14 | MCS |  | 1764 |  |  |  |  | 1764
27 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-24 | 14 | MCS | 588 | 2856 |  |  | 588 |  | 4032
28 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-25 | 14 | MCS |  |  |  |  | 4116 |  | 4116
29 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-26 | 14 | MCS |  |  |  |  | 1512 | 2562 | 4074
30 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-27 | 14 | MCS | 1764 |  |  |  |  | 1932 | 3696
31 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-28 | 14 | MCS | 3318 |  | 588 |  |  |  | 3906
32 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-29 | 14 | MCS |  |  | 168 | 2352 |  | 1512 | 4032
33 | 2026 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-30 | 14 | MCS |  |  | 1092 | 2856 |  |  | 3948
34 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-01 | 15 | MCS |  |  | 3381 | 588 |  |  | 3969
35 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-02 | 15 | MCS | 504 | 2394 | 1176 |  |  |  | 4074
36 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-03 | 15 | MCS | 588 | 3528 |  |  |  |  | 4116
37 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-04 | 15 | MCS | [6 empty] | 0
38 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-05 | 15 | MCS |  | 588 |  |  | 3528 |  | 4116
39 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-06 | 15 | MCS |  |  |  |  | 2352 | 1764 | 4116
40 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-07 | 15 | MCS | 420 |  |  |  | 336 | 3360 | 4116
41 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-08 | 15 | MCS | 4116 | [5 empty] | 4116
42 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-09 | 15 | MCS |  |  | 1176 | 1176 |  | 1512 | 3864
43 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-10 | 15 | MCS | 420 |  | 588 | 2898 |  |  | 3906
44 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-11 | 15 | MCS |  |  | 2940 | 1176 |  |  | 4116
45 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-12 | 15 | MCS |  |  | 1618 | 420 |  |  | 2038
46 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-13 | 16 | MCS | [6 empty] | 0
47 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-14 | 16 | MCS | [6 empty] | 0
48 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-15 | 16 | MCS | [6 empty] | 0
49 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-16 | 16 | MCS | [6 empty] | 0
50 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-17 | 15 | MCS | [6 empty] | 0
51 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-18 | 15 | MCS | [6 empty] | 0
52 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-19 | 15 | MCS | [6 empty] | 0
53 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-20 | 16 | MCS |  |  |  |  | 4316 |  | 4316
54 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-21 | 16 | MCS |  |  |  |  | 1900 | 2352 | 4252
55 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-22 | 16 | MCS | 688 |  |  |  |  | 3528 | 4216
56 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-23 | 16 | MCS | 3428 |  |  |  |  | 788 | 4216
57 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-24 | 16 | MCS | [6 empty] | 0
58 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-25 | 16 | MCS | [6 empty] | 0
59 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-26 | 16 | MCS | [6 empty] | 0
60 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-27 | 16 | MCS | [6 empty] | 0
61 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-28 | 16 | MCS | [6 empty] | 0
62 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-29 | 16 | MCS | [6 empty] | 0
63 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-30 | 16 | MCS | [6 empty] | 0
64 | 2026 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-31 | 16 | MCS | [6 empty] | 0
65 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-01 | 16 | MCS | [6 empty] | 0
66 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-02 | 16 | MCS | [6 empty] | 0
67 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-03 | 16 | MCS | [6 empty] | 0
68 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-04 | 16 | MCS | [6 empty] | 0
69 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-05 | 16 | MCS | [6 empty] | 0
70 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-06 | 16 | MCS | [6 empty] | 0
71 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-07 | 16 | MCS | [6 empty] | 0
72 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-08 | 16 | MCS | [6 empty] | 0
73 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-09 | 16 | MCS | [6 empty] | 0
74 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-10 | 16 | MCS | [6 empty] | 0
75 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-11 | 16 | MCS | [6 empty] | 0
76 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-12 | 16 | MCS | [6 empty] | 0
77 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-13 | 16 | MCS | [6 empty] | 0
78 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-14 | 16 | MCS | [6 empty] | 0
79 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-15 | 16 | MCS | [6 empty] | 0
80 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-16 | 16 | MCS | [6 empty] | 0
81 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-17 | 16 | MCS |  | 1176 |  | 2877 |  |  | 4053
82 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-18 | 16 | MCS |  |  | 4116 |  |  |  | 4116
83 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-19 | 16 | MCS |  | 2562 | 441 |  |  |  | 3003
84 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-20 | 16 | MCS |  | 3822 | 588 |  |  |  | 4410
85 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-21 | 16 | MCS | 504 |  |  |  | 3696 |  | 4200
86 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-22 | 17 | MCS | [6 empty] | 0
87 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-23 | 17 | MCS |  |  |  |  | 2541 | 1764 | 4305
88 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-24 | 17 | MCS | 1260 |  |  |  |  | 2940 | 4200
89 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-25 | 17 | MCS | 3864 |  | 336 |  |  |  | 4200
90 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-26 | 17 | MCS |  |  | 588 | 2310 |  | 1312 | 4210
91 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-27 | 17 | MCS |  |  |  | 2856 |  | 788 | 3644
92 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-28 | 17 | MCS |  |  | 4221 |  |  |  | 4221
93 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-29 | 17 | MCS | [6 empty] | 0
94 | 2026 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-30 | 17 | MCS | [6 empty] | 0
95 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-01 | 17 | MCS | [6 empty] | 0
96 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-02 | 17 | MCS | [6 empty] | 0
97 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-03 | 17 | MCS | [6 empty] | 0
98 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-04 | 17 | MCS | [6 empty] | 0
99 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-05 | 17 | MCS | [6 empty] | 0
100 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-06 | 17 | MCS | [6 empty] | 0
101 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-07 | 17 | MCS | [6 empty] | 0
102 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-08 | 17 | MCS | [6 empty] | 0
103 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-09 | 17 | MCS | [6 empty] | 0
104 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-10 | 17 | MCS | [6 empty] | 0
105 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-11 | 17 | MCS | [6 empty] | 0
106 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-12 | 17 | MCS | [6 empty] | 0
107 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-13 | 17 | MCS | [6 empty] | 0
108 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-14 | 17 | MCS | [6 empty] | 0
109 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-15 | 17 | MCS |  |  | 588 | 3465 |  |  | 4053
110 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-16 | 17 | MCS | 210 |  | 3969 |  |  |  | 4179
111 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-17 | 17 | MCS | 294 | 3864 |  |  |  |  | 4158
112 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-18 | 17 | MCS | 588 | 2268 |  |  | 1344 |  | 4200
113 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-19 | 17 | MCS | [6 empty] | 0
114 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-20 | 17 | MCS | [6 empty] | 0
115 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-21 | 17 | MCS |  |  |  |  | 4242 |  | 4242
116 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-22 | 17 | MCS |  |  |  |  | 1974 | 2226 | 4200
117 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-23 | 17 | MCS | [6 empty] | 0
118 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-24 | 17 | MCS | [6 empty] | 0
119 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-25 | 17 | MCS | [6 empty] | 0
120 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-26 | 17 | MCS | [6 empty] | 0
121 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-27 | 17 | MCS | [6 empty] | 0
122 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-28 | 17 | MCS | [6 empty] | 0
123 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-29 | 17 | MCS | [6 empty] | 0
124 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-30 | 17 | MCS | [6 empty] | 0
125 | 2026 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-31 | 17 | MCS | [6 empty] | 0
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Grass_Cutting
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Cycle Number | Resources | IC1_Inv1_GC | IC1_Inv2_GC | IC1_Inv3_GC | IC1_Inv4_GC | IC2_Inv1_GC | IC2_Inv2_GC | Total Number of Table cut | Remarks for the day | Column1
1 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 |  | 2025-03-29 | [8 empty] | 0
2 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 |  | 2025-03-30 | [8 empty] | 0
3 | 2025 | 2025 | Year_2 | Year_2 | 2025-03-01 |  | 2025-03-31 | [8 empty] | 0
4 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-01 | [8 empty] | 0
5 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-02 | [8 empty] | 0
6 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-03 | [8 empty] | 0
7 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-04 | [8 empty] | 0
8 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-05 | [8 empty] | 0
9 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-06 | [8 empty] | 0
10 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-07 | [8 empty] | 0
11 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-08 | [8 empty] | 0
12 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-09 | [8 empty] | 0
13 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-10 | [8 empty] | 0
14 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-11 | [8 empty] | 0
15 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-12 | [8 empty] | 0
16 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-13 | [8 empty] | 0
17 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-14 | [8 empty] | 0
18 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-15 | [8 empty] | 0
19 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-16 | [8 empty] | 0
20 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-17 | [8 empty] | 0
21 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-18 | [8 empty] | 0
22 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-19 | [8 empty] | 0
23 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-20 | [8 empty] | 0
24 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-21 | [8 empty] | 0
25 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-22 | [8 empty] | 0
26 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-23 | [8 empty] | 0
27 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-24 | [8 empty] | 0
28 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-25 | [8 empty] | 0
29 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-26 | [8 empty] | 0
30 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-27 | [8 empty] | 0
31 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-28 | [8 empty] | 0
32 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-29 | [8 empty] | 0
33 | 2026 | 2025 | Year_2 | Year_2 | 2025-04-01 |  | 2025-04-30 | [8 empty] | 0
34 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-01 | [8 empty] | 0
35 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-02 | [8 empty] | 0
36 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-03 | [8 empty] | 0
37 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-04 | [8 empty] | 0
38 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-05 | [8 empty] | 0
39 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-06 | [8 empty] | 0
40 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-07 | [8 empty] | 0
41 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-08 | [8 empty] | 0
42 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-09 | [8 empty] | 0
43 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-10 | [8 empty] | 0
44 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-11 | [8 empty] | 0
45 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-12 | [8 empty] | 0
46 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-13 | [8 empty] | 0
47 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-14 | [8 empty] | 0
48 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-15 | [8 empty] | 0
49 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-16 | [8 empty] | 0
50 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-17 | [8 empty] | 0
51 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-18 | [8 empty] | 0
52 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-19 | [8 empty] | 0
53 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-20 | [8 empty] | 0
54 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-21 | [8 empty] | 0
55 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-22 | [8 empty] | 0
56 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-23 | [8 empty] | 0
57 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-24 | [8 empty] | 0
58 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-25 | [8 empty] | 0
59 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-26 | [8 empty] | 0
60 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-27 | [8 empty] | 0
61 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-28 | [8 empty] | 0
62 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-29 | [8 empty] | 0
63 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-30 | [8 empty] | 0
64 | 2026 | 2025 | Year_2 | Year_2 | 2025-05-01 |  | 2025-05-31 | [8 empty] | 0
65 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-01 | [8 empty] | 0
66 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-02 | [8 empty] | 0
67 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-03 | [8 empty] | 0
68 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-04 | [8 empty] | 0
69 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-05 | [8 empty] | 0
70 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-06 | [8 empty] | 0
71 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-07 | [8 empty] | 0
72 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-08 | [8 empty] | 0
73 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-09 | [8 empty] | 0
74 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-10 | [8 empty] | 0
75 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-11 | [8 empty] | 0
76 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-12 | [8 empty] | 0
77 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-13 |  |  |  | 8 | 4 |  |  |  | 12 | Grid-06
78 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-14 |  |  |  |  | 4 | 10 |  |  | 14 | Grid-06
79 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-15 | [5 empty] | 28 |  |  | 28 | Grid-06
80 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-16 | [8 empty] | 0 | Grid-06
81 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-17 | [8 empty] | 0 | Grid-06
82 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-18 |  |  |  | 3 |  | 17 |  |  | 20 | Grid-06
83 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-19 | [8 empty] | 0
84 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-20 |  |  | 8 |  | 8 |  |  |  | 16 | Grid-06
85 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-21 |  |  | 11 |  |  | 10 |  |  | 21 | grid-05
86 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-22 | [8 empty] | 0
87 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-23 | [8 empty] | 0
88 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-24 | [5 empty] | 10 |  |  | 10 | grid-05
89 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-25 | [5 empty] | 5 |  |  | 5 | grid-05
90 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-26 | [5 empty] | 16 |  |  | 16 | grid-05 &4
91 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-27 |  |  |  |  | 8 | 12 |  |  | 20 | Grid-04&3
92 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-28 |  |  |  |  | 15 | 9 |  |  | 24
93 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-29 | [8 empty] | 0
94 | 2026 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 2025-06-30 |  |  | 11 | 32 |  |  |  |  | 43
95 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-01 |  |  |  | 30 |  |  |  |  | 30 | Grid-01
96 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-02 |  |  | 19 | 27 |  |  |  |  | 46 | Grid-02
97 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-03 |  |  |  | 36 |  |  |  |  | 36 | Grid-02
98 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-04 |  |  |  | 30 | 6 |  |  |  | 36 | Grid-02
99 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-05 |  |  |  |  | 18 |  | 4 |  | 22 | Grid-03
100 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-06 | [8 empty] | 0 | Grid-03
101 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-07 | [7 empty] | 32 | 32 | Grid-08
102 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-08 | [7 empty] | 32 | 32 | Grid-08
103 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-09 | [8 empty] | 0
104 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-10 |  |  | 24 |  |  |  |  | 8 | 32 | Grid-07
105 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-11 |  |  | 28 | [5 empty] | 28 | Grid-07
106 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-12 |  |  | 8 |  |  |  |  | 15 | 23 | Grid-07
107 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-13 | [8 empty] | 0
108 | 2026 | 2025 | Year_2 | Year_2 | 2025-07-01 |  | 2025-07-14 | [8 empty] | 0
109 | 2026 | 2025 |  |  |  |  | 2025-07-15 | [8 empty] | 0
110 | 2026 | 2025 |  |  |  |  | 2025-07-16 | [8 empty] | 0
111 | 2026 | 2025 |  |  |  |  | 2025-07-17 | [8 empty] | 0
112 | 2026 | 2025 |  |  |  |  | 2025-07-18 | [8 empty] | 0
113 | 2026 | 2025 |  |  |  |  | 2025-07-19 | [8 empty] | 0
114 | 2026 | 2025 |  |  |  |  | 2025-07-20 | [8 empty] | 0
115 | 2026 | 2025 |  |  |  |  | 2025-07-21 | [8 empty] | 0
116 | 2026 | 2025 |  |  |  |  | 2025-07-22 | [8 empty] | 0
117 | 2026 | 2025 |  |  |  |  | 2025-07-23 | [8 empty] | 0
118 | 2026 | 2025 |  |  |  |  | 2025-07-24 | [8 empty] | 0
119 | 2026 | 2025 |  |  |  |  | 2025-07-25 | [8 empty] | 0
120 | 2026 | 2025 |  |  |  |  | 2025-07-26 | [8 empty] | 0
121 | 2026 | 2025 |  |  |  |  | 2025-07-27 | [8 empty] | 0
122 | 2026 | 2025 |  |  |  |  | 2025-07-28 | [8 empty] | 0
123 | 2026 | 2025 |  |  |  |  | 2025-07-29 | [8 empty] | 0
124 | 2026 | 2025 |  |  |  |  | 2025-07-30 | [8 empty] | 0
125 | 2026 | 2025 |  |  |  |  | 2025-07-31 | [8 empty] | 0
126 | 2026 | 2025 |  |  |  |  | 2025-08-01 | [8 empty] | 0
127 | 2026 | 2025 |  |  |  |  | 2025-08-02 | [8 empty] | 0
128 | 2026 | 2025 |  |  |  |  | 2025-08-03 | [8 empty] | 0
129 | 2026 | 2025 |  |  |  |  | 2025-08-04 | [8 empty] | 0
130 | 2026 | 2025 |  |  |  |  | 2025-08-05 | [8 empty] | 0
131 | 2026 | 2025 |  |  |  |  | 2025-08-06 | [8 empty] | 0
132 | 2026 | 2025 |  |  |  |  | 2025-08-07 | [8 empty] | 0
133 | 2026 | 2025 |  |  |  |  | 2025-08-08 | [8 empty] | 0
134 | 2026 | 2025 |  |  |  |  | 2025-08-09 | [8 empty] | 0
135 | 2026 | 2025 |  |  |  |  | 2025-08-10 | [8 empty] | 0
136 | 2026 | 2025 |  |  |  |  | 2025-08-11 | [8 empty] | 0
137 | 2026 | 2025 |  |  |  |  | 2025-08-12 | [8 empty] | 0
138 | 2026 | 2025 |  |  |  |  | 2025-08-13 | [8 empty] | 0
139 | 2026 | 2025 |  |  |  |  | 2025-08-14 | [8 empty] | 0
140 | 2026 | 2025 |  |  |  |  | 2025-08-15 | [8 empty] | 0
141 | 2026 | 2025 |  |  |  |  | 2025-08-16 | [8 empty] | 0
142 | 2026 | 2025 |  |  |  |  | 2025-08-17 | [8 empty] | 0
143 | 2026 | 2025 |  |  |  |  | 2025-08-18 | [8 empty] | 0
144 | 2026 | 2025 |  |  |  |  | 2025-08-19 | [8 empty] | 0
145 | 2026 | 2025 |  |  |  |  | 2025-08-20 | [8 empty] | 0
146 | 2026 | 2025 |  |  |  |  | 2025-08-21 | [8 empty] | 0
147 | 2026 | 2025 |  |  |  |  | 2025-08-22 | [8 empty] | 0
148 | 2026 | 2025 |  |  |  |  | 2025-08-23 | [8 empty] | 0
149 | 2026 | 2025 |  |  |  |  | 2025-08-24 | [8 empty] | 0
150 | 2026 | 2025 |  |  |  |  | 2025-08-25 | [8 empty] | 0
Formulas:
Date = [Date, row above]+1

## Spare_Consumable
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Item Consumed | Qty Consumed | Place of Consumption | Ownership of Spare/Consumable | Remarks for the day | Column1
1 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-29 | Actuator | 1 | 17 | O2 | Replaced with with spare
2 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-29 | Actuator | 1 | 93 | O2 | Replaced with with spare
3 | 2024 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-31 | Actuator | 1 | 66 | O2 | Replaced with with spare
4 | 1900 | 1900 | Year_2 | Year_2 | 2024-04-01 | 30 |  |  | 1 |  | O2 | Replaced with with spare
5 | 1900 | 1900 | Year_2 | Year_2 | 2024-04-01 | 30 |  |  | 1 |  | O2 | Replaced with with spare
6 | 1900 | 1900 | Year_2 | Year_2 | 2024-04-01 | 30 |  |  | 1 |  | O2 | Replaced with with spare
7 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
8 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
9 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
10 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
11 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
12 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
13 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
14 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
15 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
16 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
17 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
18 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
19 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
20 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
21 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
22 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
23 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
24 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
25 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
26 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
27 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
28 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
29 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
30 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
31 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
32 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
33 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
34 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
35 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
36 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
37 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
38 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
39 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
40 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
41 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
42 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
43 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
44 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
45 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
46 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
47 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
48 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
49 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
50 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
51 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
52 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
53 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
54 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
55 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
56 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
57 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
58 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
59 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
60 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
61 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
62 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
63 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
64 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
65 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
66 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
67 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
68 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
69 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
70 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
71 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
72 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
73 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
74 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
75 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
76 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
77 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
78 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
79 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
80 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
81 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
82 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
83 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
84 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
85 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
86 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
87 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
88 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
89 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
90 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
91 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
92 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
93 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
94 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
95 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
96 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
97 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
98 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
99 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
100 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
101 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
102 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
103 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
104 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
105 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
106 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
107 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
108 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
109 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
110 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
111 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
112 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
113 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
114 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
115 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
116 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
117 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
118 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
119 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
120 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
121 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
122 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
123 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
124 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
125 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
126 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
127 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
128 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
129 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 1 |  | O2 | Replaced with with spare
130 | 1900 | 1900 | Year_2 | Year_2 |  | 31 |  |  | 5 |  | O2 | Replaced with with spare pcb
Formulas:
Days = DAY(EOMONTH([Month Year],0))

## Basic Data (hidden)
Equipment | Affected DC Capacity | Plant Equivalent Weightage | Fault Category Plant BD sheet | Fault Category Tracker BD sheet | Tracker Equipment | Weightage of BD | Plant Equivalent Weightage | Status
IC1_Inv1 | 1987.725 | 16.97% | Module | MSAT100_PCB | MSAT_Type1 (5*63) | 315 | 0.8621% | Open
IC1_Inv2 | 2031.205 | 17.35% | String Cable | MSAT200_PCB | MSAT_Type2(4*63) | 252 | 0.6897% | Close
IC1_Inv3 | 1806.68 | 15.43% | String Fuse | Tilt Sensor | MSAT_Type3(3*63) | 189 | 0.5172%
IC1_Inv4 | 1844.725 | 15.75% | SCB | Actuator | MSAT_Type4(5*42) | 210 | 0.5747%
IC2_Inv1 | 2020.105 | 17.25% | SCB Cable | Battery | MSAT_Type5(4*42) | 168 | 0.4598%
IC2_Inv2 | 2020 | 17.25% | SCB Fuse | Charge Controller | MSAT_Type6(3*42) | 126 | 0.3448%
IC1_Inv1_CB1 | 191.1 | 1.632% | Inverter | RTC | Tilt Sensor_Type1(1*63) | 63 | 0.1724%
IC1_Inv1_CB2 | 191.1 | 1.632% | InverterAC Cable | Gateway | Tilt Sensor_Type2(1*42) | 42 | 0.1149%
IC1_Inv1_CB3 | 190.965 | 1.631% | IDT | MMS | Baatery_Type1(5*63) | 315 | 0.8621%
IC1_Inv1_CB4 | 188.585 | 1.61% | IDT MV Cable |  | Baatery_Type2(4*63) | 252 | 0.6897%
IC1_Inv1_CB5 | 181.67 | 1.551% | IC MV Panel |  | Baatery_Type3(3*63) | 189 | 0.5172%
IC1_Inv1_CB6 | 190.035 | 1.623% | Incomer MV Cable |  | Baatery_Type4(5*42) | 210 | 0.5747%
IC1_Inv1_CB7 | 188.17 | 1.607% | Incomer MV Panel |  | Baatery_Type5(4*42) | 168 | 0.4598%
IC1_Inv1_CB8 | 176.61 | 1.508% | Metering System Plant |  | Baatery_Type6(3*42) | 126 | 0.3448%
IC1_Inv1_CB9 | 135.865 | 1.16% | Grid System |  | CCU_Type1(5*63) | 315 | 0.8621%
IC1_Inv1_CB10 | 165.455 | 1.413% | Metering System Grid |  | CCU_Type2(4*63) | 252 | 0.6897%
IC1_Inv2_CB11 | 188.17 | 1.607% | WMS |  | CCU_Type3(3*63) | 189 | 0.5172%
IC1_Inv2_CB1 | 185.25 | 1.582% | MMS |  | CCU_Type4(5*42) | 210 | 0.5747%
IC1_Inv2_CB2 | 185.245 | 1.582% | Battery Charger_MCR |  | CCU_Type5(4*42) | 168 | 0.4598%
IC1_Inv2_CB3 | 185.255 | 1.582% | IC_UPS |  | CCU_Type6(3*42) | 126 | 0.3448%
IC1_Inv2_CB4 | 185.23 | 1.582% | IC_Auxiliary Tranformer |  | Actuator Type1(1*63) | 63 | 0.1724%
IC1_Inv2_CB5 | 185.23 | 1.582% | IC_Auxiliary DB |  | Actuator Type2(1*42) | 42 | 0.1149%
IC1_Inv2_CB6 | 185.275 | 1.582% | IC_SCADA Panel |  | RTC
IC1_Inv2_CB7 | 191.845 | 1.638% | MC4 Connector |  | Gateway
IC1_Inv2_CB8 | 191.835 | 1.638% | Y-Connector |  | Repeater
IC1_Inv2_CB9 | 188.16 | 1.607% |  |  | Switch
IC1_Inv2_CB10 | 159.705 | 1.364%
IC1_Inv2_CB11 | 188.175 | 1.607%
IC1_Inv3_CB1 | 185.23 | 1.582%
IC1_Inv3_CB2 | 185.23 | 1.582%
IC1_Inv3_CB3 | 185.225 | 1.582%
IC1_Inv3_CB4 | 185.225 | 1.582%
IC1_Inv3_CB5 | 185.23 | 1.582%
IC1_Inv3_CB6 | 185.22 | 1.582%
IC1_Inv3_CB7 | 185.22 | 1.582%
IC1_Inv3_CB8 | 139.65 | 1.193%
IC1_Inv3_CB9 | 185.22 | 1.582%
IC1_Inv3_CB10 | 185.23 | 1.582%
IC1_Inv3_CB11 | NA
IC1_Inv4_CB1 | 188.17 | 1.607%
IC1_Inv4_CB2 | 188.19 | 1.607%
IC1_Inv4_CB3 | 188.165 | 1.607%
IC1_Inv4_CB4 | 188.175 | 1.607%
IC1_Inv4_CB5 | 188.165 | 1.607%
IC1_Inv4_CB6 | 188.17 | 1.607%
IC1_Inv4_CB7 | 190.855 | 1.63%
IC1_Inv4_CB8 | 161.92 | 1.383%
IC1_Inv4_CB9 | 174.745 | 1.492%
IC1_Inv4_CB10 | 188.17 | 1.607%
IC1_Inv4_CB11 | NA
IC2_Inv1_CB1 | 188.165 | 1.607%
IC2_Inv1_CB2 | 195.09 | 1.666%
IC2_Inv1_CB3 | 191.1 | 1.632%
IC2_Inv1_CB4 | 191.1 | 1.632%
IC2_Inv1_CB5 | 190.475 | 1.627%
IC2_Inv1_CB6 | 190.575 | 1.627%
IC2_Inv1_CB7 | 191.1 | 1.632%
IC2_Inv1_CB8 | 191.1 | 1.632%
IC2_Inv1_CB9 | 191.1 | 1.632%
IC2_Inv1_CB10 | 191.1 | 1.632%
IC2_Inv1_CB11 | 109.2 | 0.9325%
IC2_Inv2_CB1 | 191.1 | 1.632%
IC2_Inv2_CB2 | 191.1 | 1.632%
IC2_Inv2_CB3 | 190.9 | 1.63%
IC2_Inv2_CB4 | 191.1 | 1.632%
IC2_Inv2_CB5 | 191.1 | 1.632%
IC2_Inv2_CB6 | 191.1 | 1.632%
IC2_Inv2_CB7 | 191.1 | 1.632%
IC2_Inv2_CB8 | 191.1 | 1.632%
IC2_Inv2_CB9 | 191.1 | 1.632%
IC2_Inv2_CB10 | 191.1 | 1.632%
IC2_Inv2_CB11 | 109.2 | 0.9325%
IC1_IDT | 7670.335 | 65.5%
IC2_IDT | 4040.105 | 34.5%
ICOG1_IC1 | 7670.335 | 65.5%
Incomer1 | 4040.105 | 34.5%
Incomer2 | 4040.105 | 34.5%
Outgoing1 | 11710.44 | 100%
Grid CB | 11710.44 | 100%
MV Cable_Incomer1 | 7683.565 | 65.61%
MV Cable INcomer2 | 4047.035 | 34.56%
MV Cable_IC1_IDT | 7683.565 | 65.61%
MV Cable_IC2_IDT | 4047.035 | 34.56%
IC1_UPS | 7683.565 | 65.61%
IC2_UPS | 4047.035 | 34.56%
IC1_Aux Tranfo. | 7683.565 | 65.61%
IC2_Aux Tranfo. | 4047.035 | 34.56%
IC1_AUX. DB | 7683.565 | 65.61%
IC2_AUX. DB | 4047.035 | 34.56%
IC1_SCADA Panel | 0 | 0%
IC2_SCADA Panel | 0 | 0%
MCR SCADA Panel | 0 | 0%
MCR_Aux Transfo. | 11710.44 | 100%
MCR_Battery Charger | 11710.44 | 100%
String_Type1_(42*310) | 13.02 | 0.1112%
String_Type2(42*315) | 13.23 | 0.113%
String_Type3(42*320) | 13.44 | 0.1148%
String_Type4(42*325) | 13.65 | 0.1166%
String_Type5(42*330) | 13.86 | 0.1184%
String_Type6(21*310) | 6.51 | 0.05559%
String_Type7(21*315) | 6.615 | 0.05649%
String_Type8(21*320) | 6.72 | 0.05738%
String_Type9(21*325) | 6.825 | 0.05828%
String_Type10(21*330) | 6.93 | 0.05918%