## Daily Dashboard
10 MW ES Energy Private Limited Performance Summary
Month | 2025-07-01
Date | 2025-07-06
Operation Year | FY2025-26
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 31.4251 | 30.6799 | -2.372%
| E_Grid MTD(MWh) | 188.5508 | 175.1095 | -7.129%
| E_Grid YTD (MWh) | 4469.548 | 4116.5305 | -7.898%
2 | CUF Daily(%) | 12.46% | 12.17% | -2.372%
| CUF MTD(%) | 12.46% | 11.57% | -7.129%
| CUF YTD(%) | 18.27% | 16.83% | -7.898%
3 | PR_Daily (%) | 70.05% | 76.54% | 9.258%
| PR_MTD (%) | 70.05% | 75.79% | 8.188%
| PR_YTD (%) | 67.96% | 71.15% | 4.699%
4 | POA Daily (KWh/m2) | 4.2694 | 3.815 | -10.64%
| POA MTD(KWh/m2) | 25.6167 | 21.99 | -14.16%
| POA YTD(KWh/m2) | 625.9662 | 550.6515 | -12.03%
5 | PA Daily (%) | 99.5% | 100% | 0.5025%
| PA MTD(%) | 99.5% | 99.94% | 0.4428%
| PA YTD(%) | 99.5% | 99.35% | -0.1463%
6 | GA Daily (%) | 99.7% | 100% | 0.3009%
| GA MTD(%) | 99.7% | 100% | 0.3009%
| GA YTD(%) | 99.7% | 98.98% | -0.7233%
7 | TA Daily (%) | 99.9% | 100% | 0.1001%
| TA MTD(%) | 99.9% | 100% | 0.1001%
| TA YTD(%) | 99.9% | 100% | 0.1001%

## CMS_Data
Daily
Tagname | Date | Target | Actual | Difference
E Grid Target | 4584400% | 31.4251 | 30.6799 | 0.74525
Shadding | 4584400% | 0 | 0 | 0
Soiling | 4584400% | 0 | 0 | 0
IAM | 4584400% | 0 | 0 | 0
Bifacial Gain | 4584400% | 0 | 0 | 0
Temperature | 4584400% | 0 | 0 | 0
Mismatch | 4584400% | 0 | 0 | 0
DC Ohmic | 4584400% | 0 | 0 | 0
AC Ohmic | 4584400% | 0 | 0 | 0
Inverter Conversion | 4584400% | 0 | 0 | 0
MPPT Mismatch | 4584400% | 0 | 0 | 0
Clipping Loss | 4584400% | 0 | 0 | 0
Curtailment Order | 4584400% | 0 | 0 | 0
Reactive Power | 4584400% | 0 | 0 | 0
Plant Uptime | 4584400% | 99.5 | 100 | 0.5 | 0.15713
Grid Uptime | 4584400% | 99.7 | 100 | 0.3 | 0.094275
Tracker Uptime | 4584400% | 99.9 | 100 | 0.1 | 0.006285
Tracker Gain | 4584400% | 0 | 0 | 0
Dc Unbalanced Load | 4584400% | 0 | 0 | 0
Measured | 4584400% | 30.6799 | 30.6799 | 30.6799
Repowering Delay | 4584400% | 0 | 0 | 0
Capacity Shortfall | 4584400% | 0 | 0 | 0
PR | 4584400% | 0 | 2.8574 | 2.8574
POA | 4584400% | 4.2694 | 3.815 | -0.45445 | -3.3449

## Annual KPI
Till Date | 2025-07-06 | 2025-07-01
ES Energy Private Limited Performance Summary
Financial Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target TA (%) | Measured TA (%)
2026 | 97 | 625.9662 | 550.6515 | 4469.548 | 4116.5305 | 67.96% | 71.15% | 18.27% | 16.83% | 99.7% | 98.98% | 99.5% | 99.35% | 99.9% | 100%
ES Energy Private Limited Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target TA (%) | Measured TA (%)
2025-04-01 | 30 | 227.6882 | 203.345 | 1584.5717 | 1460.2205 | 66.24% | 68.34% | 20.95% | 19.3% | 99.7% | 100% | 99.5% | 98.59% | 99.9% | 100%
2025-05-01 | 31 | 215.5443 | 173.3315 | 1574.4307 | 1312.1832 | 69.52% | 72.05% | 20.14% | 16.79% | 99.7% | 99.6% | 99.5% | 99.5% | 99.9% | 100%
2025-06-01 | 30 | 157.117 | 151.985 | 1121.9949 | 1169.0173 | 67.97% | 73.21% | 14.83% | 15.45% | 99.7% | 97.11% | 99.5% | 99.85% | 99.9% | 100%
2025-07-01 | 6 | 25.6167 | 21.99 | 188.5508 | 175.1095 | 70.05% | 75.79% | 12.46% | 11.57% | 99.7% | 100% | 99.5% | 99.94% | 99.9% | 100%
2025-08-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2025-09-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2025-10-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2025-11-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2025-12-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2026-01-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2026-02-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%
2026-03-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.7% |  | 99.5% |  | 99.9%

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS_YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | Bugt Capacity | CC*Bugt | DC Capacity | 10.507
1 | April | 4 | 2022-04-01 | 2022 | FY23 | 30 | 192.7392 | 227.6882 |  | 27.5 |  | 1670.3636 | 10.507 | 69.82% | 7.5896 | 0 | 0 | 0 | 55.6788 | 0 | 0 | 22.08% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1670363.6167 | 1670.3636
2 | May | 5 | 2022-05-01 | 2022 | FY23 | 31 | 184.4934 | 215.5443 |  | 26.7001 |  | 1602.1141 | 10.507 | 70.74% | 6.953 | 0 | 0 | 0 | 51.6811 | 0 | 0 | 20.49% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1602114.0818 | 1602.1141
3 | June | 6 | 2022-06-01 | 2022 | FY23 | 30 | 140.1651 | 157.117 |  | 24.6999 |  | 1181.2419 | 10.507 | 71.55% | 5.2372 | 0 | 0 | 0 | 39.3747 | 0 | 0 | 15.61% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1181241.95 | 1181.2419
4 | July | 7 | 2022-07-01 | 2022 | FY23 | 31 | 122.3162 | 132.3528 |  | 23.8 |  | 991.3682 | 10.507 | 71.29% | 4.2694 | 0 | 0 | 0 | 31.9796 | 0 | 0 | 12.68% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 991368.2439 | 991.3682
5 | August | 8 | 2022-08-01 | 2022 | FY23 | 31 | 126.2928 | 137.8495 |  | 23.6001 |  | 1037.7429 | 10.507 | 71.65% | 4.4468 | 0 | 0 | 0 | 33.4756 | 0 | 0 | 13.28% | [6 empty] | 99.5% | 99.7% | 99.9% | [7 empty] | For wind EGA | 99.5% | 1037742.9279 | 1037.7429
6 | September | 9 | 2022-09-01 | 2022 | FY23 | 30 | 144.0447 | 163.0405 |  | 23.7001 |  | 1224.9917 | 10.507 | 71.51% | 5.4347 | 0 | 0 | 0 | 40.8331 | 0 | 0 | 16.19% | [6 empty] | 99.5% | 99.7% | 99.9% | [7 empty] | Wind PA equal Bugt PA for wind |  | 1224991.6518 | 1224.9917
7 | October | 10 | 2022-10-01 | 2022 | FY23 | 31 | 146.567 | 169.4187 |  | 23.3999 |  | 1279.2413 | 10.507 | 71.86% | 5.4651 | 0 | 0 | 0 | 41.2658 | 0 | 0 | 16.36% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1279241.2821 | 1279.2413
8 | November | 11 | 2022-11-01 | 2022 | FY23 | 30 | 136.383 | 157.9207 |  | 22.5 |  | 1206.6168 | 10.507 | 72.72% | 5.264 | 0 | 0 | 0 | 40.2206 | 0 | 0 | 15.95% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1206616.7771 | 1206.6168
9 | December | 12 | 2022-12-01 | 2022 | FY23 | 31 | 149.3793 | 175.8024 |  | 21.493 |  | 1343.1158 | 10.507 | 72.71% | 5.671 | 0 | 0 | 0 | 43.3263 | 0 | 0 | 17.18% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1343115.8468 | 1343.1158
10 | January | 1 | 2023-01-01 | 2023 | FY23 | 31 | 172.6591 | 210.7416 |  | 22.1 |  | 1607.364 | 10.507 | 72.59% | 6.7981 | 0 | 0 | 0 | 51.8505 | 0 | 0 | 20.56% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1607364.046 | 1607.364
11 | February | 2 | 2023-02-01 | 2023 | FY23 | 28 | 174.4061 | 212.7888 |  | 24.1999 |  | 1596.8641 | 10.507 | 71.42% | 7.5996 | 0 | 0 | 0 | 57.0309 | 0 | 0 | 22.62% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1596864.1176 | 1596.8641
12 | March | 3 | 2023-03-01 | 2023 | FY23 | 31 | 205.4467 | 247.3821 |  | 26.7003 |  | 1826.9875 | 10.507 | 70.29% | 7.9801 | 0 | 0 | 0 | 58.9351 | 0 | 0 | 23.37% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1826987.5493 | 1826.9875
13 | April | 4 | 2023-04-01 | 2023 | FY24 | 30 | 192.7392 | 227.6882 |  | 27.5 |  | 1610 | 10.507 | 67.3% | 7.5896 | 0 | 0 | 0 | 53.6667 | 0 | 0 | 21.28% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1610000 | 1610
14 | May | 5 | 2023-05-01 | 2023 | FY24 | 31 | 184.4934 | 215.5443 |  | 26.7001 |  | 1600 | 10.507 | 70.65% | 6.953 | 0 | 0 | 0 | 51.6129 | 0 | 0 | 20.47% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1600000 | 1600
15 | June | 6 | 2023-06-01 | 2023 | FY24 | 30 | 140.1651 | 157.117 |  | 24.6999 |  | 1140 | 10.507 | 69.06% | 5.2372 | 0 | 0 | 0 | 38 | 0 | 0 | 15.07% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1140000 | 1140
16 | July | 7 | 2023-07-01 | 2023 | FY24 | 31 | 122.3162 | 132.3528 |  | 23.8 |  | 990 | 10.507 | 71.19% | 4.2694 | 0 | 0 | 0 | 31.9355 | 0 | 0 | 12.66% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 990000 | 990
17 | August | 8 | 2023-08-01 | 2023 | FY24 | 31 | 126.2928 | 137.8495 |  | 23.6001 |  | 1040 | 10.507 | 71.8% | 4.4468 | 0 | 0 | 0 | 33.5484 | 0 | 0 | 13.3% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1040000 | 1040
18 | September | 9 | 2023-09-01 | 2023 | FY24 | 30 | 144.0447 | 163.0405 |  | 23.7001 |  | 1180 | 10.507 | 68.88% | 5.4347 | 0 | 0 | 0 | 39.3333 | 0 | 0 | 15.6% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1180000 | 1180
19 | October | 10 | 2023-10-01 | 2023 | FY24 | 31 | 146.567 | 169.4187 |  | 23.3999 |  | 1680 | 10.507 | 94.38% | 5.4651 | 0 | 0 | 0 | 54.1935 | 0 | 0 | 21.49% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1680000 | 1680
20 | November | 11 | 2023-11-01 | 2023 | FY24 | 30 | 136.383 | 157.9207 |  | 22.5 |  | 1530 | 10.507 | 92.21% | 5.264 | 0 | 0 | 0 | 51 | 0 | 0 | 20.22% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1530000 | 1530
21 | December | 12 | 2023-12-01 | 2023 | FY24 | 31 | 149.3793 | 175.8024 |  | 21.493 |  | 1760 | 10.507 | 95.28% | 5.671 | 0 | 0 | 0 | 56.7742 | 0 | 0 | 22.51% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1760000 | 1760
22 | January | 1 | 2024-01-01 | 2024 | FY24 | 31 | 172.6591 | 210.7416 |  | 22.1 |  | 2110 | 10.507 | 95.29% | 6.7981 | 0 | 0 | 0 | 68.0645 | 0 | 0 | 26.99% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 2110000 | 2110
23 | February | 2 | 2024-02-01 | 2024 | FY24 | 29 | 174.4061 | 212.7888 |  | 24.1999 |  | 1960 | 10.507 | 87.67% | 7.3375 | 0 | 0 | 0 | 67.5862 | 0 | 0 | 26.8% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1960000 | 1960
24 | March | 3 | 2024-03-01 | 2024 | FY24 | 31 | 205.4467 | 247.3821 |  | 26.7003 |  | 2400 | 10.507 | 92.33% | 7.9801 | 0 | 0 | 0 | 77.4194 | 0 | 0 | 30.7% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 2400000 | 2400
25 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 | 192.7392 | 227.6882 |  | 27.5 |  | 1598.2 | 10.507 | 66.81% | 7.5896 | 0 | 0 | 0 | 53.2733 | 0 | 0 | 21.13% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1598200 | 1598.2
26 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 | 184.4934 | 215.5443 |  | 26.7001 |  | 1587.9 | 10.507 | 70.11% | 6.953 | 0 | 0 | 0 | 51.2226 | 0 | 0 | 20.31% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1587900 | 1587.9
27 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 | 140.1651 | 157.117 |  | 24.6999 |  | 1131.6 | 10.507 | 68.55% | 5.2372 | 0 | 0 | 0 | 37.72 | 0 | 0 | 14.96% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1131600 | 1131.6
28 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 | 122.3162 | 132.3528 |  | 23.8 |  | 982.5 | 10.507 | 70.65% | 4.2694 | 0 | 0 | 0 | 31.6935 | 0 | 0 | 12.57% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 982500 | 982.5
29 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 | 126.2928 | 137.8495 |  | 23.6001 |  | 1032.2 | 10.507 | 71.27% | 4.4468 | 0 | 0 | 0 | 33.2968 | 0 | 0 | 13.2% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1032200 | 1032.2
30 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 | 144.0447 | 163.0405 |  | 23.7001 |  | 1171.3 | 10.507 | 68.37% | 5.4347 | 0 | 0 | 0 | 39.0433 | 0 | 0 | 15.48% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1171300 | 1171.3
31 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 | 146.567 | 169.4187 |  | 23.3999 |  | 1280.3 | 10.507 | 71.92% | 5.4651 | 0 | 0 | 0 | 41.3 | 0 | 0 | 16.38% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1280300 | 1280.3
32 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 | 136.383 | 157.9207 |  | 22.5 |  | 1171.3 | 10.507 | 70.59% | 5.264 | 0 | 0 | 0 | 39.0433 | 0 | 0 | 15.48% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1171300 | 1171.3
33 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 | 149.3793 | 175.8024 |  | 21.493 |  | 1349.7 | 10.507 | 73.07% | 5.671 | 0 | 0 | 0 | 43.5387 | 0 | 0 | 17.27% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1349700 | 1349.7
34 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 | 172.6591 | 210.7416 |  | 22.1 |  | 1607.8 | 10.507 | 72.61% | 6.7981 | 0 | 0 | 0 | 51.8645 | 0 | 0 | 20.57% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1607800 | 1607.8
35 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 | 174.4061 | 212.7888 |  | 24.1999 |  | 1479.9 | 10.507 | 66.19% | 7.5996 | 0 | 0 | 0 | 52.8536 | 0 | 0 | 20.96% | [6 empty] | 99.5% | 99.7% | 99.9% | [9 empty] | 1479900 | 1479.9
36 | March | 3 | 2025-03-01 | 2025 | FY25 | 31 | 205.4467 | 247.3821 |  | 26.7003 |  | 1826.1 | 10.507 | 70.26% | 7.9801 | 3 | 23.9402 | 23.9402 | 58.9065 | 176.7194 | 176.7194 | 23.36% | 23.36% | 23.36% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9% | [9 empty] | 1826100 | 1826.1
37 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 | 192.7392 | 227.6882 |  | 27.5 |  | 1584.5717 | 10.507 | 66.24% | 7.5896 | 30 | 227.6882 | 227.6882 | 52.8191 | 1584.5717 | 1584.5717 | 20.95% | 20.95% | 20.95% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
38 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 | 184.4934 | 215.5443 |  | 26.7001 |  | 1574.4307 | 10.507 | 69.52% | 6.953 | 31 | 215.5443 | 625.9662 | 50.7881 | 1574.4307 | 4469.548 | 20.14% | 20.14% | 29.06% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
39 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 | 140.1651 | 157.117 |  | 24.6999 |  | 1121.9949 | 10.507 | 67.97% | 5.2372 | 30 | 157.117 | 600.3495 | 37.3998 | 1121.9949 | 4280.9973 | 14.83% | 14.83% | 18.66% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
40 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 | 122.3162 | 132.3528 |  | 23.8 |  | 974.179 | 10.507 | 70.05% | 4.2694 | 6 | 25.6167 | 625.9662 | 31.4251 | 188.5508 | 4469.548 | 12.46% | 12.46% | 18.27% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
41 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 | 126.2928 | 137.8495 |  | 23.6001 |  | 1023.38 | 10.507 | 70.66% | 4.4468 | 0 | 0 | 625.9662 | 33.0123 | 0 | 4469.548 | 13.09% |  | 18.27% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
42 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 | 144.0447 | 163.0405 |  | 23.7001 |  | 1161.3631 | 10.507 | 67.79% | 5.4347 | 0 | 0 | 625.9662 | 38.7121 | 0 | 4469.548 | 15.35% |  | 18.27% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
43 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 | 146.567 | 169.4187 |  | 23.3999 |  | 1269.3848 | 10.507 | 71.31% | 5.4651 | 0 | 0 | 625.9662 | 40.9479 | 0 | 4469.548 | 16.24% |  | 18.27% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
44 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 | 136.383 | 157.9207 |  | 22.5 |  | 1161.3631 | 10.507 | 69.99% | 5.264 | 0 | 0 | 625.9662 | 38.7121 | 0 | 4469.548 | 15.35% |  | 18.27% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
45 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 | 149.3793 | 175.8024 |  | 21.493 |  | 1338.2661 | 10.507 | 72.45% | 5.671 | 0 | 0 | 625.9662 | 43.1699 | 0 | 4469.548 | 17.12% |  | 18.27% | 10.507 | 10.507 |  |  | 99.5% | 99.7% | 99.9%
46 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 | 172.6591 | 210.7416 |  | 22.1 |  | 1594.1111 | 10.507 | 71.99% | 6.7981 | 0 | 0 | 625.9662 | 51.4229 | 0 | 4469.548 | 20.39% |  | 18.27% |  | 10.507 |  |  | 99.5% | 99.7% | 99.9%
47 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 | 174.4061 | 212.7888 |  | 24.1999 |  | 1467.2907 | 10.507 | 65.63% | 7.5996 | 0 | 0 | 625.9662 | 52.4032 | 0 | 4469.548 | 20.78% |  | 18.27% |  | 10.507 |  |  | 99.5% | 99.7% | 99.9%
48 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 | 205.4467 | 247.3821 |  | 26.7003 |  | 1810.5953 | 10.507 | 69.66% | 7.9801 | 0 | 0 | 625.9662 | 58.4063 | 0 | 4469.548 | 23.16% |  | 18.27% |  | 10.507 |  |  | 99.5% | 99.7% | 99.9%
[12 empty] | 1796043.7401 | 1796.0437
[12 empty] | 1722663.7863 | 1722.6638
[12 empty] | 1270329.9882 | 1270.33
[12 empty] | 1065924.7176 | 1065.9247
[12 empty] | 1106298.1096 | 1106.2981
[12 empty] | 1316920.9396 | 1316.9209
[12 empty] | 1364355.656 | 1364.3557
[12 empty] | 1286868.6937 | 1286.8687
[12 empty] | 1432329.582 | 1432.3296
[12 empty] | 1634508.3255 | 1634.5083
[12 empty] | 1635740.3774 | 1635.7404
[12 empty] | 1947603.0582 | 1947.6031
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## Monthly KPI
Till Date | 2025-07-06
ES Energy Private Limited Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target TA (%) | Measured TA (%)
2025-07-01 | 6 | 25.6167 | 21.99 | 188.5508 | 175.1095 | 70.05% | 75.79% | 12.46% | 11.57% | 99.7% | 100% | 99.5% | 99.94% | 99.9% | 100%
Start Date | 2025-06-30
End Date | 2025-07-06
ES Energy Private Limited Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | Target TA (%) | Measured TA (%)
2025-07-01 | 7 | 30.8539 | 28.09 | 225.9506 | 221.6085 | 69.7% | 75.09% | 12.8% | 12.55% | 99.7% | 100% | 99.5% | 99.95% | 99.9% | 100%
Formulas:
Days = [Days, row below]-6

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 12 | 6.6 |  | 7.375 |  | 30.4938 | 46.4586 | 0.67534 | 0.69938 | [5 empty] | 100% |  |  |  | 54235 |  |  |  | 10.507 | 7.9801 | 58906.4516 | 70.26% | 23.36% | 99.5% | 99.7% | [9 empty] | 10.507
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 12.0167 | 6.48 |  | 7.35 |  | 30.195 | 46.4332 | 0.77069 | 3.0956 | 99.41% |  |  | 100% |  | 100% | 69.07% |  | 21.15% | 53893 | 53644.4 | 307.2 | 53337.2 | 10.507 | 7.9801 | 58906.4516 | 70.26% | 23.36% | 99.5% | 99.7% | [9 empty] | 10.507
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 12.0667 | 6.12 |  | 6.55 |  | 30.0404 | 44.9267 | 0.68876 | 3.2757 | 100% |  |  | 100% |  | 100% | 70.32% |  | 19.19% | 49194 | 48696.2 | 300.12 | 48396.08 | 10.507 | 7.9801 | 58906.4516 | 70.26% | 23.36% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 12.0333 | 5.15 |  | 5.39 |  | 28.4382 | 41.5418 | 0.68871 | 0.7893 | 100% |  |  | 100% |  | 100% | 70.39% |  | 15.81% | 40482 | 40160.4 | 298.14 | 39862.26 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 11.85 | 5.9 |  | 6.35 |  | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 99.72% |  |  | 100% |  | 100% | 69.35% |  | 18.35% | 46883 | 46564.5 | 297.24 | 46267.26 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 11.8167 | 3.96 |  | 4.01 |  | 25.546 | 35.8572 | 0.82389 | 5.4078 | 100% |  |  | 100% |  | 100% | 71.45% |  | 11.94% | 30661 | 30406.1 | 303.66 | 30102.44 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 11.7167 | 6.87 |  | 7.54 |  | 29.7818 | 46.949 | 0.66326 | 3.4188 | 93.78% |  |  | 100% |  | 100% | 63.81% |  | 20.05% | 51196 | 50867.5 | 315.9 | 50551.6 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 12.0333 | 5.83 |  | 6.46 |  | 28.4187 | 45.7694 | 0.68469 | 1.9063 | 94.53% |  |  | 100% |  | 100% | 62.01% |  | 16.69% | 42695 | 42409.8 | 320.28 | 42089.52 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 11.9333 | 6.67 |  | 7.57 |  | 28.7698 | 47.3622 | 0.80936 | 5.3675 | 92.12% |  |  | 100% |  | 100% | 62.28% |  | 19.64% | 50173 | 49870.8 | 333.6 | 49537.2 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 12.0833 | 6.71 |  | 7.795 |  | 30.2429 | 47.9448 | 0.93582 | 4.3852 | 95.38% |  |  | 100% |  | 100% | 64.3% |  | 20.88% | 53234 | 52971 | 306.72 | 52664.28 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 11.75 | 6.17 |  | 6.915 |  | 29.8993 | 45.5016 | 0.88285 | 3.6838 | 100% |  |  | 100% |  | 100% | 67.4% |  | 19.42% | 49687 | 49299.7 | 330.24 | 48969.46 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 11.95 | 6.37 |  | 7.28 |  | 29.6186 | 46.9441 | 0.86043 | 2.7865 | 99.55% |  |  | 100% |  | 100% | 68.17% |  | 20.68% | 52795 | 52462 | 321.78 | 52140.22 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 12.2333 | 5.79 |  | 6.5 |  | 28.7091 | 41.8396 | 1.2756 | 3.9577 | 100% |  |  | 100% |  | 100% | 70.66% |  | 19.14% | 48867 | 48565 | 310.32 | 48254.68 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 11.8833 | 6.45 |  | 7.39 |  | 30.195 | 46.4332 | 0.77069 | 3.0956 | 99.08% |  |  | 100% |  | 100% | 69% |  | 21.25% | 54147 | 53890.1 | 311.7 | 53578.4 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 6.28 |  | 6.92 |  | 29.689 | 46.6091 | 0.67979 | 4.34 | 99.76% |  |  | 100% |  | 100% | 70.78% |  | 20.41% | 52068 | 51780.9 | 316.32 | 51464.58 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 12.1167 | 6.52 |  | 7.375 |  | 30.195 | 46.4332 | 0.77069 | 3.0956 | 99.82% |  |  | 100% |  | 100% | 68.99% |  | 21.2% | 54092 | 53778 | 319.02 | 53458.98 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 12.0167 | 5.86 |  | 6.35 |  | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 100% |  |  | 100% |  | 100% | 69.22% |  | 18.32% | 46808 | 46506.6 | 321 | 46185.6 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 11.9833 | 6.99 |  | 8 |  | 30.166 | 48.516 | 0.50302 | 0.51512 | 91.22% |  |  | 100% |  | 100% | 60.2% |  | 20.07% | 51167 | 50904.5 | 302.22 | 50602.28 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 11.9167 | 5.89 |  | 6.75 |  | 28.7698 | 47.3622 | 0.80936 | 5.3675 | 100% |  |  | 100% |  | 100% | 70.1% |  | 19.71% | 50324 | 50024.5 | 311.52 | 49712.98 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 6.95 |  | 7.71 |  | 28.463 | 43.4858 | 1.6153 | 3.9035 | 99.65% |  |  | 100% |  | 100% | 69.49% |  | 22.32% | 56566 | 56633 | 340.8 | 56292.2 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 12.0333 | 6.15 |  | 6.69 |  | 28.7698 | 47.3622 | 0.80936 | 5.3675 | 100% |  |  | 100% |  | 100% | 70.09% |  | 19.54% | 50070 | 49607.9 | 338.76 | 49269.14 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 11.8167 | 6.15 |  | 6.69 |  | 30.166 | 48.516 | 0.50302 | 0.51512 | 100% |  |  | 100% |  | 100% | 72.48% |  | 20.2% | 51579 | 51255.3 | 304.86 | 50950.44 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 11.6667 | 4.3 |  | 4.67 |  | 25.0801 | 36.1312 | 1.2497 | 5.4514 | 100% |  |  | 100% |  | 100% | 73.2% |  | 14.24% | 36513 | 36221.9 | 302.64 | 35919.26 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 12.0833 | 6.23 |  | 6.94 |  | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 93.32% |  |  | 100% |  | 100% | 62.32% |  | 18.02% | 46107 | 45826.5 | 381.3 | 45445.2 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 12.1667 | 6.42 |  | 7.2 |  | 30.195 | 46.4332 | 0.77069 | 3.0956 | 100% |  |  | 100% |  | 100% | 70.21% |  | 21.06% | 53685 | 53370.8 | 257.4 | 53113.4 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 12.15 | 6.08 |  | 6.4 |  | 30.2277 | 45.4561 | 0.88646 | 4.0239 | 100% |  |  | 100% |  | 100% | 70.54% |  | 18.81% | 48034 | 47736.8 | 305.52 | 47431.28 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 12.2167 | 6.66 |  | 7.175 |  | 30.7169 | 47.3243 | 1.0548 | 4.043 | 100% |  |  | 100% |  | 100% | 69.8% |  | 20.87% | 53244 | 52925.3 | 305.76 | 52619.54 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 12.0333 | 6.14 |  | 6.48 |  | 30.479 | 47.1594 | 0.89744 | 3.3385 | 100% |  |  | 100% |  | 100% | 70.49% |  | 19.03% | 48596 | 48299.1 | 308.7 | 47990.4 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 12.25 | 6.83 |  | 7.555 |  | 30.1302 | 47.6614 | 1.2327 | 4.8132 | 99.65% |  |  | 100% |  | 100% | 68.09% |  | 21.44% | 54705 | 54362.6 | 308.88 | 54053.72 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 12.1333 | 6.07 |  | 6.38 |  | 30.2277 | 45.4561 | 0.88646 | 4.0239 | 100% |  |  | 100% |  | 100% | 70.62% |  | 18.77% | 47907 | 47634.5 | 296.58 | 47337.92 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 11.8667 | 6.45 |  | 7.2 |  | 30.195 | 46.4332 | 0.77069 | 3.0956 | 100% |  |  | 100% |  | 100% | 70.83% |  | 21.25% | 54162 | 53883 | 298.08 | 53584.92 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 12.3167 | 6.32 |  | 6.74 |  | 28.8325 | 45.3299 | 0.84028 | 4.5702 | 100% |  |  | 100% |  | 100% | 69.99% |  | 19.66% | 50174 | 49894.5 | 326.22 | 49568.28 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 12.2167 | 6.39 |  | 6.92 |  | 29.0602 | 45.8714 | 1.0987 | 8.6629 | 100% |  |  | 100% |  | 100% | 70.42% |  | 20.31% | 51819 | 51524.8 | 321.72 | 51203.08 | 10.507 | 7.5896 | 52819.0562 | 66.24% | 20.95% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 12.35 | 3.54 |  | 4.11 |  | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 100% |  |  | 92.34% |  | 100% | 70.43% |  | 12.06% | 30886 | 30715.2 | 301.14 | 30414.06 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 12.25 | 6.09 |  | 6.63 |  | 29.2157 | 45.438 | 0.72585 | 2.4936 | 100% |  |  | 100% |  | 100% | 70.34% |  | 19.43% | 49594 | 49302.6 | 303.9 | 48998.7 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 12.3333 | 6.51 |  | 7.1115 |  | 28.1139 | 44.2016 | 0.9761 | 3.9187 | 100% |  |  | 100% |  | 100% | 70.49% |  | 20.89% | 53263 | 53007.8 | 339.3 | 52668.5 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 12.5667 | 6.85 |  | 7.435 |  | 29.436 | 45.0088 | 1.0626 | 4.7309 | 100% |  |  | 100% |  | 100% | 70% |  | 21.68% | 55317 | 55015.5 | 333.9 | 54681.6 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 12.2 | 7.05 |  | 7.68 |  | 30.0837 | 48.4744 | 0.81191 | 3.4706 | 100% |  |  | 100% |  | 100% | 69.6% |  | 22.27% | 56763 | 56466.9 | 302.4 | 56164.5 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 12.4333 | 7.32 |  | 8.09 |  | 29.9635 | 46.6534 | 1.1117 | 4.0151 | 100% |  |  | 100% |  | 100% | 70.28% |  | 23.69% | 60376 | 60044.3 | 301.5 | 59742.8 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 12.3667 | 7.18 |  | 7.65 |  | 30.1719 | 46.9672 | 1.0444 | 3.5784 | 100% |  |  | 100% |  | 100% | 70.91% |  | 22.6% | 57616 | 57301.1 | 305.22 | 56995.88 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 12.4167 | 7.12 |  | 7.59 |  | 29.0606 | 46.286 | 1.1257 | 4.0229 | 100% |  |  | 100% |  | 100% | 70.37% |  | 22.26% | 56735 | 56430.1 | 308.94 | 56121.16 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 12.4833 | 6.7 |  | 6.9 |  | 29.1228 | 46.1707 | 0.85347 | 5.0674 | 100% |  |  | 100% |  | 100% | 71.25% |  | 20.49% | 52295 | 51954.8 | 297.54 | 51657.26 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 12.5333 | 7.29 |  | 8.055 |  | 29.3381 | 47.275 | 1.0885 | 4.3083 | 100% |  |  | 100% |  | 100% | 69.71% |  | 23.4% | 59587 | 59289.6 | 289.08 | 59000.52 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 12.4667 | 7.31 |  | 7.725 |  | 29.4336 | 47.5887 | 0.77545 | 3.6446 | 99.24% |  |  | 100% |  | 100% | 70.07% |  | 22.55% | 57526 | 57178.6 | 304.98 | 56873.62 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 12.25 | 6.86 |  | 7.49 |  | 29.2109 | 45.9608 | 0.87807 | 3.8396 | 99.7% |  |  | 100% |  | 100% | 67.26% |  | 20.99% | 53536 | 53230.8 | 296.64 | 52934.16 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 12.1667 | 6.74 |  | 7.425 |  | 27.805 | 44.9838 | 1.1785 | 5.2118 | 100% |  |  | 100% |  | 100% | 70.52% |  | 21.82% | 55683 | 55335.7 | 320.16 | 55015.54 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 12.4833 | 6.2 |  | 6.8 |  | 28.8336 | 44.3876 | 0.8506 | 2.5289 | 99.71% |  |  | 100% |  | 100% | 69.96% |  | 19.82% | 50584 | 50304.1 | 322.56 | 49981.54 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 12.3333 | 6.21 |  | 6.475 |  | 28.3453 | 44.0653 | 0.86462 | 3.7344 | 100% |  |  | 100% |  | 100% | 70.97% |  | 19.15% | 48886 | 48587.4 | 304.44 | 48282.96 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 12.4333 | 6.18 |  | 6.82 |  | 27.7906 | 43.4285 | 1.0359 | 5.8035 | 99.61% |  |  | 100% |  | 100% | 69.8% |  | 19.83% | 50672 | 50333.3 | 316.02 | 50017.28 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 11.9667 | 3.77 |  | 3.83 |  | 25.9971 | 35.2061 | 0.98105 | 7.1985 | 100% |  |  | 100% |  | 100% | 74.66% |  | 11.91% | 30557 | 30361.4 | 316.38 | 30045.02 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 12.3333 | 6.05 |  | 6.4 |  | 27.759 | 41.2443 | 1.1753 | 4.1536 | 98.25% |  |  | 100% |  | 100% | 71.09% |  | 18.96% | 48440 | 48124 | 320.16 | 47803.84 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 11.7333 | 2.8 |  | 2.7 |  | 24.5407 | 30.8411 | 0.73105 | 3.1102 | 100% |  |  | 100% |  | 100% | 79.58% |  | 8.952% | 23247 | 22910 | 335.28 | 22574.72 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 11.5833 | 3.4 |  | 3.32 |  | 24.4541 | 32.8874 | 0.9356 | 5.0809 | 100% |  |  | 100% |  | 100% | 76.72% |  | 10.61% | 27334 | 27107.6 | 344.52 | 26763.08 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 12.5333 | 3.84 |  | 3.87 |  | 24.4997 | 32.5266 | 1.7049 | 8.8073 | 100% |  |  | 100% |  | 100% | 75.83% |  | 12.23% | 31363 | 31150.6 | 317.64 | 30832.96 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 12.4667 | 5.17 |  | 5.38 |  | 26.4095 | 37.0329 | 1.5431 | 6.5777 | 100% |  |  | 100% |  | 100% | 74.24% |  | 16.64% | 42418 | 42265.1 | 301.2 | 41963.9 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 12.55 | 4.282 |  | 5.25 |  | 25.4426 | 35.2243 | 2.3078 | 8.0038 | 99.66% |  |  | 100% |  | 100% | 71.48% |  | 15.64% | 39983 | 39726.5 | 297.66 | 39428.84 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 12.2667 | 3.05 |  | 3.005 |  | 24.9328 | 31.1882 | 2.7855 | 9.2161 | 90.67% |  |  | 97.63% |  | 100% | 70.77% |  | 8.861% | 22845 | 22653.2 | 309.54 | 22343.66 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 12.3333 | 3.08 |  | 3.18 |  | 23.9943 | 30.1193 | 2.6118 | 8.8609 | 98.88% |  |  | 97.66% |  | 100% | 82.08% |  | 10.88% | 27658 | 27757.2 | 333.78 | 27423.42 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 12.35 | 3.52 |  | 3.48 |  | 25.965 | 35.6713 | 0.92166 | 10.1554 | 99.69% |  |  | 100% |  | 100% | 79.49% |  | 11.53% | 29675 | 29399 | 334.5 | 29064.5 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 12.4167 | 3.82 |  | 3.825 |  | 24.4997 | 32.5266 | 1.7049 | 8.8073 | 100% |  |  | 100% |  | 100% | 78.08% |  | 12.44% | 31929 | 31673.3 | 292.62 | 31380.68 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 12.0167 | 3.45 |  | 3.35 |  | 25.0635 | 31.196 | 1.7759 | 9.2261 | 99.11% |  |  | 100% |  | 100% | 77.49% |  | 10.82% | 28074 | 27668.9 | 394.98 | 27273.92 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 12.5667 | 3.82 |  | 3.73 |  | 24.8504 | 32.0049 | 1.7221 | 6.348 | 100% |  |  | 100% |  | 100% | 79.72% |  | 12.39% | 31705 | 31459.8 | 217.8 | 31242 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 12.4333 | 3.04 |  | 2.84 |  | 24.9062 | 31.002 | 1.1343 | 6.0709 | 100% |  |  | 100% |  | 100% | 79.81% |  | 9.445% | 24404 | 24174.1 | 357.72 | 23816.38 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 12.5667 | 5.15 |  | 5.185 |  | 26.5776 | 37.2281 | 0.83761 | 4.3921 | 100% |  |  | 100% |  | 100% | 74.66% |  | 16.13% | 41184 | 40932.2 | 256.02 | 40676.18 | 10.507 | 6.953 | 50788.0873 | 69.52% | 20.14% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 6.55 |  | 6.93 |  | 27.3767 | 41.1267 | 1.6266 | 6.4821 | 100% |  |  | 100% |  | 100% | 72.15% |  | 20.83% | 53154 | 52863.7 | 325.92 | 52537.78 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 12.5667 | 5.57 |  | 6.035 |  | 27.2883 | 39.0841 | 1.9193 | 5.6299 | 100% |  |  | 100% |  | 100% | 72.57% |  | 18.25% | 46599 | 46304.9 | 285.48 | 46019.42 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 12.55 | 4.89 |  | 5.14 |  | 25.605 | 36.1476 | 1.4758 | 6.5289 | 99.48% |  |  | 100% |  | 100% | 73.09% |  | 15.65% | 40194 | 39789.7 | 318.06 | 39471.64 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 12.6167 | 6.58 |  | 7.005 |  | 27.1915 | 41.3755 | 0.88924 | 4.8114 | 100% |  |  | 100% |  | 100% | 72.33% |  | 21.11% | 53894 | 53552.2 | 314.58 | 53237.62 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 6.7 |  | 7.385 |  | 27.7997 | 43.1336 | 0.7642 | 1.0214 | 100% |  |  | 98.49% |  | 100% | 70.06% |  | 21.56% | 54911 | 54650.2 | 284.76 | 54365.44 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 12.6167 | 6.98 |  | 7.81 |  | 28.4327 | 45.7312 | 0.75488 | 0.95623 | 99.44% |  |  | 100% |  | 100% | 68.92% |  | 22.43% | 57121 | 56822.9 | 266.76 | 56556.14 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 12.6667 | 7.33 |  | 8.04 |  | 27.8549 | 45.2894 | 0.74587 | 0.88982 | 99.1% |  |  | 100% |  | 100% | 68.75% |  | 23.03% | 58895 | 58384.4 | 309.24 | 58075.16 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 12.6 | 6.98 |  | 7.535 |  | 28.6728 | 45.2306 | 0.72955 | 0.89025 | 100% |  |  | 100% |  | 100% | 69.66% |  | 21.87% | 55744 | 55431.4 | 281.46 | 55149.94 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 11.1833 | 4.54 |  | 4.545 |  | 26.9089 | 38.0863 | 0.70516 | 0.81437 | 99.64% |  |  | 100% |  | 100% | 72.5% |  | 13.73% | 35220 | 34941 | 318.3 | 34622.7 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 12.6833 | 5.3 |  | 5.63 |  | 26.4095 | 37.0329 | 1.5431 | 6.5777 | 100% |  |  | 94.61% |  | 100% | 72.29% |  | 16.96% | 42814 | 43074.7 | 313.92 | 42760.78 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 11.8167 | 4.31 |  | 4.44 |  | 26.5317 | 37.1209 | 0.73589 | 7.87 | 100% |  |  | 100% |  | 100% | 74.6% |  | 13.8% | 35337 | 35099.7 | 296.88 | 34802.82 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 12.35 | 4.4 |  | 4.555 |  | 25.5925 | 35.2972 | 1.4968 | 6.8728 | 100% |  |  | 100% |  | 100% | 73.13% |  | 13.88% | 35668 | 35332.8 | 334.02 | 34998.78 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 12.3333 | 3.85 |  | 3.94 |  | 24.8504 | 32.0049 | 1.7221 | 6.348 | 100% |  |  | 100% |  | 100% | 75.23% |  | 12.35% | 31579 | 31433.3 | 291.12 | 31142.18 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 11.8167 | 3.86 |  | 3.83 |  | 25.0924 | 33.2292 | 1.4089 | 5.8479 | 99.45% |  |  | 100% |  | 100% | 74.67% |  | 11.92% | 30633 | 30367.5 | 319.62 | 30047.88 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 12.5667 | 3.1 |  | 3 |  | 23.9379 | 28.828 | 2.9794 | 8.7773 | 100% |  |  | 100% |  | 100% | 78.48% |  | 9.81% | 25311 | 25025.9 | 289.14 | 24736.76 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 12.4833 | 4.11 |  | 4.255 |  | 24.539 | 31.5177 | 2.6537 | 10.3186 | 99.68% |  |  | 100% |  | 100% | 74.33% |  | 13.18% | 33762 | 33533.7 | 301.74 | 33231.96 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 12.4833 | 3.62 |  | 3.54 |  | 24.5281 | 31.0709 | 1.4826 | 6.9411 | 100% |  |  | 100% |  | 100% | 77.36% |  | 11.41% | 29336 | 29075.5 | 301.14 | 28774.36 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 12.5333 | 4.15 |  | 4.23 |  | 25.3852 | 34.0119 | 0.74291 | 3.351 | 100% |  |  | 100% |  | 100% | 76.07% |  | 13.41% | 34349 | 34104.8 | 295.98 | 33808.82 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 4.99 |  | 5.1 |  | 26.0367 | 35.6802 | 0.64889 | 2.4967 | 98.86% |  |  | 100% |  | 100% | 74.96% |  | 15.93% | 40659 | 40461.6 | 293.46 | 40168.14 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 12.6667 | 5.7 |  | 6.12 |  | 26.5611 | 38.1114 | 1.2775 | 6.5962 | 100% |  |  | 100% |  | 100% | 72.75% |  | 18.55% | 47760 | 47072.4 | 291.36 | 46781.04 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 5.63 |  | 5.915 |  | 26.6403 | 37.3416 | 2.2367 | 6.7845 | 100% |  |  | 100% |  | 100% | 74.02% |  | 18.24% | 46582 | 46294.7 | 290.22 | 46004.48 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 12.6167 | 0.65 |  | 0.75 |  | 25.1226 | 32.9897 | 1.894 | 7.725 | 100% |  |  | 20.23% |  | 100% | 87.27% |  | 2.727% | 7264 | 7170.4 | 293.4 | 6877 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 12.35 | 4.83 |  | 4.83 |  | 25.3778 | 33.8383 | 2.7888 | 8.3454 | 100% |  |  | 100% |  | 100% | 76.74% |  | 15.44% | 39386 | 39246.1 | 301.26 | 38944.84 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 3.64 |  | 3.56 |  | 24.8022 | 31.1665 | 2.3958 | 8.3188 | 100% |  |  | 100% |  | 100% | 77.68% |  | 11.52% | 29608 | 29364.2 | 308.82 | 29055.38 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 12.5 | 2.97 |  | 2.87 |  | 23.9379 | 28.828 | 2.9794 | 8.7773 | 100% |  |  | 100% |  | 100% | 78.47% |  | 9.384% | 24215 | 23934.7 | 271.5 | 23663.2 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 12.6667 | 4.24 |  | 4.32 |  | 25.9955 | 34.2471 | 2.3294 | 6.7935 | 100% |  |  | 100% |  | 100% | 74.72% |  | 13.45% | 34482 | 34208.7 | 295.02 | 33913.68 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 12.5 | 3.85 |  | 3.935 |  | 24.8504 | 32.0049 | 1.7221 | 6.348 | 100% |  |  | 100% |  | 100% | 74.81% |  | 12.27% | 31473 | 31221 | 291.18 | 30929.82 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 12.5833 | 4.44 |  | 4.51 |  | 25.6635 | 34.8133 | 2.1412 | 6.8482 | 100% |  |  | 100% |  | 100% | 74.07% |  | 13.92% | 35660 | 35421.2 | 324.18 | 35097.02 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 12.5667 | 5.59 |  | 6.13 |  | 26.469 | 37.6205 | 2.6835 | 6.9793 | 100% |  |  | 100% |  | 100% | 72.57% |  | 18.54% | 47284 | 47039.1 | 295.56 | 46743.54 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 12.6 | 5.73 |  | 6.1 |  | 26.1369 | 36.905 | 2.8151 | 8.1669 | 100% |  |  | 100% |  | 100% | 72.55% |  | 18.44% | 47160 | 46778.8 | 279.84 | 46498.96 | 10.507 | 5.2372 | 37399.8286 | 67.97% | 14.83% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 12.5333 | 2.81 |  | 2.73 |  | 24.5237 | 29.5575 | 1.9007 | 6.3871 | 100% |  |  | 100% |  | 100% | 78.26% |  | 8.902% | 22912 | 22756.1 | 308.7 | 22447.4 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 12.5667 | 4.16 |  | 4.165 |  | 25.305 | 32.8784 | 2.7888 | 8.3454 | 100% |  |  | 100% |  | 100% | 75.08% |  | 13.03% | 33427 | 33176.8 | 322.56 | 32854.24 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 12.3333 | 3.28 |  | 3.23 |  | 24.0753 | 30.4552 | 2.0251 | 6.7358 | 100% |  |  | 100% |  | 100% | 77.51% |  | 10.43% | 26824 | 26633 | 326.94 | 26306.06 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 12.5333 | 5.62 |  | 5.42 |  | 26.1687 | 36.736 | 2.5883 | 8.6863 | 99.64% |  |  | 100% |  | 100% | 72.21% |  | 16.31% | 41656 | 41416.1 | 296.28 | 41119.82 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 12.55 | 2.71 |  | 2.63 |  | 23.9478 | 28.5037 | 1.8307 | 5.4042 | 100% |  |  | 100% |  | 100% | 78.54% |  | 8.606% | 22188 | 21980.1 | 277.98 | 21702.12 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 12.6333 | 3.76 |  | 3.815 |  | 24.2217 | 47.3601 | 2.4316 | 7.1164 | 100% |  |  | 100% |  | 100% | 76.54% |  | 12.17% | 31174 | 30965.9 | 286.02 | 30679.88 | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [22 empty] | 10.507 | 4.2694 | 31425.129 | 70.05% | 12.46% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [22 empty] | 10.507 | 4.4468 | 33012.2568 | 70.66% | 13.09% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [22 empty] | 10.507 | 5.4347 | 38712.1033 | 67.79% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [22 empty] | 10.507 | 5.4651 | 40947.8954 | 71.31% | 16.24% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [22 empty] | 10.507 | 5.264 | 38712.1033 | 69.99% | 15.35% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [22 empty] | 10.507 | 5.671 | 43169.8742 | 72.45% | 17.12% | 99.5% | 99.7% | [9 empty] | 10.507
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Raw Data
[16 empty] | 68346.586 | 9.5173 | [15 empty] | 68213.041
[7 empty] | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29
Finacial Year | Calendar Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Plant DC Capcity (MW) | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | IC1_Inv1 | IC1_Inv2 | IC1_Inv3 | IC1_Inv4 | IC2_Inv1 | IC2_Inv2 | 66 kV ABT Main Meter Reading (Export) | 66 kV CRP MFM Reading (Import) | GHI(Wh/m2) | POA1(Wh/m2) | POA2(Wh/m2) | Avg. POA Lost (W/m2) | Avg. Ambient Temp (POA>20W/m2) | Avg. Module Temp (POA>20W/m2) | Avg. Wind Speed (m/s) | Max. Wind Speed (m/s) | Rain Fall (mm) | Inverters Generation ( kWh) | Export (kWh) | Import (kWh) | Net Export (kWh) | Avg. POA without Exclusion (W/m2)2 | Net Avg. POA with Exclusion (W/m2) | 66 kV ABT Check Meter Reading (Export) | Operating Hours
FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 10.507 | 0.27014 | 0.77014 | 8820 | 9612 | 9180 | 9120 | 9072 | 8431 | 115938.3561 | 15.4725 | 6600 | 7390 | 7360 | 0 | 30.4938 | 46.4586 | 0.67534 | 0.69938 | 0 | 54235 | #REF! | #REF! | #REF! | 7375 | 7375 | 115751.6377 | 12
FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 10.507 | 0.26944 | 0.77014 | 8560 | 9650 | 9150 | 9063 | 9050 | 8420 | 115992.0005 | 15.4776 | 6480 | 7350 | 7350 | 0 | 30.195 | 46.4332 | 0.77069 | 3.0956 | 0 | 53893 | 53644.4 | 307.2 | 53337.2 | 7350 | 7350 | 115805.2136 | 12.0167
FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 10.507 | 0.26806 | 0.77083 | 7943 | 8710 | 8171 | 8270 | 8230 | 7870 | 116040.6967 | 15.4826 | 6120 | 6550 | 6550 | 0 | 30.0404 | 44.9267 | 0.68876 | 3.2757 | 0 | 49194 | 48696.2 | 300.12 | 48396.08 | 6550 | 6550 | 115853.8466 | 12.0667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-01 | 10.507 | 0.27014 | 0.77153 | 6540 | 7074 | 6790 | 6934 | 6783 | 6361 | 116080.8571 | 15.4876 | 5150 | 5390 | 5390 | 0 | 28.4382 | 41.5418 | 0.68871 | 0.7893 | 0 | 40482 | 40160.4 | 298.14 | 39862.26 | 5390 | 5390 | 115893.9519 | 12.0333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 10.507 | 0.26597 | 0.75972 | 7520 | 8243 | 7860 | 8010 | 7820 | 7430 | 116127.4216 | 15.4925 | 5900 | 6350 | 6350 | 0 | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 0 | 46883 | 46564.5 | 297.24 | 46267.26 | 6350 | 6350 | 115940.4547 | 11.85
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-03 | 10.507 | 0.26319 | 0.75556 | 4840 | 5440 | 5230 | 5361 | 4910 | 4880 | 116157.8277 | 15.4976 | 3960 | 4010 | 4010 | 0 | 25.546 | 35.8572 | 0.82389 | 5.4078 | 3.81 | 30661 | 30406.1 | 303.66 | 30102.44 | 4010 | 4010 | 115970.8189 | 11.8167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 10.507 | 0.27153 | 0.75972 | 8884 | 9660 | 9350 | 6091 | 8770 | 8441 | 116208.6952 | 15.5029 | 6870 | 7540 | 7540 | 0 | 29.7818 | 46.949 | 0.66326 | 3.4188 | 0 | 51196 | 50867.5 | 315.9 | 50551.6 | 7540 | 7540 | 116021.6216 | 11.7167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 10.507 | 0.26458 | 0.76597 | 7660 | 8382 | 7993 | 3420 | 7810 | 7430 | 116251.105 | 15.5082 | 5830 | 6460 | 6460 | 0 | 28.4187 | 45.7694 | 0.68469 | 1.9063 | 0 | 42695 | 42409.8 | 320.28 | 42089.52 | 6460 | 6460 | 116063.9771 | 12.0333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 10.507 | 0.27083 | 0.76806 | 8570 | 9534 | 9143 | 5111 | 9171 | 8644 | 116300.9758 | 15.5138 | 6670 | 7600 | 7540 | 0 | 28.7698 | 47.3622 | 0.80936 | 5.3675 | 4.11 | 50173 | 49870.8 | 333.6 | 49537.2 | 7570 | 7570 | 116113.785 | 11.9333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 10.507 | 0.26458 | 0.76806 | 9130 | 9772 | 9340 | 6838 | 9373 | 8781 | 116353.9468 | 15.5189 | 6710 | 7840 | 7750 | 0 | 30.2429 | 47.9448 | 0.93582 | 4.3852 | 0 | 53234 | 52971 | 306.72 | 52664.28 | 7795 | 7795 | 116166.6905 | 12.0833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-08 | 10.507 | 0.26319 | 0.75278 | 7940 | 8753 | 8484 | 8450 | 8290 | 7770 | 116403.2465 | 15.5244 | 6170 | 6980 | 6850 | 0 | 29.8993 | 45.5016 | 0.88285 | 3.6838 | 0 | 49687 | 49299.7 | 330.24 | 48969.46 | 6915 | 6915 | 116215.9293 | 11.75
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-09 | 10.507 | 0.2625 | 0.76042 | 8330 | 9320 | 9010 | 9142 | 8763 | 8230 | 116455.7085 | 15.5297 | 6370 | 7300 | 7260 | 0 | 29.6186 | 46.9441 | 0.86043 | 2.7865 | 0 | 52795 | 52462 | 321.78 | 52140.22 | 7280 | 7280 | 116268.3252 | 11.95
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-10 | 10.507 | 0.26319 | 0.77292 | 7913 | 8490 | 8390 | 8324 | 8130 | 7620 | 116504.2735 | 15.5349 | 5790 | 6500 | 6500 | 0 | 28.7091 | 41.8396 | 1.2756 | 3.9577 | 0 | 48867 | 48565 | 310.32 | 48254.68 | 6500 | 6500 | 116316.8291 | 12.2333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-11 | 10.507 | 0.26389 | 0.75903 | 8463 | 9493 | 9450 | 9360 | 8881 | 8500 | 116558.1636 | 15.5401 | 6450 | 7420 | 7360 | 0 | 30.195 | 46.4332 | 0.77069 | 3.0956 | 0 | 54147 | 53890.1 | 311.7 | 53578.4 | 7390 | 7390 | 116370.6522 | 11.8833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-12 | 10.507 | 0.26458 | 0.76458 | 8304 | 9120 | 9022 | 9000 | 8620 | 8002 | 116609.9445 | 15.5454 | 6280 | 6940 | 6900 | 0 | 29.689 | 46.6091 | 0.67979 | 4.34 | 0.98 | 52068 | 51780.9 | 316.32 | 51464.58 | 6920 | 6920 | 116422.3683 | 12
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-13 | 10.507 | 0.26389 | 0.76875 | 8700 | 9442 | 9341 | 9224 | 9003 | 8382 | 116663.7225 | 15.5507 | 6520 | 7400 | 7350 | 0 | 30.195 | 46.4332 | 0.77069 | 3.0956 | 0 | 54092 | 53778 | 319.02 | 53458.98 | 7375 | 7375 | 116476.0812 | 12.1167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-14 | 10.507 | 0.26389 | 0.76458 | 7373 | 8182 | 8150 | 8023 | 7800 | 7280 | 116710.2291 | 15.5561 | 5860 | 6350 | 6350 | 0 | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 1.34 | 46808 | 46506.6 | 321 | 46185.6 | 6350 | 6350 | 116522.5312 | 12.0167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-15 | 10.507 | 0.26528 | 0.76458 | 9430 | 9863 | 9980 | 3352 | 9640 | 8902 | 116761.1336 | 15.5611 | 6990 | 8000 | 8000 | 0 | 30.166 | 48.516 | 0.50302 | 0.51512 | 0 | 51167 | 50904.5 | 302.22 | 50602.28 | 8000 | 8000 | 116573.3731 | 11.9833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-16 | 10.507 | 0.26736 | 0.76389 | 8150 | 8624 | 8654 | 8440 | 8466 | 7990 | 116811.1581 | 15.5663 | 5890 | 6750 | 6750 | 0 | 28.7698 | 47.3622 | 0.80936 | 5.3675 | 0 | 50324 | 50024.5 | 311.52 | 49712.98 | 6750 | 6750 | 116623.3354 | 11.9167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-17 | 10.507 | 0.26389 | 0.76389 | 8560 | 9994 | 9810 | 9742 | 9540 | 8920 | 116867.7911 | 15.572 | 6950 | 7710 | 7710 | 0 | 28.463 | 43.4858 | 1.6153 | 3.9035 | 0 | 56566 | 56633 | 340.8 | 56292.2 | 7710 | 7710 | 116679.899 | 12
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-18 | 10.507 | 0.26458 | 0.76597 | 7910 | 8822 | 8600 | 8810 | 8114 | 7814 | 116917.399 | 15.5776 | 6150 | 6690 | 6690 | 0 | 28.7698 | 47.3622 | 0.80936 | 5.3675 | 0 | 50070 | 49607.9 | 338.76 | 49269.14 | 6690 | 6690 | 116729.4457 | 12.0333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-19 | 10.507 | 0.26597 | 0.75833 | 8310 | 8910 | 8811 | 8844 | 8650 | 8054 | 116968.6543 | 15.5827 | 6150 | 6690 | 6690 | 0 | 30.166 | 48.516 | 0.50302 | 0.51512 | 4.24 | 51579 | 51255.3 | 304.86 | 50950.44 | 6690 | 6690 | 116780.6388 | 11.8167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-20 | 10.507 | 0.26736 | 0.75347 | 5892 | 6274 | 6310 | 6382 | 5975 | 5680 | 117004.8762 | 15.5877 | 4300 | 4670 | 4670 | 0 | 25.0801 | 36.1312 | 1.2497 | 5.4514 | 0 | 36513 | 36221.9 | 302.64 | 35919.26 | 4670 | 4670 | 116816.8163 | 11.6667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-21 | 10.507 | 0.26319 | 0.76667 | 8020 | 8530 | 8550 | 5164 | 8150 | 7693 | 117050.7027 | 15.5941 | 6230 | 6940 | 6940 | 0 | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 0 | 46107 | 45826.5 | 381.3 | 45445.2 | 6940 | 6940 | 116862.5864 | 12.0833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-22 | 10.507 | 0.26042 | 0.76736 | 8742 | 9490 | 9130 | 8990 | 8891 | 8442 | 117104.0735 | 15.5984 | 6420 | 7200 | 7200 | 0 | 30.195 | 46.4332 | 0.77069 | 3.0956 | 0 | 53685 | 53370.8 | 257.4 | 53113.4 | 7200 | 7200 | 116915.8931 | 12.1667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-23 | 10.507 | 0.25972 | 0.76597 | 7754 | 8430 | 8210 | 8030 | 8060 | 7550 | 117151.8103 | 15.6035 | 6080 | 6450 | 6350 | 0 | 30.2277 | 45.4561 | 0.88646 | 4.0239 | 0 | 48034 | 47736.8 | 305.52 | 47431.28 | 6400 | 6400 | 116963.5723 | 12.15
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-24 | 10.507 | 0.26042 | 0.76944 | 8640 | 9480 | 9200 | 8880 | 8784 | 8260 | 117204.7356 | 15.6086 | 6660 | 7200 | 7150 | 0 | 30.7169 | 47.3243 | 1.0548 | 4.043 | 0 | 53244 | 52925.3 | 305.76 | 52619.54 | 7175 | 7175 | 117016.4341 | 12.2167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-25 | 10.507 | 0.26528 | 0.76667 | 7962 | 8503 | 8341 | 8020 | 8130 | 7640 | 117253.0347 | 15.6137 | 6140 | 6510 | 6450 | 0 | 30.479 | 47.1594 | 0.89744 | 3.3385 | 0 | 48596 | 48299.1 | 308.7 | 47990.4 | 6480 | 6480 | 117064.6736 | 12.0333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-26 | 10.507 | 0.25625 | 0.76667 | 8730 | 9490 | 9420 | 9260 | 9122 | 8683 | 117307.3973 | 15.6189 | 6830 | 7600 | 7510 | 0 | 30.1302 | 47.6614 | 1.2327 | 4.8132 | 0 | 54705 | 54362.6 | 308.88 | 54053.72 | 7555 | 7555 | 117118.9704 | 12.25
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-27 | 10.507 | 0.25833 | 0.76389 | 7660 | 8302 | 8050 | 7940 | 8224 | 7731 | 117355.0318 | 15.6238 | 6070 | 6380 | 6380 | 0 | 30.2277 | 45.4561 | 0.88646 | 4.0239 | 0 | 47907 | 47634.5 | 296.58 | 47337.92 | 6380 | 6380 | 117166.5503 | 12.1333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-28 | 10.507 | 0.26042 | 0.75486 | 8650 | 9430 | 9140 | 9240 | 9082 | 8620 | 117408.9148 | 15.6288 | 6450 | 7200 | 7200 | 0 | 30.195 | 46.4332 | 0.77069 | 3.0956 | 3.45 | 54162 | 53883 | 298.08 | 53584.92 | 7200 | 7200 | 117220.3686 | 11.8667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-29 | 10.507 | 0.25486 | 0.76806 | 7980 | 8610 | 8541 | 8650 | 8423 | 7970 | 117458.8093 | 15.6342 | 6320 | 6740 | 6740 | 0 | 28.8325 | 45.3299 | 0.84028 | 4.5702 | 1.98 | 50174 | 49894.5 | 326.22 | 49568.28 | 6740 | 6740 | 117270.2043 | 12.3167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-04-01 | 30 | 2025-04-30 | 10.507 | 0.25694 | 0.76597 | 8224 | 9020 | 8731 | 9010 | 8534 | 8300 | 117510.3341 | 15.6396 | 6390 | 6920 | 6920 | 0 | 29.0602 | 45.8714 | 1.0987 | 8.6629 | 0 | 51819 | 51524.8 | 321.72 | 51203.08 | 6920 | 6920 | 117321.6687 | 12.2167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-01 | 10.507 | 0.25694 | 0.77153 | 4980 | 5343 | 5060 | 5243 | 5250 | 5010 | 117541.0493 | 15.6446 | 3540 | 4110 | 4110 | 0 | 28.4789 | 44.0566 | 0.68469 | 1.9063 | 0 | 30886 | 30715.2 | 301.14 | 30414.06 | 4110 | 4110 | 117352.3465 | 12.35
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-02 | 10.507 | 0.25694 | 0.76736 | 7950 | 8510 | 8290 | 8470 | 8490 | 7884 | 117590.3519 | 15.6497 | 6090 | 6630 | 6630 | 0 | 29.2157 | 45.438 | 0.72585 | 2.4936 | 0 | 49594 | 49302.6 | 303.9 | 48998.7 | 6630 | 6630 | 117401.5885 | 12.25
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-03 | 10.507 | 0.25625 | 0.77014 | 8600 | 9220 | 8970 | 9012 | 8980 | 8481 | 117643.3597 | 15.6553 | 6510 | 7110 | 7113 | 0 | 28.1139 | 44.2016 | 0.9761 | 3.9187 | 0 | 53263 | 53007.8 | 339.3 | 52668.5 | 7111.5 | 7111.5 | 117454.5298 | 12.3333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-04 | 10.507 | 0.25694 | 0.78056 | 8891 | 9560 | 9361 | 9471 | 9260 | 8774 | 117698.3752 | 15.6609 | 6850 | 7420 | 7450 | 0 | 29.436 | 45.0088 | 1.0626 | 4.7309 | 0 | 55317 | 55015.5 | 333.9 | 54681.6 | 7435 | 7435 | 117509.4785 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-05 | 10.507 | 0.25556 | 0.76389 | 9100 | 9803 | 9530 | 9760 | 9570 | 9000 | 117754.8421 | 15.6659 | 7050 | 7710 | 7650 | 0 | 30.0837 | 48.4744 | 0.81191 | 3.4706 | 0 | 56763 | 56466.9 | 302.4 | 56164.5 | 7680 | 7680 | 117565.8779 | 12.2
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-06 | 10.507 | 0.25625 | 0.77431 | 9800 | 10640 | 10010 | 10300 | 10094 | 9532 | 117814.8864 | 15.6709 | 7320 | 8090 | 8090 | 0 | 29.9635 | 46.6534 | 1.1117 | 4.0151 | 0 | 60376 | 60044.3 | 301.5 | 59742.8 | 8090 | 8090 | 117625.8493 | 12.4333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-07 | 10.507 | 0.25556 | 0.77083 | 9301 | 10081 | 9670 | 9854 | 9630 | 9080 | 117872.1875 | 15.676 | 7180 | 7650 | 7650 | 0 | 30.1719 | 46.9672 | 1.0444 | 3.5784 | 0 | 57616 | 57301.1 | 305.22 | 56995.88 | 7650 | 7650 | 117683.0804 | 12.3667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-08 | 10.507 | 0.25417 | 0.77153 | 9160 | 10032 | 9581 | 9762 | 9380 | 8820 | 117928.6176 | 15.6812 | 7120 | 7590 | 7590 | 0 | 29.0606 | 46.286 | 1.1257 | 4.0229 | 0 | 56735 | 56430.1 | 308.94 | 56121.16 | 7590 | 7590 | 117739.4425 | 12.4167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-09 | 10.507 | 0.25347 | 0.77361 | 8540 | 9290 | 8832 | 8852 | 8610 | 8171 | 117980.5724 | 15.6861 | 6700 | 6920 | 6880 | 0 | 29.1228 | 46.1707 | 0.85347 | 5.0674 | 0 | 52295 | 51954.8 | 297.54 | 51657.26 | 6900 | 6900 | 117791.3332 | 12.4833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-10 | 10.507 | 0.25208 | 0.77431 | 9780 | 10564 | 10073 | 10100 | 9930 | 9140 | 118039.862 | 15.691 | 7290 | 8080 | 8030 | 0 | 29.3381 | 47.275 | 1.0885 | 4.3083 | 0 | 59587 | 59289.6 | 289.08 | 59000.52 | 8055 | 8055 | 117850.5505 | 12.5333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-11 | 10.507 | 0.25347 | 0.77292 | 8991 | 10070 | 9841 | 9880 | 9780 | 8964 | 118097.0406 | 15.696 | 7310 | 7770 | 7680 | 0 | 29.4336 | 47.5887 | 0.77545 | 3.6446 | 0 | 57526 | 57178.6 | 304.98 | 56873.62 | 7725 | 7725 | 117907.66 | 12.4667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-12 | 10.507 | 0.25139 | 0.76181 | 8641 | 9370 | 9152 | 9140 | 8853 | 8380 | 118150.2714 | 15.701 | 6860 | 7490 | 7490 | 0 | 29.2109 | 45.9608 | 0.87807 | 3.8396 | 0 | 53536 | 53230.8 | 296.64 | 52934.16 | 7490 | 7490 | 117960.8263 | 12.25
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-13 | 10.507 | 0.25625 | 0.76319 | 9032 | 9752 | 9354 | 9360 | 9274 | 8911 | 118205.6071 | 15.7063 | 6740 | 7450 | 7400 | 0 | 27.805 | 44.9838 | 1.1785 | 5.2118 | 1.72 | 55683 | 55335.7 | 320.16 | 55015.54 | 7425 | 7425 | 118016.0937 | 12.1667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-14 | 10.507 | 0.25208 | 0.77222 | 8091 | 8810 | 8560 | 8660 | 8403 | 8060 | 118255.9112 | 15.7117 | 6200 | 6850 | 6750 | 0 | 28.8336 | 44.3876 | 0.8506 | 2.5289 | 1.02 | 50584 | 50304.1 | 322.56 | 49981.54 | 6800 | 6800 | 118066.3357 | 12.4833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-15 | 10.507 | 0.25347 | 0.76736 | 7753 | 8440 | 8311 | 8372 | 8180 | 7830 | 118304.4986 | 15.7168 | 6210 | 6510 | 6440 | 0 | 28.3453 | 44.0653 | 0.86462 | 3.7344 | 0 | 48886 | 48587.4 | 304.44 | 48282.96 | 6475 | 6475 | 118114.8616 | 12.3333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-16 | 10.507 | 0.25347 | 0.77153 | 8023 | 8782 | 8643 | 8653 | 8401 | 8170 | 118354.8319 | 15.722 | 6180 | 6860 | 6780 | 0 | 27.7906 | 43.4285 | 1.0359 | 5.8035 | 0 | 50672 | 50333.3 | 316.02 | 50017.28 | 6820 | 6820 | 118165.1416 | 12.4333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-17 | 10.507 | 0.2625 | 0.76111 | 4873 | 5240 | 5251 | 5240 | 5103 | 4850 | 118385.1933 | 15.7273 | 3770 | 3830 | 3830 | 0 | 25.9971 | 35.2061 | 0.98105 | 7.1985 | 2.24 | 30557 | 30361.4 | 316.38 | 30045.02 | 3830 | 3830 | 118195.4548 | 11.9667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-18 | 10.507 | 0.25903 | 0.77292 | 7091 | 8424 | 8420 | 8413 | 8262 | 7830 | 118433.3173 | 15.7326 | 6050 | 6370 | 6430 | 0 | 27.759 | 41.2443 | 1.1753 | 4.1536 | 0 | 48440 | 48124 | 320.16 | 47803.84 | 6400 | 6400 | 118243.5218 | 12.3333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-19 | 10.507 | 0.27222 | 0.76111 | 3680 | 3950 | 4031 | 3983 | 3960 | 3643 | 118456.2273 | 15.7382 | 2800 | 2690 | 2710 | 0 | 24.5407 | 30.8411 | 0.73105 | 3.1102 | 3.24 | 23247 | 22910 | 335.28 | 22574.72 | 2700 | 2700 | 118266.3984 | 11.7333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-20 | 10.507 | 0.28889 | 0.77153 | 4362 | 4641 | 4806 | 4760 | 4474 | 4291 | 118483.3349 | 15.744 | 3400 | 3380 | 3260 | 0 | 24.4541 | 32.8874 | 0.9356 | 5.0809 | 2.43 | 27334 | 27107.6 | 344.52 | 26763.08 | 3320 | 3320 | 118293.4682 | 11.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-21 | 10.507 | 0.25278 | 0.775 | 5010 | 5360 | 5422 | 5411 | 5180 | 4980 | 118514.4855 | 15.7493 | 3840 | 3910 | 3830 | 0 | 24.4997 | 32.5266 | 1.7049 | 8.8073 | 1.43 | 31363 | 31150.6 | 317.64 | 30832.96 | 3870 | 3870 | 118324.5757 | 12.5333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-22 | 10.507 | 0.25556 | 0.775 | 6942 | 7274 | 7250 | 7222 | 7000 | 6730 | 118556.7506 | 15.7543 | 5170 | 5400 | 5360 | 0 | 26.4095 | 37.0329 | 1.5431 | 6.5777 | 0 | 42418 | 42265.1 | 301.2 | 41963.9 | 5380 | 5380 | 118366.7862 | 12.4667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-23 | 10.507 | 0.25278 | 0.77569 | 6620 | 6810 | 6870 | 6800 | 6443 | 6440 | 118596.4771 | 15.7592 | 4282 | 5250 | 5250 | 0 | 25.4426 | 35.2243 | 2.3078 | 8.0038 | 1.21 | 39983 | 39726.5 | 297.66 | 39428.84 | 5250 | 5250 | 118406.4582 | 12.55
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-24 | 10.507 | 0.25278 | 0.76389 | 4030 | 4320 | 4290 | 1955 | 4190 | 4060 | 118619.1303 | 15.7644 | 3050 | 3040 | 2970 | 0 | 24.9328 | 31.1882 | 2.7855 | 9.2161 | 2.12 | 22845 | 22653.2 | 309.54 | 22343.66 | 3005 | 3005 | 11829.0783 | 12.2667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-25 | 10.507 | 0.25833 | 0.77222 | 4590 | 4380 | 4883 | 4344 | 4821 | 4640 | 118646.8875 | 15.77 | 3080 | 3180 | 3180 | 0 | 23.9943 | 30.1193 | 2.6118 | 8.8609 | 5.2 | 27658 | 27757.2 | 333.78 | 27423.42 | 3180 | 3180 | 118456.796 | 12.3333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-26 | 10.507 | 0.25694 | 0.77153 | 4620 | 5083 | 5130 | 5092 | 4990 | 4760 | 118676.2865 | 15.7755 | 3520 | 3480 | 3480 | 0 | 25.965 | 35.6713 | 0.92166 | 10.1554 | 2.1 | 29675 | 29399 | 334.5 | 29064.5 | 3480 | 3480 | 118486.1554 | 12.35
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-27 | 10.507 | 0.25694 | 0.77431 | 5150 | 5414 | 5460 | 5411 | 5362 | 5132 | 118707.9598 | 15.7804 | 3820 | 3830 | 3820 | 0 | 24.4997 | 32.5266 | 1.7049 | 8.8073 | 0.52 | 31929 | 31673.3 | 292.62 | 31380.68 | 3825 | 3825 | 118517.7861 | 12.4167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-28 | 10.507 | 0.25417 | 0.75486 | 4540 | 4770 | 4862 | 4830 | 4630 | 4442 | 118735.6287 | 15.787 | 3450 | 3340 | 3360 | 0 | 25.0635 | 31.196 | 1.7759 | 9.2261 | 0.21 | 28074 | 27668.9 | 394.98 | 27273.92 | 3350 | 3350 | 118545.4165 | 12.0167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-29 | 10.507 | 0.25347 | 0.77708 | 5094 | 5370 | 5461 | 5470 | 5260 | 5050 | 118767.0885 | 15.7906 | 3820 | 3750 | 3710 | 0 | 24.8504 | 32.0049 | 1.7221 | 6.348 | 0.19 | 31705 | 31459.8 | 217.8 | 31242 | 3730 | 3730 | 118576.8343 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-30 | 10.507 | 0.25139 | 0.76944 | 3930 | 4144 | 4223 | 4152 | 4081 | 3874 | 118791.2626 | 15.7966 | 3040 | 2850 | 2830 | 0 | 24.9062 | 31.002 | 1.1343 | 6.0709 | 0 | 24404 | 24174.1 | 357.72 | 23816.38 | 2840 | 2840 | 118600.9739 | 12.4333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-05-01 | 31 | 2025-05-31 | 10.507 | 0.25347 | 0.77708 | 6630 | 7132 | 7072 | 6970 | 6810 | 6570 | 118832.1948 | 15.8009 | 5150 | 5190 | 5180 | 0 | 26.5776 | 37.2281 | 0.83761 | 4.3921 | 0 | 41184 | 40932.2 | 256.02 | 40676.18 | 5185 | 5185 | 118641.8536 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-01 | 10.507 | 0.25 | 0.77431 | 8764 | 9300 | 8953 | 8902 | 8663 | 8572 | 118885.0585 | 15.8063 | 6550 | 7050 | 6810 | 0 | 27.3767 | 41.1267 | 1.6266 | 6.4821 | 0 | 53154 | 52863.7 | 325.92 | 52537.78 | 6930 | 6930 | 118694.65 | 12.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-02 | 10.507 | 0.25208 | 0.77569 | 7630 | 8110 | 7970 | 7804 | 7671 | 7414 | 118931.3634 | 15.8111 | 5570 | 6030 | 6040 | 0 | 27.2883 | 39.0841 | 1.9193 | 5.6299 | 0 | 46599 | 46304.9 | 285.48 | 46019.42 | 6035 | 6035 | 118740.8962 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-03 | 10.507 | 0.25139 | 0.77431 | 6550 | 6800 | 6972 | 6780 | 6670 | 6422 | 118971.1531 | 15.8164 | 4890 | 5250 | 5030 | 0 | 25.605 | 36.1476 | 1.4758 | 6.5289 | 0 | 40194 | 39789.7 | 318.06 | 39471.64 | 5140 | 5140 | 118780.6318 | 12.55
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-04 | 10.507 | 0.24861 | 0.77431 | 8710 | 9490 | 9170 | 9034 | 8870 | 8620 | 119024.7053 | 15.8216 | 6580 | 7170 | 6840 | 0 | 27.1915 | 41.3755 | 0.88924 | 4.8114 | 0 | 53894 | 53552.2 | 314.58 | 53237.62 | 7005 | 7005 | 118834.1161 | 12.6167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-05 | 10.507 | 0.25 | 0.77431 | 8760 | 9661 | 9500 | 9230 | 8920 | 8840 | 119079.3555 | 15.8263 | 6700 | 7520 | 7250 | 0 | 27.7997 | 43.1336 | 0.7642 | 1.0214 | 0.98 | 54911 | 54650.2 | 284.76 | 54365.44 | 7385 | 7385 | 118888.6974 | 12.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-06 | 10.507 | 0.25069 | 0.77639 | 9050 | 10124 | 9770 | 9810 | 9254 | 9113 | 119136.1784 | 15.8308 | 6980 | 7810 | 7810 | 0 | 28.4327 | 45.7312 | 0.75488 | 0.95623 | 0 | 57121 | 56822.9 | 266.76 | 56556.14 | 7810 | 7810 | 118945.45 | 12.6167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-07 | 10.507 | 0.25069 | 0.77847 | 8972 | 10569 | 10080 | 10140 | 9772 | 9362 | 119194.5628 | 15.8359 | 7330 | 8040 | 8040 | 0 | 27.8549 | 45.2894 | 0.74587 | 0.88982 | 0 | 58895 | 58384.4 | 309.24 | 58075.16 | 8040 | 8040 | 119003.7605 | 12.6667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-08 | 10.507 | 0.24931 | 0.77431 | 9050 | 9940 | 9500 | 9310 | 9204 | 8740 | 119249.9942 | 15.8406 | 6980 | 7590 | 7480 | 0 | 28.6728 | 45.2306 | 0.72955 | 0.89025 | 0 | 55744 | 55431.4 | 281.46 | 55149.94 | 7535 | 7535 | 119059.1237 | 12.6
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-09 | 10.507 | 0.25069 | 0.71667 | 5570 | 6285 | 6084 | 5970 | 5781 | 5530 | 119284.9352 | 15.8459 | 4540 | 4550 | 4540 | 0 | 26.9089 | 38.0863 | 0.70516 | 0.81437 | 0.81 | 35220 | 34941 | 318.3 | 34622.7 | 4545 | 4545 | 119094.018 | 11.1833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-10 | 10.507 | 0.24931 | 0.77778 | 6940 | 7590 | 7400 | 7092 | 7050 | 6742 | 119328.0099 | 15.8512 | 5300 | 5680 | 5580 | 0 | 26.4095 | 37.0329 | 1.5431 | 6.5777 | 0 | 42814 | 43074.7 | 313.92 | 42760.78 | 5630 | 5630 | 119137.038 | 12.6833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-11 | 10.507 | 0.25417 | 0.74653 | 5660 | 6214 | 6071 | 5910 | 5900 | 5582 | 119363.1096 | 15.8561 | 4310 | 4440 | 4440 | 0 | 26.5317 | 37.1209 | 0.73589 | 7.87 | 0 | 35337 | 35099.7 | 296.88 | 34802.82 | 4440 | 4440 | 119172.0926 | 11.8167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-12 | 10.507 | 0.2625 | 0.77708 | 5800 | 6200 | 6121 | 5954 | 5913 | 5680 | 119398.4424 | 15.8617 | 4400 | 4570 | 4540 | 0 | 25.5925 | 35.2972 | 1.4968 | 6.8728 | 1.27 | 35668 | 35332.8 | 334.02 | 34998.78 | 4555 | 4555 | 119207.3791 | 12.35
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-13 | 10.507 | 0.26181 | 0.77569 | 5080 | 5582 | 5401 | 5252 | 5230 | 5034 | 119429.8757 | 15.8665 | 3850 | 3940 | 3940 | 0 | 24.8504 | 32.0049 | 1.7221 | 6.348 | 0 | 31579 | 31433.3 | 291.12 | 31142.18 | 3940 | 3940 | 119238.768 | 12.3333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-14 | 10.507 | 0.25069 | 0.74306 | 4820 | 5390 | 5334 | 5123 | 5124 | 4842 | 119460.2432 | 15.8719 | 3860 | 3850 | 3810 | 0 | 25.0924 | 33.2292 | 1.4089 | 5.8479 | 1.98 | 30633 | 30367.5 | 319.62 | 30047.88 | 3830 | 3830 | 119269.0935 | 11.8167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-15 | 10.507 | 0.25417 | 0.77778 | 4080 | 4470 | 4370 | 4210 | 4200 | 3981 | 119485.2691 | 15.8767 | 3100 | 3010 | 2990 | 0 | 23.9379 | 28.828 | 2.9794 | 8.7773 | 1.75 | 25311 | 25025.9 | 289.14 | 24736.76 | 3000 | 3000 | 119294.0843 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-16 | 10.507 | 0.25347 | 0.77361 | 5490 | 5894 | 5784 | 5643 | 5591 | 5360 | 119518.8028 | 15.8817 | 4110 | 4250 | 4260 | 0 | 24.539 | 31.5177 | 2.6537 | 10.3186 | 0 | 33762 | 33533.7 | 301.74 | 33231.96 | 4255 | 4255 | 119327.5719 | 12.4833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-17 | 10.507 | 0.25764 | 0.77778 | 4714 | 5060 | 5040 | 4960 | 4900 | 4662 | 119547.8783 | 15.8867 | 3620 | 3550 | 3530 | 0 | 24.5281 | 31.0709 | 1.4826 | 6.9411 | 0 | 29336 | 29075.5 | 301.14 | 28774.36 | 3540 | 3540 | 119356.6076 | 12.4833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-18 | 10.507 | 0.25417 | 0.77639 | 5543 | 6090 | 5883 | 5713 | 5740 | 5380 | 119581.9831 | 15.8917 | 4150 | 4230 | 4230 | 0 | 25.3852 | 34.0119 | 0.74291 | 3.351 | 0 | 34349 | 34104.8 | 295.98 | 33808.82 | 4230 | 4230 | 119390.6666 | 12.5333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-19 | 10.507 | 0.25417 | 0.77847 | 6663 | 7320 | 7040 | 6393 | 6823 | 6420 | 119622.4447 | 15.8966 | 4990 | 5130 | 5070 | 0 | 26.0367 | 35.6802 | 0.64889 | 2.4967 | 0 | 40659 | 40461.6 | 293.46 | 40168.14 | 5100 | 5100 | 119431.0748 | 12.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-20 | 10.507 | 0.25208 | 0.77986 | 7710 | 8540 | 8120 | 8040 | 7810 | 7540 | 119669.5171 | 15.9014 | 5700 | 6120 | 6120 | 0 | 26.5611 | 38.1114 | 1.2775 | 6.5962 | 0 | 47760 | 47072.4 | 291.36 | 46781.04 | 6120 | 6120 | 119478.0818 | 12.6667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-21 | 10.507 | 0.25347 | 0.77778 | 7630 | 8350 | 7940 | 7761 | 7620 | 7281 | 119715.8118 | 15.9062 | 5630 | 5950 | 5880 | 0 | 26.6403 | 37.3416 | 2.2367 | 6.7845 | 0 | 46582 | 46294.7 | 290.22 | 46004.48 | 5915 | 5915 | 119524.3192 | 12.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-22 | 10.507 | 0.25278 | 0.77847 | 1170 | 1310 | 1243 | 1200 | 1201 | 1140 | 119722.9822 | 15.9111 | 650 | 750 | 750 | 0 | 25.1226 | 32.9897 | 1.894 | 7.725 | 0 | 7264 | 7170.4 | 293.4 | 6877 | 750 | 750 | 119531.4777 | 12.6167
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-23 | 10.507 | 0.26042 | 0.775 | 6350 | 6973 | 6753 | 6640 | 6480 | 6190 | 119762.2283 | 15.9162 | 4830 | 4830 | 4830 | 0 | 25.3778 | 33.8383 | 2.7888 | 8.3454 | 0 | 39386 | 39246.1 | 301.26 | 38944.84 | 4830 | 4830 | 119570.6723 | 12.35
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-24 | 10.507 | 0.25625 | 0.78056 | 4790 | 5203 | 5070 | 5010 | 4903 | 4632 | 119791.5925 | 15.9213 | 3640 | 3560 | 3560 | 0 | 24.8022 | 31.1665 | 2.3958 | 8.3188 | 0.51 | 29608 | 29364.2 | 308.82 | 29055.38 | 3560 | 3560 | 119599.9961 | 12.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-25 | 10.507 | 0.25694 | 0.77778 | 3992 | 4174 | 4190 | 4122 | 3950 | 3787 | 119815.5272 | 15.9258 | 2970 | 2870 | 2870 | 0 | 23.9379 | 28.828 | 2.9794 | 8.7773 | 0 | 24215 | 23934.7 | 271.5 | 23663.2 | 2870 | 2870 | 119623.8965 | 12.5
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-26 | 10.507 | 0.25486 | 0.78264 | 5560 | 6120 | 5970 | 5732 | 5710 | 5390 | 119849.7359 | 15.9307 | 4240 | 4320 | 4320 | 0 | 25.9955 | 34.2471 | 2.3294 | 6.7935 | 0 | 34482 | 34208.7 | 295.02 | 33913.68 | 4320 | 4320 | 119658.0609 | 12.6667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-27 | 10.507 | 0.25347 | 0.77431 | 5071 | 5532 | 5410 | 5320 | 5230 | 4910 | 119880.9569 | 15.9356 | 3850 | 3935 | 3935 | 0 | 24.8504 | 32.0049 | 1.7221 | 6.348 | 0 | 31473 | 31221 | 291.18 | 30929.82 | 3935 | 3935 | 119689.2426 | 12.5
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-28 | 10.507 | 0.25833 | 0.78264 | 5640 | 6302 | 6130 | 6103 | 5894 | 5591 | 119916.3781 | 15.941 | 4440 | 4530 | 4490 | 0 | 25.6635 | 34.8133 | 2.1412 | 6.8482 | 0 | 35660 | 35421.2 | 324.18 | 35097.02 | 4510 | 4510 | 119724.6182 | 12.5833
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-29 | 10.507 | 0.25625 | 0.77986 | 7650 | 8270 | 8023 | 8080 | 7800 | 7461 | 119963.4172 | 15.9459 | 5590 | 6130 | 6130 | 0 | 26.469 | 37.6205 | 2.6835 | 6.9793 | 0 | 47284 | 47039.1 | 295.56 | 46743.54 | 6130 | 6130 | 119771.6001 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-06-30 | 10.507 | 0.25764 | 0.78264 | 7680 | 8240 | 8061 | 8023 | 7762 | 7394 | 120010.196 | 15.9506 | 5730 | 6100 | 6100 | 0 | 26.1369 | 36.905 | 2.8151 | 8.1669 | 0 | 47160 | 46778.8 | 279.84 | 46498.96 | 6100 | 6100 | 119818.3237 | 12.6
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-06-01 | 30 | 2025-07-01 | 10.507 | 0.25625 | 0.77847 | 3680 | 4000 | 3950 | 3922 | 3770 | 3590 | 120032.9521 | 15.9557 | 2810 | 2730 | 2730 | 0 | 24.5237 | 29.5575 | 1.9007 | 6.3871 | 0 | 22912 | 22756.1 | 308.7 | 22447.4 | 2730 | 2730 | 119841.0467 | 12.5333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-02 | 10.507 | 0.25625 | 0.77986 | 5420 | 5850 | 5732 | 5722 | 5503 | 5200 | 120066.1289 | 15.9611 | 4160 | 4180 | 4150 | 0 | 25.305 | 32.8784 | 2.7888 | 8.3454 | 0 | 33427 | 33176.8 | 322.56 | 32854.24 | 4165 | 4165 | 119874.1808 | 12.5667
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-03 | 10.507 | 0.26181 | 0.77569 | 4340 | 4690 | 4610 | 4601 | 4423 | 4160 | 120092.7619 | 15.9666 | 3280 | 3280 | 3180 | 0 | 24.0753 | 30.4552 | 2.0251 | 6.7358 | 2.54 | 26824 | 26633 | 326.94 | 26306.06 | 3230 | 3230 | 119900.7768 | 12.3333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-04 | 10.507 | 0.25486 | 0.77708 | 6760 | 7273 | 7150 | 7201 | 6770 | 6502 | 120134.178 | 15.9715 | 5620 | 5420 | 5420 | 0 | 26.1687 | 36.736 | 2.5883 | 8.6863 | 0.75 | 41656 | 41416.1 | 296.28 | 41119.82 | 5420 | 5420 | 119942.1462 | 12.5333
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-05 | 10.507 | 0.25694 | 0.77986 | 3550 | 3890 | 3798 | 3796 | 3686 | 3468 | 120156.1581 | 15.9761 | 2710 | 2630 | 2630 | 0 | 23.9478 | 28.5037 | 1.8307 | 5.4042 | 0.762 | 22188 | 21980.1 | 277.98 | 21702.12 | 2630 | 2630 | 119964.0942 | 12.55
FY2025-26 | 2025 | Year_2 | Year_3 | 2025-07-01 | 31 | 2025-07-06 | 10.507 | 0.25486 | 0.78125 | 5027 | 5477 | 5334 | 5342 | 5165 | 4829 | 120187.124 | 15.9809 | 3760 | 3820 | 3810 | 0 | 24.2217 | 47.3601 | 2.4316 | 7.1164 | 2.032 | 31174 | 30965.9 | 286.02 | 30679.88 | 3815 | 3815 | 119995.0177 | 12.6333
Formulas:
Days = DAY(EOMONTH(Raw_Data[[#This Row],[Month Year]],0))

## Inv_SY
[9 empty] | 1669.29 | 1833.3 | 1785.84 | 1785.42 | 1763.16 | 1669.29
Finacial Year | Start Month | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Plant DC Capcity (MW) | IC1_Inv1 | IC1_Inv2 | IC1_Inv3 | IC1_Inv4 | IC2_Inv1 | IC2_Inv2 | Avg. SY | Max. SY
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-08-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-01-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-03-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2023-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-29 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-30 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-31 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 5 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-01 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-02 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-03 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-04 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-05 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-06 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-07 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-08 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-09 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-10 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-11 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-12 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-13 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-14 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-15 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-16 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-17 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-18 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-19 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-20 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-22 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-23 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-24 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-25 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-26 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-28 | 10.507 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF!
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 10.507 | 5.2837 | 5.243 | 5.1404 | 5.108 | 5.1453 | 5.0507 | 5.1619 | 5.2837
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 10.507 | 5.1279 | 5.2637 | 5.1236 | 5.0761 | 5.1328 | 5.0441 | 5.1281 | 5.2637
FY2024-25 | 3 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 10.507 | 4.7583 | 4.751 | 4.5754 | 4.632 | 4.6678 | 4.7146 | 4.6832 | 4.7583
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-01 | 10.507 | 3.9178 | 3.8586 | 3.8021 | 3.8837 | 3.8471 | 3.8106 | 3.8533 | 3.9178
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-02 | 10.507 | 4.5049 | 4.4963 | 4.4013 | 4.4863 | 4.4352 | 4.451 | 4.4625 | 4.5049
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-03 | 10.507 | 2.8994 | 2.9673 | 2.9286 | 3.0027 | 2.7848 | 2.9234 | 2.9177 | 3.0027
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-04 | 10.507 | 5.322 | 5.2692 | 5.2356 | 3.4115 | 4.974 | 5.0566 | 4.8782 | 5.322
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-05 | 10.507 | 4.5888 | 4.5721 | 4.4758 | 1.9155 | 4.4295 | 4.451 | 4.0721 | 4.5888
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-06 | 10.507 | 5.1339 | 5.2005 | 5.1197 | 2.8626 | 5.2015 | 5.1782 | 4.7827 | 5.2015
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-07 | 10.507 | 5.4694 | 5.3303 | 5.23 | 3.8299 | 5.316 | 5.2603 | 5.0727 | 5.4694
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-08 | 10.507 | 4.7565 | 4.7745 | 4.7507 | 4.7328 | 4.7018 | 4.6547 | 4.7285 | 4.7745
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-09 | 10.507 | 4.9901 | 5.0837 | 5.0452 | 5.1204 | 4.9701 | 4.9302 | 5.0233 | 5.1204
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-10 | 10.507 | 4.7403 | 4.631 | 4.6981 | 4.6622 | 4.611 | 4.5648 | 4.6512 | 4.7403
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-11 | 10.507 | 5.0698 | 5.1781 | 5.2916 | 5.2425 | 5.037 | 5.092 | 5.1518 | 5.2916
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-12 | 10.507 | 4.9746 | 4.9746 | 5.052 | 5.0408 | 4.8889 | 4.7937 | 4.9541 | 5.052
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-13 | 10.507 | 5.2118 | 5.1503 | 5.2306 | 5.1663 | 5.1062 | 5.0213 | 5.1477 | 5.2306
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-14 | 10.507 | 4.4168 | 4.463 | 4.5637 | 4.4936 | 4.4239 | 4.3611 | 4.4537 | 4.5637
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-15 | 10.507 | 5.6491 | 5.3799 | 5.5884 | 1.8774 | 5.4675 | 5.3328 | 4.8825 | 5.6491
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-16 | 10.507 | 4.8823 | 4.7041 | 4.8459 | 4.7272 | 4.8016 | 4.7865 | 4.7913 | 4.8823
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-17 | 10.507 | 5.1279 | 5.4514 | 5.4932 | 5.4564 | 5.4107 | 5.3436 | 5.3805 | 5.4932
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-18 | 10.507 | 4.7385 | 4.8121 | 4.8157 | 4.9344 | 4.602 | 4.681 | 4.7639 | 4.9344
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-19 | 10.507 | 4.9782 | 4.8601 | 4.9338 | 4.9535 | 4.906 | 4.8248 | 4.9094 | 4.9782
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-20 | 10.507 | 3.5296 | 3.4222 | 3.5334 | 3.5745 | 3.3888 | 3.4026 | 3.4752 | 3.5745
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-21 | 10.507 | 4.8044 | 4.6528 | 4.7877 | 2.8923 | 4.6224 | 4.6085 | 4.3947 | 4.8044
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-22 | 10.507 | 5.237 | 5.1765 | 5.1124 | 5.0352 | 5.0427 | 5.0572 | 5.1102 | 5.237
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-23 | 10.507 | 4.6451 | 4.5983 | 4.5973 | 4.4975 | 4.5713 | 4.5229 | 4.5721 | 4.6451
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-24 | 10.507 | 5.1759 | 5.171 | 5.1516 | 4.9736 | 4.982 | 4.9482 | 5.067 | 5.1759
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-25 | 10.507 | 4.7697 | 4.6381 | 4.6706 | 4.4919 | 4.611 | 4.5768 | 4.6264 | 4.7697
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-26 | 10.507 | 5.2298 | 5.1765 | 5.2748 | 5.1865 | 5.1737 | 5.2016 | 5.2071 | 5.2748
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-27 | 10.507 | 4.5888 | 4.5284 | 4.5077 | 4.4471 | 4.6644 | 4.6313 | 4.5613 | 4.6644
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-28 | 10.507 | 5.1818 | 5.1437 | 5.118 | 5.1753 | 5.151 | 5.1639 | 5.1556 | 5.1818
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-29 | 10.507 | 4.7805 | 4.6964 | 4.7826 | 4.8448 | 4.7772 | 4.7745 | 4.776 | 4.8448
FY2025-26 | 4 | 2025 | Year_3 | Year_3 | 2025-04-01 | 30 | 2025-04-30 | 10.507 | 4.9266 | 4.9201 | 4.889 | 5.0464 | 4.8402 | 4.9722 | 4.9324 | 5.0464
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-01 | 10.507 | 2.9833 | 2.9144 | 2.8334 | 2.9366 | 2.9776 | 3.0013 | 2.9411 | 3.0013
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-02 | 10.507 | 4.7625 | 4.6419 | 4.6421 | 4.744 | 4.8152 | 4.723 | 4.7214 | 4.8152
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-03 | 10.507 | 5.1519 | 5.0292 | 5.0228 | 5.0476 | 5.0931 | 5.0806 | 5.0709 | 5.1519
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-04 | 10.507 | 5.3262 | 5.2146 | 5.2418 | 5.3046 | 5.2519 | 5.2561 | 5.2659 | 5.3262
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-05 | 10.507 | 5.4514 | 5.3472 | 5.3364 | 5.4665 | 5.4278 | 5.3915 | 5.4035 | 5.4665
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-06 | 10.507 | 5.8708 | 5.8037 | 5.6052 | 5.769 | 5.7249 | 5.7102 | 5.7473 | 5.8708
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-07 | 10.507 | 5.5718 | 5.4988 | 5.4148 | 5.5191 | 5.4618 | 5.4394 | 5.4843 | 5.5718
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-08 | 10.507 | 5.4874 | 5.4721 | 5.365 | 5.4676 | 5.32 | 5.2837 | 5.3993 | 5.4874
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-09 | 10.507 | 5.1159 | 5.0674 | 4.9456 | 4.9579 | 4.8833 | 4.8949 | 4.9775 | 5.1159
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-10 | 10.507 | 5.8588 | 5.7623 | 5.6405 | 5.6569 | 5.6319 | 5.4754 | 5.671 | 5.8588
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-11 | 10.507 | 5.3861 | 5.4928 | 5.5106 | 5.5337 | 5.5469 | 5.3699 | 5.4733 | 5.5469
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-12 | 10.507 | 5.1765 | 5.111 | 5.1248 | 5.1192 | 5.0211 | 5.0201 | 5.0954 | 5.1765
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-13 | 10.507 | 5.4107 | 5.3194 | 5.2379 | 5.2425 | 5.2599 | 5.3382 | 5.3014 | 5.4107
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-14 | 10.507 | 4.847 | 4.8055 | 4.7933 | 4.8504 | 4.7659 | 4.8284 | 4.8151 | 4.8504
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-15 | 10.507 | 4.6445 | 4.6037 | 4.6538 | 4.6891 | 4.6394 | 4.6906 | 4.6535 | 4.6906
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-16 | 10.507 | 4.8062 | 4.7903 | 4.8397 | 4.8465 | 4.7647 | 4.8943 | 4.8236 | 4.8943
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-17 | 10.507 | 2.9192 | 2.8582 | 2.9404 | 2.9349 | 2.8942 | 2.9054 | 2.9087 | 2.9404
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-18 | 10.507 | 4.2479 | 4.595 | 4.7149 | 4.7121 | 4.6859 | 4.6906 | 4.6077 | 4.7149
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-19 | 10.507 | 2.2045 | 2.1546 | 2.2572 | 2.2308 | 2.246 | 2.1824 | 2.2126 | 2.2572
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-20 | 10.507 | 2.6131 | 2.5315 | 2.6912 | 2.666 | 2.5375 | 2.5706 | 2.6016 | 2.6912
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-21 | 10.507 | 3.0013 | 2.9237 | 3.0361 | 3.0307 | 2.9379 | 2.9833 | 2.9855 | 3.0361
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-22 | 10.507 | 4.1587 | 3.9677 | 4.0597 | 4.045 | 3.9701 | 4.0317 | 4.0388 | 4.1587
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-23 | 10.507 | 3.9658 | 3.7146 | 3.8469 | 3.8086 | 3.6542 | 3.8579 | 3.808 | 3.9658
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-24 | 10.507 | 2.4142 | 2.3564 | 2.4022 | 1.095 | 2.3764 | 2.4322 | 2.1794 | 2.4322
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-25 | 10.507 | 2.7497 | 2.3891 | 2.7343 | 2.433 | 2.7343 | 2.7796 | 2.6367 | 2.7796
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-26 | 10.507 | 2.7676 | 2.7726 | 2.8726 | 2.852 | 2.8301 | 2.8515 | 2.8244 | 2.8726
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-27 | 10.507 | 3.0851 | 2.9531 | 3.0574 | 3.0307 | 3.0411 | 3.0744 | 3.0403 | 3.0851
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-28 | 10.507 | 2.7197 | 2.6019 | 2.7225 | 2.7052 | 2.626 | 2.661 | 2.6727 | 2.7225
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-29 | 10.507 | 3.0516 | 2.9291 | 3.0579 | 3.0637 | 2.9833 | 3.0252 | 3.0185 | 3.0637
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-30 | 10.507 | 2.3543 | 2.2604 | 2.3647 | 2.3255 | 2.3146 | 2.3207 | 2.3234 | 2.3647
FY2025-26 | 5 | 2025 | Year_3 | Year_3 | 2025-05-01 | 31 | 2025-05-31 | 10.507 | 3.9717 | 3.8903 | 3.96 | 3.9038 | 3.8624 | 3.9358 | 3.9207 | 3.9717
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-01 | 10.507 | 5.2501 | 5.0728 | 5.0133 | 4.9859 | 4.9133 | 5.1351 | 5.0618 | 5.2501
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-02 | 10.507 | 4.5708 | 4.4237 | 4.4629 | 4.371 | 4.3507 | 4.4414 | 4.4367 | 4.5708
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-03 | 10.507 | 3.9238 | 3.7092 | 3.904 | 3.7974 | 3.783 | 3.8471 | 3.8274 | 3.9238
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-04 | 10.507 | 5.2178 | 5.1765 | 5.1348 | 5.0599 | 5.0307 | 5.1639 | 5.1306 | 5.2178
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-05 | 10.507 | 5.2477 | 5.2697 | 5.3196 | 5.1697 | 5.0591 | 5.2957 | 5.2269 | 5.3196
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-06 | 10.507 | 5.4215 | 5.5223 | 5.4708 | 5.4945 | 5.2485 | 5.4592 | 5.4361 | 5.5223
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-07 | 10.507 | 5.3747 | 5.765 | 5.6444 | 5.6793 | 5.5423 | 5.6084 | 5.6024 | 5.765
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-08 | 10.507 | 5.4215 | 5.4219 | 5.3196 | 5.2145 | 5.2202 | 5.2358 | 5.3056 | 5.4219
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-09 | 10.507 | 3.3367 | 3.4282 | 3.4068 | 3.3438 | 3.2788 | 3.3128 | 3.3512 | 3.4282
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-10 | 10.507 | 4.1575 | 4.1401 | 4.1437 | 3.9722 | 3.9985 | 4.0388 | 4.0751 | 4.1575
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-11 | 10.507 | 3.3907 | 3.3895 | 3.3995 | 3.3101 | 3.3463 | 3.3439 | 3.3633 | 3.3995
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-12 | 10.507 | 3.4745 | 3.3819 | 3.4275 | 3.3348 | 3.3536 | 3.4026 | 3.3958 | 3.4745
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-13 | 10.507 | 3.0432 | 3.0448 | 3.0243 | 2.9416 | 2.9663 | 3.0157 | 3.006 | 3.0448
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-14 | 10.507 | 2.8875 | 2.9401 | 2.9868 | 2.8694 | 2.9061 | 2.9006 | 2.9151 | 2.9868
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-15 | 10.507 | 2.4442 | 2.4382 | 2.447 | 2.358 | 2.3821 | 2.3848 | 2.4091 | 2.447
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-16 | 10.507 | 3.2888 | 3.215 | 3.2388 | 3.1606 | 3.171 | 3.2109 | 3.2142 | 3.2888
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-17 | 10.507 | 2.824 | 2.7601 | 2.8222 | 2.7781 | 2.7791 | 2.7928 | 2.7927 | 2.824
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-18 | 10.507 | 3.3206 | 3.3219 | 3.2942 | 3.1998 | 3.2555 | 3.2229 | 3.2692 | 3.3219
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-19 | 10.507 | 3.9915 | 3.9928 | 3.9421 | 3.5807 | 3.8698 | 3.8459 | 3.8705 | 3.9928
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-20 | 10.507 | 4.6187 | 4.6583 | 4.5469 | 4.5031 | 4.4295 | 4.5169 | 4.5456 | 4.6583
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-21 | 10.507 | 4.5708 | 4.5546 | 4.4461 | 4.3469 | 4.3218 | 4.3617 | 4.4337 | 4.5708
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-22 | 10.507 | 0.7009 | 0.71456 | 0.69603 | 0.67211 | 0.68116 | 0.68293 | 0.69128 | 0.71456
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-23 | 10.507 | 3.804 | 3.8035 | 3.7814 | 3.719 | 3.6752 | 3.7082 | 3.7486 | 3.804
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-24 | 10.507 | 2.8695 | 2.8381 | 2.839 | 2.8061 | 2.7808 | 2.7748 | 2.818 | 2.8695
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-25 | 10.507 | 2.3914 | 2.2768 | 2.3462 | 2.3087 | 2.2403 | 2.2686 | 2.3053 | 2.3914
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-26 | 10.507 | 3.3308 | 3.3382 | 3.343 | 3.2104 | 3.2385 | 3.2289 | 3.2816 | 3.343
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-27 | 10.507 | 3.0378 | 3.0175 | 3.0294 | 2.9797 | 2.9663 | 2.9414 | 2.9953 | 3.0378
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-28 | 10.507 | 3.3787 | 3.4375 | 3.4326 | 3.4182 | 3.3429 | 3.3493 | 3.3932 | 3.4375
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-29 | 10.507 | 4.5828 | 4.511 | 4.4926 | 4.5255 | 4.4239 | 4.4696 | 4.5009 | 4.5828
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-06-01 | 30 | 2025-06-30 | 10.507 | 4.6008 | 4.4946 | 4.5138 | 4.4936 | 4.4023 | 4.4294 | 4.4891 | 4.6008
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-01 | 10.507 | 2.2045 | 2.1819 | 2.2118 | 2.1967 | 2.1382 | 2.1506 | 2.1806 | 2.2118
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-02 | 10.507 | 3.2469 | 3.191 | 3.2097 | 3.2048 | 3.1211 | 3.1151 | 3.1814 | 3.2469
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-03 | 10.507 | 2.5999 | 2.5582 | 2.5814 | 2.577 | 2.5086 | 2.4921 | 2.5529 | 2.5999
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-04 | 10.507 | 4.0496 | 3.9672 | 4.0037 | 4.0332 | 3.8397 | 3.8951 | 3.9647 | 4.0496
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-05 | 10.507 | 3.0115 | 2.9875 | 2.9868 | 2.992 | 2.9294 | 2.8928 | 2.9667 | 3.0115
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-06 | 10.507 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-07 | 10.507 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-08 | 10.507 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-09 | 10.507 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
FY2025-26 | 6 | 2025 | Year_3 | Year_3 | 2025-07-01 | 31 | 2025-07-10 | 10.507 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-07-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
[6 empty] | 31 | 2025-08-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Inv_SY_Dev
Finacial Year | Start Month | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Plant DC Capcity (MW) | IC1_Inv1 WRT Avg. | IC1_Inv2 wrt Avg. | IC1_Inv3 wrt Avg. | IC1_Inv4 wrt Avg. | IC2_Inv1 wrt Avg. | IC2_Inv2 wrt Avg. | IC1_Inv1 wrt Max. | IC1_Inv2 wrt Max. | IC1_Inv3 wrt Max. | IC1_Inv4 wrt Max. | IC2_Inv1 wrt Max. | IC2_Inv2 wrt Max.
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-31 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-31 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-31 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-31 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-01 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-02 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-03 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-04 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-05 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-07 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-08 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-09 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-10 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-12 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-13 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-14 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-16 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-17 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-18 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-19 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-20 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-21 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-22 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-23 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-24 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-27 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-28 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-30 | 10.507
FY2022-23 | 4 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-31 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-01 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-02 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-03 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-04 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-06 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-07 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-08 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-09 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-10 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-11 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-12 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-13 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-14 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-17 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-18 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-19 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-21 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-22 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-23 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-24 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-25 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-26 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-27 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-29 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-30 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-31 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-01 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-03 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-04 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-06 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-08 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-10 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-11 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-12 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-13 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-15 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-16 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-18 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-19 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-20 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-23 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-27 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-28 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-01 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-03 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-06 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-07 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-08 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-10 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-11 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-12 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-13 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-14 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-15 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-16 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-17 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-18 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-19 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-20 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-21 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-22 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-23 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-27 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-28 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-29 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-30 | 10.507
FY2022-23 | 4 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-01 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-02 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-03 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-04 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-05 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-06 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-07 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-08 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-09 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-10 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-11 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-12 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-13 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-14 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-15 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-16 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-17 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-18 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-19 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-20 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-21 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-22 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-23 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-24 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-25 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-26 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-27 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-28 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-29 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-04-01 | 30 | 2023-04-30 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-01 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-02 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-03 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-04 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-05 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-06 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-07 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-08 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-09 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-10 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-11 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-12 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-13 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-14 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-15 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-16 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-17 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-18 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-19 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-20 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-21 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-22 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-23 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-24 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-25 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-26 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-27 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-28 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-29 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-30 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-05-01 | 31 | 2023-05-31 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-01 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-02 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-03 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-04 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-05 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-06 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-07 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-08 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-09 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-10 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-11 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-12 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-13 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-14 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-15 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-16 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-17 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-18 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-19 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-20 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-21 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-22 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-23 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-24 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-25 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-26 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-27 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-28 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-29 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-06-01 | 30 | 2023-06-30 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-01 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-02 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-03 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-04 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-05 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-06 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-07 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-08 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-09 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-10 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-11 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-12 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-13 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-14 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-15 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-16 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-17 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-18 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-19 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-20 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-21 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-22 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-23 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-24 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-25 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-26 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-27 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-28 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-29 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-30 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-07-01 | 31 | 2023-07-31 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-01 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-02 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-03 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-04 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-05 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-06 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-07 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-08 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-09 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-10 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-11 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-12 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-13 | 10.507
FY2023-24 | 4 | 2023 | Year_1 | Year_1 | 2023-08-01 | 31 | 2023-08-14 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-15 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-16 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-17 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-18 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-19 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-20 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-21 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-22 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-23 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-24 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-25 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-26 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-27 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-28 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-29 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-30 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-31 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-01 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-02 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-03 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-04 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-05 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-06 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-07 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-08 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-09 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-10 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-11 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-12 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-13 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-14 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-15 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-16 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-17 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-18 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-19 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-20 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-21 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-22 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-23 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-24 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-25 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-26 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-27 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-28 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-29 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-30 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-09 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-11 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-12 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-13 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-19 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-20 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-22 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-24 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-25 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-26 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-27 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-31 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-01 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-02 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-03 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-04 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-05 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-06 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-07 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-08 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-09 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-10 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-11 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-12 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-13 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-14 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-15 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-16 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-17 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-18 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-19 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-20 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-21 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-22 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-23 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-24 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-25 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-26 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-27 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-28 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-29 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-30 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-01 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-02 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-03 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-05 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-06 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-07 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-08 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-09 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-10 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-12 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-13 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-14 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-16 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-17 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-18 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-19 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-20 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-21 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-23 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-24 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-25 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-26 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-28 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-29 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-30 | 10.507
FY2023-24 | 4 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-31 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-01 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-02 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-03 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-04 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-05 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-07 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-08 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-09 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-10 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-12 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-13 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-15 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-16 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-17 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-18 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-19 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-20 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-21 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-22 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-23 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-24 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-25 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-27 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-28 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-29 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-30 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-01 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-02 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-03 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-04 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-05 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-06 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-07 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-08 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-09 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-10 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-14 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-15 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-16 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-17 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-18 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-20 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-21 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-22 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-23 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-25 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-27 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-28 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-29 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-01 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-02 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-03 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-04 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-05 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-07 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-08 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-09 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-10 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-13 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-14 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-15 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-16 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-17 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-18 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-19 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-20 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-21 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-22 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-23 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-24 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-25 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-26 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-27 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-28 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-29 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-30 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-31 | 10.507
FY2023-24 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-01 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-02 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-03 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-04 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-05 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-06 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-07 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-08 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-09 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-10 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-11 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-12 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-13 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-14 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-15 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-16 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-17 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-18 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-19 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-20 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-21 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-22 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-23 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-24 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-25 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-26 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-27 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-28 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-29 | 10.507
FY2024-25 | 4 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-30 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-01 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-02 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-03 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-04 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-05 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-06 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-07 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-11 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-12 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-13 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-14 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-15 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-16 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-17 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-18 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-19 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-20 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-21 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-22 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-23 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-24 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-25 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-26 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-27 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-28 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-29 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-30 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-01 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-02 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-03 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-04 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-05 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-06 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-07 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-08 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-09 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-10 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-11 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-12 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-13 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-14 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-15 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-16 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-17 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-18 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-19 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-20 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-21 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-22 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-23 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-24 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-25 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-26 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-27 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-28 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-29 | 10.507
FY2024-25 | 5 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-30 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-01 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-02 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-03 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-04 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-05 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-06 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-07 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-08 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-09 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-10 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-11 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-12 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-13 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-14 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-15 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-16 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-17 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-18 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-19 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-20 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-21 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-22 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-23 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-24 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-25 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-26 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-27 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-28 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-29 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-30 | 10.507
FY2024-25 | 7 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-31 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-01 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-02 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-03 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-04 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-05 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-06 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-08 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-09 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-10 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-11 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-13 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-14 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-15 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-16 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-17 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-18 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-20 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-21 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-22 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-23 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-24 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-25 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-26 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-27 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-28 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-29 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-30 | 10.507
FY2024-25 | 8 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-31 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-01 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-02 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-03 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-04 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-05 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-06 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-07 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-08 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-09 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-10 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-11 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-12 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-13 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-14 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-15 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-16 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-17 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-18 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-19 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-20 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-21 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-22 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-23 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-24 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-25 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-26 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-27 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-28 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-29 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-30 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-01 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-02 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-04 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-05 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-06 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-07 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-08 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-09 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-10 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-11 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-12 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-13 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-14 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-15 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-16 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-17 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-18 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-19 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-20 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-21 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-22 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-23 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-26 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-27 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-28 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-30 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-01 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-03 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-04 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-06 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-07 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-08 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-09 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-10 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-11 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-12 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-13 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-14 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-15 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-16 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-17 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-19 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-20 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-21 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-22 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-23 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-24 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-25 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-26 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-27 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-28 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-29 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-30 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-01 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-02 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-03 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-04 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-05 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-06 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-07 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-08 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-09 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-10 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-11 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-12 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-13 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-14 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-15 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-16 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-17 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-18 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-19 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-20 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-21 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-22 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-23 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-24 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-25 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-26 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-27 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-28 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-29 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-30 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-31 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-01 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-02 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-03 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-04 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-05 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-07 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-09 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-10 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-11 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-12 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-13 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-14 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-15 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-16 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-17 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-18 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-19 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-20 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-21 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-22 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-23 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-24 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-26 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-27 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-29 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-30 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-31 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-01 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-02 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-03 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-04 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-05 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-06 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-07 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-08 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-09 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-10 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-11 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-12 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-13 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-14 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-15 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-16 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-17 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-18 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-19 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-20 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-21 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-22 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-23 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-24 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-25 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-26 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-27 | 10.507
FY2024-25 | 9 | 2024 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-28 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-01 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-02 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-03 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-04 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-05 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-06 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-07 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-08 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-09 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-10 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-11 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-12 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-13 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-14 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-15 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-16 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-17 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-18 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-19 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-20 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-22 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-23 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-24 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-25 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-26 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-28 | 10.507
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 10.507 | 2.36% | 1.572% | -0.4149% | -1.043% | -0.3206% | -2.154% | 0% | -0.7699% | -2.711% | -3.324% | -2.619% | -4.41%
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 10.507 | -0.002389% | 2.646% | -0.08603% | -1.013% | 0.09318% | -1.638% | -2.58% | 0% | -2.661% | -3.564% | -2.487% | -4.173%
FY2024-25 | 3 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 10.507 | 1.604% | 1.448% | -2.3% | -1.093% | -0.3292% | 0.6706% | 0% | -0.1537% | -3.843% | -2.655% | -1.903% | -0.919%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 10.507 | 1.674% | 0.1374% | -1.328% | 0.7878% | -0.1623% | -1.109% | 0% | -1.511% | -2.953% | -0.8717% | -1.806% | -2.737%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 10.507 | 0.9503% | 0.7565% | -1.372% | 0.5342% | -0.6114% | -0.2579% | 0% | -0.1919% | -2.3% | -0.4122% | -1.547% | -1.197%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 10.507 | -0.6259% | 1.701% | 0.3735% | 2.912% | -4.556% | 0.1954% | -3.438% | -1.177% | -2.467% | 0% | -7.256% | -2.64%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 10.507 | 9.099% | 8.016% | 7.328% | -30.07% | 1.965% | 3.659% | 0% | -0.9928% | -1.623% | -35.9% | -6.539% | -4.986%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 10.507 | 12.69% | 12.28% | 9.913% | -52.96% | 8.778% | 9.304% | 0% | -0.3638% | -2.463% | -58.26% | -3.47% | -3.003%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 10.507 | 7.343% | 8.734% | 7.046% | -40.15% | 8.755% | 8.27% | -1.298% | -0.01919% | -1.571% | -44.96% | 0% | -0.4462%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 10.507 | 7.821% | 5.079% | 3.102% | -24.5% | 4.798% | 3.699% | 0% | -2.543% | -4.376% | -29.98% | -2.804% | -3.823%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 10.507 | 0.5928% | 0.9721% | 0.4699% | 0.09084% | -0.5646% | -1.561% | -0.3757% | 0% | -0.4973% | -0.8728% | -1.522% | -2.509%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 10.507 | -0.6599% | 1.203% | 0.4369% | 1.932% | -1.06% | -1.852% | -2.543% | -0.7155% | -1.467% | 0% | -2.936% | -3.713%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 10.507 | 1.916% | -0.4354% | 1.007% | 0.2357% | -0.8644% | -1.858% | 0% | -2.307% | -0.8917% | -1.648% | -2.728% | -3.703%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 10.507 | -1.592% | 0.5098% | 2.714% | 1.759% | -2.229% | -1.162% | -4.192% | -2.146% | 0% | -0.9291% | -4.812% | -3.773%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 10.507 | 0.4132% | 0.4145% | 1.975% | 1.751% | -1.315% | -3.239% | -1.532% | -1.531% | 0% | -0.2204% | -3.227% | -5.113%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 10.507 | 1.244% | 0.0493% | 1.61% | 0.3604% | -0.8074% | -2.456% | -0.3593% | -1.536% | 0% | -1.229% | -2.379% | -4.001%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 10.507 | -0.8273% | 0.2088% | 2.47% | 0.8965% | -0.6695% | -2.078% | -3.217% | -2.206% | 0% | -1.535% | -3.063% | -4.438%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 10.507 | 15.7% | 10.19% | 14.46% | -61.55% | 11.98% | 9.222% | 0% | -4.765% | -1.075% | -66.77% | -3.216% | -5.599%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 10.507 | 1.9% | -1.819% | 1.14% | -1.337% | 0.216% | -0.1% | 0% | -3.651% | -0.7459% | -3.178% | -1.653% | -1.963%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 10.507 | -4.695% | 1.316% | 2.094% | 1.41% | 0.5612% | -0.6868% | -6.65% | -0.7617% | 0% | -0.6698% | -1.501% | -2.724%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 10.507 | -0.5333% | 1.01% | 1.085% | 3.578% | -3.4% | -1.741% | -3.97% | -2.479% | -2.407% | 0% | -6.737% | -5.135%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 10.507 | 1.401% | -1.004% | 0.4976% | 0.8978% | -0.06962% | -1.723% | 0% | -2.372% | -0.8909% | -0.4963% | -1.45% | -3.081%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 10.507 | 1.567% | -1.524% | 1.673% | 2.858% | -2.486% | -2.088% | -1.255% | -4.26% | -1.151% | 0% | -5.195% | -4.808%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 10.507 | 9.324% | 5.873% | 8.942% | -34.19% | 5.181% | 4.866% | 0% | -3.156% | -0.3492% | -39.8% | -3.789% | -4.077%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 10.507 | 2.481% | 1.297% | 0.04457% | -1.466% | -1.321% | -1.036% | 0% | -1.155% | -2.378% | -3.852% | -3.71% | -3.432%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 10.507 | 1.597% | 0.5731% | 0.5514% | -1.63% | -0.01591% | -1.076% | 0% | -1.008% | -1.029% | -3.176% | -1.588% | -2.631%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 10.507 | 2.147% | 2.052% | 1.669% | -1.844% | -1.679% | -2.345% | 0% | -0.09371% | -0.4679% | -3.907% | -3.746% | -4.398%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 10.507 | 3.098% | 0.2533% | 0.9568% | -2.906% | -0.3312% | -1.071% | 0% | -2.759% | -2.077% | -5.823% | -3.326% | -4.044%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 10.507 | 0.4347% | -0.5891% | 1.3% | -0.3971% | -0.6427% | -0.106% | -0.8543% | -1.865% | 0% | -1.675% | -1.918% | -1.388%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 10.507 | 0.6028% | -0.7199% | -1.175% | -2.503% | 2.26% | 1.535% | -1.62% | -2.914% | -3.359% | -4.657% | 0% | -0.7084%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 10.507 | 0.5087% | -0.2306% | -0.7289% | 0.3808% | -0.09001% | 0.1601% | 0% | -0.7355% | -1.231% | -0.1272% | -0.5956% | -0.3468%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 10.507 | 0.09354% | -1.666% | 0.1385% | 1.44% | 0.02533% | -0.03189% | -1.328% | -3.062% | -1.283% | 0% | -1.395% | -1.451%
FY2025-26 | 3 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 10.507 | -0.1171% | -0.25% | -0.88% | 2.311% | -1.87% | 0.8059% | -2.374% | -2.504% | -3.119% | 0% | -4.087% | -1.471%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 10.507 | 1.435% | -0.9071% | -3.662% | -0.1541% | 1.241% | 2.046% | -0.5988% | -2.894% | -5.593% | -2.156% | -0.7886% | 0%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 10.507 | 0.8697% | -1.685% | -1.681% | 0.4774% | 1.986% | 0.0323% | -1.095% | -3.599% | -3.596% | -1.479% | 0% | -1.916%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 10.507 | 1.598% | -0.822% | -0.947% | -0.4598% | 0.439% | 0.192% | 0% | -2.382% | -2.505% | -2.025% | -1.141% | -1.384%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 10.507 | 1.146% | -0.9732% | -0.4577% | 0.7357% | -0.265% | -0.1854% | 0% | -2.095% | -1.585% | -0.4052% | -1.395% | -1.316%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 10.507 | 0.8874% | -1.042% | -1.241% | 1.167% | 0.4495% | -0.2212% | -0.2759% | -2.183% | -2.38% | 0% | -0.7088% | -1.372%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 10.507 | 2.148% | 0.982% | -2.472% | 0.3767% | -0.389% | -0.6454% | 0% | -1.142% | -4.523% | -1.734% | -2.484% | -2.735%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 10.507 | 1.596% | 0.2647% | -1.267% | 0.6353% | -0.4107% | -0.8181% | 0% | -1.31% | -2.818% | -0.9455% | -1.975% | -2.376%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 10.507 | 1.631% | 1.348% | -0.6354% | 1.266% | -1.469% | -2.141% | 0% | -0.2782% | -2.23% | -0.3598% | -3.05% | -3.712%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 10.507 | 2.781% | 1.805% | -0.6414% | -0.393% | -1.893% | -1.66% | 0% | -0.9496% | -3.33% | -3.089% | -4.548% | -4.321%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 10.507 | 3.312% | 1.61% | -0.5375% | -0.2475% | -0.6883% | -3.449% | 0% | -1.647% | -3.726% | -3.445% | -3.872% | -6.544%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 10.507 | -1.594% | 0.356% | 0.6802% | 1.103% | 1.343% | -1.889% | -2.898% | -0.9741% | -0.6542% | -0.237% | 0% | -3.189%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 10.507 | 1.59% | 0.3054% | 0.5754% | 0.4671% | -1.459% | -1.479% | 0% | -1.264% | -0.9986% | -1.105% | -3.001% | -3.02%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 10.507 | 2.061% | 0.3388% | -1.199% | -1.112% | -0.7835% | 0.6939% | 0% | -1.688% | -3.194% | -3.109% | -2.787% | -1.34%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 10.507 | 0.6624% | -0.198% | -0.453% | 0.7336% | -1.022% | 0.2767% | -0.07068% | -0.9248% | -1.178% | 0% | -1.743% | -0.4536%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 10.507 | -0.1942% | -1.07% | 0.006608% | 0.7643% | -0.3036% | 0.7971% | -0.9834% | -1.853% | -0.7842% | -0.03249% | -1.092% | 0%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 10.507 | -0.3605% | -0.6915% | 0.334% | 0.4738% | -1.221% | 1.465% | -1.799% | -2.125% | -1.115% | -0.977% | -2.647% | 0%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 10.507 | 0.3604% | -1.736% | 1.087% | 0.8994% | -0.4981% | -0.1133% | -0.7192% | -2.793% | 0% | -0.186% | -1.568% | -1.188%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 10.507 | -7.809% | -0.2763% | 2.325% | 2.264% | 1.697% | 1.799% | -9.904% | -2.542% | 0% | -0.05963% | -0.6143% | -0.5144%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 10.507 | -0.3639% | -2.621% | 2.017% | 0.8255% | 1.509% | -1.366% | -2.333% | -4.546% | 0% | -1.168% | -0.4977% | -3.315%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 10.507 | 0.44% | -2.696% | 3.441% | 2.475% | -2.466% | -1.195% | -2.901% | -5.933% | 0% | -0.9338% | -5.711% | -4.482%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 10.507 | 0.5287% | -2.07% | 1.695% | 1.513% | -1.594% | -0.07323% | -1.147% | -3.703% | 0% | -0.1794% | -3.234% | -1.739%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 10.507 | 2.967% | -1.76% | 0.5176% | 0.1529% | -1.7% | -0.1772% | 0% | -4.592% | -2.379% | -2.733% | -4.533% | -3.054%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 10.507 | 4.142% | -2.453% | 1.022% | 0.01609% | -4.038% | 1.311% | 0% | -6.333% | -2.996% | -3.962% | -7.855% | -2.719%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 10.507 | 10.77% | 8.122% | 10.22% | -49.76% | 9.04% | 11.6% | -0.7389% | -3.115% | -1.231% | -54.98% | -2.292% | 0%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 10.507 | 4.286% | -9.388% | 3.702% | -7.723% | 3.702% | 5.422% | -1.078% | -14.05% | -1.631% | -12.47% | -1.631% | 0%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 10.507 | -2.01% | -1.835% | 1.706% | 0.9763% | 0.2029% | 0.9594% | -3.654% | -3.481% | 0% | -0.7174% | -1.478% | -0.734%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 10.507 | 1.475% | -2.867% | 0.5618% | -0.3172% | 0.02719% | 1.12% | 0% | -4.279% | -0.8998% | -1.766% | -1.427% | -0.3495%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 10.507 | 1.758% | -2.651% | 1.863% | 1.217% | -1.749% | -0.4382% | -0.1032% | -4.432% | 0% | -0.6348% | -3.547% | -2.26%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 10.507 | 1.097% | -2.96% | 1.307% | 1.498% | -1.166% | 0.2237% | -0.3952% | -4.392% | -0.188% | 0% | -2.625% | -1.256%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 10.507 | 1.331% | -2.71% | 1.779% | 0.09155% | -0.378% | -0.1132% | -0.4406% | -4.411% | 0% | -1.658% | -2.119% | -1.859%
FY2025-26 | 5 | 2024 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 10.507 | 1.303% | -0.7761% | 1.004% | -0.4294% | -1.487% | 0.3858% | 0% | -2.052% | -0.2948% | -1.71% | -2.754% | -0.905%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 10.507 | 3.721% | 0.2181% | -0.9572% | -1.498% | -2.933% | 1.449% | 0% | -3.377% | -4.511% | -5.032% | -6.415% | -2.191%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 10.507 | 3.022% | -0.2937% | 0.5891% | -1.483% | -1.939% | 0.1051% | 0% | -3.218% | -2.361% | -4.372% | -4.815% | -2.831%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 10.507 | 2.519% | -3.09% | 2.002% | -0.7839% | -1.161% | 0.5151% | 0% | -5.471% | -0.5041% | -3.221% | -3.589% | -1.954%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 10.507 | 1.699% | 0.8939% | 0.08271% | -1.378% | -1.946% | 0.6486% | 0% | -0.7921% | -1.59% | -3.026% | -3.585% | -1.033%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 10.507 | 0.3983% | 0.8191% | 1.774% | -1.096% | -3.211% | 1.315% | -1.351% | -0.9379% | 0% | -2.819% | -4.897% | -0.4504%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 10.507 | -0.2698% | 1.585% | 0.638% | 1.074% | -3.451% | 0.4244% | -1.826% | 0% | -0.932% | -0.503% | -4.957% | -1.142%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 10.507 | -4.063% | 2.903% | 0.7504% | 1.374% | -1.072% | 0.1072% | -6.77% | 0% | -2.092% | -1.486% | -3.863% | -2.717%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 10.507 | 2.184% | 2.193% | 0.265% | -1.717% | -1.61% | -1.316% | -0.008302% | 0% | -1.887% | -3.826% | -3.721% | -3.433%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 10.507 | -0.4308% | 2.3% | 1.66% | -0.2218% | -2.161% | -1.146% | -2.669% | 0% | -0.6255% | -2.465% | -4.36% | -3.368%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 10.507 | 2.02% | 1.594% | 1.683% | -2.526% | -1.88% | -0.8904% | 0% | -0.4181% | -0.3307% | -4.457% | -3.823% | -2.853%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 10.507 | 0.8123% | 0.7782% | 1.076% | -1.582% | -0.5077% | -0.5769% | -0.2606% | -0.2943% | 0% | -2.629% | -1.567% | -1.635%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 10.507 | 2.317% | -0.4109% | 0.9331% | -1.798% | -1.243% | 0.2006% | 0% | -2.667% | -1.353% | -4.022% | -3.479% | -2.069%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 10.507 | 1.239% | 1.291% | 0.6111% | -2.141% | -1.321% | 0.3219% | -0.05165% | 0% | -0.6712% | -3.389% | -2.579% | -0.9567%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 10.507 | -0.9476% | 0.8567% | 2.461% | -1.569% | -0.3064% | -0.4955% | -3.327% | -1.566% | 0% | -3.933% | -2.701% | -2.886%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 10.507 | 1.457% | 1.211% | 1.576% | -2.12% | -1.119% | -1.005% | -0.1175% | -0.3597% | 0% | -3.639% | -2.654% | -2.541%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 10.507 | 2.322% | 0.02408% | 0.7659% | -1.667% | -1.343% | -0.101% | 0% | -2.246% | -1.521% | -3.899% | -3.582% | -2.368%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 10.507 | 1.119% | -1.169% | 1.057% | -0.5241% | -0.4868% | 0.003909% | 0% | -2.263% | -0.0621% | -1.625% | -1.588% | -1.103%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 10.507 | 1.573% | 1.613% | 0.7675% | -2.121% | -0.4172% | -1.414% | -0.03929% | 0% | -0.8318% | -3.675% | -1.998% | -2.979%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 10.507 | 3.127% | 3.161% | 1.851% | -7.487% | -0.0184% | -0.6336% | -0.03212% | 0% | -1.269% | -10.32% | -3.082% | -3.678%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 10.507 | 1.609% | 2.479% | 0.02868% | -0.9335% | -2.553% | -0.6311% | -0.8487% | 0% | -2.391% | -3.33% | -4.91% | -3.035%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 10.507 | 3.093% | 2.729% | 0.2804% | -1.957% | -2.523% | -1.622% | 0% | -0.3539% | -2.729% | -4.899% | -5.448% | -4.574%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 10.507 | 1.391% | 3.367% | 0.6871% | -2.773% | -1.464% | -1.209% | -1.912% | 0% | -2.593% | -5.94% | -4.674% | -4.427%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 10.507 | 1.479% | 1.466% | 0.8765% | -0.7882% | -1.956% | -1.078% | 0% | -0.01285% | -0.5941% | -2.234% | -3.386% | -2.52%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 10.507 | 1.826% | 0.7102% | 0.7438% | -0.425% | -1.321% | -1.533% | 0% | -1.095% | -1.062% | -2.21% | -3.09% | -3.299%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 10.507 | 3.734% | -1.24% | 1.774% | 0.1456% | -2.822% | -1.593% | 0% | -4.795% | -1.89% | -3.46% | -6.32% | -5.135%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 10.507 | 1.497% | 1.725% | 1.869% | -2.169% | -1.314% | -1.607% | -0.3652% | -0.1413% | 0% | -3.964% | -3.125% | -3.412%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 10.507 | 1.418% | 0.7401% | 1.137% | -0.5224% | -0.9707% | -1.802% | 0% | -0.6685% | -0.2776% | -1.913% | -2.355% | -3.175%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 10.507 | -0.4278% | 1.306% | 1.16% | 0.7381% | -1.483% | -1.293% | -1.712% | 0% | -0.1443% | -0.5607% | -2.754% | -2.565%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 10.507 | 1.82% | 0.2245% | -0.1849% | 0.5478% | -1.711% | -0.6959% | 0% | -1.567% | -1.969% | -1.249% | -3.468% | -2.471%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 10.507 | 2.487% | 0.1231% | 0.5512% | 0.1007% | -1.933% | -1.329% | 0% | -2.307% | -1.889% | -2.329% | -4.313% | -3.724%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 10.507 | 1.096% | 0.05665% | 1.432% | 0.7365% | -1.945% | -1.376% | -0.3307% | -1.356% | 0% | -0.6855% | -3.329% | -2.768%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 10.507 | 2.057% | 0.2997% | 0.8883% | 0.736% | -1.896% | -2.085% | 0% | -1.722% | -1.146% | -1.295% | -3.874% | -4.059%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 10.507 | 1.843% | 0.2102% | 1.119% | 0.9449% | -1.735% | -2.381% | 0% | -1.603% | -0.7112% | -0.8817% | -3.513% | -4.147%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 10.507 | 2.141% | 0.06087% | 0.9829% | 1.727% | -3.154% | -1.757% | 0% | -2.036% | -1.134% | -0.405% | -5.184% | -3.817%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 10.507 | 1.51% | 0.7022% | 0.6793% | 0.854% | -1.257% | -2.489% | 0% | -0.7953% | -0.8179% | -0.6458% | -2.725% | -3.939%
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 10.507
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-07 | 10.507
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-08 | 10.507
FY2025-26 | 6 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-09 | 10.507
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Tracker_BD
Sr. No. | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Date | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affected Equipment | Plant Equivalent Weightage | Angle of affected equipment | Inv Number | Gateway Number | Grid Number | MSAT Number | Table Number | Fault Category | Fault Code (As per HMI) | Breakdown Description | Fault Time | Fault Acknowledgement Time | Work Start time on Fault | Work Completion time on fault | Acknowledgement time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Avg. Target Angle during Fault Time (Radians) | Approximate Energy Loss Factor (%) | Plant Equivalent breakdown | Old equipment Serial Number | New Equipment Serial Number | Column1
1 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:29 | 18:29 | 12 | Actuator Type1 |  | 0 | IC1_Inv4 | G5 | G4 | 37 | T108 | Actuator | Actuator fail | Actuator fail | 8:10 | 8:10 | 8:10 | 8:50 | 0 | 0 | 0.66667 | 0.66667 | Actuator 2 No Limit Switch was replaced | Close
2 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:29 | 18:29 | 12 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 | 64 | T95 | Actuator | Actuator fail | Actuator fail | 8:40 | 8:40 | 8:40 | 9:30 | 0 | 0 | 0.83333 | 0.83333 | 1 No Medium Gear Replaced | Close
3 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:29 | 18:29 | 12 | Actuator Type1 |  | 0 | IC1_Inv2 | G5 | G4 | 27 | T65 | Actuator | Actuator fail | Actuator fail | 9:20 | 9:20 | 9:20 | 10:10 | 0 | 0 | 0.83333 | 0.83333 | 1 No Actuator Motor | Close
4 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 6:29 | 18:29 | 12 | Actuator Type1 |  | 0 | IC1_Inv3 | G1 | G3 | 12 | T57 | Actuator | Actuator fail | Actuator fail | 9:40 | 9:40 | 9:40 | 10:20 | 0 | 0 | 0.66667 | 0.66667 | Actuator 2 No Limit Switch was replaced | Close
5 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:23 | 18:14 | 11.85 | Actuator Type1 |  | 0 | IC1_Inv3 | G5 | G4 | 30 | T80 | Actuator | Actuator fail | Actuator fail | 15:50 | 15:50 | 15:50 | 16:20 | 0 | 0 | 0.5 | 0.5 | 2 Nos Actuator Bearing Replaced | Close
6 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:23 | 18:14 | 11.85 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 21 | T34 | Actuator | Actuator fail | Actuator fail | 16:30 | 16:30 | 16:30 | 17:30 | 0 | 0 | 1 | 1 | 1 No Actuator Motor | Close
7 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:31 | 18:14 | 11.7167 | Actuator Type1 |  | 0 | IC1_Inv3 | G5 | G4 | 30 | T80 | Actuator | Actuator fail | Actuator fail | 7:10 | 7:10 | 7:10 | 7:50 | 0 | 0 | 0.66667 | 0.66667 | Actuator 2 No Limit Switch was replaced | Close
8 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:31 | 18:14 | 11.7167 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 63 | T70 | Actuator | Actuator fail | Actuator fail | 8:20 | 8:20 | 8:20 | 8:30 | 0 | 0 | 0.16667 | 0.16667 | Actuator motor 2 no.s Carbon brushes | Close
9 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:31 | 18:14 | 11.7167 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 21 | T32 | Actuator | Actuator fail | Actuator fail | 8:40 | 8:40 | 8:40 | 9:40 | 0 | 0 | 1 | 1 | 1 No Big Gear Replaced | Close
10 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:31 | 18:14 | 11.7167 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 4 | T17 | Actuator | Actuator fail | Actuator fail | 9:10 | 9:10 | 9:10 | 10:10 | 0 | 0 | 1 | 1 | 2 Nos Actuator Bearing Replaced | Close
11 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:21 | 18:23 | 12.0333 | Actuator Type1 |  | 0 | IC2_Inv1 | G5 | G4 | 18 | T20 | Actuator | Actuator fail | Actuator fail | 16:20 | 16:20 | 16:20 | 16:40 | 0 | 0 | 0.33333 | 0.33333 | 1 No Big Gear Replaced | Close |  |  | 0
12 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:21 | 18:23 | 12.0333 | Actuator Type1 |  | 0 | IC1_Inv4 | G3 | G5 | 69 | T116 | Actuator | Actuator fail | Actuator fail | 17:20 | 17:20 | 17:20 | 17:50 | 0 | 0 | 0.5 | 0.5 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
13 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:21 | 18:23 | 12.0333 | Actuator Type1 |  | 0 | IC1_Inv4 | G3 | G5 | 73 | T136 | Actuator | Actuator fail | Actuator fail | 17:35 | 17:35 | 17:35 | 18:20 | 0 | 0 | 0.75 | 0.75 | 1 No Actuator Motor | Close |  |  | 0
14 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:30 | 18:26 | 11.9333 | Actuator Type1 |  | 0 | IC2_Inv1 | G1 | G3 | 121 | TW01 | Actuator | Actuator fail | Actuator fail | 15:30 | 15:30 | 15:30 | 16:30 | 0 | 0 | 1 | 1 | 1 No Actuator Motor | Close |  |  | 0
15 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:30 | 18:26 | 11.9333 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 3 | T16 | Actuator | Actuator fail | Actuator fail | 15:50 | 15:50 | 15:50 | 16:40 | 0 | 0 | 0.83333 | 0.83333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
16 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:30 | 18:26 | 11.9333 | Actuator Type1 |  | 0 | IC1_Inv2 | G1 | G3 | 10 | T50 | Actuator | Actuator fail | Actuator fail | 16:45 | 16:45 | 16:45 | 17:20 | 0 | 0 | 0.58333 | 0.58333 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
17 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC1_Inv3 | G5 | G4 | 33 | T88 to T92 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 11:10 | 11:10 | 11:10 | 11:30 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
18 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC2_Inv2 | G4 | G6 | 82 | T21 to T25 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 11:40 | 11:40 | 11:40 | 12:00 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
19 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC2_Inv2 | G4 | G6 | 87 | T46 TO T50 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 12:30 | 12:30 | 12:30 | 12:40 | 0 | 0 | 0.16667 | 0.16667 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
20 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC2_Inv2 | G4 | G6 | 79 | T6 TO T10 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 13:30 | 13:30 | 13:30 | 13:50 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
21 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC2_Inv2 | G4 | G6 | 80 | T11 to T15 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 14:00 | 14:00 | 14:00 | 14:20 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
22 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC2_Inv2 | G4 | G6 | 81 | T16 to T20 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 14:30 | 14:30 | 14:30 | 14:40 | 0 | 0 | 0.16667 | 0.16667 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
23 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC1_Inv4 | G3 | G5 | 72 | T131 to T135 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 14:50 | 14:50 | 14:50 | 15:10 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
24 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC1_Inv1 | G3 | G5 | 52 | T36 to T40 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 15:20 | 15:20 | 15:20 | 15:40 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
25 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | MSAT_Type3 |  | 0 | IC1_Inv4 | G3 | G5 | 68 | T111 TO T115 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 15:30 | 15:30 | 15:30 | 15:50 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
26 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:19 | 18:33 | 12.2333 | Actuator Type1 |  | 0 | IC1_Inv4 | G5 | G4 | 40 | T126 | Actuator | Actuator fail | Actuator fail | 15:20 | 15:20 | 15:20 | 16:00 | 0 | 0 | 0.66667 | 0.66667 | 1 No Big Gear Replaced | Close |  |  | 0
27 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 6:19 | 18:33 | 12.2333 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 42 | T49 | Actuator | Actuator fail | Actuator fail | 16:20 | 16:20 | 16:20 | 16:40 | 0 | 0 | 0.33333 | 0.33333 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
28 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:20 | 18:13 | 11.8833 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G2 | 100 | T21 | Actuator | Actuator fail | Actuator fail | 14:30 | 14:30 | 14:30 | 15:10 | 0 | 0 | 0.66667 | 0.66667 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
29 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:20 | 18:13 | 11.8833 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G1 | 108 | T23 | Actuator | Actuator fail | Actuator fail | 14:50 | 14:50 | 14:50 | 15:20 | 0 | 0 | 0.5 | 0.5 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
30 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:20 | 18:13 | 11.8833 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G2 | 99 | T17 | Actuator | Actuator fail | Actuator fail | 15:40 | 15:40 | 15:40 | 16:30 | 0 | 0 | 0.83333 | 0.83333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
31 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:20 | 18:13 | 11.8833 | MSAT_Type3 |  | 0 | IC2_Inv1 | G7 | G1 | 107 | T16 to T20 | PCB | PCB_100 Type communication problem | PCB_100 Type communication problem | 16:50 | 16:50 | 16:50 | 17:10 | 0 | 0 | 0.33333 | 0.33333 | PCB_100 Type was Replaced By PCB_100 Type | Close |  |  | 0
32 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:21 | 18:21 | 12 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 5 | T20 | Actuator | Actuator fail | Actuator fail | 15:25 | 15:25 | 15:25 | 15:50 | 0 | 0 | 0.41667 | 0.41667 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
33 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:20 | 18:21 | 12.0167 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 2 | T08 | Actuator | Actuator fail | Actuator fail | 11:00 | 11:00 | 11:00 | 11:40 | 0 | 0 | 0.66667 | 0.66667 | 1 No Medium Gear Replaced | Close |  |  | 0
34 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 6:20 | 18:21 | 12.0167 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 3 | T10 | Actuator | Actuator fail | Actuator fail | 11:20 | 11:20 | 11:20 | 12:10 | 0 | 0 | 0.83333 | 0.83333 | 1 No Big Gear Replaced | Close |  |  | 0
35 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:22 | 18:21 | 11.9833 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 | 32 | T86 | Actuator | Actuator fail | Actuator fail | 15:45 | 15:45 | 15:45 | 17:20 | 0 | 0 | 1.5833 | 1.5833 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
36 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:20 | 18:20 | 12 | Actuator Type1 |  | 0 | IC1_Inv2 | G4 | G6 | 90 | T65 | Actuator | Actuator fail | Actuator fail | 8:30 | 8:30 | 8:30 | 9:45 | 0 | 0 | 1.25 | 1.25 | 1 No Actuator Motor | Close |  |  | 0
37 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:23 | 18:12 | 11.8167 | Actuator Type1 |  | 0 | IC1_Inv4 | G3 | G5 | 73 | T142 | Actuator | Actuator fail | Actuator fail | 8:45 | 8:45 | 8:45 | 9:50 | 0 | 0 | 1.0833 | 1.0833 | 1 No Medium Gear Replaced | Close |  |  | 0
38 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:23 | 18:12 | 11.8167 | Actuator Type1 |  | 0 | IC1_Inv4 | G3 | G5 | 67 | T110 | Actuator | Actuator fail | Actuator fail | 9:35 | 9:35 | 9:35 | 10:45 | 0 | 0 | 1.1667 | 1.1667 | 1 No Actuator Motor | Close |  |  | 0
39 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 6:23 | 18:12 | 11.8167 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 | 64 | T94 | Actuator | Actuator fail | Actuator fail | 10:00 | 10:00 | 10:00 | 11:00 | 0 | 0 | 1 | 1 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
40 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 6:25 | 18:05 | 11.6667 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 120 | T16 | Actuator | Actuator fail | Actuator fail | 9:45 | 9:45 | 9:45 | 11:15 | 0 | 0 | 1.5 | 1.5 | 1 No. Nylon brass bush replaced | Close |  |  | 0
41 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:19 | 18:24 | 12.0833 | Actuator Type1 |  | 0 | IC1_Inv3 | G1 | G3 | 12 | T55 | Actuator | Actuator fail | Actuator fail | 14:10 | 14:10 | 14:10 | 14:50 | 0 | 0 | 0.66667 | 0.66667 | 1 No Medium Gear Replaced | Close |  |  | 0
42 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:19 | 18:24 | 12.0833 | Actuator Type1 |  | 0 | IC1_Inv1 | G4 | G6 | 86 | T43 | Actuator | Actuator fail | Actuator fail | 14:40 | 14:40 | 14:40 | 15:40 | 0 | 0 | 1 | 1 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
43 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:19 | 18:24 | 12.0833 | Actuator Type1 |  | 0 | IC1_Inv1 | G4 | G6 | 86 | T45 | Actuator | Actuator fail | Actuator fail | 15:35 | 15:35 | 15:35 | 16:10 | 0 | 0 | 0.58333 | 0.58333 | 1 No Medium Gear Replaced | Close |  |  | 0
44 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:15 | 18:25 | 12.1667 | Actuator Type1 |  | 0 | IC1_Inv4 | G4 | G6 | 116 | TW1 | Actuator | Actuator fail | Actuator fail | 16:10 | 16:10 | 16:10 | 16:40 | 0 | 0 | 0.5 | 0.5 | 1 No. Nylon brass bush replaced | Close |  |  | 0
45 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 6:15 | 18:25 | 12.1667 | Actuator Type1 |  | 0 | IC2_Inv1 | G5 | G4 | 19 | T23 | Actuator | Actuator fail | Actuator fail | 17:20 | 17:20 | 17:20 | 17:50 | 0 | 0 | 0.5 | 0.5 | 1 No Medium Gear Replaced | Close |  |  | 0
46 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:15 | 18:28 | 12.2167 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 45 | T01 | Actuator | Actuator fail | Actuator fail | 14:30 | 14:30 | 14:30 | 15:10 | 0 | 0 | 0.66667 | 0.66667 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
47 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 6:15 | 18:28 | 12.2167 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 47 | T13 | Actuator | Actuator fail | Actuator fail | 15:20 | 15:20 | 15:20 | 15:40 | 0 | 0 | 0.33333 | 0.33333 | 1 No. Nylon brass bush replaced | Close |  |  | 0
48 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:09 | 18:24 | 12.25 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 45 | T05 | Actuator | Actuator fail | Actuator fail | 9:10 | 9:10 | 9:10 | 10:30 | 0 | 0 | 1.3333 | 1.3333 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
49 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:09 | 18:24 | 12.25 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 53 | T42 | Actuator | Actuator fail | Actuator fail | 14:20 | 14:20 | 14:20 | 15:40 | 0 | 0 | 1.3333 | 1.3333 | 1 No Small Gear Replaced | Close |  |  | 0
50 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:15 | 18:07 | 11.8667 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 41 | T42 | Actuator | Actuator fail | Actuator fail | 15:10 | 15:10 | 15:10 | 15:50 | 0 | 0 | 0.66667 | 0.66667 | 1 No Medium Gear Replaced | Close |  |  | 0
51 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 6:15 | 18:07 | 11.8667 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 41 | T44 | Actuator | Actuator fail | Actuator fail | 16:20 | 16:20 | 16:20 | 17:20 | 0 | 0 | 1 | 1 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
52 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 6:07 | 18:26 | 12.3167 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 27 | T64 | Actuator | Actuator fail | Actuator fail | 13:20 | 13:20 | 13:20 | 14:20 | 0 | 0 | 1 | 1 | 1 No Medium Gear Replaced | Close |  |  | 0
53 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:10 | 18:23 | 12.2167 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 23 | T44 | Actuator | Actuator fail | Actuator fail | 9:10 | 9:10 | 9:10 | 10:20 | 0 | 0 | 1.1667 | 1.1667 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
54 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:10 | 18:23 | 12.2167 | Actuator Type1 |  | 0 | IC1_Inv2 | G4 | G6 | 84 | T27 | Actuator | Actuator fail | Actuator fail | 10:20 | 10:20 | 10:20 | 11:10 | 0 | 0 | 0.83333 | 0.83333 | 1 No. Nylon brass bush replaced | Close |  |  | 0
55 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 6:10 | 18:23 | 12.2167 | Actuator Type1 |  | 0 | IC1_Inv2 | G4 | G6 | 89 | T60 | Actuator | Actuator fail | Actuator fail | 11:10 | 11:10 | 11:10 | 12:30 | 0 | 0 | 1.3333 | 1.3333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
56 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:09 | 18:29 | 12.3333 | Actuator Type1 |  | 0 | IC1_Inv1 | G3 | G5 | 118 | Tw5 | Actuator | Actuator fail | Actuator fail | 8:20 | 8:20 | 8:20 | 9:40 | 0 | 0 | 1.3333 | 1.3333 | 1 No Actuator Motor | Close |  |  | 0
57 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 6:09 | 18:29 | 12.3333 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 58 | T70 | Actuator | Actuator fail | Actuator fail | 12:20 | 12:20 | 12:20 | 13:40 | 0 | 0 | 1.3333 | 1.3333 | 1 No Medium Gear Replaced | Close |  |  | 0
58 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 6:08 | 18:30 | 12.3667 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 2 | T08 | Actuator | Actuator fail | Actuator fail | 11:30 | 11:30 | 11:30 | 12:30 | 0 | 0 | 1 | 1 | 1 No. Nylon brass bush replaced | Close |  |  | 0
59 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:35 | 12.5333 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 4 | T16 | Actuator | Actuator fail | Actuator fail | 8:10 | 8:10 | 8:10 | 9:30 | 0 | 0 | 1.3333 | 1.3333 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
60 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 6:03 | 18:35 | 12.5333 | Actuator Type1 |  | 0 | IC1_Inv2 | G1 | G3 | 11 | T52 | Actuator | Actuator fail | Actuator fail | 9:20 | 9:20 | 9:20 | 10:10 | 0 | 0 | 0.83333 | 0.83333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
61 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:05 | 18:33 | 12.4667 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 25 | T52 | Actuator | Actuator fail | Actuator fail | 14:20 | 14:20 | 14:20 | 15:25 | 0 | 0 | 1.0833 | 1.0833 | 1 No Actuator Motor | Close |  |  | 0
62 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:05 | 18:33 | 12.4667 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 55 | T31 | Actuator | Actuator fail | Actuator fail | 15:30 | 15:30 | 15:30 | 16:10 | 0 | 0 | 0.66667 | 0.66667 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
63 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:02 | 18:17 | 12.25 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 23 | T42 | Actuator | Actuator fail | Actuator fail | 12:00 | 12:00 | 12:00 | 12:50 | 0 | 0 | 0.83333 | 0.83333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
64 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:09 | 18:19 | 12.1667 | Actuator Type1 |  | 0 | IC1_Inv2 | G4 | G6 | 90 | T62 | Actuator | Actuator fail | Actuator fail | 9:10 | 9:10 | 9:10 | 10:25 | 0 | 0 | 1.25 | 1.25 | 1 No. Nylon brass bush replaced | Close |  |  | 0
65 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 6:09 | 18:19 | 12.1667 | Actuator Type1 |  | 0 | IC1_Inv1 | G4 | G6 | 86 | T45 | Actuator | Actuator fail | Actuator fail | 10:20 | 10:20 | 10:20 | 11:10 | 0 | 0 | 0.83333 | 0.83333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
66 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:03 | 18:32 | 12.4833 | Actuator Type1 |  | 0 | IC2_Inv2 | G4 | G6 | 83 | T27 | Actuator | Actuator fail | Actuator fail | 10:20 | 10:20 | 10:20 | 11:30 | 0 | 0 | 1.1667 | 1.1667 | 1 No Actuator Motor | Close |  |  | 0
67 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:13 | 18:33 | 12.3333 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 56 | T37 | Actuator | Actuator fail | Actuator fail | 14:40 | 14:40 | 14:40 | 15:20 | 0 | 0 | 0.66667 | 0.66667 | 1 No Medium Gear Replaced | Close |  |  | 0
68 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 6:56 | 18:31 | 11.5833 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 |  | T106 | Actuator | Actuator fail | Actuator fail | 10:20 | 10:20 | 10:20 | 11:35 | 0 | 0 | 1.25 | 1.25 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
69 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 6:56 | 18:31 | 11.5833 | Actuator Type1 |  | 0 | IC1_Inv3 | G5 | G4 |  | T95 | Actuator | Actuator fail | Actuator fail | 11:20 | 11:20 | 11:20 | 11:50 | 0 | 0 | 0.5 | 0.5 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
70 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 6:04 | 18:36 | 12.5333 | Actuator Type1 |  | 0 | IC2_Inv2 | G4 | G6 | 54 | T10 | Actuator | Actuator fail | Actuator fail | 9:10 | 9:10 | 9:10 | 10:20 | 0 | 0 | 1.1667 | 1.1667 | 1 No Medium Gear Replaced | Close |  |  | 0
71 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 6:08 | 18:36 | 12.4667 | Actuator Type1 |  | 0 | IC1_Inv3 | G5 | G4 | 93 | T80 | Actuator | Actuator fail | Actuator fail | 8:30 | 8:30 | 8:30 | 9:45 | 0 | 0 | 1.25 | 1.25 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
72 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:04 | 18:37 | 12.55 | Actuator Type1 |  | 0 | IC1_Inv4 | G5 | G4 | 66 | T133 | Actuator | Actuator fail | Actuator fail | 14:20 | 14:20 | 14:20 | 15:10 | 0 | 0 | 0.83333 | 0.83333 | 1 No. Nylon brass bush replaced | Close |  |  | 0
73 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:04 | 18:37 | 12.55 | Actuator Type1 |  | 0 | IC2_Inv2 | G4 | G6 | 81 | T18 | Actuator | Actuator fail | Actuator fail | 14:50 | 14:50 | 14:50 | 15:50 | 0 | 0 | 1 | 1 | 1 No. Nylon brass bush replaced | Close |  |  | 0
74 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:10 | 18:31 | 12.35 | Actuator Type1 |  | 0 | IC1_Inv2 | G1 | G3 | 11 | T55 | Actuator | Actuator fail | Actuator fail | 15:10 | 15:10 | 15:10 | 16:20 | 0 | 0 | 1.1667 | 1.1667 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
75 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:06 | 18:07 | 12.0167 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 | 60 | T76 | Actuator | Actuator fail | Actuator fail | 10:10 | 10:10 | 10:10 | 10:40 | 0 | 0 | 0.5 | 0.5 | 1 No. Nylon brass bush replaced | Close |  |  | 0
76 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:06 | 18:07 | 12.0167 | Actuator Type1 |  | 0 | IC1_Inv3 | G5 | G4 | 34 | T97 | Actuator | Actuator fail | Actuator fail | 15:40 | 15:40 | 15:40 | 16:25 | 0 | 0 | 0.75 | 0.75 | 1 No. Nylon brass bush replaced | Close |  |  | 0
77 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:02 | 18:28 | 12.4333 | Actuator Type1 |  | 0 | IC1_Inv4 | G3 | G5 | 73 | T137 | Actuator | Actuator fail | Actuator fail | 8:20 | 8:20 | 8:20 | 9:35 | 0 | 0 | 1.25 | 1.25 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
78 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 6:02 | 18:28 | 12.4333 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 50 | T30 | Actuator | Actuator fail | Actuator fail | 10:10 | 10:10 | 10:10 | 11:20 | 0 | 0 | 1.1667 | 1.1667 | 1 No Medium Gear Replaced | Close |  |  | 0
79 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 5:58 | 18:35 | 12.6167 | Battery Type_1 |  | 0 | IC1_Inv3 | G3 | G5 | 65 | T97 TO T101 | Battery | Battery Fail | Battery Fail | 9:20 | 9:20 | 9:20 | 12:20 | 0 | 0 | 3 | 3 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
80 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 6:00 | 18:35 | 12.5833 | Actuator Type1 |  | 0 | IC1_Inv2 | G3 | G5 | 56 | T59 | Actuator | Actuator fail | Actuator fail | 8:20 | 8:20 | 8:20 | 10:30 | 0 | 0 | 2.1667 | 2.1667 | 1 No. Nylon brass bush replaced | Close |  |  | 0
81 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 6:00 | 18:35 | 12.5833 | Battery Type_1 |  | 0 | IC1_Inv4 | G5 | G4 | 40 | T122 TO T126 | Battery | Battery Fail | Battery Fail | 12:10 | 12:10 | 12:10 | 13:20 | 0 | 0 | 1.1667 | 1.1667 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
82 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 6:00 | 18:35 | 12.5833 | Battery Type_1 |  | 0 | IC1_Inv2 | G3 | G5 | 54 | T46 TO T50 | Battery | Battery Fail | Battery Fail | 12:45 | 12:45 | 12:45 | 13:40 | 0 | 0 | 0.91667 | 0.91667 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
83 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:38 | 12.6167 | Battery Type_1 |  | 0 | IC1_Inv4 | G3 | G5 | 71 | T126 TO T130 | Battery | Battery Fail | Battery Fail | 9:30 | 9:30 | 9:30 | 10:40 | 0 | 0 | 1.1667 | 1.1667 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
84 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:38 | 12.6167 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 4 | T20 | Actuator | Actuator fail | Actuator fail | 16:20 | 16:20 | 16:20 | 17:10 | 0 | 0 | 0.83333 | 0.83333 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
85 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 6:01 | 18:41 | 12.6667 | Battery Type_1 |  | 0 | IC1_Inv1 | G1 | G3 | 12 | T56 TO T60 | Battery | Battery Fail | Battery Fail | 11:00 | 11:00 | 11:00 | 11:35 | 0 | 0 | 0.58333 | 0.58333 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
86 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 6:01 | 18:41 | 12.6667 | Actuator Type1 |  | 0 | IC1_Inv1 | G1 | G3 | 6 | T30 | Actuator | Actuator fail | Actuator fail | 12:20 | 12:20 | 12:20 | 12:50 | 0 | 0 | 0.5 | 0.5 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
87 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:01 | 17:12 | 11.1833 | Actuator Type1 |  | 0 | IC2_Inv1 | G5 | G4 | 15 | T5 | Actuator | Actuator fail | Actuator fail | 8:10 | 8:10 | 8:10 | 9:25 | 0 | 0 | 1.25 | 1.25 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
88 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 5:59 | 18:40 | 12.6833 | Battery Type_1 |  | 0 | IC2_Inv2 | G3 | G5 | 46 | T6 TO T10 | Battery | Battery Fail | Battery Fail | 9:30 | 9:30 | 9:30 | 10:35 | 0 | 0 | 1.0833 | 1.0833 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
89 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 6:06 | 17:55 | 11.8167 | Battery Type_1 |  | 0 | IC1_Inv2 | G3 | G5 | 55 | T51 TO T55 | Battery | Battery Fail | Battery Fail | 11:10 | 11:10 | 11:10 | 12:10 | 0 | 0 | 1 | 1 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
90 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:01 | 17:50 | 11.8167 | Actuator Type1 |  | 0 | IC2_Inv1 | G5 | G4 | 18 | T16 | Actuator | Actuator fail | Actuator fail | 10:10 | 10:10 | 10:10 | 11:25 | 0 | 0 | 1.25 | 1.25 | 1 No Medium Gear Replaced | Close |  |  | 0
91 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:01 | 17:50 | 11.8167 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 | 66 | T106 | Actuator | Actuator fail | Actuator fail | 12:20 | 12:20 | 12:20 | 13:25 | 0 | 0 | 1.0833 | 1.0833 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
92 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 6:11 | 18:40 | 12.4833 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G2 | 54 | T31 | Actuator | Actuator fail | Actuator fail | 8:00 | 8:00 | 8:00 | 8:50 | 0 | 0 | 0.83333 | 0.83333 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
93 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 6:11 | 18:40 | 12.4833 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G1 | 35 | T2 | Actuator | Actuator fail | Actuator fail | 9:35 | 9:35 | 9:35 | 10:50 | 0 | 0 | 1.25 | 1.25 | 1 No Actuator Motor | Close |  |  | 0
94 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 6:11 | 18:40 | 12.4833 | Actuator Type1 |  | 0 | IC1_Inv3 | G1 | G3 | 21 | T42 | Actuator | Actuator fail | Actuator fail | 15:30 | 15:30 | 15:30 | 16:45 | 0 | 0 | 1.25 | 1.25 | Actuator 2 No Limit Switch was replaced | Close |  |  | 0
95 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 6:06 | 18:38 | 12.5333 | Battery Type_1 |  | 0 | IC2_Inv1 | G7 | G2 | 102 | T31 TO T35 | Battery | Battery Fail | Battery Fail | 15:20 | 15:20 | 15:20 | 16:05 | 0 | 0 | 0.75 | 0.75 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
96 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 6:06 | 18:38 | 12.5333 | Battery Type_1 |  | 0 | IC2_Inv1 | G7 | G1 | 113 | T46 TO T49 | Battery | Battery Fail | Battery Fail | 16:10 | 16:10 | 16:10 | 16:45 | 0 | 0 | 0.58333 | 0.58333 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
97 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 6:06 | 18:41 | 12.5833 | Battery Type_1 |  | 0 | IC1_Inv1 | G1 | G3 | 8 | T36 to T40 | Battery | Battery Fail | Battery Fail | 15:20 | 15:20 | 15:20 | 16:30 | 0 | 0 | 1.1667 | 1.1667 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
98 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 6:09 | 18:44 | 12.5833 | Actuator Type1 |  | 0 | IC1_Inv3 | G3 | G5 | 66 | T106 | Actuator | Actuator fail | Actuator fail | 11:20 | 11:20 | 11:20 | 12:25 | 0 | 0 | 1.0833 | 1.0833 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
99 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:10 | 18:40 | 12.5 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 21 | T32 | Actuator | Actuator fail | Actuator fail | 10:10 | 10:10 | 10:10 | 11:00 | 0 | 0 | 0.83333 | 0.83333 | 1 No Medium Gear Replaced | Close |  |  | 0
100 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:10 | 18:40 | 12.5 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 25 | T51 | Actuator | Actuator fail | Actuator fail | 10:30 | 10:30 | 10:30 | 11:25 | 0 | 0 | 0.91667 | 0.91667 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
101 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 6:10 | 18:40 | 12.5 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 25 | T52 | Actuator | Actuator fail | Actuator fail | 11:10 | 11:10 | 11:10 | 12:10 | 0 | 0 | 1 | 1 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
102 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 6:07 | 18:47 | 12.6667 | Actuator Type1 |  | 0 | IC1_Inv2 | G4 | G6 | 87 | T51 | Actuator | Actuator fail | Actuator fail | 12:10 | 12:10 | 12:10 | 12:45 | 0 | 0 | 0.58333 | 0.58333 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
103 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 6:09 | 18:43 | 12.5667 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 51 | T32 | Actuator | Actuator fail | Actuator fail | 10:00 | 10:00 | 10:00 | 11:10 | 0 | 0 | 1.1667 | 1.1667 | 1 No Medium Gear Replaced | Close |  |  | 0
104 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 6:09 | 18:43 | 12.5667 | Actuator Type1 |  | 0 | IC1_Inv1 | G5 | G4 | 21 | T32 | Actuator | Actuator fail | Actuator fail | 10:30 | 10:30 | 10:30 | 11:25 | 0 | 0 | 0.91667 | 0.91667 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
105 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 6:09 | 18:43 | 12.5667 | Battery Type_1 |  | 0 | IC1_Inv4 | G3 | G5 | 74 | T146 TO T150 | Battery | Battery Fail | Battery Fail | 12:00 | 12:00 | 12:00 | 12:35 | 0 | 0 | 0.58333 | 0.58333 | 1 no 25.6v 24Ah Li-ion Battery Replaced | Close |  |  | 0
106 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 6:11 | 18:47 | 12.6 | Actuator Type1 |  | 0 | IC2_Inv2 | G3 | G5 | 54 | T47 | Actuator | Actuator fail | Actuator fail | 11:10 | 11:10 | 11:10 | 12:25 | 0 | 0 | 1.25 | 1.25 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
107 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 6:09 | 18:43 | 12.5667 | Actuator Type1 |  | 0 | IC1_Inv2 | G1 | G3 | 10 | T50 | Actuator | Actuator fail | Actuator fail | 13:10 | 13:10 | 13:10 | 14:30 | 0 | 0 | 1.3333 | 1.3333 | Actuator motor 2 no.s Carbon brushes | Close |  |  | 0
108 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:07 | 18:45 | 12.6333 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G1 | 3 | T15 | Actuator | Actuator fail | Actuator fail | 13:10 | 13:10 | 13:10 | 14:30 | 0 | 0 | 1.3333 | 1.3333 | 2 Nos Actuator Bearing Replaced | Close |  |  | 0
109 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 6:07 | 18:45 | 12.6333 | Actuator Type1 |  | 0 | IC2_Inv1 | G7 | G2 | 11 | T37 | Actuator | Actuator fail | Actuator fail | 15:32 | 0.64722 | 0.64722 | 16:12 | 0 | 0 | 0.66667 | 0.66667 | 1 No Medium Gear Replaced | Close |  |  | 0
Formulas:
Days = DAY(EOMONTH(Tracker_BD[[#This Row],[Month Year]],0))

## Plant BD
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affceted Equipment | DC Capacity Affceted (kW) | Plant Equivalent Weightage | Affected Equipmenet Location | Fault Catrgory | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgemnet Time | Work Start time on Fault | Work Completiuon time on fualt | Acknowdlegemnet time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost POA | Approxuimate Energy Loss (KWh) | PTW No. | Job Card No.
1 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 6:28 | 18:29 | 12.0167 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.55903 | 0.55903 | 0.55903 | 0.57083 | 0 | 0 | 0.28333 | 0.28333 | Physically checked & resetted | Close | 0.045017 | 0.26 | 315
2 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 6:23 | 18:14 | 11.85 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.46875 | 0.46875 | 0.46875 | 0.47431 | 0 | 0 | 0.13333 | 0.13333 | Physically checked & resetted | Close | 0.021185 | 0.1152 | 130
3 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 6:31 | 18:14 | 11.7167 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.50556 | 0.50556 | 0.50556 | 0.61806 | 0 | 0 | 2.7 | 2.7 | Half Load running due to inverter su 2 side bu current difference | Close | 0.45883 | 2.15 | 3350
4 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 6:21 | 18:23 | 12.0333 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.36875 | 0.36875 | 0.36875 | 0.46042 | 0 | 0 | 2.2 | 2.2 | Half Load running due to inverter su 2 side bu current difference 2000A Fuse blown replaced | Close | 0.37386 | 2.05 | 2435
5 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 6:30 | 18:26 | 11.9333 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.39236 | 0.39236 | 0.39236 | 0.43264 | 0 | 0 | 0.96667 | 0.96667 | Half Load running due to inverter su 2 side bu current difference | Close | 0.16427 | 3.02 | 4235
6 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 6:21 | 18:26 | 12.0833 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.36736 | 0.36736 | 0.36736 | 0.46528 | 0 | 0 | 2.35 | 2.35 | LCL Filter Replaced | Close | 0.39935 | 2.1 | 2550
7 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 6:18 | 18:15 | 11.95 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.54306 | 0.54306 | 0.54306 | 0.55208 | 0 | 0 | 0.21667 | 0.21667 | Physically checked & resetted | Close | 0.03682 | 0.2 | 238.1101
8 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 6:20 | 18:13 | 11.8833 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.6125 | 0.6125 | 0.6125 | 0.63194 | 0 | 0 | 0.46667 | 0.46667 | Physically checked & resetted | Close | 0.074146 | 0.41 | 499.5317
9 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 6:21 | 18:21 | 12 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.40486 | 0.40486 | 0.40486 | 0.40972 | 0 | 0 | 0.11667 | 0.11667 | Physically checked & resetted | Close | 0.018537 | 0.1 | 124
10 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 6:20 | 18:27 | 12.1167 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.44167 | 0.44167 | 0.44167 | 0.44792 | 0 | 0 | 0.15 | 0.15 | Physically checked & resetted | Close | 0.023833 | 0.08 | 97
11 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 6:22 | 18:21 | 11.9833 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.37639 | 0.37639 | 0.37639 | 0.76528 | 0 | 0 | 9.3333 | 9.3333 | Half Load running due to inverter su 2 side bu current difference | Close | 1.5861 | 8 | 4870.56
12 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 6:20 | 18:20 | 12 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.37361 | 0.37361 | 0.37361 | 0.3875 | 0 | 0 | 0.33333 | 0.33333 | Physically checked & resetted | Close | 0.052962 | 0.2 | 200
13 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 6:19 | 18:24 | 12.0833 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.44792 | 0.44792 | 0.44792 | 0.63333 | 0 | 0 | 4.45 | 4.45 | 2000A Fuse and AC Contactor CL18 Connector Replaced | Close | 0.75622 | 5.34 | 3251.0988
14 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 6:09 | 18:24 | 12.25 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.41181 | 0.41181 | 0.41181 | 0.41875 | 0 | 0 | 0.16667 | 0.16667 | Physically checked & resetted | Close | 0.026481 | 0.16 | 190
15 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 6:05 | 18:33 | 12.4667 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.38542 | 0.38542 | 0.38542 | 0.40417 | 0 | 0 | 0.45 | 0.45 | Physically checked & resetted | Close | 0.071498 | 0.35 | 435
16 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 6:02 | 18:17 | 12.25 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.49653 | 0.49653 | 0.49653 | 0.50139 | 0 | 0 | 0.11667 | 0.11667 | Physically checked & resetted | Close | 0.018537 | 0.1324 | 158
17 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 6:03 | 18:32 | 12.4833 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.53056 | 0.53056 | 0.53056 | 0.5375 | 0 | 0 | 0.16667 | 0.16667 | Physically checked & resetted | Close | 0.026481 | 0.123 | 146
18 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:05 | 18:31 | 12.4333 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.53542 | 0.53542 | 0.53542 | 0.54444 | 0 | 0 | 0.21667 | 0.21667 | Physically checked & resetted | Close | 0.034425 | 0.070417 | 85.7936
19 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 6:05 | 18:31 | 12.4333 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.59861 | 0.59861 | 0.59861 | 0.60486 | 0 | 0 | 0.15 | 0.15 | Physically checked & resetted | Close | 0.023833 | 0.09 | 109.6533
20 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 6:13 | 18:33 | 12.3333 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.48819 | 0.48819 | 0.48819 | 0.51736 | 0 | 0 | 0.7 | 0.7 | Physically checked & resetted | Close | 0.11122 | 0.7 | 853
21 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 6:04 | 18:37 | 12.55 | IC1_Inv2 | 1833.3 | 17.45% | IC1_Inv2 | Inverter | Excess Temperature Difference | Excess Temperature Difference | 0.49792 | 0.49792 | 0.49792 | 0.50764 | 0 | 0 | 0.23333 | 0.23333 | Physically checked & resetted | Close | 0.040716 | 0.12 | 135
22 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:04 | 18:20 | 12.2667 | IC1_Inv4 | 892 | 16.99% | IC1_Inv4 | Inverter | Reduced Run | Reduced Run | 0.45347 | 0.45347 | 0.45347 | 0.76389 | 0 | 0 | 7.45 | 7.45 | AC Contactor Replaced | Close | 1.266 | 3.24 | 2300
23 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 6:12 | 18:32 | 12.3333 | IC1_Inv2 | 1833.3 | 17.45% | IC1_Inv2 | Inverter | Excess Temperature Difference | Excess Temperature Difference | 0.51944 | 0.51944 | 0.51944 | 0.52986 | 0 | 0 | 0.25 | 0.25 | Physically checked & resetted | Close | 0.043624 | 0.23 | 312
24 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 6:10 | 18:31 | 12.35 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.44583 | 0.44583 | 0.44583 | 0.45486 | 0 | 0 | 0.21667 | 0.21667 | Physically checked & resetted | Close | 0.034425 | 0.07 | 90
25 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 6:06 | 18:07 | 12.0167 | IC1_Inv2 | 1833.3 | 17.45% | IC1_Inv2 | Inverter | Excess Temperature Difference | Excess Temperature Difference | 0.49375 | 0.49375 | 0.49375 | 0.50069 | 0 | 0 | 0.16667 | 0.16667 | Physically checked & resetted | Close | 0.029083 | 0.18 | 245
26 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 6:02 | 18:35 | 12.55 | IC1_Inv2 | 1833.3 | 17.45% | IC1_Inv2 | Inverter | Excess Temperature Difference | Excess Temperature Difference | 0.47153 | 0.47153 | 0.47153 | 0.48125 | 0 | 0 | 0.23333 | 0.23333 | Physically checked & resetted | Close | 0.040716 | 0.15 | 207
27 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 6:01 | 18:38 | 12.6167 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.62569 | 0.62569 | 0.62569 | 0.63819 | 0 | 0 | 0.3 | 0.3 | Physically checked & resetted | Close | 0.047665 | 0.25 | 320
28 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 6:01 | 18:41 | 12.6667 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.36111 | 0.36111 | 0.36111 | 0.39236 | 0 | 0 | 0.75 | 0.75 | Physically checked & resetted | Close | 0.11916 | 0.58575 | 525
29 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 6:01 | 17:12 | 11.1833 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.37847 | 0.37847 | 0.37847 | 0.38542 | 0 | 0 | 0.16667 | 0.16667 | Physically checked & resetted | Close | 0.026481 | 0.11633 | 126
30 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 6:01 | 17:50 | 11.8167 | IC1_Inv1 | 1669.29 | 15.89% | IC1_Inv1 | Inverter | BU Current difference | BU Current difference | 0.54792 | 0.54792 | 0.54792 | 0.55486 | 0 | 0 | 0.16667 | 0.16667 | Physically checked & resetted | Close | 0.026481 | 0.14 | 167.3228
31 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 6:05 | 18:34 | 12.4833 | IC1_Inv2 | 1833.3 | 17.45% | IC1_Inv2 | Inverter | Excess Temperature Difference | Excess Temperature Difference | 0.54236 | 0.54236 | 0.54236 | 0.54931 | 0 | 0 | 0.16667 | 0.16667 | Physically checked & resetted | Close | 0.029083 | 0.084333 | 107.0472
32 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 6:06 | 18:41 | 12.5833 | IC1_Inv4 | 1785.42 | 16.99% | IC1_Inv4 | Inverter | BU Current difference | BU Current difference | 0.36806 | 0.36806 | 0.36806 | 0.39306 | 0 | 0 | 0.6 | 0.6 | Physically checked & resetted | Close | 0.10196 | 0.38 | 462.7369
33 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 30 | 2025-07-04 | 6:07 | 18:39 | 12.5333 | IC1_Inv2 | 1833.3 | 17.45% | IC1_Inv2 | Inverter | Excess Temperature Difference | Excess Temperature Difference | 0.48403 | 0.48403 | 0.48403 | 0.49306 | 0 | 0 | 0.21667 | 0.21667 | Physically checked & resetted | Close | 0.037807 | 0.11 | 147
34 | [21 empty] | 0 | 0 | 0 | 0
35 | [21 empty] | 0 | 0 | 0 | 0
36 | [21 empty] | 0 | 0 | 0 | 0
37 | [21 empty] | 0 | 0 | 0 | 0
38 | [21 empty] | 0 | 0 | 0 | 0
39 | [21 empty] | 0 | 0 | 0 | 0
40 | [21 empty] | 0 | 0 | 0 | 0
41 | [21 empty] | 0 | 0 | 0 | 0
42 | [21 empty] | 0 | 0 | 0 | 0
43 | [21 empty] | 0 | 0 | 0 | 0
44 | [21 empty] | 0 | 0 | 0 | 0
45 | [21 empty] | 0 | 0 | 0 | 0
46 | [21 empty] | 0 | 0 | 0 | 0
47 | [21 empty] | 0 | 0 | 0 | 0
48 | [21 empty] | 0 | 0 | 0 | 0
49 | [21 empty] | 0 | 0 | 0 | 0
50 | [21 empty] | 0 | 0 | 0 | 0
51 | [21 empty] | 0 | 0 | 0 | 0
52 | [21 empty] | 0 | 0 | 0 | 0
53 | [21 empty] | 0 | 0 | 0 | 0
54 | [21 empty] | 0 | 0 | 0 | 0
55 | [21 empty] | 0 | 0 | 0 | 0
56 | [21 empty] | 0 | 0 | 0 | 0
57 | [21 empty] | 0 | 0 | 0 | 0
58 | [21 empty] | 0 | 0 | 0 | 0
59 | [21 empty] | 0 | 0 | 0 | 0
60 | [21 empty] | 0 | 0 | 0 | 0
61 | [21 empty] | 0 | 0 | 0 | 0
62 | [21 empty] | 0 | 0 | 0 | 0
63 | [21 empty] | 0 | 0 | 0 | 0
64 | [21 empty] | 0 | 0 | 0 | 0
65 | [21 empty] | 0 | 0 | 0 | 0
66 | [21 empty] | 0 | 0 | 0 | 0
67 | [21 empty] | 0 | 0 | 0 | 0
68 | [21 empty] | 0 | 0 | 0 | 0
69 | [21 empty] | 0 | 0 | 0 | 0
70 | [21 empty] | 0 | 0 | 0 | 0
71 | [21 empty] | 0 | 0 | 0 | 0
72 | [21 empty] | 0 | 0 | 0 | 0
73 | [21 empty] | 0 | 0 | 0 | 0
74 | [21 empty] | 0 | 0 | 0 | 0
75 | [21 empty] | 0 | 0 | 0 | 0
76 | [21 empty] | 0 | 0 | 0 | 0
77 | [21 empty] | 0 | 0 | 0 | 0
78 | [21 empty] | 0 | 0 | 0 | 0
79 | [21 empty] | 0 | 0 | 0 | 0
80 | [21 empty] | 0 | 0 | 0 | 0
81 | [21 empty] | 0 | 0 | 0 | 0
82 | [21 empty] | 0 | 0 | 0 | 0
83 | [21 empty] | 0 | 0 | 0 | 0
84 | [21 empty] | 0 | 0 | 0 | 0
85 | [21 empty] | 0 | 0 | 0 | 0
86 | [21 empty] | 0 | 0 | 0 | 0
87 | [21 empty] | 0 | 0 | 0 | 0
88 | [21 empty] | 0 | 0 | 0 | 0
89 | [21 empty] | 0 | 0 | 0 | 0
90 | [21 empty] | 0 | 0 | 0 | 0
91 | [21 empty] | 0 | 0 | 0 | 0
92 | [21 empty] | 0 | 0 | 0 | 0
93 | [21 empty] | 0 | 0 | 0 | 0
94 | [21 empty] | 0 | 0 | 0 | 0
95 | [21 empty] | 0 | 0 | 0 | 0
96 | [21 empty] | 0 | 0 | 0 | 0
97 | [21 empty] | 0 | 0 | 0 | 0
98 | [21 empty] | 0 | 0 | 0 | 0
99 | [21 empty] | 0 | 0 | 0 | 0
100 | [21 empty] | 0 | 0 | 0 | 0
101 | [21 empty] | 0 | 0 | 0 | 0
102 | [21 empty] | 0 | 0 | 0 | 0
103 | [21 empty] | 0 | 0 | 0 | 0
104 | [21 empty] | 0 | 0 | 0 | 0
105 | [21 empty] | 0 | 0 | 0 | 0
106 | [21 empty] | 0 | 0 | 0 | 0
107 | [21 empty] | 0 | 0 | 0 | 0
108 | [21 empty] | 0 | 0 | 0 | 0
109 | [21 empty] | 0 | 0 | 0 | 0
110 | [21 empty] | 0 | 0 | 0 | 0
111 | [21 empty] | 0 | 0 | 0 | 0
112 | [21 empty] | 0 | 0 | 0 | 0
113 | [21 empty] | 0 | 0 | 0 | 0
114 | [21 empty] | 0 | 0 | 0 | 0
115 | [21 empty] | 0 | 0 | 0 | 0
116 | [21 empty] | 0 | 0 | 0 | 0
117 | [21 empty] | 0 | 0 | 0 | 0
118 | [21 empty] | 0 | 0 | 0 | 0
119 | [21 empty] | 0 | 0 | 0 | 0
120 | [21 empty] | 0 | 0 | 0 | 0
121 | [21 empty] | 0 | 0 | 0 | 0
122 | [21 empty] | 0 | 0 | 0 | 0
123 | [21 empty] | 0 | 0 | 0 | 0
124 | [21 empty] | 0 | 0 | 0 | 0
125 | [21 empty] | 0 | 0 | 0 | 0
126 | [21 empty] | 0 | 0 | 0 | 0
127 | [21 empty] | 0 | 0 | 0 | 0
128 | [21 empty] | 0 | 0 | 0 | 0
129 | [21 empty] | 0 | 0 | 0 | 0
130 | [21 empty] | 0 | 0 | 0 | 0
131 | [21 empty] | 0 | 0 | 0 | 0
132 | [21 empty] | 0 | 0 | 0 | 0
133 | [21 empty] | 0 | 0 | 0 | 0
134 | [21 empty] | 0 | 0 | 0 | 0
135 | [21 empty] | 0 | 0 | 0 | 0
136 | [21 empty] | 0 | 0 | 0 | 0
137 | [21 empty] | 0 | 0 | 0 | 0
138 | [21 empty] | 0 | 0 | 0 | 0
139 | [21 empty] | 0 | 0 | 0 | 0
140 | [21 empty] | 0 | 0 | 0 | 0
141 | [21 empty] | 0 | 0 | 0 | 0
142 | [21 empty] | 0 | 0 | 0 | 0
143 | [21 empty] | 0 | 0 | 0 | 0
144 | [21 empty] | 0 | 0 | 0 | 0
145 | [21 empty] | 0 | 0 | 0 | 0
146 | [21 empty] | 0 | 0 | 0 | 0
147 | [21 empty] | 0 | 0 | 0 | 0
148 | [21 empty] | 0 | 0 | 0 | 0
149 | [21 empty] | 0 | 0 | 0 | 0
150 | [21 empty] | 0 | 0 | 0 | 0
151 | [21 empty] | 0 | 0 | 0 | 0
152 | [21 empty] | 0 | 0 | 0 | 0
153 | [21 empty] | 0 | 0 | 0 | 0
154 | [21 empty] | 0 | 0 | 0 | 0
155 | [21 empty] | 0 | 0 | 0 | 0
156 | [21 empty] | 0 | 0 | 0 | 0
157 | [21 empty] | 0 | 0 | 0 | 0
158 | [21 empty] | 0 | 0 | 0 | 0
159 | [21 empty] | 0 | 0 | 0 | 0
160 | [21 empty] | 0 | 0 | 0 | 0
161 | [21 empty] | 0 | 0 | 0 | 0
162 | [21 empty] | 0 | 0 | 0 | 0
163 | [21 empty] | 0 | 0 | 0 | 0
164 | [21 empty] | 0 | 0 | 0 | 0
165 | [21 empty] | 0 | 0 | 0 | 0
166 | [21 empty] | 0 | 0 | 0 | 0
167 | [21 empty] | 0 | 0 | 0 | 0
168 | [21 empty] | 0 | 0 | 0 | 0
169 | [21 empty] | 0 | 0 | 0 | 0
170 | [21 empty] | 0 | 0 | 0 | 0
171 | [21 empty] | 0 | 0 | 0 | 0
172 | [21 empty] | 0 | 0 | 0 | 0
173 | [21 empty] | 0 | 0 | 0 | 0
174 | [21 empty] | 0 | 0 | 0 | 0
175 | [21 empty] | 0 | 0 | 0 | 0
176 | [21 empty] | 0 | 0 | 0 | 0
177 | [21 empty] | 0 | 0 | 0 | 0
178 | [21 empty] | 0 | 0 | 0 | 0
179 | [21 empty] | 0 | 0 | 0 | 0
180 | [21 empty] | 0 | 0 | 0 | 0
181 | [21 empty] | 0 | 0 | 0 | 0
182 | [21 empty] | 0 | 0 | 0 | 0
183 | [21 empty] | 0 | 0 | 0 | 0
184 | [21 empty] | 0 | 0 | 0 | 0
185 | [21 empty] | 0 | 0 | 0 | 0
186 | [21 empty] | 0 | 0 | 0 | 0
187 | [21 empty] | 0 | 0 | 0 | 0
188 | [21 empty] | 0 | 0 | 0 | 0
189 | [21 empty] | 0 | 0 | 0 | 0
190 | [21 empty] | 0 | 0 | 0 | 0
191 | [21 empty] | 0 | 0 | 0 | 0
192 | [21 empty] | 0 | 0 | 0 | 0
193 | [21 empty] | 0 | 0 | 0 | 0
194 | [21 empty] | 0 | 0 | 0 | 0
195 | [21 empty] | 0 | 0 | 0 | 0
196 | [21 empty] | 0 | 0 | 0 | 0
197 | [21 empty] | 0 | 0 | 0 | 0
198 | [21 empty] | 0 | 0 | 0 | 0
199 | [21 empty] | 0 | 0 | 0 | 0
200 | [21 empty] | 0 | 0 | 0 | 0
201 | [21 empty] | 0 | 0 | 0 | 0
202 | [21 empty] | 0 | 0 | 0 | 0
203 | [21 empty] | 0 | 0 | 0 | 0
204 | [21 empty] | 0 | 0 | 0 | 0
205 | [21 empty] | 0 | 0 | 0 | 0
206 | [21 empty] | 0 | 0 | 0 | 0
207 | [21 empty] | 0 | 0 | 0 | 0
208 | [21 empty] | 0 | 0 | 0 | 0
209 | [21 empty] | 0 | 0 | 0 | 0
210 | [21 empty] | 0 | 0 | 0 | 0
211 | [21 empty] | 0 | 0 | 0 | 0
212 | [21 empty] | 0 | 0 | 0 | 0
213 | [21 empty] | 0 | 0 | 0 | 0
214 | [21 empty] | 0 | 0 | 0 | 0
215 | [21 empty] | 0 | 0 | 0 | 0
216 | [21 empty] | 0 | 0 | 0 | 0
217 | [21 empty] | 0 | 0 | 0 | 0
218 | [21 empty] | 0 | 0 | 0 | 0
219 | [21 empty] | 0 | 0 | 0 | 0
220 | [21 empty] | 0 | 0 | 0 | 0
221 | [21 empty] | 0 | 0 | 0 | 0
222 | [21 empty] | 0 | 0 | 0 | 0
223 | [21 empty] | 0 | 0 | 0 | 0
224 | [21 empty] | 0 | 0 | 0 | 0
225 | [21 empty] | 0 | 0 | 0 | 0
226 | [21 empty] | 0 | 0 | 0 | 0
227 | [21 empty] | 0 | 0 | 0 | 0
228 | [21 empty] | 0 | 0 | 0 | 0
229 | [21 empty] | 0 | 0 | 0 | 0
230 | [21 empty] | 0 | 0 | 0 | 0
231 | [21 empty] | 0 | 0 | 0 | 0
232 | [21 empty] | 0 | 0 | 0 | 0
233 | [21 empty] | 0 | 0 | 0 | 0
234 | [21 empty] | 0 | 0 | 0 | 0
235 | [21 empty] | 0 | 0 | 0 | 0
236 | [21 empty] | 0 | 0 | 0 | 0
237 | [21 empty] | 0 | 0 | 0 | 0
238 | [21 empty] | 0 | 0 | 0 | 0
239 | [21 empty] | 0 | 0 | 0 | 0
240 | [21 empty] | 0 | 0 | 0 | 0
241 | [21 empty] | 0 | 0 | 0 | 0
242 | [21 empty] | 0 | 0 | 0 | 0
243 | [21 empty] | 0 | 0 | 0 | 0
244 | [21 empty] | 0 | 0 | 0 | 0
245 | [21 empty] | 0 | 0 | 0 | 0
246 | [21 empty] | 0 | 0 | 0 | 0
247 | [21 empty] | 0 | 0 | 0 | 0
248 | [21 empty] | 0 | 0 | 0 | 0
249 | [21 empty] | 0 | 0 | 0 | 0
250 | [21 empty] | 0 | 0 | 0 | 0
251 | [21 empty] | 0 | 0 | 0 | 0
252 | [21 empty] | 0 | 0 | 0 | 0
253 | [21 empty] | 0 | 0 | 0 | 0
254 | [21 empty] | 0 | 0 | 0 | 0
255 | [21 empty] | 0 | 0 | 0 | 0
256 | [21 empty] | 0 | 0 | 0 | 0
257 | [21 empty] | 0 | 0 | 0 | 0
258 | [21 empty] | 0 | 0 | 0 | 0
259 | [21 empty] | 0 | 0 | 0 | 0
260 | [21 empty] | 0 | 0 | 0 | 0
261 | [21 empty] | 0 | 0 | 0 | 0
262 | [21 empty] | 0 | 0 | 0 | 0
263 | [21 empty] | 0 | 0 | 0 | 0
264 | [21 empty] | 0 | 0 | 0 | 0
265 | [21 empty] | 0 | 0 | 0 | 0
266 | [21 empty] | 0 | 0 | 0 | 0
267 | [21 empty] | 0 | 0 | 0 | 0
268 | [21 empty] | 0 | 0 | 0 | 0
269 | [21 empty] | 0 | 0 | 0 | 0
270 | [21 empty] | 0 | 0 | 0 | 0
271 | [21 empty] | 0 | 0 | 0 | 0
272 | [21 empty] | 0 | 0 | 0 | 0
273 | [21 empty] | 0 | 0 | 0 | 0
274 | [21 empty] | 0 | 0 | 0 | 0
275 | [21 empty] | 0 | 0 | 0 | 0
276 | [21 empty] | 0 | 0 | 0 | 0
277 | [21 empty] | 0 | 0 | 0 | 0
278 | [21 empty] | 0 | 0 | 0 | 0
279 | [21 empty] | 0 | 0 | 0 | 0
280 | [21 empty] | 0 | 0 | 0 | 0
281 | [21 empty] | 0 | 0 | 0 | 0
282 | [21 empty] | 0 | 0 | 0 | 0
283 | [21 empty] | 0 | 0 | 0 | 0
284 | [21 empty] | 0 | 0 | 0 | 0
285 | [21 empty] | 0 | 0 | 0 | 0
286 | [21 empty] | 0 | 0 | 0 | 0
287 | [21 empty] | 0 | 0 | 0 | 0
288 | [21 empty] | 0 | 0 | 0 | 0
289 | [21 empty] | 0 | 0 | 0 | 0
290 | [21 empty] | 0 | 0 | 0 | 0
291 | [21 empty] | 0 | 0 | 0 | 0
292 | [21 empty] | 0 | 0 | 0 | 0
293 | [21 empty] | 0 | 0 | 0 | 0
294 | [21 empty] | 0 | 0 | 0 | 0
295 | [21 empty] | 0 | 0 | 0 | 0
296 | [21 empty] | 0 | 0 | 0 | 0
297 | [21 empty] | 0 | 0 | 0 | 0
298 | [21 empty] | 0 | 0 | 0 | 0
299 | [21 empty] | 0 | 0 | 0 | 0
300 | [21 empty] | 0 | 0 | 0 | 0
301 | [21 empty] | 0 | 0 | 0 | 0
302 | [21 empty] | 0 | 0 | 0 | 0
303 | [21 empty] | 0 | 0 | 0 | 0
304 | [21 empty] | 0 | 0 | 0 | 0
305 | [21 empty] | 0 | 0 | 0 | 0
306 | [21 empty] | 0 | 0 | 0 | 0
307 | [21 empty] | 0 | 0 | 0 | 0
308 | [21 empty] | 0 | 0 | 0 | 0
309 | [21 empty] | 0 | 0 | 0 | 0
310 | [21 empty] | 0 | 0 | 0 | 0
311 | [21 empty] | 0 | 0 | 0 | 0
312 | [21 empty] | 0 | 0 | 0 | 0
313 | [21 empty] | 0 | 0 | 0 | 0
314 | [21 empty] | 0 | 0 | 0 | 0
315 | [21 empty] | 0 | 0 | 0 | 0
316 | [21 empty] | 0 | 0 | 0 | 0
317 | [21 empty] | 0 | 0 | 0 | 0
318 | [21 empty] | 0 | 0 | 0 | 0
319 | [21 empty] | 0 | 0 | 0 | 0
320 | [21 empty] | 0 | 0 | 0 | 0
321 | [21 empty] | 0 | 0 | 0 | 0
322 | [21 empty] | 0 | 0 | 0 | 0
323 | [21 empty] | 0 | 0 | 0 | 0
324 | [21 empty] | 0 | 0 | 0 | 0
325 | [21 empty] | 0 | 0 | 0 | 0
326 | [21 empty] | 0 | 0 | 0 | 0
327 | [21 empty] | 0 | 0 | 0 | 0
328 | [21 empty] | 0 | 0 | 0 | 0
329 | [21 empty] | 0 | 0 | 0 | 0
330 | [21 empty] | 0 | 0 | 0 | 0
331 | [21 empty] | 0 | 0 | 0 | 0
332 | [21 empty] | 0 | 0 | 0 | 0
333 | [21 empty] | 0 | 0 | 0 | 0
334 | [21 empty] | 0 | 0 | 0 | 0
335 | [21 empty] | 0 | 0 | 0 | 0
336 | [21 empty] | 0 | 0 | 0 | 0
337 | [21 empty] | 0 | 0 | 0 | 0
338 | [21 empty] | 0 | 0 | 0 | 0
339 | [21 empty] | 0 | 0 | 0 | 0
340 | [21 empty] | 0 | 0 | 0 | 0
341 | [21 empty] | 0 | 0 | 0 | 0
342 | [21 empty] | 0 | 0 | 0 | 0
343 | [21 empty] | 0 | 0 | 0 | 0
344 | [21 empty] | 0 | 0 | 0 | 0
345 | [21 empty] | 0 | 0 | 0 | 0
346 | [21 empty] | 0 | 0 | 0 | 0
347 | [21 empty] | 0 | 0 | 0 | 0
348 | [21 empty] | 0 | 0 | 0 | 0
349 | [21 empty] | 0 | 0 | 0 | 0
350 | [21 empty] | 0 | 0 | 0 | 0
351 | [21 empty] | 0 | 0 | 0 | 0
352 | [21 empty] | 0 | 0 | 0 | 0
353 | [21 empty] | 0 | 0 | 0 | 0
354 | [21 empty] | 0 | 0 | 0 | 0
355 | [21 empty] | 0 | 0 | 0 | 0
356 | [21 empty] | 0 | 0 | 0 | 0
357 | [21 empty] | 0 | 0 | 0 | 0
358 | [21 empty] | 0 | 0 | 0 | 0
359 | [21 empty] | 0 | 0 | 0 | 0
360 | [21 empty] | 0 | 0 | 0 | 0
361 | [21 empty] | 0 | 0 | 0 | 0
362 | [21 empty] | 0 | 0 | 0 | 0
363 | [21 empty] | 0 | 0 | 0 | 0
364 | [21 empty] | 0 | 0 | 0 | 0
365 | [21 empty] | 0 | 0 | 0 | 0
366 | [21 empty] | 0 | 0 | 0 | 0
367 | [21 empty] | 0 | 0 | 0 | 0
368 | [21 empty] | 0 | 0 | 0 | 0
369 | [21 empty] | 0 | 0 | 0 | 0
370 | [21 empty] | 0 | 0 | 0 | 0
371 | [21 empty] | 0 | 0 | 0 | 0
372 | [21 empty] | 0 | 0 | 0 | 0
373 | [21 empty] | 0 | 0 | 0 | 0
374 | [21 empty] | 0 | 0 | 0 | 0
375 | [21 empty] | 0 | 0 | 0 | 0
376 | [21 empty] | 0 | 0 | 0 | 0
377 | [21 empty] | 0 | 0 | 0 | 0
378 | [21 empty] | 0 | 0 | 0 | 0
379 | [21 empty] | 0 | 0 | 0 | 0
380 | [21 empty] | 0 | 0 | 0 | 0
381 | [21 empty] | 0 | 0 | 0 | 0
382 | [21 empty] | 0 | 0 | 0 | 0
383 | [21 empty] | 0 | 0 | 0 | 0
384 | [21 empty] | 0 | 0 | 0 | 0
385 | [21 empty] | 0 | 0 | 0 | 0
386 | [21 empty] | 0 | 0 | 0 | 0
387 | [21 empty] | 0 | 0 | 0 | 0
388 | [21 empty] | 0 | 0 | 0 | 0
389 | [21 empty] | 0 | 0 | 0 | 0
390 | [21 empty] | 0 | 0 | 0 | 0
391 | [21 empty] | 0 | 0 | 0 | 0
392 | [21 empty] | 0 | 0 | 0 | 0
393 | [21 empty] | 0 | 0 | 0 | 0
394 | [21 empty] | 0 | 0 | 0 | 0
395 | [21 empty] | 0 | 0 | 0 | 0
396 | [21 empty] | 0 | 0 | 0 | 0
397 | [21 empty] | 0 | 0 | 0 | 0
398 | [21 empty] | 0 | 0 | 0 | 0
399 | [21 empty] | 0 | 0 | 0 | 0

## Grid BD
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affceted Equipment | DC Capacity Affceted (kW) | Affected Equipmenet Location | Fault Catrgory | Plant Equivalent Weightage | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgemnet Time | Work Start time on Fault | Work Completiuon time on fualt | Acknowdlegemnet time | Response Time | Resolution Time | Action taken | Status | Plant Equivalent breakdown | Lost POA | Approxuimate Energy Loss (KWh)
1 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 6:10 | 18:31 | 12.35 |  | 10507 |  | Grid System | 100% |  | Grid failure due to 220 kV main supply failure | 0.25694 | 0.25694 | 0.25694 | 0.49028 | 0 | 0 | 5.6 |  |  | 5.6 | 2.9 | 2523
2 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 6:04 | 18:20 | 12.2667 |  | 10507 |  | Grid System | 100% |  | Grid failure due to 220 kV main supply failure | 0.43194 | 0.43194 | 0.43194 | 0.45486 | 0 | 0 | 0.55 |  |  | 0.55 | 0.27 | 543
3 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 6:12 | 18:32 | 12.3333 |  | 10507 |  | Grid System | 100% |  | Grid failure due to 220 kV main supply failure | 0.55278 | 0.55278 | 0.55278 | 0.57083 | 0 | 0 | 0.43333 |  |  | 0.43333 | 0.15 | 657
4 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 2025-06-05 | 6:00 | 18:35 | 12.5833 |  | 10507 |  | Grid System | 100% |  | Grid failure due to 220 kV main supply failure | 0.71042 | 0.71042 | 0.71042 | 0.77431 | 0 | 0 | 1.5333 |  |  | 1.5333 | 0.17 | 835
5 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 2025-06-10 | 5:59 | 18:40 | 12.6833 |  | 10507 |  | Grid System | 100% |  | Grid failure due to 220 kV main supply failure | 0.61042 | 0.61042 | 0.61042 | 0.66458 | 0 | 0 | 1.3 |  |  | 1.3 | 0.8177 | 2435
6 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 2025-06-22 | 6:04 | 18:41 | 12.6167 |  | 10507 |  | Grid System | 100% |  | Grid failure due to 220 kV main supply failure for Quaterly mainteance | 0.41597 | 0.41597 | 0.41597 | 0.71875 | 0 | 0 | 7.2667 |  |  | 7.2667 | 3.42 | 27123
7 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:07 | 18:39 | 12.5333 |  | 10507 |  | Grid System | 100% |  | Shut down taken from22okV KPTCL Substatio Achepalya for Tower repair work | 0.38194 | 0.38194 | 0.38194 | 0.40764 | 0 | 0 | 0.61667 |  |  | 0.61667
8 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 6:07 | 18:39 | 12.5333 |  | 10507 |  | Grid System | 100% |  | Shut down taken from22okV KPTCL Substatio Achepalya for Tower repair work | 0.69792 | 0.69792 | 0.69792 | 0.71181 | 0 | 0 | 0.33333 |  |  | 0.33333
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
204
205
206
207
208
209
210
211
212
213
214
215
216
217
218
219
220
221
222
223
224
225
226
227
228
229
230
231
232
233
234
235
236
237
238
239
240
241
242
243
244
245
246
247
248
249
250
251
252
253
254
255
256
257
258
259
260
261
262
263
264
265
266
267
268
269
270
271
272
273
274
275
276
277
278
279
280
281
282
283
284
285
286
287
288
289
290
291
292
293
294
295
296
297
298
299
300
301
302
303
304
305
306
307
308
309
310
311
312
313
314
315
316
317
318
319
320
321
322
323
324
325
326
327
328
329
330
331
332
333
334
335
336
337
338
339
340
341
342
343
344
345
346
347
348
349
350
351
352
353
354
355
356
357
358
359
360
361
362
363
364
365
366
367
368
369
370
371
372
373
374
375
376
377
378
379
380
381
382
383
384
385
386
387
388
389
390
391
392
393
394
395
396
397
398
399
400
401
402
403
404
405
406
407
408
409
410
411
412
413
414
415
416
417
418
419
420
421
422
423
424
425
426
427
428
429
430
431
432
433
434
435
436
437
438
439
440
441
442
443
444
445
446
447
448
449
450
451
452
453
454
455
456
457
458
459
460
461
462
463
464
465
466
467
468
469
470
471
472
473
474
475
476
477
478
479
480
481
482
483
484
485
486
487
488
489
490
491
492
493
494
495
496
497
498
499
500
501
502
503
504
505
506
507
508
509
510
511
512
513
514
515
516
517
518
519
520
521
522
523
524
525
526
527
528
529
530
531
532
533
534
535
536
537
538
539
540
541
542
543
544
545
546
547
548
549
550
551
552
553
554
555
556
557
558
559
560
561
562
563
564
565
566
567
568
569
570
571
572
573
574
575
576
577
578
579
580
581
582
583
584
585
586
587
588
589
590
591
592
593
594
595
596
597
598
599
600
601
602
603
604
605
606
607
608
609
610
611
612
613
614
615
616
617
618
619
620
621
622
623
624
625
626
627
628
629
630
631
632
633
634
635
636
637
638
639
640
641
642
643
644
645
646
647
648
649
650
651
652
653
654
655
656
657
658
659
660
661
662
663
664
665
666
667
668
669
670
671
672
673
674
675
676
677
678
679
680
681
682
683
684
685
686
687
688
689
690
691
692
693
694
695
696
697
698
699
700
701
702
703
704
705
706
707
708
709
710
711
712
713
714
715
716
717
718
719
720
721
722
723
724
725
726
727
728
729
730
731
732
733
734
735
736
737
738
739
740
741
742
743
744
745
746
747
748
749
750
751
752
753
754
755
756
757
758
759
760
761
762
763
764
765
766
767
768
769
770
771
772
773
774
775
776
777
778
779
780
781
782
783
784
785
786
787
788
789
790
791
792
793
794
795
796
797
798
799
800
801
802
803
804
805
806
807
808
809
810
811
812
813
814
815
816
817
818
819
820
821
822
823
824
825
826
827
828
829
830
831
832
833
834
835
836
837
838
839
840
841
842
843
844
845
846
847
848
849
850
851
852
853
854
855
856
857
858
859
860
861
862
863
864
865
866
867
868
869
870
871
872
873
874
875
876
877
878
879
880
881
882
883
884
885
886
887
888
889
890
891
892
893
894
Formulas:
Acknowdlegemnet time = (GA[[#This Row],[Acknowledgemnet Time ]]-GA[[#This Row],[Fault Time]])*24

## Mod_CL
sl no | FY | Calendar Year | Year | year2 | Month Year | Days | Date | Cycle Number | Resources | IC1_Inv1_MC | IC1_Inv2_MC | IC1_Inv3_MC | IC1_Inv4_MC | IC2_Inv1_MC | IC2_Inv2_MC | Total Module cleaned | Morning Start Time | Morning End Time | Evening Start Time | Evening End time | Brush/MOP Replcemnet | Water Test Report | Remarks for the day
1 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-01 | [8 empty] | 0
2 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-02 | [8 empty] | 0
3 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-03 | [8 empty] | 0
4 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-04 | [8 empty] | 0
5 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-05 | [8 empty] | 0
6 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-06 | [8 empty] | 0
7 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-07 | [8 empty] | 0
8 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-08 | [8 empty] | 0
9 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-09 | [8 empty] | 0
10 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-10 | [8 empty] | 0
11 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-11 | [8 empty] | 0
12 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-12 | [8 empty] | 0
13 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-13 | [8 empty] | 0
14 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-14 | [8 empty] | 0
15 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-15 | [8 empty] | 0
16 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-16 | [8 empty] | 0
17 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-17 | [8 empty] | 0
18 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-18 | [8 empty] | 0
19 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-19 | [8 empty] | 0
20 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-20 | [8 empty] | 0
21 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-21 | [8 empty] | 0
22 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-22 | [8 empty] | 0
23 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-23 | [8 empty] | 0
24 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-24 | [8 empty] | 0
25 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-25 | [8 empty] | 0
26 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-26 | [8 empty] | 0
27 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-27 | [8 empty] | 0
28 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-28 | [8 empty] | 0
29 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-29 | [8 empty] | 0
30 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-30 | [8 empty] | 0
31 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-01 | [8 empty] | 0
32 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-02 | [8 empty] | 0
33 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-03 | [8 empty] | 0
34 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-04 | [8 empty] | 0
35 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-05 | [8 empty] | 0
36 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | [8 empty] | 0
37 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-07 | [8 empty] | 0
38 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-08 | [8 empty] | 0
39 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-09 | [8 empty] | 0
40 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-10 | [8 empty] | 0
41 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-11 | [8 empty] | 0
42 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-12 | [8 empty] | 0
43 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-13 | [8 empty] | 0
44 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-14 | [8 empty] | 0
45 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-15 | [8 empty] | 0
46 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-16 | [8 empty] | 0
47 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-17 | [8 empty] | 0
48 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-18 | [8 empty] | 0
49 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-19 | [8 empty] | 0
50 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-20 | [8 empty] | 0
51 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-21 | [8 empty] | 0
52 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-22 | [8 empty] | 0
53 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-23 | [8 empty] | 0
54 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-24 | [8 empty] | 0
55 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-25 | [8 empty] | 0
56 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-26 | [8 empty] | 0
57 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-27 | [8 empty] | 0
58 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-28 | [8 empty] | 0
59 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-29 | [8 empty] | 0
60 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-30 | [8 empty] | 0
61 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-31 | [8 empty] | 0
62 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-01 | [8 empty] | 0
63 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-02 | [8 empty] | 0
64 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-03 | [8 empty] | 0
65 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-04 | [8 empty] | 0
66 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-05 | [8 empty] | 0
67 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-06 | [8 empty] | 0
68 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-07 | [8 empty] | 0
69 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-08 | [8 empty] | 0
70 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-09 | [8 empty] | 0
71 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-10 | [8 empty] | 0
72 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-11 | [8 empty] | 0
73 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-12 | [8 empty] | 0
74 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-13 | [8 empty] | 0
75 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-14 | [8 empty] | 0
76 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-15 | [8 empty] | 0
77 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-16 | [8 empty] | 0
78 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-17 | [8 empty] | 0
79 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-18 | [8 empty] | 0
80 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-19 | [8 empty] | 0
81 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-20 | [8 empty] | 0
82 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-21 | [8 empty] | 0
83 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-22 | [8 empty] | 0
84 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-23 | [8 empty] | 0
85 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-24 | [8 empty] | 0
86 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-25 | [8 empty] | 0
87 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-26 | [8 empty] | 0
88 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-27 | [8 empty] | 0
89 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-28 | [8 empty] | 0
90 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-29 | [8 empty] | 0
91 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-30 | [8 empty] | 0
92 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-01 | [8 empty] | 0
93 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-02 | [8 empty] | 0
94 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-03 | [8 empty] | 0
95 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-04 | [8 empty] | 0
96 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-05 | [8 empty] | 0
97 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-06 | [8 empty] | 0
98 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-07 | [8 empty] | 0
99 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-08 | [8 empty] | 0
100 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-09 | [8 empty] | 0
101 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-10 | [8 empty] | 0
102 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-11 | [8 empty] | 0
103 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | [8 empty] | 0
104 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-13 | [8 empty] | 0
105 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-14 | [8 empty] | 0
106 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | [8 empty] | 0
107 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-16 | [8 empty] | 0
108 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-17 | [8 empty] | 0
109 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-18 | [8 empty] | 0
110 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-19 | [8 empty] | 0
111 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-20 | [8 empty] | 0
112 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-21 | [8 empty] | 0
113 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-22 | [8 empty] | 0
114 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-23 | [8 empty] | 0
115 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-24 | [8 empty] | 0
116 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-25 | [8 empty] | 0
117 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-26 | [8 empty] | 0
118 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-27 | [8 empty] | 0
119 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-28 | [8 empty] | 0
120 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-29 | [8 empty] | 0
121 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-30 | [8 empty] | 0
122 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-31 | 1 | 4 | 980 | 1036 | 1008 | 1008 | 0 | 0 | 4032 | 0.20833 | 0.375 | 0.16667 | 0.83333 | Brush
123 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-01 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-02 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-03 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Modulecleaning stopped due to rain at site so Modules are cleaned
126 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-04 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Modulecleaning stopped due to rain at site so Modules are cleaned
127 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-05 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Modulecleaning stopped due to rain at site so Modules are cleaned
128 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-06 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Modulecleaning stopped due to rain at site so Modules are cleaned
129 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-07 | 1 | 2 | 0 | 0 | 0 | 1028 | 0 | 0 | 1028 | 0 | 0 | 0.66667 | 0.83333 | Brush
130 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-08 | 1 | 2 | 0 | 0 | 0 | 2016 | 0 | 0 | 2016 | 0.20833 | 0.375 | 0.66667 | 0.83333 | Brush
131 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-09 | 1 | 2 | 2032 | 0 | 0 | 0 | 0 | 0 | 2032 | 0.20833 | 0.375 | 0.66667 | 0.83333 | Brush
132 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-10 | 1 | 2 | 0 | 1008 | 0 | 0 | 1008 | 0 | 2016 | 0.20833 | 0.375 | 0.66667 | 0.83333 | Brush
133 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-11 | 1 | 2 | 1008 | 0 | 1092 | 0 | 0 | 0 | 2100 | 0.20833 | 0.375 | 0.66667 | 0.83333 | Brush
134 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-12 | 1 | 2 | 0 | 0 | 0 | 1016 | 0 | 1016 | 2032 | 0.20833 | 0.375 | 0.66667 | 0.83333 | Brush
135 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-13 | 1 | 2 | 0 | 1008 | 0 | 0 | 1008 | 0 | 2016 | 0.20833 | 0.375 | 0.66667 | 0.83333 | Brush
136 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-15 | [8 empty] | 0
138 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-16 | [8 empty] | 0
139 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-17 | [8 empty] | 0
140 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-18 | [8 empty] | 0
141 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | [8 empty] | 0
142 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-20 | [8 empty] | 0
143 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-21 | [8 empty] | 0
144 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-22 | [8 empty] | 0
145 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-23 | [8 empty] | 0
146 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-24 | [8 empty] | 0
147 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-25 | [8 empty] | 0
148 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-26 | [8 empty] | 0
149 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | [8 empty] | 0
150 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-28 | [8 empty] | 0
151 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-29 | [8 empty] | 0
152 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-30 | [8 empty] | 0
153 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-31 | [8 empty] | 0
154 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-01 | [8 empty] | 0
155 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-02 | [8 empty] | 0
156 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | [8 empty] | 0
157 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | [8 empty] | 0
158 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-05 | [8 empty] | 0
159 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-06 | [8 empty] | 0
160 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-07 | [8 empty] | 0
161 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-08 | [8 empty] | 0
162 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-09 | [8 empty] | 0
163 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-10 | [8 empty] | 0
164 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-11 | [8 empty] | 0
165 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-12 | [8 empty] | 0
166 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-13 | [8 empty] | 0
167 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-14 | [8 empty] | 0
168 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-15 | [8 empty] | 0
169 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-16 | [8 empty] | 0
170 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-17 | [8 empty] | 0
171 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-18 | [8 empty] | 0
172 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-19 | [8 empty] | 0
173 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-20 | [8 empty] | 0
174 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-21 | [8 empty] | 0
175 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-22 | [8 empty] | 0
176 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-23 | [8 empty] | 0
177 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-24 | [8 empty] | 0
178 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-25 | [8 empty] | 0
179 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-26 | [8 empty] | 0
180 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-27 | [8 empty] | 0
181 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-28 | [8 empty] | 0
182 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-29 | [8 empty] | 0
183 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-30 | [8 empty] | 0
184 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-01 | [8 empty] | 0
185 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-02 | [8 empty] | 0
186 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-03 | [8 empty] | 0
187 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-04 | [8 empty] | 0
188 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-05 | [8 empty] | 0
189 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-06 | [8 empty] | 0
190 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | [8 empty] | 0
191 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-08 | [8 empty] | 0
192 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-09 | [8 empty] | 0
193 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-10 | [8 empty] | 0
194 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | [8 empty] | 0
195 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-12 | [8 empty] | 0
196 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-13 | [8 empty] | 0
197 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-14 | [8 empty] | 0
198 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-15 | [8 empty] | 0
199 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-16 | [8 empty] | 0
200 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-17 | [8 empty] | 0
201 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-18 | [8 empty] | 0
202 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-19 | [8 empty] | 0
203 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-20 | [8 empty] | 0
204 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-21 | [8 empty] | 0
205 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-22 | [8 empty] | 0
206 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-23 | [8 empty] | 0
207 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-24 | [8 empty] | 0
208 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-25 | [8 empty] | 0
209 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-26 | [8 empty] | 0
210 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-27 | [8 empty] | 0
211 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | [8 empty] | 0
212 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-29 | [8 empty] | 0
213 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-30 | [8 empty] | 0
214 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-31 | [8 empty] | 0
215 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-01 | [8 empty] | 0
216 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-02 | [8 empty] | 0
217 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-03 | [8 empty] | 0
218 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-04 | [8 empty] | 0
219 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-05 | [8 empty] | 0
220 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-06 | [8 empty] | 0
221 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-07 | [8 empty] | 0
222 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-08 | [8 empty] | 0
223 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-09 | [8 empty] | 0
224 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-10 | [8 empty] | 0
225 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-11 | [8 empty] | 0
226 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-12 | [8 empty] | 0
227 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-13 | [8 empty] | 0
228 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-14 | [8 empty] | 0
229 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-15 | [8 empty] | 0
230 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-16 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 1995 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
231 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-17 | 1 | 2 | 0 | 504 | 504 | 462 | 0 | 588 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
232 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-18 | 1 | 2 | 336 | 672 | 0 | 0 | 0 | 735 | 1743 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
233 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-19 | 1 | 2 | 567 | 0 | 0 | 0 | 1428 | 0 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
234 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-20 | 1 | 2 | 1764 | 252 | 0 | 0 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
235 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-21 | 1 | 2 | 0 | 1071 | 945 | 0 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
236 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-22 | 1 | 2 | 0 | 756 | 1008 | 252 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
237 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-23 | 1 | 2 | 0 | 0 | 693 | 1302 | 0 | 0 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
238 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-24 | 1 | 2 | 0 | 0 | 0 | 0 | 2016 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
239 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-25 | 1 | 2 | 0 | 0 | 0 | 0 | 1470 | 294 | 1764 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
240 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-26 | 1 | 2 | 0 | 0 | 0 | 672 | 0 | 126 | 798 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
241 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-27 | 1 | 2 | 0 | 0 | 0 | 1407 | 0 | 0 | 1407 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
242 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-28 | 1 | 2 | 0 | 0 | 567 | 1428 | 0 | 0 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
243 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-29 | 1 | 2 | 0 | 0 | 987 | 0 | 0 | 0 | 987 | 0.25 | 0.41667 |  |  | MOP
244 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-30 | 1 | 2 | 0 | 0 | 987 | 0 | 0 | 0 | 987 | 0.25 | 0.41667 |  |  | MOP
245 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-01 | 1 | 2 | 1386 | 0 | 0 | 0 | 609 | 0 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
246 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-02 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 1512 | 1512 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
247 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-03 | 1 | 2 | 63 | 0 | 0 | 0 | 0 | 945 | 1008 |  |  | 0.66667 | 0.83333 | MOP
248 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-04 | [8 empty] | 0
249 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-05 | 1 | 2 | 189 | 1827 | 0 | 0 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
250 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | 1 | 2 | 0 | 168 | 819 | 0 | 0 | 0 | 987 |  |  | 0.66667 | 0.83333 | MOP |  | Cycle 1 Completed
251 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-07 | 2 | 2 | 0 | 0 | 756 | 1302 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
252 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-08 | 2 | 2 | 0 | 0 | 0 | 1956 | 0 | 0 | 1956 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
253 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-09 | 2 | 2 | 0 | 0 | 504 | 1491 | 0 | 0 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
254 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-10 | 2 | 2 | 0 | 252 | 1575 | 0 | 0 | 0 | 1827 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
255 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | 2 | 2 | 630 | 378 | 0 | 0 | 0 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
256 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-12 | 2 | 2 | 1008 | 0 | 0 | 0 | 0 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
257 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-13 | 2 | 2 | 693 | 0 | 0 | 0 | 315 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
258 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-14 | 2 | 2 | 0 | 0 | 0 | 0 | 1008 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
259 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 2 | 2 | 0 | 0 | 0 | 0 | 84 | 1302 | 1386 | 0.25 | 0.41667 |  |  | MOP
260 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-16 | 2 | 2 | 0 | 0 | 294 | 252 | 0 | 504 | 1050 | 0.25 | 0.41667 |  |  | MOP
261 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-17 | 2 | 2 | 0 | 462 | 252 | 252 | 504 | 0 | 1470 | 0.25 | 0.41667 |  |  | MOP
262 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-18 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 1008 | 1008 | 0.25 | 0.41667 |  |  | MOP
263 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-19 | 2 | 2 | 63 | 0 | 0 | 0 | 0 | 945 | 1008 | 0.25 | 0.41667 |  |  | MOP
264 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-20 | 2 | 2 | 189 | 819 | 0 | 0 | 0 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
265 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-21 | 2 | 2 | 0 | 1176 | 378 | 0 | 0 | 0 | 1554 | 0.25 | 0.41667 |  |  | MOP
266 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-22 | 2 | 2 | 0 | 0 | 1323 | 0 | 0 | 0 | 1323 | 0.25 | 0.41667 |  |  | MOP
267 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-23 | 2 | 2 | 0 | 1743 | 294 | 0 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
268 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-24 | 2 | 2 | 252 | 294 | 0 | 0 | 0 | 1512 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
269 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | 2 | 2 | 693 | 0 | 0 | 0 | 609 | 735 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
270 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | 2 | 2 | 1638 | 378 | 0 | 0 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
271 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-27 | 2 | 2 | 0 | 189 | 861 | 0 | 588 | 420 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
272 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-28 | 2 | 2 | 0 | 0 | 0 | 0 | 2016 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 2 Completed
273 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | 3 | 2 | 0 | 63 | 2079 | 0 | 882 | 0 | 3024 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
274 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-30 | 3 | 2 | 1449 | 567 | 63 | 1974 | 0 | 0 | 4053 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
275 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-31 | 3 | 2 | 252 | 0 | 0 | 2184 | 0 | 1827 | 4263 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
276 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-01 | 3 | 2 | 1008 | 0 | 126 | 882 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
277 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-02 | 3 | 2 | 0 | 0 | 0 | 0 | 294 | 1680 | 1974 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
278 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-03 | 3 | 2 | 252 | 1155 | 0 | 0 | 0 | 567 | 1974 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
279 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-04 | 3 | 2 | 0 | 882 | 819 | 0 | 252 | 0 | 1953 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
280 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | 3 | 2 | 0 | 0 | 882 | 1176 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
281 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-06 | 3 | 2 | 0 | 0 | 0 | 2016 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
282 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-07 | 3 | 2 | 0 | 441 | 945 | 840 | 0 | 0 | 2226 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
283 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-08 | 3 | 2 | 1449 | 315 | 378 | 0 | 0 | 0 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
284 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-09 | 3 | 2 | 1008 | 0 | 0 | 0 | 1134 | 0 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
285 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-10 | 3&4 | 2 | 1449 | 0 | 0 | 0 | 609 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 3 Completed
286 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-11 | 4 | 2 | 882 | 567 | 630 | 0 | 0 | 0 | 2079 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
287 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-12 | [8 empty] | 0
288 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-13 | 4 | 2 | 0 | 0 | 1491 | 504 | 0 | 0 | 1995 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
289 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-14 | 4 | 2 | 0 | 0 | 0 | 2100 | 0 | 0 | 2100 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
290 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | [8 empty] | 0
291 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 4 | 2 | 0 | 504 | 504 | 462 | 0 | 567 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
292 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-17 | 4 | 2 | 0 | 0 | 0 | 0 | 588 | 1428 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
293 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-18 | 4 | 2 | 0 | 0 | 0 | 0 | 2016 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
294 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-19 | 4 | 2 | 252 | 0 | 0 | 0 | 840 | 882 | 1974 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
295 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | 4 | 2 | 0 | 1995 | 42 | 0 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
296 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-21 | 4 | 2 | 0 | 0 | 336 | 1722 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
297 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-22 | 4 | 2 | 0 | 0 | 1323 | 735 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
298 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-23 | 4 | 2 | 0 | 1659 | 378 | 0 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
299 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-24 | 4 | 2 | 252 | 378 | 0 | 0 | 0 | 1386 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
300 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-25 | 4 | 2 | 0 | 0 | 0 | 0 | 735 | 861 | 1596 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
301 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-26 | [8 empty] | 0
302 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-27 | 4 | 2 | 1323 | 0 | 0 | 0 | 693 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
303 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | 4 | 2 | 0 | 1701 | 63 | 0 | 0 | 0 | 1764 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
304 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-29 | 4 | 2 | 0 | 0 | 1449 | 252 | 0 | 0 | 1701 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
305 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-30 | 4&5 | 2 | 630 | 567 | 861 | 0 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 4 Completed
306 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-31 | 5 | 2 | 1701 | 0 | 0 | 0 | 357 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
307 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-01 | 5 | 2 | 0 | 504 | 504 | 462 | 252 | 315 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
308 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | 5 | 2 | 0 | 0 | 0 | 0 | 0 | 2079 | 2079 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
309 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-03 | 5 | 2 | 0 | 0 | 0 | 0 | 1764 | 252 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
310 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-04 | 5 | 2 | 252 | 0 | 0 | 0 | 1722 | 168 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
311 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | [8 empty] | 0
312 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-06 | 5 | 2 | 252 | 1533 | 0 | 0 | 0 | 252 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
313 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | 5 | 2 | 0 | 462 | 1575 | 0 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
314 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-08 | 5 | 2 | 0 | 504 | 84 | 1428 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
315 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | 5 | 2 | 0 | 336 | 0 | 714 | 0 | 0 | 1050 | 0.25 | 0.41667 |  |  | MOP
316 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-10 | 5 | 2 | 0 | 0 | 0 | 2016 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
317 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-11 | 5 | 2 | 0 | 504 | 210 | 1323 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
318 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-12 | 5 | 2 | 0 | 819 | 945 | 252 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
319 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-13 | 5 | 2 | 0 | 1722 | 252 | 252 | 0 | 0 | 2226 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
320 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | 5 | 2 | 252 | 252 | 0 | 0 | 0 | 1575 | 2079 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
321 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-15 | 5 | 2 | 0 | 336 | 252 | 210 | 546 | 672 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
322 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-16 | 5 | 2 | 0 | 0 | 0 | 0 | 2016 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 5 Completed
323 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | 6 | 2 | 0 | 0 | 0 | 0 | 1722 | 420 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
324 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-18 | 6 | 2 | 378 | 0 | 0 | 0 | 630 | 1008 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
325 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-19 | 6 | 2 | 0 | 0 | 0 | 0 | 0 | 1008 | 1008 | 0.25 | 0.41667 |  |  | MOP
326 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-20 | 6 | 2 | 252 | 1323 | 0 | 0 | 0 | 441 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
327 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | 6 | 2 | 0 | 672 | 1197 | 42 | 0 | 0 | 1911 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
328 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | [8 empty] | 0
329 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-23 | 6 | 2 | 0 | 0 | 441 | 1491 | 0 | 0 | 1932 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
330 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | 6 | 2 | 0 | 0 | 0 | 2016 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
331 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | 6 | 2 | 0 | 0 | 882 | 1176 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
332 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | 6 | 2 | 0 | 1008 | 1575 | 0 | 0 | 0 | 2583 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
333 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-27 | 6 | 2 | 1890 | 126 | 0 | 0 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
334 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-28 | 6 | 2 | 693 | 0 | 0 | 0 | 1428 | 0 | 2121 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
335 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-01 | 6 | 2 | 819 | 0 | 0 | 0 | 1113 | 0 | 1932 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
336 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | 6 | 2 | 1953 | 0 | 0 | 0 | 63 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
337 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-03 | 6 | 2 | 378 | 567 | 861 | 210 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
338 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | 6 | 2 | 0 | 1491 | 504 | 42 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
339 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | 6 | 2 | 252 | 546 | 0 | 0 | 1008 | 252 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 6 Completed
340 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-06 | 7 | 2 | 0 | 0 | 0 | 0 | 1974 | 0 | 1974 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
341 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-07 | 7 | 2 | 0 | 0 | 0 | 0 | 504 | 1680 | 2184 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
342 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-08 | 7 | 2 | 0 | 504 | 420 | 252 | 0 | 861 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
343 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | 7 | 2 | 0 | 0 | 84 | 210 | 0 | 1512 | 1806 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
344 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-10 | 7 | 2 | 252 | 315 | 0 | 0 | 0 | 1008 | 1575 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
345 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-11 | 7 | 2 | 0 | 1680 | 252 | 0 | 0 | 0 | 1932 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
346 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-12 | 7 | 1 | 0 | 0 | 1197 | 546 | 0 | 0 | 1743 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
347 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-13 | 7 | 2 | 0 | 0 | 0 | 2037 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
348 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-14
349 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-15 | 7 | 2 | 0 | 0 | 0 | 1050 | 0 | 0 | 1050 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
350 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-16 | 7 | 2 | 0 | 0 | 819 | 2016 | 1176 | 0 | 4011 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
351 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-17 | 7 | 2 | 0 | 0 | 0 | 0 | 1176 | 420 | 1596 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
352 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-18 | 7 | 2 | 0 | 0 | 0 | 0 | 1008 | 0 | 1008 |  |  | 0.66667 | 0.83333 | MOP
353 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-19 | 7 | 2 | 378 | 0 | 0 | 0 | 903 | 0 | 1281 |  |  | 0.66667 | 0.83333 | MOP
354 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-20 | 7 | 2 | 1134 | 0 | 0 | 0 | 0 | 0 | 1134 |  |  | 0.66667 | 0.83333 | MOP
355 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-21 | 7 | 2 | 693 | 567 | 0 | 0 | 0 | 0 | 1260 |  |  | 0.66667 | 0.83333 | MOP
356 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-22 | 7 | 2 | 0 | 1008 | 0 | 0 | 0 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
357 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-23 | 7 | 2 | 441 | 0 | 0 | 0 | 609 | 0 | 1050 | 0.25 | 0.41667 |  |  | MOP
358 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | 7 | 2 | 1890 | 189 | 0 | 0 | 0 | 0 | 2079 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
359 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | 7 | 2 | 0 | 0 | 0 | 0 | 588 | 420 | 1008 | 0.25 | 0.41667 |  |  | MOP
360 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | 7&8 | 2 | 0 | o | 0 | 0 | 1050 | 0 | 1050 | 0.25 | 0.41667 |  |  | MOP |  | Cycle 7 Completed
361 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-27 | 8 | 2 | 0 | 0 | 0 | 0 | 1974 | 0 | 1974 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
362 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-28 | 8 | 2 | 756 | 567 | 735 | 0 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
363 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-29 | 8 | 2 | 1575 | 0 | 0 | 0 | 609 | 0 | 2184 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
364 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-30 | 8 | 2 | 0 | 504 | 504 | 462 | 252 | 378 | 2100 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
365 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | 8 | 2 | 252 | 0 | 0 | 0 | 0 | 1890 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
366 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-01 | [8 empty] | 0
367 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-02 | [8 empty] | 0
368 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-03 | [8 empty] | 0
369 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-04 | [8 empty] | 0
370 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-05 | [8 empty] | 0
371 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-06 | [8 empty] | 0
372 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-07 | [8 empty] | 0
373 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-08 | 8 | 3 | 252 | 252 | 0 | 0 | 1722 | 1575 | 3801 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
374 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | 8 | 4 | 0 | 1743 | 630 | 0 | 1764 | 420 | 4557 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
375 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | 8 | 2 | 0 | 1533 | 504 | 252 | 0 | 0 | 2289 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
376 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | 8 | 2 | 252 | 504 | 0 | 0 | 0 | 1575 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
377 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | 8 | 2 | 252 | 0 | 0 | 0 | 1428 | 672 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
378 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-13 | 8 | 2 | 252 | 651 | 0 | 0 | 0 | 441 | 1344 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Grid failure
379 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-14 | 8 | 2 | 567 | 630 | 1260 | 0 | 0 | 0 | 2457 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
380 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-15 | 8 | 2 | 0 | 0 | 819 | 1491 | 0 | 0 | 2310 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 8 Completed
381 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-16 | 9 | 2 | 0 | 0 | 0 | 2331 | 0 | 0 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
382 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-17 | 9 | 2 | 0 | 0 | 1365 | 987 | 0 | 0 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
383 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | 9 | 2 | 1134 | 567 | 693 | 0 | 0 | 0 | 2394 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
384 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-19 | 9 | 2 | 1197 | 84 | 252 | 210 | 609 | 0 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
385 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-20 | 9 | 4 | 0 | 315 | 693 | 0 | 1932 | 420 | 3360 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
386 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-21 | 9 | 4 | 0 | 336 | 252 | 210 | 1554 | 1302 | 3654 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
387 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-22 | 9 | 2 | 189 | 168 | 252 | 252 | 0 | 1701 | 2562 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
388 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-23 | 9 | 2 | 252 | 1386 | 0 | 0 | 0 | 756 | 2394 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
389 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | 9 | 2 | 0 | 1302 | 882 | 252 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
390 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-25 | [8 empty] | 0
391 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | [8 empty] | 0
392 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | [8 empty] | 0
393 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-28 | [8 empty] | 0
394 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-29 | [8 empty] | 0 | [6 empty] | Grid5 TW12 to TW18 - 336 No.s ModulesChemical cleaning work completed
395 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-30 | [8 empty] | 0 | [6 empty] | Grid6 TW10 to TW18 & Grid5 TW1 to TW11 - 756 No.s ModulesChemical cleaning work completed
396 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-01 | [8 empty] | 0 | [6 empty] | Grid6 T1 to T13 - 819 No.s Modules Chemical cleaning work completed
397 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-02 | [8 empty] | 0 | [6 empty] | Grid6 T14 - 63 No.s Modules Chemical cleaning work completed
398 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-03 | [8 empty] | 0
399 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-04 | [8 empty] | 0 | [6 empty] | Grid6 T15 to T28 - 882 No.s Modules Chemical cleaning work completed
400 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-05 | [8 empty] | 0 | [6 empty] | Grid6 T29 to T43 - 945 No.s Modules Chemical cleaning work completed
401 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-06 | [8 empty] | 0 | [6 empty] | Grid6 T44 to T59 - 1008 No.s Modules Chemical cleaning work completed
402 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-07 | [8 empty] | 0 | [6 empty] | Grid6 T44 to T59 - 1008 No.s Modules Chemical cleaning work completed
403 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-08 | [8 empty] | 0 | [6 empty] | Grid6 T60 to T68 & TW01 to TW09 - 903 No.s Modules Chemical cleaning work completed
404 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-09 | [8 empty] | 0 | [6 empty] | Grid6 T69 to T88 - 840 No.s Modules Chemical cleaning work completed
405 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-10 | [8 empty] | 0
406 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-11 | [8 empty] | 0 | [6 empty] | Grid5 T92 to T97 - 378 No.s Modules Chemical cleaning work completed
407 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-12 | [8 empty] | 0 | [6 empty] | Grid5 T98 to T105 & Grid2 TW01, T1 to T11 - 1008 No.s Modules Chemical cleaning work completed
408 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-13 | [8 empty] | 0 | [6 empty] | Grid2 T12 to T35 - 1008 No.s Modules Chemical cleaning work completed
409 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-14 | [8 empty] | 0 | [6 empty] | Grid2 T36 to T40 & Grid1 T43 to T52 - 588 No.s Modules Chemical cleaning work completed
410 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-15 | [8 empty] | 0 | [6 empty] | Grid1 T20 to T42 - 966 No.s Modules Chemical cleaning work completed
411 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-16 | [8 empty] | 0 | [6 empty] | Grid1 T1 to T19 & Grid5 T88 to T91 - 966 No.s Modules Chemical cleaning work completed
412 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-17 | [8 empty] | 0 | [6 empty] | Grid5 T70 to T87 - 966 No.s Modules Chemical cleaning work completed
413 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-18 | [8 empty] | 0 | [6 empty] | Grid5 T54 to T69 - 1008 No.s Modules Chemical cleaning work completed
414 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-19 | [8 empty] | 0 | [6 empty] | Grid5 T36 to T53 - 966 No.s Modules Chemical cleaning work completed
415 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | [8 empty] | 0 | [6 empty] | Grid5 T20 to T35 - 1008 No.s Modules Chemical cleaning work completed
416 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-21 | [8 empty] | 0
417 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-22 | [8 empty] | 0 | [6 empty] | Grid5 T04 to T19 - 1008 No.s Modules Chemical cleaning work completed
418 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-23 | [8 empty] | 0 | [6 empty] | Grid5 T01 to T03 & Grid4 T01 to T15 - 966 No.s Modules Chemical cleaning work completed
419 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-24 | [8 empty] | 0 | [6 empty] | Grid4 T16 to T20 - 315 No.s Modules Chemical cleaning work completed
420 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | [8 empty] | 0 | [6 empty] | Grid4 T29 to T44 - 1008 No.s Modules Chemical cleaning work completed
421 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | [8 empty] | 0
422 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-27 | [8 empty] | 0 | [6 empty] | Grid4 T45 to T60 - 1008 No.s Modules Chemical cleaning work completed
423 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-28 | [8 empty] | 0 | [6 empty] | Grid4 T61 to T76 - 1008 No.s Modules Chemical cleaning work completed
424 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-29 | [8 empty] | 0 | [6 empty] | Grid4 T77 to T88 - 756 No.s Modules Chemical cleaning work completed
425 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-30 | [8 empty] | 0 | [6 empty] | Grid3 T54 to T68 - 861 No.s Modules Chemical cleaning work completed
426 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-31 | [8 empty] | 0 | [6 empty] | Grid3 T38 to T53 - 1008 No.s Modules Chemical cleaning work completed
427 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-01 | [8 empty] | 0 | [6 empty] | Grid3 T22 to T37 - 1008 No.s Modules Chemical cleaning work completed
428 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-02 | [8 empty] | 0 | [6 empty] | Grid3 T6 to T21 - 1008 No.s Modules Chemical cleaning work completed
429 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-03 | [8 empty] | 0 | [6 empty] | Grid3 T1 to T5, TW1, Grid3A T1 to T5 & Grid4 T88 to T95 - 987 No.s Modules Chemical cleaning work completed
430 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-04 | [8 empty] | 0 | [6 empty] | Grid4 T96 to T111 - 1008 No.s Modules Chemical cleaning work completed
431 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-05 | [8 empty] | 0 | [6 empty] | Grid4 T112 to T116 - 315 No.s Modules Chemical cleaning work completed
432 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-06 | [8 empty] | 0 | [6 empty] | Grid4 T117 to T136 - 1029 No.s Modules Chemical cleaning work completed
433 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-07 | [8 empty] | 0 | [6 empty] | Grid4 T137 to T143 & Grid5 T145 to T158 - 1029 No.s Modules Chemical cleaning work completed
434 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | [8 empty] | 0 | [6 empty] | Grid5 T127 to T144 - 1008 No.s Modules Chemical cleaning work completed
435 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-09 | [8 empty] | 0 | [6 empty] | Grid5 T111 to T126 - 1008 No.s Modules Chemical cleaning work completed
436 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-10 | [8 empty] | 0 | [6 empty] | Grid5 T105 to T110 & Grid5A T110- 357 No.s Modules Chemical cleaning work completed - Modules Chemical cleanng Cycle 1 completed
437 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-11 | [8 empty] | 0
438 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-12 | [8 empty] | 0
439 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-13 | [8 empty] | 0
440 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-14 | [8 empty] | 0
441 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-15 | [8 empty] | 0
442 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-16 | [8 empty] | 0
443 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-17 | [8 empty] | 0
444 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-18 | [8 empty] | 0
445 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-19 | [8 empty] | 0
446 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-20 | [8 empty] | 0
447 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-21 | [8 empty] | 0
448 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-22 | [8 empty] | 0
449 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-23 | [8 empty] | 0
450 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-24 | [8 empty] | 0
451 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-25 | [8 empty] | 0
452 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-26 | [8 empty] | 0
453 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-27 | 9 | 2 | 0 | 0 | 0 | 0 | 2268 | 0 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
454 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-28 | 9 | 2 | 63 | 0 | 0 | 0 | 1827 | 420 | 2310 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
455 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-29 | 9 | 2 | 2268 | 0 | 0 | 0 | 0 | 0 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
456 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-30 | [8 empty] | 0
457 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-01 | [8 empty] | 0
458 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | [8 empty] | 0
459 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-03 | [8 empty] | 0
460 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-04 | [8 empty] | 0
461 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-05 | [8 empty] | 0
462 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-06 | [8 empty] | 0
463 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-07 | [8 empty] | 0
464 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-08 | [8 empty] | 0
465 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-09 | [8 empty] | 0
466 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-10 | [8 empty] | 0
467 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-11 | [8 empty] | 0
468 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-12 | [8 empty] | 0
469 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-13 | [8 empty] | 0
470 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-14 | [8 empty] | 0
471 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-15 | [8 empty] | 0
472 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-16 | [8 empty] | 0
473 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-17 | [8 empty] | 0
474 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-18 | 9 | 2 | 693 | 567 | 861 | 0 | 0 | 0 | 2121 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
475 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-19 | 9 | 2 | 1197 | 504 | 252 | 210 | 0 | 0 | 2163 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 9 Completed
476 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 1323 | 1323 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
477 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-21 | 10 | 2 | 441 | 336 | 252 | 210 | 903 | 0 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
478 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-22 | 10 | 2 | 630 | 168 | 252 | 252 | 1134 | 0 | 2436 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
479 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-23 | 10 | 2 | 1764 | 63 | 0 | 0 | 504 | 0 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
480 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-24 | 10 | 2 | 0 | 567 | 819 | 0 | 0 | 0 | 1386 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
481 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | [8 empty] | 0
482 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-26 | [8 empty] | 0
483 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | [8 empty] | 0
484 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-28 | [8 empty] | 0
485 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | [8 empty] | 0
486 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-30 | [8 empty] | 0
487 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-31 | [8 empty] | 0
488 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-01 | [8 empty] | 0
489 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-02 | 10 | 2 | 0 | 252 | 2079 | 63 | 0 | 0 | 2394 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
490 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-03 | 10 | 2 | 0 | 0 | 0 | 1197 | 0 | 0 | 1197 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
491 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-04 | [8 empty] | 0
492 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-05 | 10 | 2 | 0 | 504 | 1134 | 966 | 0 | 0 | 2604 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
493 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-06 | [8 empty] | 0
494 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-07 | [8 empty] | 0
495 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-08 | 10 | 2 | 0 | 0 | 567 | 609 | 1302 | 0 | 2478 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
496 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-09 | 10 | 2 | 0 | 504 | 504 | 462 | 987 | 0 | 2457 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
497 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-10 | 10 | 2 | 0 | 0 | 168 | 2184 | 0 | 0 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
498 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-11 | 10 | 2 | 0 | 0 | 0 | 0 | 1764 | 420 | 2184 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
499 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-12 | 10 | 2 | 0 | 245 | 175 | 0 | 1848 | 0 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
500 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-13 | [8 empty] | 0
501 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-14 | [8 empty] | 0
502 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-15 | [8 empty] | 0
503 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-16 | [8 empty] | 0
504 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-17 | [8 empty] | 0
505 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-18 | [8 empty] | 0
506 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-19 | [8 empty] | 0
507 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-20 | [8 empty] | 0
508 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-21 | [8 empty] | 0
509 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-22 | [8 empty] | 0
510 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-23 | [8 empty] | 0
511 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-24 | [8 empty] | 0
512 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-25 | [8 empty] | 0
513 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-26 | [8 empty] | 0
514 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-27 | [8 empty] | 0
515 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-28 | 1 | 2 | 0 | 504 | 504 | 462 | 0 | 735 | 2205 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
516 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-29 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 1512 | 1512 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
517 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-30 | [8 empty] | 0
518 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-31 | [8 empty] | 0
519 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-01 | [8 empty] | 0
520 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-02 | [8 empty] | 0
521 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-03 | [8 empty] | 0
522 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-04 | [8 empty] | 0
523 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-05 | [8 empty] | 0
524 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-06 | [8 empty] | 0
525 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-07 | [8 empty] | 0
526 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-08 | [8 empty] | 0
527 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-09 | [8 empty] | 0
528 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-10 | [8 empty] | 0
529 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-11 | [8 empty] | 0
530 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-12 | 1 | 2 | 504 | 0 | 0 | 0 | 609 | 0 | 1113 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
531 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-13 | 1 | 2 | 1827 | 126 | 0 | 0 | 0 | 0 | 1953 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
532 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-14 | 1 | 2 | 0 | 441 | 1806 | 0 | 0 | 0 | 2247 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
533 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-15 | 1 | 2 | 1701 | 630 | 0 | 0 | 0 | 0 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
534 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-16 | 1 | 2 | 0 | 756 | 504 | 210 | 0 | 819 | 2289 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
535 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-17 | [8 empty] | 0
536 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-18 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 1008 | 1008 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
537 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-19 | 1 | 2 | 252 | 1155 | 0 | 0 | 0 | 798 | 2205 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
538 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-20 | 1 | 2 | 0 | 1176 | 546 | 252 | 0 | 0 | 1974 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
539 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-21 | 1 | 2 | 1197 | 630 | 567 | 0 | 0 | 0 | 2394 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
540 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-22 | 1 | 2 | 252 | 189 | 0 | 0 | 0 | 1890 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
541 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-23 | 1 | 2 | 504 | 0 | 0 | 0 | 1428 | 357 | 2289 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
542 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-24 | 1 | 2 | 126 | 0 | 1134 | 1008 | 0 | 0 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
543 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-25 | 1 | 2 | 0 | 0 | 0 | 0 | 2221 | 0 | 2221 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
544 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-26 | 1 | 2 | 0 | 0 | 630 | 1680 | 0 | 0 | 2310 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 1 Completed
545 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-27 | 2 | 2 | 0 | 0 | 567 | 0 | 1764 | 0 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
546 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-28 | 2 | 2 | 0 | 0 | 0 | 0 | 1134 | 0 | 1134 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
547 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-29 | [8 empty] | 0
548 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-30 | 2 | 2 | 0 | 735 | 378 | 0 | 546 | 420 | 2079 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
549 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 2 | 2 | 252 | 1260 | 0 | 0 | 0 | 441 | 1953 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
550 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | 2 | 2 | 0 | 0 | 0 | 168 | 0 | 1134 | 1302 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
551 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | 2 | 2 | 0 | 504 | 504 | 294 | 0 | 882 | 2184 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
552 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | [8 empty] | 0
553 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | [8 empty] | 0
554 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | [8 empty] | 0
555 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | 2 | 2 | 0 | 504 | 504 | 462 | 0 | 798 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
556 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | 2 | 2 | 0 | 0 | 0 | 0 | 714 | 1554 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
557 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-09 | 2 | 2 | 0 | 0 | 0 | 0 | 1134 | 0 | 1134 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
558 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | [8 empty] | 0
559 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-11 | 2 | 2 | 189 | 0 | 0 | 0 | 1638 | 315 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
560 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-12 | 2 | 2 | 63 | 2037 | 189 | 0 | 0 | 0 | 2289 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
561 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-13 | 2 | 2 | 0 | 0 | 1512 | 546 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
562 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | [8 empty] | 0
563 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | 2 | 2 | 0 | 0 | 0 | 2247 | 0 | 0 | 2247 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
564 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | 2 | 2 | 0 | 0 | 63 | 2142 | 0 | 0 | 2205 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
565 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | 2 | 2 | 0 | 189 | 2016 | 0 | 0 | 0 | 2205 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
566 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | 2 | 2 | 1827 | 441 | 0 | 0 | 0 | 0 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 2 Completed
567 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-19 | 3 | 2 | 504 | 0 | 0 | 0 | 1764 | 0 | 2268 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
568 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-20 | 3 | 2 | 2079 | 0 | 0 | 0 | 273 | 0 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
569 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | 3 | 2 | 252 | 903 | 1113 | 210 | 0 | 0 | 2478 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
570 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-22 | 3 | 2 | 0 | 231 | 252 | 252 | 0 | 1701 | 2436 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
571 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | 3 | 2 | 252 | 819 | 0 | 0 | 0 | 756 | 1827 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
572 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-24 | 3 | 2 | 0 | 1239 | 882 | 252 | 0 | 0 | 2373 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
573 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-25 | 3 | 2 | 252 | 1974 | 0 | 0 | 0 | 126 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
574 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-26 | 3 | 2 | 0 | 0 | 0 | 0 | 252 | 2121 | 2373 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
575 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-27 | 3 | 2 | 0 | 0 | 0 | 0 | 1932 | 420 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
576 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | 3 | 2 | 0 | 0 | 0 | 0 | 2352 | 0 | 2352 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
577 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | 3 | 2 | 1764 | 0 | 0 | 0 | 378 | 0 | 2142 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
578 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | 3 | 2 | 567 | 630 | 1134 | 0 | 0 | 0 | 2331 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
579 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-31 | 3 | 2 | 0 | 0 | 945 | 1344 | 0 | 0 | 2289 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
580 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-01 | 3 | 2 | 0 | 0 | 0 | 2394 | 0 | 0 | 2394 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
581 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-02 | 3 | 2 | 0 | 273 | 1197 | 1113 | 0 | 0 | 2583 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP |  | Cycle 3 Completed
582 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-03 | 4 | 2 | 882 | 567 | 1113 | 0 | 0 | 0 | 2562 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
583 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-04 | 4 | 2 | 1449 | 0 | 252 | 252 | 609 | 0 | 2562 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
584 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-05 | 4 | 2 | 0 | 504 | 504 | 462 | 546 | 504 | 2520 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
585 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-06 | 4 | 2 | 252 | 315 | 0 | 0 | 0 | 1953 | 2520 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
586 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-07 | 4 | 2 | 0 | 1869 | 378 | 294 | 0 | 0 | 2541 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
587 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-08 | 4 | 2 | 0 | 1449 | 588 | 504 | 0 | 0 | 2541 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
588 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-09 | 4 | 2 | 252 | 588 | 0 | 252 | 0 | 1449 | 2541 | 0.25 | 0.41667 | 0.66667 | 0.83333 | MOP
589 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
590 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-11 | 4 | 2 | 0 | 336 | 0 | 0 | 1428 | 798 | 2562 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
591 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-12 | 4 | 2 | 1197 | 0 | 0 | 0 | 0 | 0 | 1197 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
592 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-13 | 4 | 2 | 1134 | 630 | 441 | 294 | 0 | 0 | 2499 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
593 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-14 | 4 | 2 | 0 | 0 | 1638 | 378 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
594 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-15 | 4 | 2 | 0 | 0 | 0 | 2499 | 0 | 0 | 2499 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
595 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-16 | 4 | 2 | 0 | 0 | 189 | 2058 | 294 | 0 | 2541 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
596 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-17 | 4 | 2 | 0 | 441 | 1869 | 0 | 0 | 252 | 2562 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP |  | Cycle 4 Completed
597 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-18 | 5 | 2 | 2205 | 0 | 0 | 0 | 0 | 0 | 2205 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
598 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-19 | 5 | 2 | 2205 | 315 | 0 | 0 | 0 | 0 | 2520 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
599 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-20 | 5 | 2 | 126 | 0 | 0 | 0 | 1029 | 1354 | 2509 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
600 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-21 | 5 | 2 | 0 | 0 | 0 | 0 | 2142 | 378 | 2520 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
601 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-22 | 5 | 2 | 0 | 336 | 252 | 588 | 924 | 420 | 2520 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
602 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-23 | 5 | 2 | 0 | 352 | 294 | 252 | 1638 | 0 | 2536 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
603 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-24 | 5 | 2 | 252 | 882 | 0 | 0 | 0 | 945 | 2079 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
604 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-25 | 5 | 2 | 252 | 1758 | 252 | 0 | 0 | 252 | 2514 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
605 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-26 | 5 | 2 | 252 | 1194 | 1071 | 0 | 0 | 0 | 2517 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
606 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-27 | 5 | 2 | 1071 | 0 | 0 | 0 | 1428 | 0 | 2499 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
607 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-28 | 5 | 2 | 294 | 0 | 0 | 0 | 0 | 2247 | 2541 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
608 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-29 | [8 empty] | 0
609 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-30 | 5 | 2 | 1386 | 0 | 0 | 0 | 1176 | 0 | 2562 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
610 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-01 | 5 | 2 | 1449 | 630 | 441 | 0 | 0 | 0 | 2520 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP |  | Cycle 5 Completed
611 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-02 | 6 | 2 | 252 | 630 | 1449 | 0 | 0 | 0 | 2331 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
612 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-03 | 6 | 2 | 0 | 0 | 630 | 567 | 0 | 0 | 1197 | 0.25 | 0.41667 |  |  | MOP
613 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | [8 empty] | 0
614 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-05 | 6 | 2 | 0 | 0 | 0 | 2436 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
615 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-06 | 6 | 2 | 0 | 0 | 441 | 1617 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
616 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-07 | 6 | 2 | 0 | 0 | 1554 | 924 | 0 | 0 | 2478 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
617 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-08 | 6 | 2 | 1071 | 567 | 861 | 0 | 0 | 0 | 2499 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
618 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-09 | 6 | 2 | 1260 | 231 | 0 | 336 | 609 | 0 | 2436 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
619 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-10 | 6 | 2 | 0 | 0 | 0 | 0 | 1984 | 420 | 2404 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
620 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | 6 | 2 | 0 | 504 | 210 | 0 | 1722 | 0 | 2436 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
621 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-12 | 6 | 2 | 0 | 298 | 252 | 252 | 0 | 1638 | 2440 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
622 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-13 | 6 | 2 | 252 | 1071 | 0 | 0 | 0 | 1134 | 2457 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
623 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-14 | 6 | 2 | 0 | 1554 | 630 | 252 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
624 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | 6 | 2 | 0 | 1947 | 504 | 0 | 0 | 0 | 2451 | 0.25 | 0.41667 | 0.625 | 0.79167 | MOP
625 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-16 | 6 | 2 | 252 | 378 | 0 | 0 | 0 | 1827 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
626 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-17 | 7 | 2 | 630 | 0 | 0 | 0 | 1428 | 420 | 2478 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
627 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-18 | 7 | 2 | 1260 | 0 | 0 | 0 | 0 | 0 | 1260 | 0.25 | 0.41667 |  |  | MOP
628 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-19 | 7 | 2 | 1324 | 630 | 504 | 0 | 0 | 0 | 2458 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
629 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-20 | 7 | 2 | 0 | 0 | 1134 | 0 | 1302 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
630 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-21 | 7 | 2 | 0 | 0 | 0 | 0 | 2016 | 0 | 2016 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
631 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | 7 | 2 | 0 | 0 | 567 | 693 | 1176 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
632 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-23 | 7 | 2 | 0 | 0 | 0 | 2404 | 0 | 0 | 2404 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
633 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-24 | 7 | 2 | 0 | 0 | 252 | 2142 | 0 | 0 | 2394 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
634 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-25 | 7 | 2 | 0 | 189 | 2058 | 168 | 0 | 0 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
635 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-26 | 7 | 2 | 1827 | 567 | 63 | 0 | 0 | 0 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
636 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | 7 | 2 | 756 | 0 | 0 | 0 | 441 | 0 | 1197 | 0.25 | 0.41667 |  |  | MOP
637 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-28 | 7 | 2 | 0 | 462 | 504 | 504 | 210 | 756 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
638 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-29 | 7 | 2 | 252 | 315 | 0 | 0 | 0 | 1890 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
639 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-30 | 7 | 2 | 0 | 2058 | 378 | 0 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
640 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-31 | 7 | 2 | 0 | 1050 | 1197 | 231 | 0 | 0 | 2478 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
641 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-01 | 8 | 2 | 252 | 840 | 0 | 0 | 0 | 1323 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
642 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-02 | 8 | 2 | 0 | 0 | 0 | 0 | 1438 | 987 | 2425 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
643 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-03 | 8 | 2 | 1575 | 0 | 0 | 0 | 861 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
644 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-04 | 8 | 2 | 1071 | 630 | 756 | 0 | 0 | 0 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
645 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-05 | 8 | 2 | 0 | 0 | 1512 | 945 | 0 | 0 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
646 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | 8 | 2 | 0 | 0 | 0 | 2436 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
647 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-07 | 8 | 2 | 0 | 0 | 0 | 1785 | 630 | 0 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
648 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-08 | 8 | 2 | 0 | 0 | 0 | 0 | 2000 | 420 | 2420 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
649 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-09 | 8 | 2 | 0 | 0 | 252 | 1113 | 1050 | 0 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
650 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-10 | 8 | 2 | 0 | 630 | 1806 | 0 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
651 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | 8 | 2 | 1953 | 504 | 0 | 0 | 0 | 0 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
652 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-12 | 8 | 2 | 882 | 504 | 252 | 167 | 609 | 0 | 2414 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
653 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-13 | 8 | 2 | 0 | 231 | 252 | 252 | 0 | 1701 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 8 Completed
654 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | 9 | 2 | 252 | 1134 | 0 | 0 | 0 | 1018 | 2404 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
655 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-15 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Due to festival
656 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-16 | 9 | 2 | 0 | 1113 | 819 | 504 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
657 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-17 | 9 | 2 | 189 | 2037 | 189 | 0 | 0 | 0 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
658 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-18 | 9 | 2 | 0 | 0 | 0 | 0 | 0 | 1512 | 1512 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
659 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-19 | 9 | 2 | 0 | 0 | 0 | 0 | 294 | 861 | 1155 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
660 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-20 | 9 | 2 | 63 | 0 | 0 | 0 | 1134 | 0 | 1197 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
661 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-21 | 9 | 2 | 2331 | 126 | 0 | 0 | 0 | 0 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
662 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-22 | 9 | 2 | 0 | 630 | 1806 | 0 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
663 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-23 | 9 | 2 | 0 | 1071 | 378 | 0 | 1050 | 0 | 2499 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
664 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-24 | 9 | 2 | 0 | 0 | 0 | 0 | 1890 | 420 | 2310 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
665 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-25 | 9 | 2 | 0 | 252 | 0 | 0 | 1722 | 441 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
666 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | 9 | 2 | 0 | 0 | 0 | 1407 | 0 | 0 | 1407 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
667 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-27 | 9 | 2 | 0 | 0 | 0 | 2377 | 0 | 0 | 2377 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
668 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-28 | 9 | 2 | 0 | 0 | 0 | 2331 | 126 | 0 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
669 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-29 | 9 | 2 | 0 | 0 | 702 | 696 | 0 | 1008 | 2406 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
670 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-30 | 9 | 2 | 252 | 768 | 0 | 0 | 0 | 1394 | 2414 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 9 Completed
671 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | 10 | 4 | 630 | 2279 | 630 | 210 | 609 | 0 | 4358 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
672 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-01 | 10 | 2 | 441 | 168 | 252 | 252 | 894 | 420 | 2427 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
673 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-02 | 10 | 4 | 0 | 0 | 0 | 0 | 3434 | 0 | 3434 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
674 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-03 | 10 | 2 | 1386 | 567 | 0 | 0 | 462 | 0 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
675 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-04 | 10 | 2 | 0 | 252 | 1995 | 189 | 0 | 0 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
676 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-05 | 10 | 4 | 1701 | 693 | 0 | 1050 | 504 | 0 | 3948 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
677 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-06 | 10 | 4 | 630 | 567 | 0 | 2242 | 0 | 0 | 3439 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
678 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-07 | 10 | 4 | 0 | 315 | 2331 | 1869 | 0 | 0 | 4515 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
679 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-08 | 10 | 2 | 0 | 1533 | 882 | 0 | 0 | 0 | 2415 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
680 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-09 | 10 | 2 | 294 | 378 | 0 | 0 | 0 | 1764 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 10 Completed
681 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-10 | 11 | 2 | 0 | 0 | 0 | 0 | 0 | 2436 | 2436 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
682 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | 11 | 2 | 0 | 0 | 0 | 0 | 1964 | 440 | 2404 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
683 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | 11 | 2 | 252 | 1386 | 0 | 0 | 0 | 819 | 2457 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
684 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | 11 | 4 | 0 | 1428 | 504 | 252 | 1554 | 0 | 3738 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
685 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-14 | 11 | 4 | 562 | 504 | 1475 | 504 | 1197 | 0 | 4242 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
686 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-15 | 11 | 4 | 1890 | 315 | 0 | 0 | 1071 | 0 | 3276 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
687 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-16 | 11 | 4 | 0 | 252 | 1806 | 1092 | 0 | 0 | 3150 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
688 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-17 | 11 | 4 | 1512 | 819 | 0 | 987 | 0 | 0 | 3318 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
689 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-18 | 11 | 2 | 945 | 0 | 0 | 0 | 1468 | 0 | 2413 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
690 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | 11 | 4 | 0 | 0 | 0 | 1092 | 168 | 1932 | 3192 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 11 Completed
691 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-20 | 12 | 4 | 252 | 1596 | 1554 | 630 | 0 | 315 | 4347 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
692 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-21 | 12 | 4 | 0 | 945 | 882 | 315 | 1176 | 0 | 3318 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
693 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-22 | 12 | 4 | 252 | 1491 | 0 | 0 | 756 | 861 | 3360 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
694 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-23 | 12 | 4 | 0 | 0 | 0 | 210 | 1134 | 2016 | 3360 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
695 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | 12 | 4 | 693 | 1407 | 903 | 0 | 504 | 861 | 4368 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
696 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-25 | 12 | 4 | 1890 | 546 | 0 | 0 | 609 | 1386 | 4431 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
697 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | 12 | 2 | 0 | 1386 | 504 | 441 | 0 | 0 | 2331 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
698 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-27 | 12 | 4 | 819 | 0 | 819 | 0 | 1428 | 0 | 3066 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
699 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-28 | 12 | 4 | 1575 | 630 | 1113 | 0 | 0 | 0 | 3318 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
700 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-29 | 12 | 4 | 0 | 189 | 945 | 1113 | 1092 | 0 | 3339 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 12 Completed
701 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-01 | 13 | 4 | 0 | 0 | 0 | 2205 | 672 | 420 | 3297 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
702 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-02 | 13 | 2 | 0 | 0 | 0 | 1176 | 1218 | 0 | 2394 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
703 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-03 | 13 | 4 | 189 | 567 | 1365 | 630 | 588 | 0 | 3339 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
704 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-04 | 13 | 4 | 2205 | 1113 | 1071 | 0 | 0 | 0 | 4389 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
705 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-05 | 13 | 4 | 252 | 882 | 0 | 0 | 2163 | 1113 | 4410 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
706 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | 13 | 4 | 1134 | 294 | 252 | 252 | 0 | 1386 | 3318 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
707 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-07 | 13 | 4 | 1134 | 336 | 252 | 210 | 0 | 1491 | 3423 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
708 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-08 | 13 | 4 | 504 | 1659 | 504 | 0 | 0 | 756 | 3423 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
709 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-09 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
710 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-10 | 13 | 4 | 0 | 1449 | 2646 | 567 | 0 | 0 | 4662 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | cycle 13 Completed
711 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | 14 | 4 | 0 | 0 | 0 | 2142 | 0 | 0 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
712 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | 14 | 4 | 0 | 1491 | 420 | 2331 | 0 | 0 | 4242 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
713 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-13 | 14 | 4 | 252 | 630 | 0 | 0 | 0 | 1323 | 2205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
714 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-14 | 14 | 2 | 0 | 0 | 1806 | 1455 | 0 | 0 | 3261 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
715 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-15 | 14 | 2 | 2200 | 0 | 0 | 0 | 0 | 0 | 2200 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
716 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-16 | 14 | 2 | 1008 | 0 | 0 | 0 | 1197 | 0 | 2205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
717 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-17 | 14 | 2 | 0 | 0 | 0 | 0 | 2248 | 0 | 2248 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
718 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-18 | 14 | 4 | 0 | 504 | 504 | 462 | 1533 | 987 | 3990 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
719 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-19 | 14 | 4 | 1386 | 0 | 0 | 0 | 819 | 2142 | 4347 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
720 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-20 | 14 | 2 | 0 | 2163 | 0 | 0 | 0 | 0 | 2163 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
721 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-21 | 14 | 4 | 1071 | 630 | 2079 | 609 | 0 | 0 | 4389 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | cycle 14 completed
722 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-02 | 31 | 2024-03-22 | 15 | 4 | 0 | 0 | 1764 | 2541 | 0 | 0 | 4305 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
723 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-03 | 31 | 2024-03-23 | 15 | 2 | 0 | 0 | 0 | 1512 | 1113 | 0 | 2625 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
724 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-24 | 15 | 2 | 0 | 630 | 861 | 546 | 0 | 0 | 2037 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
725 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-25 | 15 | 2 | 0 | 1806 | 378 | 0 | 0 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
726 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-26 | 15 | 4 | 2394 | 315 | 0 | 0 | 0 | 1638 | 4347 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
727 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-27 | 15 | 4 | 0 | 504 | 504 | 252 | 2252 | 819 | 4331 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
728 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-28 | 15 | 4 | 0 | 0 | 0 | 0 | 1722 | 2352 | 4074 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
729 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-29 | 15 | 4 | 630 | 1533 | 0 | 0 | 2100 | 315 | 4578 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
730 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-30 | 15 | 4 | 1134 | 504 | 1386 | 252 | 0 | 0 | 3276 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 15 completed
731 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-31 | 16 | 4 | 882 | 630 | 567 | 2147 | 0 | 0 | 4226 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
732 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-01 | 16 | 4 | 378 | 567 | 1176 | 1127 | 0 | 0 | 3248 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
733 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-02 | 16 | 2 | 1134 | 0 | 0 | 0 | 0 | 0 | 1134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
734 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-03 | 16 | 2 | 1008 | 0 | 0 | 0 | 126 | 0 | 1134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
735 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-04 | 16 | 2 | 0 | 0 | 0 | 1239 | 966 | 0 | 2205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
736 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-05 | 16 | 2 | 0 | 0 | 0 | 0 | 1764 | 420 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
737 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-06 | 16 | 2 | 0 | 0 | 126 | 693 | 1376 | 0 | 2195 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
738 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-07 | 16 | 2 | 0 | 0 | 1367 | 704 | 0 | 0 | 2071 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
739 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-08 | 16 | 2 | 0 | 1113 | 1071 | 0 | 0 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
740 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-09 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
741 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-10 | 16 | 2 | 0 | 1109 | 0 | 0 | 0 | 0 | 1109 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
742 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-11 | 16 | 2 | 252 | 812 | 0 | 0 | 0 | 1134 | 2198 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
743 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-12 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 2373 | 2373 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
744 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-13 | 16 | 2 | 0 | 315 | 252 | 210 | 0 | 1365 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
745 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-14 | 16 | 4 | 882 | 903 | 0 | 0 | 1428 | 1008 | 4221 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | cycle 16 completed
746 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-15 | 17 | 2 | 0 | 1323 | 504 | 315 | 0 | 0 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
747 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-16 | 17 | 4 | 1701 | 378 | 1197 | 609 | 0 | 0 | 3885 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
748 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-17 | 17 | 4 | 0 | 315 | 1743 | 2184 | 0 | 0 | 4242 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
749 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-18 | 17 | 4 | 441 | 630 | 63 | 1974 | 0 | 0 | 3108 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
750 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-19 | 17 | 4 | 1890 | 462 | 1575 | 0 | 189 | 0 | 4116 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
751 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-20 | 17 | 2 | 0 | 1050 | 0 | 0 | 1099 | 0 | 2149 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
752 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-21 | 17 | 2 | 252 | 0 | 0 | 0 | 819 | 0 | 1071 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
753 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-22 | 17 | 4 | 1071 | 504 | 0 | 0 | 0 | 1512 | 3087 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
754 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-23 | 17 | 4 | 1071 | 630 | 378 | 0 | 0 | 1071 | 3150 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
755 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-24 | 17 | 4 | 0 | 504 | 504 | 504 | 0 | 609 | 2121 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
756 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-25 | 17 | 4 | 0 | 0 | 0 | 0 | 0 | 2079 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
757 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-04 | 30 | 2024-04-26 | 17 | 4 | 0 | 1092 | 0 | 0 | 0 | 0 | 1092 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
758 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-05 | 30 | 2024-04-27 | 17 | 2 | 0 | 1134 | 0 | 0 | 1072 | 0 | 2206 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
759 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-06 | 30 | 2024-04-28 | 18 | 2 | 0 | 0 | 0 | 0 | 1722 | 420 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
760 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-07 | 30 | 2024-04-29 | 18 | 2 | 0 | 189 | 819 | 252 | 0 | 0 | 1260 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
761 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-07 | 30 | 2024-04-30 | 18 | 2 | 0 | 0 | 1197 | 987 | 0 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
762 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-01 | 18 | 2 | 0 | 0 | 441 | 966 | 672 | 0 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
763 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-02 | 18 | 2 | 0 | 0 | 0 | 2080 | 0 | 0 | 2080 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
764 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-03 | 18 | 2 | 0 | 0 | 1134 | 882 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
765 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-04 | 18 | 2 | 630 | 567 | 861 | 0 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
766 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-05 | 18 | 2 | 1764 | 0 | 0 | 0 | 357 | 0 | 2121 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
767 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-06 | 18 | 2 | 0 | 1617 | 378 | 0 | 210 | 0 | 2205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
768 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-07 | 18 | 2 | 252 | 693 | 0 | 0 | 0 | 1197 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
769 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | 18 | 2 | 0 | 0 | 0 | 0 | 0 | 2016 | 2016 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
770 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | 18 | 2 | 0 | 504 | 504 | 462 | 0 | 567 | 2037 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
771 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
772 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-11 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
773 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-12 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
774 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
775 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-14 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
776 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-15 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
777 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-16 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
778 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-17 | 18 | 2 | 1017 | 0 | 0 | 0 | 0 | 0 | 1017 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
779 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-18 | 18 | 2 | 0 | 1110 | 0 | 0 | 0 | 0 | 1110 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
780 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-19 | 18 | 2 | 0 | 0 | 0 | 0 | 0 | 1143 | 1143 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
781 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-20 | 18 | 2 | 0 | 0 | 0 | 0 | 0 | 2143 | 2143 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
782 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-21 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
783 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-22 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
784 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-23 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
785 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-24 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
786 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-25 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
787 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-26 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
788 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-27 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
789 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-28 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
790 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-29 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
791 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-30 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
792 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
793 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-01 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
794 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-02 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
795 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-03 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
796 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-04 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
797 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-05 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
798 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-06 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
799 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-07 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
800 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-08 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
801 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-09 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
802 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-10 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
803 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-11 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
804 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-12 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
805 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-13 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
806 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-14 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
807 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-15 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
808 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-16 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-17 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
810 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
811 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-19 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
812 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-20 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
813 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-21 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
814 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-22 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
815 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-23 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
816 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-24 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
817 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-25 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
818 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-26 | [8 empty] | 0
819 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-27 | [8 empty] | 0
820 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-28 | [8 empty] | 0
821 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-29 | [8 empty] | 0
822 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-30 | [8 empty] | 0
823 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-01 | [8 empty] | 0
824 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-02 | [8 empty] | 0
825 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-03 | [8 empty] | 0
826 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-04 | [8 empty] | 0
827 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-05 | [8 empty] | 0
828 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-06 | [8 empty] | 0
829 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-07 | [8 empty] | 0
830 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-08 | [8 empty] | 0
831 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-09 | [8 empty] | 0
832 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-10 | [8 empty] | 0
833 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-11 | [8 empty] | 0
834 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-12 | [8 empty] | 0
835 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-13 | [8 empty] | 0
836 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-14 | [8 empty] | 0
837 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-15 | [8 empty] | 0
838 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-16 | [8 empty] | 0
839 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-17 | [8 empty] | 0
840 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-18 | [8 empty] | 0
841 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-19 | [8 empty] | 0
842 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-20 | [8 empty] | 0
843 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-21 | [8 empty] | 0
844 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-22 | [8 empty] | 0
845 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-23 | [8 empty] | 0
846 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-24 | [8 empty] | 0
847 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-25 | [8 empty] | 0
848 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-26 | [8 empty] | 0
849 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-27 | [8 empty] | 0
850 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-28 | [8 empty] | 0
851 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-29 | [8 empty] | 0
852 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-30 | [8 empty] | 0
853 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-31 | [8 empty] | 0
854 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-01 | [8 empty] | 0
855 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-02 | [8 empty] | 0
856 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-03 | [8 empty] | 0
857 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-04 | [8 empty] | 0
858 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-05 | [8 empty] | 0
859 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-06 | [8 empty] | 0
860 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | [8 empty] | 0
861 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-08 | [8 empty] | 0
862 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-09 | [8 empty] | 0
863 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-10 | [8 empty] | 0
864 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-11 | [8 empty] | 0
865 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | [8 empty] | 0
866 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-13 | [8 empty] | 0
867 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-14 | 1 | 2 | 0 | 0 | 0 | 0 | 1764 | 294 | 2058 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
868 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-15 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
869 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-16 | 1 | 2 | 0 | 0 | 0 | 0 | 1722 | 420 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
870 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-17 | 1 | 2 | 0 | 0 | 0 | 0 | 1143 | 0 | 1143 | 0.25 | 0.41667 |  |  | MOP
871 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-18 | [8 empty] | 0
872 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | [8 empty] | 0
873 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-20 | [8 empty] | 0
874 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-21 | [8 empty] | 0
875 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-22 | [8 empty] | 0
876 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-23 | [8 empty] | 0
877 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-24 | [8 empty] | 0
878 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-25 | [8 empty] | 0
879 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-26 | [8 empty] | 0
880 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-27 | [8 empty] | 0
881 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-28 | [8 empty] | 0
882 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-29 | [8 empty] | 0
883 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-30 | [8 empty] | 0
884 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-31 | [8 empty] | 0
885 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-01 | [8 empty] | 0
886 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-02 | [8 empty] | 0
887 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-03 | [8 empty] | 0
888 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-04 | [8 empty] | 0
889 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-05 | [8 empty] | 0
890 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-06 | [8 empty] | 0
891 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-07 | [8 empty] | 0
892 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-08 | [8 empty] | 0
893 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-09 | [8 empty] | 0
894 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-10 | [8 empty] | 0
895 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-11 | [8 empty] | 0
896 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-12 | [8 empty] | 0
897 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-13 | [8 empty] | 0
898 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-14 | [8 empty] | 0
899 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-15 | [8 empty] | 0
900 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-16 | [8 empty] | 0
901 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-17 | [8 empty] | 0
902 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-18 | [8 empty] | 0
903 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-19 | [8 empty] | 0
904 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-20 | [8 empty] | 0
905 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-21 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 2142 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
906 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-22 | 1 | 2 | 252 | 1533 | 0 | 0 | 0 | 252 | 2037 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
907 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-23 | 1 | 2 | 0 | 1533 | 567 | 0 | 0 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
908 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-24 | [8 empty] | 0 | [6 empty] | Due to Rain
909 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-25 | 1 | 2 | 0 | 0 | 0 | 2113 | 0 | 0 | 2113 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
910 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-26 | 1 | 2 | 0 | 0 | 513 | 1443 | 0 | 0 | 1956 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
911 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-27 | 1 | 2 | 0 | 0 | 0 | 933 | 0 | 0 | 933 | 0.25 | 0.41667 |  |  | MOP |  | MCS Pipe Damaged
912 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-28 | 1 | 2 | 0 | 0 | 0 | 2110 | 0 | 0 | 2110 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
913 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-29 | 1 | 2 | 0 | 0 | 1112 | 1026 | 0 | 0 | 2138 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
914 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-30 | 1 | 2 | 0 | 0 | 1112 | 984 | 0 | 0 | 2096 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
915 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-01 | [8 empty] | 0 | [6 empty] | Labour taken weekoff
916 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-02 | [8 empty] | 0 | [6 empty] | Due to Rain
917 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | [8 empty] | 0 | [6 empty] | Due to Rain
918 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-04 | [8 empty] | 0 | [6 empty] | Due to Rain
919 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-05 | [8 empty] | 0 | [6 empty] | Due to Rain
920 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-06 | [8 empty] | 0 | [6 empty] | Due to Rain
921 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-07 | [8 empty] | 0 | [6 empty] | Due to Rain
922 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-08 | [8 empty] | 0 | [6 empty] | Due to Rain
923 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-09 | [8 empty] | 0 | [6 empty] | Due to Rain
924 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-10 | [8 empty] | 0 | [6 empty] | Due to Rain
925 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-11 | [8 empty] | 0 | [6 empty] | Due to Rain
926 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-12 | [8 empty] | 0 | [6 empty] | Due to Rain
927 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-13 | [8 empty] | 0 | [6 empty] | Due to Rain
928 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-14 | [8 empty] | 0 | [6 empty] | Due to Rain
929 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-15 | [8 empty] | 0
930 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-16 | [8 empty] | 0
931 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-17 | [8 empty] | 0
932 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-18 | [8 empty] | 0
933 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-19 | [8 empty] | 0
934 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-20 | [8 empty] | 0
935 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-21 | [8 empty] | 0
936 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-22 | [8 empty] | 0
937 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-23 | [8 empty] | 0
938 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | [8 empty] | 0
939 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | [8 empty] | 0
940 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-26 | [8 empty] | 0
941 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-27 | [8 empty] | 0
942 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-28 | [8 empty] | 0
943 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | [8 empty] | 0
944 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-30 | [8 empty] | 0
945 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | [8 empty] | 0
946 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-01 | [8 empty] | 0
947 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | [8 empty] | 0
948 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-03 | [8 empty] | 0
949 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-04 | [8 empty] | 0
950 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | [8 empty] | 0
951 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-06 | [8 empty] | 0
952 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-07 | [8 empty] | 0
953 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-08 | [8 empty] | 0
954 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-09 | [8 empty] | 0
955 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-10 | 1 | 2 | 1134 | 0 | 0 | 0 | 966 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
956 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-11 | 1 | 2 | 1054 | 0 | 0 | 0 | 0 | 0 | 1054 | 0.25 | 0.41667 |  |  | MOP
957 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-12 | 1 | 2 | 0 | 1124 | 980 | 0 | 0 | 0 | 2104 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
958 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-13 | 1 | 2 | 0 | 1024 | 896 | 0 | 0 | 0 | 1920 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
959 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-14 | 1 | 2 | 126 | 1120 | 868 | 0 | 0 | 0 | 2114 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
960 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-15 | 2 | 2 | 1134 | 0 | 0 | 0 | 966 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
961 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-16 | [8 empty] | 0 | [6 empty] | Due to rain Module cleaning stop
962 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-17 | [8 empty] | 0 | [6 empty] | Due to rain Module cleaning stop
963 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | 2 | 2 | 0 | 0 | 840 | 0 | 1120 | 0 | 1960 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
964 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-19 | 2 | 2 | 0 | 916 | 0 | 0 | 0 | 0 | 916 | 0.25 | 0.41667 |  |  | MOP
965 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-20 | 2 | 2 | 988 | 0 | 0 | 0 | 0 | 0 | 988 | 0.25 | 0.41667 |  |  | MOP
966 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-21 | 2 | 2 | 0 | 0 | 0 | 0 | 1008 | 0 | 1008 | 0.25 | 0.41667 |  |  | MOP
967 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-22 | 2 | 2 | 1386 | 0 | 0 | 0 | 756 | 0 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
968 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-23 | 2 | 2 | 0 | 504 | 630 | 210 | 672 | 0 | 2016 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
969 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-24 | 2 | 2 | 0 | 0 | 0 | 940 | 0 | 1120 | 2060 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
970 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-25 | 2 | 2 | 0 | 634 | 0 | 0 | 0 | 1340 | 1974 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
971 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-26 | 2 | 2 | 0 | 984 | 514 | 0 | 0 | 688 | 2186 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
972 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-27 | 2 | 2 | 0 | 0 | 1197 | 861 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
973 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-28 | 2 | 2 | 0 | 0 | 0 | 1995 | 0 | 0 | 1995 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
974 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-29 | 2 | 2 | 0 | 0 | 0 | 2034 | 0 | 0 | 2034 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
975 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-30 | 2 | 2 | 0 | 0 | 2142 | 0 | 0 | 0 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
976 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-01 | 2 | 2 | 1543 | 0 | 0 | 0 | 0 | 0 | 1543 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
977 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-02 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | not done due to rain
978 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-03 | 2 | 2 | 0 | 0 | 1012 | 0 | 0 | 0 | 1012 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
979 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-04 | 2 | 2 | 0 | 988 | 0 | 1024 | 0 | 0 | 2012 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
980 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-05 | 2 | 2 | 1046 | 0 | 985 | 0 | 0 | 0 | 2031 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
981 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-06 | 2 | 2 | 252 | 252 | 0 | 0 | 0 | 1512 | 2016 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 2 Completed
982 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-07 | 3 | 2 | 0 | 0 | 0 | 0 | 1344 | 735 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
983 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-08 | 3 | 2 | 0 | 0 | 0 | 0 | 2058 | 0 | 2058 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
984 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-09 | 3 | 2 | 882 | 0 | 0 | 0 | 1155 | 0 | 2037 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
985 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-10 | 3 | 2 | 1449 | 630 | 0 | 0 | 0 | 0 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
986 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-11 | 3 | 2 | 441 | 567 | 1050 | 0 | 0 | 0 | 2058 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
987 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-12 | 3 | 2 | 315 | 756 | 1008 | 0 | 0 | 0 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
988 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-13 | 3 | 2 | 1523 | 441 | 126 | 0 | 0 | 0 | 2090 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
989 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-14 | 3 | 2 | 1008 | 0 | 0 | 0 | 1134 | 0 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
990 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-15 | 3 | 2 | 0 | 504 | 504 | 462 | 0 | 672 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
991 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-16 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 2079 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
992 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-17 | 3 | 4 | 252 | 1869 | 0 | 0 | 0 | 1239 | 3360 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
993 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-18 | 3 | 4 | 0 | 126 | 2845 | 294 | 0 | 0 | 3265 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
994 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-19 | 3 | 4 | 0 | 0 | 1201 | 2094 | 0 | 0 | 3295 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 3 Completed
995 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-20 | 4 | 4 | 0 | 0 | 1342 | 2024 | 0 | 0 | 3366 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
996 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-21 | 4 | 4 | 0 | 252 | 1436 | 1302 | 252 | 0 | 3242 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
997 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-22 | 4 | 2 | 324 | 630 | 819 | 252 | 252 | 0 | 2277 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
998 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-23 | 4 | 4 | 1250 | 1407 | 0 | 0 | 0 | 378 | 3035 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
997 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-24 | 4 | 4 | 1204 | 0 | 0 | 0 | 294 | 1743 | 3241 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
998 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-25 | 4 | 4 | 0 | 1242 | 0 | 0 | 2113 | 0 | 3355 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
999 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-26 | 4 | 2 | 0 | 0 | 0 | 0 | 1024 | 0 | 1024 | 0.25 | 0.41667 |  |  | MOP
1000 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-27 | 4 | 4 | 0 | 0 | 1038 | 252 | 2058 | 0 | 3348 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1001 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-28 | 4 | 4 | 2016 | 0 | 0 | 1024 | 189 | 0 | 3229 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1002 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-29 | 4 | 4 | 252 | 569 | 1113 | 0 | 1234 | 0 | 3168 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1003 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-30 | 4 | 4 | 1324 | 1824 | 0 | 0 | 0 | 0 | 3148 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 4 Completed
1004 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-31 | 5 | 4 | 0 | 2145 | 1345 | 0 | 0 | 0 | 3490 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1005 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-01 | 5 | 4 | 504 | 504 | 504 | 462 | 1428 | 168 | 3570 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1006 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-02 | 5 | 4 | 0 | 0 | 252 | 252 | 0 | 2646 | 3150 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1007 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-03 | 5 | 4 | 252 | 1785 | 0 | 0 | 0 | 1197 | 3234 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1008 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-04 | 5 | 4 | 252 | 1386 | 504 | 252 | 0 | 756 | 3150 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1009 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-05 | 5 | 2 | 0 | 1239 | 378 | 504 | 0 | 0 | 2121 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1010 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | 5 | 2 | 0 | 252 | 756 | 609 | 630 | 0 | 2247 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1011 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-07 | 5 | 4 | 0 | 0 | 0 | 2037 | 1050 | 0 | 3087 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1012 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | 5 | 4 | 0 | 0 | 1024 | 2101 | 0 | 0 | 3125 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1013 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-09 | 5 | 4 | 0 | 0 | 1743 | 378 | 1050 | 0 | 3171 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1014 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-10 | 5 | 4 | 1197 | 567 | 315 | 0 | 1050 | 0 | 3129 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 5 Completed
1015 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-11 | 6 | 2 | 1134 | 504 | 0 | 0 | 609 | 0 | 2247 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1016 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-12 | 6 | 2 | 0 | 504 | 504 | 462 | 0 | 672 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1017 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-13 | 6 | 4 | 630 | 0 | 0 | 0 | 1428 | 1124 | 3182 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1018 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-14 | 6 | 2 | 1764 | 0 | 252 | 0 | 0 | 0 | 2016 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1019 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-15 | 6 | 4 | 693 | 630 | 882 | 0 | 0 | 1134 | 3339 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1020 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-16 | 6 | 4 | 252 | 1071 | 0 | 892 | 0 | 945 | 3160 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1021 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-17 | 6 | 4 | 430 | 1113 | 378 | 609 | 630 | 0 | 3160 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1022 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-18 | 6 | 4 | 0 | 0 | 1197 | 1113 | 0 | 0 | 2310 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1023 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-19 | 6 | 4 | 0 | 0 | 0 | 2100 | 0 | 1124 | 3224 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1024 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-20 | 6 | 2 | 0 | 0 | 0 | 2184 | 0 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1025 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-21 | 6 | 2 | 0 | 0 | 1323 | 630 | 0 | 252 | 2205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1026 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-22 | 6 | 4 | 0 | 1323 | 504 | 252 | 1113 | 0 | 3192 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 6 Completed
1027 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-23 | 7 | 4 | 252 | 1092 | 0 | 1197 | 0 | 693 | 3234 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1028 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-24 | 7 | 2 | 0 | 0 | 0 | 0 | 0 | 2164 | 2164 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1029 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | 7 | 2 | 0 | 0 | 0 | 0 | 2204 | 0 | 2204 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1030 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-26 | 7 | 2 | 0 | 0 | 0 | 0 | 2163 | 0 | 2163 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1031 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-27 | 7 | 4 | 0 | 504 | 504 | 462 | 1420 | 315 | 3205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1032 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | 7 | 4 | 693 | 567 | 861 | 0 | 0 | 2071 | 4192 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1033 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-29 | 7 | 4 | 252 | 756 | 1134 | 0 | 0 | 1197 | 3339 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1034 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-30 | 7 | 4 | 1638 | 1123 | 0 | 0 | 609 | 0 | 3370 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1035 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-31 | 7 | 4 | 423 | 420 | 630 | 0 | 1638 | 0 | 3111 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1036 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-01 | 7 | 4 | 1071 | 0 | 1945 | 168 | 0 | 0 | 3184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1037 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-02 | 7 | 4 | 1824 | 0 | 1264 | 0 | 252 | 0 | 3340 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 7 Completed
1038 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-03 | 8 | 4 | 945 | 126 | 0 | 2184 | 0 | 0 | 3255 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1039 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-04 | 8 | 2 | 0 | 804 | 1323 | 0 | 0 | 0 | 2127 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1040 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-05 | 8 | 2 | 0 | 0 | 1512 | 693 | 0 | 0 | 2205 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1041 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-06 | 8 | 2 | 0 | 0 | 441 | 609 | 0 | 0 | 1050 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1042 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-07 | 8 | 2 | 0 | 2153 | 0 | 0 | 0 | 0 | 2153 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1043 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-08 | 8 | 2 | 252 | 0 | 0 | 0 | 0 | 819 | 1071 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1044 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-09 | 8 | 2 | 0 | 0 | 0 | 0 | 0 | 1008 | 1008 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1045 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-10 | 8 | 4 | 0 | 1123 | 0 | 0 | 0 | 2142 | 3265 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1046 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-11 | 8 | 4 | 824 | 946 | 0 | 1424 | 0 | 0 | 3194 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1047 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-12 | 8 | 4 | 0 | 1244 | 252 | 1684 | 0 | 0 | 3180 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1048 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-13 | 8 | 2 | 0 | 2146 | 0 | 0 | 0 | 0 | 2146 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1049 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-14 | 8 | 2 | 0 | 1342 | 842 | 0 | 0 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1050 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-15 | 8 | 2 | 1846 | 252 | 0 | 0 | 0 | 0 | 2098 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1051 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-16 | 8 | 4 | 1134 | 0 | 0 | 0 | 2164 | 0 | 3298 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 8 Completed
1052 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-17 | 9 | 4 | 1204 | 0 | 0 | 0 | 0 | 2240 | 3444 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1053 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-18 | 9 | 4 | 567 | 945 | 0 | 0 | 483 | 1134 | 3129 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1054 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-19 | 9 | 4 | 567 | 1232 | 0 | 0 | 1554 | 0 | 3353 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1055 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-20 | 9 | 4 | 1071 | 1365 | 630 | 252 | 0 | 0 | 3318 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1056 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-21 | 9 | 2 | 0 | 0 | 1008 | 1176 | 0 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1057 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-22 | 9 | 2 | 0 | 0 | 0 | 2134 | 0 | 1134 | 3268 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1058 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-23 | 9 | 2 | 0 | 1024 | 0 | 1244 | 0 | 0 | 2268 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1059 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-24 | 9 | 2 | 0 | 0 | 0 | 2100 | 0 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1060 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-25 | 9 | 4 | 0 | 1134 | 1386 | 630 | 0 | 0 | 3150 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1061 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-26 | 9 | 4 | 2394 | 0 | 630 | 0 | 0 | 0 | 3024 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1062 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-27 | 9 | 2 | 1230 | 0 | 0 | 0 | 0 | 0 | 1230 | 0.25 | 0.41667 |  |  | MOP |  | Due to festival labours taken weekoff/Cycle 9 completed
1063 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-28 | 10 | 4 | 1701 | 0 | 0 | 252 | 745 | 420 | 3118 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1064 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-01 | 10 | 2 | 0 | 0 | 0 | 0 | 2134 | 0 | 2134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1065 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-02 | 10 | 2 | 0 | 0 | 0 | 0 | 1113 | 0 | 1113 |  |  | 0.60417 | 0.77083 | MOP
1066 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-03 | 10 | 4 | 0 | 252 | 252 | 0 | 1092 | 1743 | 3339 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1067 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-04 | 10 | 4 | 252 | 504 | 504 | 252 | 1234 | 504 | 3250 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1068 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-05 | 10 | 4 | 0 | 945 | 1824 | 0 | 0 | 0 | 2769 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1069 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-06 | 10 | 4 | 0 | 1120 | 1449 | 252 | 0 | 0 | 2821 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1070 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-07 | 10 | 4 | 0 | 0 | 315 | 1743 | 0 | 2079 | 4137 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1071 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-08 | 10 | 4 | 2234 | 1124 | 0 | 0 | 0 | 0 | 3358 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1072 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-09 | 10 | 2 | 0 | 2144 | 0 | 0 | 0 | 0 | 2144 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1073 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-10 | 10 | 2 | 0 | 0 | 2343 | 0 | 0 | 0 | 2343 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1074 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-11 | 10 | 4 | 0 | 0 | 252 | 2724 | 0 | 0 | 2976 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 10 Completed
1075 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-12 | 11 | 2 | 0 | 0 | 2121 | 0 | 0 | 0 | 2121 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1076 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-13 | 11 | 4 | 0 | 0 | 820 | 2346 | 0 | 0 | 3166 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1077 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-14 | 11 | 2 | 1764 | 0 | 0 | 0 | 315 | 0 | 2079 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1078 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-15 | 11 | 4 | 252 | 1449 | 0 | 0 | 1176 | 378 | 3255 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1079 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-16 | 11 | 2 | 0 | 1352 | 504 | 252 | 0 | 0 | 2108 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1080 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-17 | 11 | 2 | 2346 | 0 | 0 | 0 | 0 | 0 | 2346 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1081 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-18 | 11 | 4 | 1260 | 567 | 0 | 0 | 693 | 0 | 2520 | 0.25 | 0.41667 |  |  | MOP
1082 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-19 | 11 | 2 | 252 | 714 | 252 | 0 | 0 | 1071 | 2289 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1083 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-20 | 11 | 2 | 0 | 504 | 504 | 462 | 0 | 1176 | 2646 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1084 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 11 | 4 | 2016 | 1124 | 0 | 0 | 0 | 0 | 3140 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1085 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-22 | 11 | 4 | 0 | 630 | 1449 | 0 | 1320 | 0 | 3399 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1086 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-23 | 11 | 2 | 2124 | 0 | 0 | 0 | 0 | 0 | 2124 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1087 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-24 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | not done due to rain
1088 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-25 | 12 | 2 | 0 | 2120 | 0 | 0 | 0 | 0 | 2120 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1089 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-26 | 12 | 4 | 1214 | 2134 | 0 | 0 | 0 | 0 | 3348 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1090 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | 12 | 4 | 0 | 684 | 252 | 0 | 2234 | 0 | 3170 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1091 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-28 | 12 | 4 | 0 | 1894 | 0 | 0 | 1324 | 0 | 3218 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1092 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 12 | 4 | 0 | 0 | 1142 | 0 | 2134 | 0 | 3276 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1093 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | 12 | 0 | [6 empty] | 0 | [6 empty] | Due to festival labours taken weekoff
1094 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | 12 | 4 | 0 | 1324 | 1134 | 945 | 0 | 0 | 3403 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1095 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | 12 | 2 | 1320 | 0 | 0 | 0 | 0 | 0 | 1320 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1096 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 12 | 2 | 0 | 1743 | 378 | 0 | 0 | 0 | 2121 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1097 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | 12 | 2 | 252 | 315 | 0 | 0 | 0 | 567 | 1134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1098 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 12 | 0 | [6 empty] | 0 | [6 empty] | not done due to rain
1099 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 12 | 0 | [6 empty] | 0 | [6 empty] | not done due to rain
1100 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 12 | 4 | 2342 | 0 | 0 | 0 | 0 | 1234 | 3576 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1101 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | 12 | 4 | 1164 | 2434 | 0 | 0 | 0 | 0 | 3598 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1102 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | 12 | 2 | 0 | 0 | 1224 | 0 | 1110 | 0 | 2334 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | Cycle 12 Completed
1103 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | 13 | 4 | 1224 | 544 | 424 | 0 | 0 | 0 | 2192 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1104 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 13 | 2 | 1434 | 682 | 0 | 0 | 0 | 0 | 2116 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1105 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 13 | 2 | 1646 | 0 | 0 | 0 | 686 | 0 | 2332 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1106 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | 13 | 2 | 0 | 0 | 1454 | 824 | 0 | 0 | 2278 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1107 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 13 | 2 | 868 | 1232 | 0 | 0 | 0 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1108 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | 13 | 2 | 0 | 0 | 3224 | 0 | 0 | 0 | 3224 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1109 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | 13 | 2 | 0 | 2324 | 0 | 0 | 0 | 0 | 2324 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1110 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | 13 | 2 | 0 | 0 | 2268 | 0 | 0 | 0 | 2268 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1111 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | 13 | 2 | 0 | 0 | 252 | 1980 | 0 | 0 | 2232 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1112 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 2224 | 2224 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1112 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 13 | 2 | 0 | 0 | 0 | 0 | 2134 | 0 | 2134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1113 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 13 | 2 | 0 | 0 | 1224 | 0 | 0 | 0 | 1224 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1114 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 13 | 2 | 1124 | 0 | 0 | 0 | 0 | 0 | 1124 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1115 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 13 | 2 | 0 | 0 | 0 | 0 | 2134 | 0 | 2134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1116 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | 13 | 2 | 0 | 2245 | 0 | 0 | 0 | 0 | 2245 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1117 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 14 | 2 | 0 | 0 | 2320 | 0 | 0 | 0 | 2320 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1118 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | 14 | 4 | 0 | 0 | 0 | 2342 | 0 | 1104 | 3446 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1119 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 14 | 4 | 0 | 0 | 624 | 2546 | 0 | 0 | 3170 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1120 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | 14 | 4 | 0 | 0 | 0 | 0 | 3224 | 0 | 3224 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1121 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | not done due to rain
1122 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 14 | 2 | 2324 | 0 | 0 | 0 | 0 | 0 | 2324 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1123 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 14 | 2 | 0 | 2246 | 0 | 0 | 0 | 0 | 2246 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1124 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | 14 | 2 | 0 | 0 | 1134 | 0 | 0 | 0 | 1134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1125 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1126 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 14 | 4 | 0 | 3212 | 0 | 1110 | 0 | 0 | 4322 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1127 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 14 | 2 | 0 | 0 | 0 | 0 | 1344 | 684 | 2028 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1128 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not done due to labour taken weeklyoff
1129 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 14 | 2 | 0 | 2264 | 0 | 0 | 0 | 0 | 2264 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1130 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 14 | 2 | 1242 | 0 | 0 | 0 | 942 | 0 | 2184 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1131 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 14 | 2 | 2246 | 0 | 0 | 0 | 0 | 0 | 2246 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1132 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | 14 | 2 | 1024 | 504 | 504 | 252 | 0 | 0 | 2284 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP |  | cycle 14 completed
1133 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 15 | 2 | 0 | 735 | 1113 | 252 | 0 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1134 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | 15 | 2 | 1024 | 1232 | 0 | 0 | 0 | 0 | 2256 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1135 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | 15 | 2 | 252 | 0 | 0 | 0 | 1924 | 0 | 2176 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1136 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | 15 | 2 | 1624 | 525 | 0 | 0 | 0 | 0 | 2149 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1137 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | 15 | 2 | 0 | 0 | 1638 | 504 | 0 | 0 | 2142 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1138 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | 15 | 2 | 0 | 0 | 0 | 2324 | 0 | 0 | 2324 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1139 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | 15 | 2 | 0 | 0 | 0 | 1324 | 0 | 0 | 1324 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1140 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | 15 | 2 | 0 | 0 | 0 | 2132 | 0 | 0 | 2132 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1141 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not Done due to Rain
1142 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not Done due to Rain
1143 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | 15 | 2 | 0 | 0 | 1324 | 0 | 0 | 0 | 1324 |  |  | 0.60417 | 0.77083 | MOP
1144 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | 15 | 2 | 0 | 0 | 1320 | 0 | 0 | 0 | 1320 |  |  | 0.60417 | 0.77083 | MOP
1145 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | 15 | 2 | 0 | 0 | 1244 | 0 | 0 | 0 | 1244 |  |  | 0.60417 | 0.77083 | MOP
1146 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not Done due to Rain
1147 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not Done due to Rain
1148 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1149 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not Done due to Rain
1150 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | 15 | 2 | 1324 | 0 | 0 | 0 | 0 | 0 | 1324 |  |  | 0.60417 | 0.77083 | MOP
1151 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | 15 | 2 | 1120 | 0 | 0 | 0 | 0 | 0 | 1120 | 0.25 | 0.41667
1152 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | 15 | 2 | 0 | 2120 | 0 | 0 | 0 | 0 | 2120 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1153 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | 15 | 2 | 0 | 2246 | 0 | 0 | 0 | 0 | 2246 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1154 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | 15 | 2 | 0 | 2186 | 0 | 0 | 0 | 0 | 2186 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1155 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | 15 | 2 | 0 | 1214 | 1024 | 0 | 0 | 0 | 2238 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1156 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 16 | 2 | 0 | 0 | 0 | 1232 | 0 | 0 | 1232 | 0.25 | 0.41667
1157 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | 16 | [7 empty] | 0
1158 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 16 | 2 | 1424 | 252 | 624 | 0 | 0 | 0 | 2300 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1159 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 16 | 2 | 0 | 0 | 0 | 2132 | 0 | 0 | 2132 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1160 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 16 | 2 | 0 | 0 | 0 | 2234 | 0 | 0 | 2234 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1161 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 16 | 2 | 0 | 0 | 2424 | 0 | 0 | 0 | 2424 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1162 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 16 | 2 | 0 | 1212 | 0 | 0 | 0 | 0 | 1212 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1163 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 16 | 2 | 0 | 2240 | 0 | 0 | 0 | 0 | 2240 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1164 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1165 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | Not Done due to Rain
1166 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 16 | 2 | 0 | 0 | 1214 | 0 | 0 | 0 | 1214 | 0.25 | 0.41667
1167 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 16 | 2 | 0 | 0 | 1124 | 0 | 0 | 0 | 1124 | 0.25 | 0.41667
1168 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 16 | 2 | 0 | 2320 | 0 | 0 | 0 | 0 | 2320 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1169 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 16 | 2 | 2100 | 0 | 0 | 0 | 0 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1170 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 16 | 2 | 0 | 0 | 2134 | 0 | 0 | 0 | 2134 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1171 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 16 | 2 | 0 | 0 | 0 | 2232 | 0 | 0 | 2232 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1172 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 16 | 2 | 0 | 0 | 0 | 0 | 2104 | 0 | 2104 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1173 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 16 | 2 | 0 | 0 | 1124 | 0 | 0 | 0 | 1124 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1174 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 16 | 2 | 0 | 2232 | 0 | 0 | 0 | 0 | 2232 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1175 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 16 | 2 | 0 | 0 | 0 | 2263 | 0 | 0 | 2263 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1176 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1177 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 17 | 2 | 0 | 0 | 0 | 0 | 2100 | 0 | 2100 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1178 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 17 | 2 | 0 | 0 | 2332 | 0 | 0 | 0 | 2332 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1179 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 17 | 2 | 0 | 0 | 0 | 2123 | 0 | 0 | 2123 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1180 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1181 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 17 | 2 | 0 | 2342 | 0 | 0 | 0 | 0 | 2342 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1182 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 17 | 2 | 0 | 0 | 2323 | 0 | 0 | 0 | 2323 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1183 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 17 | 2 | 0 | 0 | 0 | 0 | 2124 | 0 | 2124 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1184 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 17 | 2 | 0 | 0 | 0 | 0 | 0 | 2234 | 2234 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1185 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 17 | 2 | 2120 | 0 | 0 | 0 | 0 | 0 | 2120 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1186 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 17 | 2 | 2234 | 0 | 0 | 0 | 0 | 0 | 2234 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1187 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 17 | 2 | 0 | 2340 | 0 | 0 | 0 | 0 | 2340 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1188 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 17 | 2 | 0 | 0 | 0 | 0 | 2324 | 0 | 2324 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
1189 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 17 | 2 | 0 | 0 | 2120 | 0 | 0 | 0 | 2120 | 0.25 | 0.41667 | 0.60417 | 0.77083 | MOP
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Grass_Cutting
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Cycle Number | Resources | IC1_Inv1_GC | IC1_Inv2_GC | IC1_Inv3_GC | IC1_Inv4_GC | IC2_Inv1_GC | IC2_Inv2_GC | Total Number of Table cut | Remarks for the day | Column1
1 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-01 | [8 empty] | 0
2 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-02 | [8 empty] | 0
3 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-03 | [8 empty] | 0
4 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-04 | [8 empty] | 0
5 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-05 | [8 empty] | 0
6 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-06 | [8 empty] | 0
7 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-07 | [8 empty] | 0
8 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-08 | [8 empty] | 0
9 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-09 | [8 empty] | 0
10 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-10 | [8 empty] | 0
11 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-11 | [8 empty] | 0
12 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-12 | [8 empty] | 0
13 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-13 | [8 empty] | 0
14 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-14 | [8 empty] | 0
15 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-15 | [8 empty] | 0
16 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-16 | [8 empty] | 0
17 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-17 | [8 empty] | 0
18 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-18 | [8 empty] | 0
19 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-19 | [8 empty] | 0
20 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-20 | [8 empty] | 0
21 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-21 | [8 empty] | 0
22 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-22 | [8 empty] | 0
23 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-23 | [8 empty] | 0
24 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-24 | [8 empty] | 0
25 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-25 | [8 empty] | 0
26 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-26 | [8 empty] | 0
27 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-27 | [8 empty] | 0
28 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-28 | [8 empty] | 0
29 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-29 | [8 empty] | 0
30 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-04-01 | 30 | 2022-04-30 | [8 empty] | 0
31 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-01 | [8 empty] | 0
32 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-02 | [8 empty] | 0
33 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-03 | [8 empty] | 0
34 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-04 | [8 empty] | 0
35 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-05 | [8 empty] | 0
36 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | [8 empty] | 0
37 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-07 | [8 empty] | 0
38 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-08 | [8 empty] | 0
39 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-09 | [8 empty] | 0
40 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-10 | [8 empty] | 0
41 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-11 | [8 empty] | 0
42 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-12 | [8 empty] | 0
43 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-13 | [8 empty] | 0
44 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-14 | [8 empty] | 0
45 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-15 | [8 empty] | 0
46 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-16 | [8 empty] | 0
47 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-17 | [8 empty] | 0
48 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-18 | [8 empty] | 0
49 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-19 | [8 empty] | 0
50 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-20 | [8 empty] | 0
51 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-21 | [8 empty] | 0
52 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-22 | [8 empty] | 0
53 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-23 | [8 empty] | 0
54 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-24 | [8 empty] | 0
55 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-25 | [8 empty] | 0
56 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-26 | [8 empty] | 0
57 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-27 | [8 empty] | 0
58 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-28 | [8 empty] | 0
59 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-29 | [8 empty] | 0
60 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-30 | [8 empty] | 0
61 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-31 | [8 empty] | 0
62 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-01 | [8 empty] | 0
63 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-02 | [8 empty] | 0
64 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-03 | [8 empty] | 0
65 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-04 | [8 empty] | 0
66 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-05 | [8 empty] | 0
67 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-06 | [8 empty] | 0
68 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-07 | [8 empty] | 0
69 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-08 | [8 empty] | 0
70 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-09 | [8 empty] | 0
71 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-10 | [8 empty] | 0
72 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-11 | [8 empty] | 0
73 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-12 | [8 empty] | 0
74 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-13 | [8 empty] | 0
75 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-14 | [8 empty] | 0
76 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-15 | [8 empty] | 0
77 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-16 | [8 empty] | 0
78 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-17 | [8 empty] | 0
79 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-18 | [8 empty] | 0
80 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-19 | [8 empty] | 0
81 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-20 | [8 empty] | 0
82 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-21 | [8 empty] | 0
83 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-22 | [8 empty] | 0
84 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-23 | [8 empty] | 0
85 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-24 | [8 empty] | 0
86 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-25 | [8 empty] | 0
87 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-26 | [8 empty] | 0
88 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-27 | [8 empty] | 0
89 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-28 | [8 empty] | 0
90 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-29 | [8 empty] | 0
91 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-06-01 | 30 | 2022-06-30 | [8 empty] | 0
92 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-01 | [8 empty] | 0
93 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-02 | [8 empty] | 0
94 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-03 | [8 empty] | 0
95 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-04 | [8 empty] | 0
96 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-05 | [8 empty] | 0
97 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-06 | [8 empty] | 0
98 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-07 | [8 empty] | 0
99 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-08 | [8 empty] | 0
100 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-09 | [8 empty] | 0
101 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-10 | [8 empty] | 0
102 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-11 | [8 empty] | 0
103 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | [8 empty] | 0
104 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-13 | [8 empty] | 0
105 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-14 | [8 empty] | 0
106 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | [8 empty] | 0
107 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-16 | [8 empty] | 0
108 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-17 | [8 empty] | 0
109 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-18 | [8 empty] | 0
110 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-19 | [8 empty] | 0
111 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-20 | [8 empty] | 0
112 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-21 | [8 empty] | 0
113 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-22 | [8 empty] | 0
114 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-23 | [8 empty] | 0
115 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-24 | [8 empty] | 0
116 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-25 | [8 empty] | 0
117 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-26 | [8 empty] | 0
118 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-27 | [8 empty] | 0
119 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-28 | [8 empty] | 0
120 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-29 | [8 empty] | 0
121 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-30 | [8 empty] | 0
122 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-31 | 1 | 2 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | Manually bushes cuttting
123 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-01 |  | 0 | [6 empty] | 0
124 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-02 | 1 | 2 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | Manually bushes cuttting Work completed
125 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-03 | 1 | 2 | 14 | 9 | 0 | 0 | 0 | 0 | 23 | Manually bushes cuttting Work completed
126 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-04 | 1 | 2 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | Manually bushes cuttting Work completed
127 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-05 | 1 | 2 | 6 | 0 | 0 | 0 | 0 | 21 | 27 | Manually bushes cuttting Work completed
128 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-06 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 24 | 24 | Manually bushes cuttting Work completed
129 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-07 | 1 | 2 | 0 | 0 | 0 | 0 | 3 | 27 | 30 | Manually bushes cuttting Work completed
130 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-08 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | Manually bushes cuttting Work completed
131 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-09 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | GRASS CUTTING WORK COMPLETED
132 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-10 | [8 empty] | 0
133 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-11 | [8 empty] | 0
134 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-12 | [8 empty] | 0
135 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-13 | [8 empty] | 0
136 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-14 | [8 empty] | 0
137 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-15 | [8 empty] | 0
138 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-16 | [8 empty] | 0
139 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-17 | [8 empty] | 0
140 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-18 | [8 empty] | 0
141 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | [8 empty] | 0
142 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-20 | [8 empty] | 0
143 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-21 | [8 empty] | 0
144 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-22 | [8 empty] | 0
145 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-23 | [8 empty] | 0
146 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-24 | [8 empty] | 0
147 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-25 | [8 empty] | 0
148 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-26 | [8 empty] | 0
149 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | [8 empty] | 0
150 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-28 | [8 empty] | 0
151 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-29 | [8 empty] | 0
152 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-30 | [8 empty] | 0
153 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-31 | [8 empty] | 0
154 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-01 | [8 empty] | 0
155 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-02 | [8 empty] | 0
156 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | [8 empty] | 0
157 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | [8 empty] | 0
158 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-05 | [8 empty] | 0
159 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-06 | [8 empty] | 0
160 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-07 | [8 empty] | 0
161 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-08 | [8 empty] | 0
162 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-09 | [8 empty] | 0
163 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-10 | [8 empty] | 0
164 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-11 | [8 empty] | 0
165 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-12 | [8 empty] | 0
166 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-13 | [8 empty] | 0
167 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-14 | 1 | 0 | [6 empty] | 0 | Spare area grass cutting work in progress
168 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-15 | 1 | 0 | [6 empty] | 0 | Spare area grass cutting work was completed
169 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-16 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | MCR,Switchyard Grass cutting work was completed
170 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-17 | 1 | 0 | 0 | 0 | 0 | 0 | 1.5 | 0 | 1.5 | Grass cutting work was completed
171 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-18 | [8 empty] | 0
172 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-19 | 1 | 0 | 9 | 0 | 0 | 0 | 4 | 0 | 13 | Grass cutting work was completed
173 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-20 | 1 | 0 | 21 | 0 | 0 | 0 | 0 | 0 | 21 | Grass cutting work was completed
174 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-21 | 1 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | Grass cutting work was completed
175 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-22 | 1 | 0 | 13 | 6 | 0 | 0 | 0 | 0 | 19 | Grass cutting work was completed
176 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-23 | [8 empty] | 0
177 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-24 | [8 empty] | 0
178 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-25 | [8 empty] | 0
179 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-26 | [8 empty] | 0
180 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-27 | 1 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | Grass cutting work was completed
181 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-28 | 1 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 11 | ICR 2 Road side Grass cutting work was completed
182 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-29 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | Grass cutting work was completed
183 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-30 | [8 empty] | 0
184 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-01 | [8 empty] | 0
185 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-02 | [8 empty] | 0
186 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-03 | [8 empty] | 0
187 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-04 | [8 empty] | 0
188 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-05 | [8 empty] | 0
189 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-06 | [8 empty] | 0
190 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | [8 empty] | 0
191 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-08 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR gate & ICR2 outside area Grass cutting work was completed
192 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-09 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR road side & Store outside area Grass cutting work was completed
193 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-10 | [8 empty] | 0
194 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | [8 empty] | 0
195 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-12 | [8 empty] | 0
196 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-13 | 1 | 0 | 0 | 8 | 1.5 | 0 | 0 | 0 | 9.5 | Main gate & MCR fence area grass cutting work was completed
197 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-14 | 1 | 0 | 0 | 0 | 17.5 | 0 | 0 | 0 | 17.5 | Grass cutting work was completed
198 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-15 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | ICR 1 surrounding area grass cutting work was completed
199 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-16 | [8 empty] | 0
200 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-17 | 1 | 0 | 0 | 0 | 8.5 | 0 | 0 | 0 | 8.5 | Weather station, MCS area grass cutting work was completed
201 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-18 | [8 empty] | 0
202 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-19 | [8 empty] | 0
203 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-20 | [8 empty] | 0
204 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-21 | [8 empty] | 0
205 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-22 | [8 empty] | 0
206 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-23 | [8 empty] | 0
207 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-24 | [8 empty] | 0
208 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-25 | [8 empty] | 0
209 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-26 | [8 empty] | 0
210 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-27 | [8 empty] | 0
211 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | [8 empty] | 0
212 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-29 | [8 empty] | 0
213 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-30 | [8 empty] | 0
214 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-31 | [8 empty] | 0
215 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-01 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR & Switch yard area grass cutting work was completed
216 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-02 | [8 empty] | 0
217 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-03 | [8 empty] | 0
218 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-04 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 2.5 | 2.5 | Main gate road side area grass cutting work was completed
219 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-05 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.5 | 7.5 | Grass cutting work was completed
220 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-06 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 32 | 32 | Grass cutting work was completed
221 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-07 | 1 | 2 | 4 | 0 | 0 | 0 | 0 | 14 | 18 | Grass cutting work was completed
222 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-08 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 31 | 31 | Grass cutting work was completed
223 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-09 | [8 empty] | 0
224 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-10 | [8 empty] | 0
225 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-11 | [8 empty] | 0
226 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-12 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 20.5 | 20.5 | Grass cutting work was completed
227 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-13 | 1 | 2 | 0 | 8 | 6 | 7 | 0 | 0 | 21 | Grass cutting work was completed
228 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-14 | 1 | 2 | 6 | 14 | 6 | 4 | 0 | 0 | 30 | Grass cutting work was completed
229 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-15 | 1 | 2 | 23 | 8.5 | 0 | 0 | 0 | 0 | 31.5 | Grass cutting work was completed
230 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-16 | 1 | 1 | 15.5 | 0 | 0 | 0 | 0 | 0 | 15.5 | Grass cutting work was completed
231 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-17 | 1 | 2 | 24.5 | 8 | 0 | 0 | 4.5 | 0 | 37 | Grass cutting work was completed
232 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-18 | 1 | 1 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | Grass cutting work was completed
233 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-19 | 1 | 2 | 0 | 17.5 | 0 | 0 | 0 | 0 | 17.5 | Grass cutting work was completed
234 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-20 | 1 | 1 | 0 | 10.5 | 0 | 0 | 0 | 0 | 10.5 | Grass cutting work was completed
235 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-21 | [8 empty] | 0
236 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-22 | [8 empty] | 0
237 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-23 | [8 empty] | 0
238 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-24 | 1 | 2 | 0 | 1 | 10 | 0 | 0 | 0 | 11 | Grid5-Grass cutting work done
239 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-25 | 1 | 2 | 4 | 6 | 0 | 6 | 0 | 6 | 22 | Grid5&6-Grass cutting work done
240 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-26 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Grid 5&6 road side area grass cutting work was completed
241 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-27 | 1 | 1 | 0 | 0 | 4 | 1 | 0 | 0 | 5 | Grid 3&4 road side area grass cutting work was completed
242 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-28 | 1 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | Grid5 Grass Cutting work completed
243 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-29 | [8 empty] | 0
244 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 30 | 2022-11-30 | 1 | 2 | 0 | 0 | 6 | 11 | 0 | 0 | 17 | Grid5 Grass Cutting work completed
245 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-01 | 1 | 2 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | Grid5 Grass Cutting work completed
246 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-02 | 1 | 2 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | Grid5 Grass Cutting work completed
247 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-03 | 1 | 2 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | Grid4&5 Grass Cutting work completed
248 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-04 | 1 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | Grid4 Grass Cutting work completed
249 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-05 | [8 empty] | 0
250 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 10 | 12 | Grid1 Grass Cutting work completed
251 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-07 | 1 | 1 | 0 | 0 | 0 | 0 | 14 | 0 | 14 | Grid1 Grass Cutting work completed
252 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-08 | 1 | 2 | 0 | 0 | 0 | 0 | 29 | 0 | 29 | Grid1&2 Grass Cutting work completed
253 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-09 | [8 empty] | 0
254 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-10 | [8 empty] | 0
255 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | 1 | 2 | 0 | 0 | 0 | 0 | 27 | 0 | 27 | Grid 2 - Inv 5 - T3 to T29 - 27 Tables Grass cutting work completed
256 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-12 | 1 | 2 | 0 | 0 | 13 | 0 | 11 | 0 | 24 | Grid2-Inv5-T30 to T40 & Grid4-Inv3-T88 to T100 - 24 Tables Grass cutting work completed
257 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-13 | 1 | 2 | 0 | 0 | 5 | 16 | 0 | 0 | 21 | Grid4-Inv3-T101 to T105 & Inv4-T106 to T121 - 21 Tables Grass cutting work completed
258 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-14 | 1 | 2 | 0 | 24 | 0 | 5 | 0 | 0 | 29 | Grid4-Inv4-T122 to T126 & Grid6-Inv2-T50 to T73-29 Tables Grass cutting work completed
259 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 1&2 | 2 | 0 | 6 | 9 | 0 | 17 | 0 | 32 | G6-Inv2-6nos&Inv3-9nos-T74 to T88-15Tables(Cycle1 Completed) & G4-Inv5-T1toT17-17 Tables
260 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-16 | [8 empty] | 0
261 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-17 | 2 | 1 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | G4-Inv5-T18 to 23 - 6 Tables Grass cutting work completed
262 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-18 | 2 | 1 | 6 | 0 | 0 | 0 | 13 | 0 | 19 | G3-Inv1-T8 to T13 & Inv5 -G3A- T1 to T5, G3-TW01,T1 to T7-19 Tables
263 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-19 | [8 empty] | 0
264 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-20 | 2 | 2 | 14 | 0 | 0 | 0 | 0 | 0 | 14 | G3-Inv1-T14 to T27 - 14 Tables Grass cutting work completed
265 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-21 | [8 empty] | 0
266 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-22 | 2 | 1 | 11 | 0 | 0 | 0 | 2 | 0 | 13 | Grid4-Inv5-T24 to T25 & Inv1-T26 to T36 - 13 Tables Grass Cutting work completed
267 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-23 | 2 | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | Inv1-T37 to T48 - 12 Tables Grass Cutting work completed
268 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-24 | [8 empty] | 0
269 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | [8 empty] | 0
270 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | [8 empty] | 0
271 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-27 | [8 empty] | 0
272 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-28 | [8 empty] | 0
273 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | [8 empty] | 0
274 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-30 | [8 empty] | 0
275 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-31 | [8 empty] | 0
276 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-01 | [8 empty] | 0
277 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-02 | [8 empty] | 0
278 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-03 | [8 empty] | 0
279 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-04 | [8 empty] | 0
280 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | [8 empty] | 0
281 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-06 | [8 empty] | 0
282 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-07 | [8 empty] | 0
283 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-08 | [8 empty] | 0
284 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-09 | [8 empty] | 0
285 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-10 | [8 empty] | 0
286 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-11 | 2 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G3-Inv1-T28 to T35 - 08 Tables & Storage yard area Grass cutting work completed
287 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-12 | 2 | 1 | 9 | 4 | 0 | 0 | 0 | 0 | 13 | G3-T36 to T49 - 13 Tables & Storage yard area Grass cutting work completed
288 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-13 | 2 | 1 | 0 | 4 | 15 | 0 | 0 | 0 | 19 | G3-T50 to T68 - 19 Tables Grass cutting work completed
289 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-14 | [8 empty] | 0
290 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | [8 empty] | 0
291 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | [8 empty] | 0
292 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-17 | [8 empty] | 0
293 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-18 | 3 | 1 | [6 empty] | 0 | ICR 1&2 Non PV area Grass Cutting work done
294 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-19 | 3 | 1 | [6 empty] | 0 | MCR & Storage yard area Grass Cutting work done
295 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | [8 empty] | 0
296 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-21 | [8 empty] | 0
297 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-22 | [8 empty] | 0
298 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-23 | [8 empty] | 0
299 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-24 | [8 empty] | 0
300 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-25 | [8 empty] | 0
301 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-26 | [8 empty] | 0
302 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-27 | [8 empty] | 0
303 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | [8 empty] | 0
304 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-29 | [8 empty] | 0
305 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-30 | [8 empty] | 0
306 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-31 | [8 empty] | 0
307 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-01 | [8 empty] | 0
308 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | [8 empty] | 0
309 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-03 | [8 empty] | 0
310 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-04 | [8 empty] | 0
311 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | [8 empty] | 0
312 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-06 | [8 empty] | 0
313 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | [8 empty] | 0
314 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-08 | [8 empty] | 0
315 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | [8 empty] | 0
316 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-10 | [8 empty] | 0
317 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-11 | [8 empty] | 0
318 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-12 | [8 empty] | 0
319 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-13 | [8 empty] | 0
320 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | [8 empty] | 0
321 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-15 | [8 empty] | 0
322 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-16 | [8 empty] | 0
323 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | [8 empty] | 0
324 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-18 | [8 empty] | 0
325 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-19 | [8 empty] | 0
326 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-20 | [8 empty] | 0
327 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | [8 empty] | 0
328 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | [8 empty] | 0
329 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-23 | [8 empty] | 0
330 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | [8 empty] | 0
331 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | [8 empty] | 0
332 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | [8 empty] | 0
333 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-27 | [8 empty] | 0
334 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-28 | [8 empty] | 0
335 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-01 | [8 empty] | 0
336 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | [8 empty] | 0
337 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-03 | [8 empty] | 0
338 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | [8 empty] | 0
339 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | [8 empty] | 0
340 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-06 | [8 empty] | 0
341 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-07 | [8 empty] | 0
342 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-08 | [8 empty] | 0
343 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | [8 empty] | 0
344 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-10 | [8 empty] | 0
345 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-11 | [8 empty] | 0
346 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-12 | [8 empty] | 0
347 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-13 | [8 empty] | 0
348 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-14 | [8 empty] | 0
349 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-15 | [8 empty] | 0
350 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-16 | [8 empty] | 0
351 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-17 | [8 empty] | 0
352 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-18 | [8 empty] | 0
353 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-19 | [8 empty] | 0
354 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-20 | [8 empty] | 0
355 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-21 | [8 empty] | 0
356 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-22 | [8 empty] | 0
357 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-23 | [8 empty] | 0
358 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | [8 empty] | 0
359 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | [8 empty] | 0
360 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | [8 empty] | 0
361 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-27 | [8 empty] | 0
362 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-28 | [8 empty] | 0
363 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-29 | [8 empty] | 0
364 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-30 | [8 empty] | 0
365 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | [8 empty] | 0
366 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-01 | [8 empty] | 0
367 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-02 | [8 empty] | 0
368 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-03 | [8 empty] | 0
369 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-04 | [8 empty] | 0
370 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-05 | [8 empty] | 0
371 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-06 | [8 empty] | 0
372 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-07 | [8 empty] | 0
373 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-08 | [8 empty] | 0
374 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | [8 empty] | 0
375 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | [8 empty] | 0
376 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | [8 empty] | 0
377 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | [8 empty] | 0
378 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-13 | [8 empty] | 0
379 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-14 | [8 empty] | 0
380 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-15 | [8 empty] | 0
381 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-16 | [8 empty] | 0
382 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-17 | [8 empty] | 0
383 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | [8 empty] | 0
384 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-19 | [8 empty] | 0
385 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-20 | [8 empty] | 0
386 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-21 | [8 empty] | 0
387 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-22 | [8 empty] | 0
388 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-23 | [8 empty] | 0
389 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | [8 empty] | 0
390 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-25 | [8 empty] | 0
391 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | [8 empty] | 0
392 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | [8 empty] | 0
393 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-28 | [8 empty] | 0
394 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-29 | [8 empty] | 0
395 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-30 | [8 empty] | 0
396 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-01 | [8 empty] | 0
397 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-02 | [8 empty] | 0
398 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-03 | [8 empty] | 0
399 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-04 | [8 empty] | 0
400 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-05 | [8 empty] | 0
401 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-06 | [8 empty] | 0
402 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-07 | [8 empty] | 0
403 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-08 | [8 empty] | 0
404 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-09 | [8 empty] | 0
405 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-10 | [8 empty] | 0
406 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-11 | [8 empty] | 0
407 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-12 | [8 empty] | 0
408 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-13 | [8 empty] | 0
409 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-14 | [8 empty] | 0
410 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-15 | [8 empty] | 0
411 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-16 | [8 empty] | 0
412 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-17 | [8 empty] | 0
413 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-18 | [8 empty] | 0
414 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-19 | [8 empty] | 0
415 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | [8 empty] | 0
416 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-21 | [8 empty] | 0
417 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-22 | [8 empty] | 0
418 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-23 | [8 empty] | 0
419 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-24 | [8 empty] | 0
420 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | [8 empty] | 0
421 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | [8 empty] | 0
422 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-27 | [8 empty] | 0
423 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-28 | 2 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G3A-Inv5-TW1, T1 to T5 - 06 Tables & G3-Inv5-T1 to T4 - 04 Tables Grass cutting work completed
424 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-29 | [8 empty] | 0
425 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-30 | 2 | 1 | 3 | 0 | 0 | 0 | 3 | 0 | 6 | G3-Inv5-T5 to T7 & Inv1-T8 toT10 - 06 Tables Grass cutting work completed
426 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-31 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ICR 1 & 2 Surrounding Area Grass cutting work completed
427 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-01 | 2 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G3-Inv1-T11 toT19 - 09 Tables Grass cutting work completed
428 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-02 | [8 empty] | 0
429 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-03 | 2 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | G3-Inv1-T20 toT21 - 02 Tables Grass cutting work completed
430 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-04 | 2 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | G3-Inv1-T22 toT26 - 05 Tables Grass cutting work completed
431 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-05 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Non PV area Grass cutting work done
432 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-06 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Non PV area Grass cutting work done
433 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-07 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Non PV area Grass cutting work done
434 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Non PV area Grass cutting work done
435 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-09 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Non PV area Grass cutting work done
436 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-10 | 2 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | G3-Inv1-T27 toT31 - 05 Tables Grass cutting work completed
437 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-11 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G3-Inv1-T32 toT37 - 06 Tables Grass cutting work completed
438 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-12 | [8 empty] | 0
439 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-13 | [8 empty] | 0
440 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-14 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G3-Inv1-T38 toT43 - 06 Tables Grass cutting work completed
441 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-15 | 2 | 2 | 1 | 9 | 2 | 0 | 0 | 0 | 12 | G3-Inv1-T44, Inv2-T45 to T53 & Inv3-T54 toT55 - 12 Tables Grass cutting work completed
442 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-16 | 2 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | G3-Inv3-T56 toT65 - 10 Tables Grass cutting work completed
443 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-17 | 2 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | G3-Inv3-T66 toT68 & G4-Inv3-T85 to T88 - 7 Tables Grass cutting work completed
444 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-18 | 2 | 1 | 0 | 0 | 4 | 0 | 0 | 0 | 4 | G4-Inv3-T81 toT84 - 4 Tables & MCR surrounding area Grass cutting work completed
445 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-19 | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | G4-Inv3-T78 toT80 - 3 Tables & MCR surrounding area Grass cutting work completed
446 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-20 | 2 | 1 | 0 | 1 | 5 | 0 | 0 | 0 | 6 | G4-Inv2-T72 & Inv3 - T73 toT77 - 6 Tables Grass cutting work completed
447 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-21 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ICR 1 surrounding area grass cutting work was completed
448 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-22 | 2 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | G4-Inv3 - T88 toT93 - 6 Tables Grass cutting work completed
449 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-23 | 2 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | G4-Inv3 - T94 toT100 - 7 Tables Grass cutting work completed
450 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-24 | 2 | 1 | 0 | 0 | 5 | 1 | 2 | 0 | 8 | G4-Inv3 - T101 toT105, Inv4 - T106 & Inv5 - T10 to T11 - 8 Tables Grass cutting work completed
451 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-25 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4-Inv4 - T107 toT114 - 8 Tables Grass cutting work completed
452 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-26 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4-Inv4 - T115 toT122 - 8 Tables Grass cutting work completed
453 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-27 | 2 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | G4-Inv4 - T123 toT131 - 9 Tables Grass cutting work completed
454 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-28 | 2 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | G4-Inv4 - T132 toT140 - 9 Tables Grass cutting work completed
455 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-29 | [8 empty] | 0
456 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-30 | [8 empty] | 0
457 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-01 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | G1-Inv6 - T47 toT52 - 6 Tables & MCR road side area Grass cutting work completed
458 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | 2 | 1 | 0 | 0 | 0 | 0 | 7 | 4 | 11 | G1-Inv6 - T43 toT46 & Inv5 - T36 to T42 - 11 Tables Grass cutting work completed
459 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-03 | 2 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G1-Inv5 - T26 to T35 - 10 Tables Grass cutting work completed
460 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-04 | 2 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G1-Inv5 - T17 to T25 - 9 Tables Grass cutting work completed
461 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-05 | 2 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G1-Inv5 - T8 to T16 - 9 Tables Grass cutting work completed
462 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-06 | 2 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G1-Inv5 - T1 to T7 & G2-Inv5 - TW1 - 8 Tables Grass cutting work completed
463 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-07 | 2 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G2-Inv5 - T1 to T7 - 7 Tables Grass cutting work completed
464 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-08 | 2 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G2-Inv5 - T8 to T15 - 8 Tables Grass cutting work completed
465 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-09 | 2 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G2-Inv5 - T16 to T23 - 8 Tables Grass cutting work completed
466 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-10 | 2 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G2-Inv5 - T24 to T31 - 8 Tables Grass cutting work completed
467 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-11 | 2 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G2-Inv5 - T32 to T40 - 9 Tables Grass cutting work completed
468 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-12 | 2 | 1 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | G4-Inv5 - T1 to T6 - 6 Tables & MCR surrounding area Grass cutting work completed
469 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-13 | 2 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G4-Inv5 - T7 to T13 - 7 Tables Grass cutting work completed
470 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-14 | 2 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G4-Inv5 - T14 to T20 - 7 Tables Grass cutting work completed
471 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-15 | 2 | 1 | 2 | 0 | 0 | 0 | 5 | 0 | 7 | G4-Inv5 & Inv1 - T21 to T27 - 7 Tables Grass cutting work completed
472 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-16 | 2 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | G4-Inv1 - T28 to T32 - 5 Tables Grass cutting work completed
473 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-17 | 2 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | G4-Inv1 - T33 to T37 - 5 Tables Grass cutting work completed
474 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-18 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G4-Inv1 - T38 to T43 - 6 Tables Grass cutting work completed
475 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-19 | 2 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G4-Inv1 - T44 to T50 - 7 Tables Grass cutting work completed
476 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G4-Inv1 - T51 to T56 - 6 Tables Grass cutting work completed
477 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-21 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G4-Inv1 - T57 to T62 - 6 Tables Grass cutting work completed
478 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-22 | 2 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | G4-Inv2 - T63 to T68 - 6 Tables Grass cutting work completed
479 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-23 | 2 | 1 | 0 | 3 | 2 | 0 | 0 | 0 | 5 | G4-Inv2 - T69 to T71 G5-Inv3-T93 to T94 -5 Tables Grass cutting work completed
480 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-24 | 2 | 1 | 0 | 0 | 4 | 0 | 0 | 0 | 4 | G5-Inv3 - T 94 to T 97 - 4 Tables Grass cutting work completed
481 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | G5-Inv3 - T 98 to T 100 - 3 Tables Grass cutting work completed
482 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-26 | [8 empty] | 0
483 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | [8 empty] | 0
484 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-28 | 2 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 5 | G4-Inv3 - T 87 to T 91 - 5 Tables Grass cutting work completed
485 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | 2 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | G5-Inv3 - T 101 to T 108 - 8 Tables Grass cutting work completed
486 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-30 | 2 | 1 | 0 | 0 | 2 | 4 | 0 | 0 | 6 | G5-Inv3 & Inv4 - T109 to T113 - 6 Tables Grass cutting work completed
487 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-31 | 2 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | G5- Inv4 - T114 to T118 - 5 Tables Grass cutting work completed
488 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-01 | 2 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | G5- Inv4 - T119 to T123 - 5 Tables Grass cutting work completed
489 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-02 | 2 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | G5- Inv4 - T124 to T128 - 5 Tables Grass cutting work completed
490 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-03 | 2 | 2 | 0 | 0 | 3 | 7 | 0 | 0 | 10 | G5- Inv4 - T129 to T135 - 7 Tables & G6-Inv3 - T 86 to T 88 - 3 Tables Grass cutting work completed
491 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-04 | 2 | 2 | 0 | 6 | 6 | 12 | 0 | 0 | 24 | G5- Inv4 - T136 to T147 - 12 Tables & G6-Inv2 & Inv 3 - T 86 to T 88 - 12 Tables Grass cutting work completed
492 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-05 | 2 | 2 | 0 | 12 | 0 | 11 | 0 | 0 | 23 | G5- Inv4 - T148 to T158 - 11 Tables & G6-Inv2 - T 62 to T 73 - 12 Tables Grass cutting work completed
493 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-06 | 2 | 2 | 0 | 9 | 0 | 0 | 0 | 8 | 17 | G5- Inv6 - T1 to T8 - 8 Tables & G6-Inv2 - T 53 to T 61 - 9 Tables Grass cutting work completed
494 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-07 | 2 | 2 | 0 | 8 | 0 | 0 | 0 | 10 | 18 | G5- Inv6 - T9 to T18 - 10 Tables & G6-Inv2 - T 45 to T 52 - 8 Tables Grass cutting work completed
495 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-08 | 2 | 2 | 4 | 1 | 0 | 0 | 0 | 10 | 15 | G5- Inv6 - T19 to T22 - 4 Tables & G6- Inv1,2 & 6 - T 44 to T 34 - 11 Tables Grass cutting work completed
496 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-09 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | G6- Inv6 - T 23 to T 33 - 11 Tables Grass cutting work completed - Cycle 2 Completed
497 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-10 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 13 | 13 | G6- Inv6 - T 22 to T 12 - 11 Tables Grass cutting work completed & G5- Inv6 - 23 to 24 - 2
498 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-11 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | G6- Inv6 - T 6 to T 11 - 6 Tables & Grid 5 Non PV area Grass cutting work completed
499 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-12 | 3 | 1 | 0 | 0 | 0 | 1 | 0 | 5 | 6 | G6- Inv6&4 - T 1 to T 5 & TW1 - 6 Tables Grass cutting work completed
500 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-13 | 3 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 10 | G5- Inv3&4 - TW2 to TW11 - 10 Tables Grass cutting work completed
501 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-14 | 3 | 2 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | G5- Inv2 - TW12 to TW18 - 7 Tables & G6- Inv2 - TW13 to TW16 - 4 Tables & MCR Area Grass cutting work completed
502 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-15 | 1 | 1 | 0 | 0 | 6 | 6 | 0 | 0 | 12 | G6- Inv3 &Inv4 - TW1 to TW12 - 12 Tables Grass cutting work completed - 2nd Contractual year started
503 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-16 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | G5- Inv6 - T25 to T30 - 6 Tables Grass cutting work completed
504 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-17 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | G5- Inv6 - T31 to T35 - 5 Tables Grass cutting work completed
505 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-18 | 1 | 1 | 4 | 1 | 0 | 0 | 0 | 1 | 6 | G5- Inv6 - T36 to T41 - 6 Tables Grass cutting work completed
506 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-19 | 1 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | G5- Inv6 - T42 to T48 - 7 Tables Grass cutting work completed
507 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-20 | 1 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | G5- Inv6 - T49 to T57 - 9 Tables Grass cutting work completed
508 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-21 | 1 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | G5- Inv6 - T58 to T63 - 6 Tables Grass cutting work completed
509 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-22 | 1 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | G5- Inv6 - T64 to T70 - 7 Tables Grass cutting work completed
510 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-23 | 1 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | G5- Inv6 - T71 to T75 - 5 Tables Grass cutting work completed
511 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-24 | 1 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | G5- Inv3 - T76 to T81 - 6 Tables Grass cutting work completed
512 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-25 | 1 | 1 | 0 | 0 | 4 | 6 | 0 | 0 | 10 | G5- Inv3&4 - T82 to T86 & G4-Inv4-T139 to T143 - 10 Tables Grass cutting work completed
513 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-26 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Store Spare Area Grass Cutting Work Done
514 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-27 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Store Spare Area Grass Cutting Work Done
515 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-28 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G3-TW1 & T1, G3A-T1 to T5 - Inv5 - 7 Tables Grass cutting work completed
516 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-29 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Fence side area Grass cutting work done
517 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-30 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Fence side area Grass cutting work done
518 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-31 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Fence side area Grass cutting work done
519 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-01 | 1 | 1 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | G3 -T3 to T6-Inv 5 -6 Tables Grass cutting work completed & G4 Fence side area Grass cutting work done
520 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-02 | 1 | 1 | 4 | 0 | 0 | 0 | 1 | 0 | 5 | G3 -T7 to T11-Inv 5 & Inv 1 -5 Tables Grass cutting work completed
521 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-03 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G3 -T12 to T20- Inv 1 -9 Tables Grass cutting work completed
522 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-04 | 1 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G3 -T21 to T28- Inv 1 -8 Tables Grass cutting work completed
523 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-05 | 1 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | G3 -T29 to T38- Inv 1 -10 Tables Grass cutting work completed
524 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-06 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
525 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-07 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Store Spare Area Grass Cutting Work Done
526 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-08 | 1 | 1 | 6 | 4 | 0 | 0 | 0 | 0 | 10 | G3 -T39 to T48- Inv 1 & Inv 2 -10 Tables Grass cutting work completed
527 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-09 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Main gate road side area grass cutting work was completed
528 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-10 | 1 | 1 | 0 | 5 | 5 | 0 | 0 | 0 | 10 | G3 -T49 to T58- Inv2 & Inv 3 -10 Tables Grass cutting work completed
529 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-11 | 1 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | G3 -T59 to T68- Inv 3 -10 Tables Grass cutting work completed
530 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-12 | 1 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | G4 -T81 to T87- Inv 3 -07 Tables & Main gate road side area Grass cutting work completed
531 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-13 | 1 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 5 | G4 -T76 to T80- Inv 3 -05 Tables Grass cutting work completed
532 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-14 | 1 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | G4 -T88 to T93- Inv 3 -06 Tables Grass cutting work completed
533 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-15 | 1 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | G4 -T94 to T101- Inv 3 -08 Tables Grass cutting work completed
534 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-16 | 1 | 1 | 0 | 0 | 4 | 4 | 0 | 0 | 8 | G4 -T102 to T109- Inv 3& Inv 4 -08 Tables Grass cutting work completed
535 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-17 | 1 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | G4 -T110 to T119- Inv 4 -10 Tables Grass cutting work completed
536 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-18 | 1 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | G4 -T120 to T125- Inv 4 -06 Tables Grass cutting work completed
537 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-19 | [8 empty] | 0
538 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-20 | [8 empty] | 0
539 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-21 | 1 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | G4 -T126 to T131- Inv 4 -06 Tables Grass cutting work completed
540 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-22 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | G4 -T32 to T134- Inv 4 -02 Tables Grass cutting work completed
541 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-23 | [7 empty] | 0 | 0 | Store Spare Area & G6 Non PV Area Grass Cutting Work Done
542 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-24 | [8 empty] | 0
543 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-25 | [8 empty] | 0
544 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-26 | [8 empty] | 0
545 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-27 | [8 empty] | 0
546 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-28 | [8 empty] | 0
547 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-29 | [8 empty] | 0
548 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 30 | 2023-09-30 | [8 empty] | 0
549 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | [8 empty] | 0
550 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | [8 empty] | 0
551 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | [8 empty] | 0
552 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | [8 empty] | 0
553 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | [8 empty] | 0
554 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | [8 empty] | 0
555 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | [8 empty] | 0
556 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | [8 empty] | 0
557 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-09 | [8 empty] | 0
558 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | [8 empty] | 0
559 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-11 | [8 empty] | 0
560 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-12 | [8 empty] | 0
561 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-13 | [8 empty] | 0
562 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | [8 empty] | 0
563 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | [8 empty] | 0
564 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | [8 empty] | 0
565 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | [8 empty] | 0
566 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | [8 empty] | 0
567 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-19 | [8 empty] | 0
568 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-20 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | G5- Inv4 - T120 to T121 - 2 Tables Grass cutting work completed
569 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | 1 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | G5- Inv4 - T122 to T126 - 5 Tables Grass cutting work completed
570 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-22 | 1 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | G5- Inv4 - T127 to T132 - 6 Tables Grass cutting work completed
571 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | [8 empty] | 0
572 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-24 | [8 empty] | 0
573 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-25 | [8 empty] | 0
574 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-26 | 1 | 1 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | G5- Inv4 - T133 to T146 - 14 Tables Grass cutting work completed
575 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-27 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G4- Inv1 - T31 to T39 - 9 Tables Grass cutting work completed
576 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | 1 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | G4- Inv1 - T40 to T49 - 10 Tables Grass cutting work completed
577 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | 1 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 11 | G4- Inv1 - T50 to T60 - 11 Tables Grass cutting work completed
578 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | 1 | 1 | 2 | 8 | 0 | 0 | 0 | 0 | 10 | G4- Inv1&2 - T61 to T70 - 10 Tables Grass cutting work completed
579 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-31 | 1 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G3A T1 to T5, G3-TW1, T1 to T6 - Inv5 - 12 Tables Grass cutting work completed
580 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-11-01 | 1 | 1 | 10 | 0 | 0 | 0 | 1 | 0 | 11 | G3 - Inv5&1 -T7 to T17- 11 Tables Grass cutting work completed
581 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-02 | 1 | 1 | 6 | 0 | 0 | 0 | 4 | 0 | 10 | G4 -Inv5&1 - T31 to 21-10 Tables Grass Cutting Work completed
582 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-03 | 1 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4 -Inv4 - T136 to T143-8 Tables Grass Cutting Work completed
583 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-04 | 1 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G4 -Inv5 - T14 to T21-8 Tables Grass Cutting Work completed
584 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-05 | 1 | 1 | 0 | 3 | 9 | 0 | 0 | 0 | 12 | G6 -Inv2&3 - T77 to T88-12 Tables Grass Cutting Work completed
585 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-06 | 1 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | G6 -Inv2 - T68 to T76-09 Tables & ICR1 Surrounding Area Grass Cutting Work completed
586 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-07 | 1 | 1 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | G6 -Inv2 - T57 to T67-11 Tables Grass Cutting Work Completed
587 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
588 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-09 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | G6 -Inv2 - T53 to T56-04 Tables Grass Cutting Work Completed
589 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-10 | 1 | 1 | 0 | 3 | 9 | 0 | 0 | 0 | 12 | G6 -Inv2&1 - T41 to T52-12 Tables Grass Cutting Work Completed
590 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-11 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 10 | 11 | G6 -Inv6&1 - T40 to T30-11 Tables Grass Cutting Work Completed
591 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-12 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G6 -Inv6 - T20 to T29-10 Tables Grass Cutting Work Completed
592 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-13 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | G6 -Inv6 - T01 to T11-11 Tables Grass Cutting Work Completed
593 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-14 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G6 -Inv6 - T12 to T19 & G5-Inv 6 T01 to T02-10 Tables Grass Cutting Work Completed
594 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-15 | 1 | 1 | 0 | 0 | 5 | 5 | 0 | 0 | 10 | G5 -Inv3&4 - TW01 to TW10-10 Tables Grass Cutting Work Completed
595 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-16 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G5 -Inv6 - T3 to T12-10 Tables Grass Cutting Work Completed
596 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-17 | 1 | 1 | 0 | 0 | 0 | 0 | 13 | 0 | 13 | G2 -Inv5 - T28 to T40-13 Tables Grass Cutting Work Completed
597 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-18 | 1 | 1 | 0 | 0 | 0 | 0 | 11 | 0 | 11 | G2 -Inv5 - T17 to T27-11 Tables Grass Cutting Work Completed
598 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-19 | 1 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G2 -Inv5 - T07 to T16-10 Tables Grass Cutting Work Completed
599 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-20 | 1 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G2 -Inv5 - TW1,T01 to T06 & G1-Inv 5 T01 to T02-09 Tables Grass Cutting Work Completed
600 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-21 | 1 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G1-Inv 5 T03 to T12-10 Tables Grass Cutting Work Completed
601 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-22 | 1 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G1-Inv 5 T13 to T21-9 Tables Grass Cutting Work Completed
602 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-23 | 1 | 1 | 0 | 0 | 0 | 0 | 13 | 0 | 13 | G1-Inv 5 T22 to T34-13 Tables Grass Cutting Work Completed
603 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-24 | 1 | 1 | 0 | 0 | 0 | 0 | 8 | 3 | 11 | G1-Inv 5 T35 to T45-11 Tables Grass Cutting Work Completed
604 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-25 | 1 | 1 | 6 | 0 | 0 | 0 | 0 | 7 | 13 | G1 -Inv6 - T46 to T52 & G3-Inv1 T18 to T23-13 Tables Grass Cutting Work Completed
605 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-26 | 1 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 11 | G3-Inv1 T24 to T34-11 Tables Grass Cutting Work Completed
606 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-27 | 1 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G3-Inv1 T35 to T41-7 Tables Grass Cutting Work Completed
607 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-28 | 1 | 1 | 3 | 8 | 0 | 0 | 0 | 0 | 11 | G3-Inv1&2 T42 to T52-11 Tables Grass Cutting Work Completed
608 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-29 | 1 | 1 | 0 | 1 | 9 | 0 | 0 | 0 | 10 | G3-Inv2&3 T53 to T62-10 Tables Grass Cutting Work Completed
609 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 30 | 2023-11-30
610 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-01 | 1 | 1 | 0 | 0 | 6 | 5 | 0 | 0 | 11 | G3-Inv3 T63 to T68 & G5-Inv 4 T 154 to T158-11 Tables Grass Cutting Work Completed
611 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-02 | 1 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | G5-Inv 4 T 118,119, 146 to T153-10 Tables Grass Cutting Work Completed | Cycle 1 Completed
612 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-03 | 2 | 1 | 0 | 0 | 0 | 5 | 2 | 0 | 7 | G5-Inv 4 113 to T117 & G4-Inv 5 T10 to T11-7 Tables Grass Cutting Work Completed
613 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | 2 | 1 | 0 | 0 | 5 | 3 | 0 | 0 | 8 | G5-Inv3 & 4 T106 to T112 -8 Tables Grass Cutting Work Completed
614 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-05 | 2 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 5 | G5-Inv3 T101 to T105 -5 Tables Grass Cutting Work Completed
615 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-06 | 2 | 1 | 0 | 0 | 8 | 3 | 0 | 0 | 11 | G5-Inv3 & 4 T90 to T100 -11 Tables Grass Cutting Work Completed
616 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-07 | 2 | 1 | 0 | 0 | 7 | 4 | 0 | 0 | 11 | G5-Inv3 & 4 T79 to T89 -11 Tables Grass Cutting Work Completed
617 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-08 | 2 | 1 | 0 | 0 | 3 | 4 | 0 | 0 | 7 | G5-Inv3 & 4 T72 to T78 -7 Tables Grass Cutting Work Completed
618 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-09 | 2 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | G5-Inv2 T63 to T71 -9 Tables Grass Cutting Work Completed
619 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-10 | [8 empty] | 0
620 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | 2 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | G5-Inv2 T56 to T62-7 Tables Grass Cutting Work Completed
621 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-12 | 2 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | G5-Inv2 T47 to T55-9 Tables Grass Cutting Work Completed
622 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-13 | 2 | 1 | 1 | 6 | 0 | 0 | 0 | 0 | 7 | G5-Inv1 & 2 T40 to T46-7 Tables Grass Cutting Work Completed
623 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-14 | 2 | 1 | 0 | 2 | 8 | 0 | 0 | 0 | 10 | G4-Inv2 & 3 T71 to T80-10 Tables Grass Cutting Work Completed
624 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | 2 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | G4-Inv 3 T81 to T87-7 Tables Grass Cutting Work Completed
625 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-16 | 2 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | G4-Inv 3 T88 to T95-8 Tables Grass Cutting Work Completed
626 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-17 | 2 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | G4-Inv 3 T96 to T105-10 Tables Grass Cutting Work Completed
627 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-18 | 2 | 1 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | G4-Inv 5 T01 to T05-5 Tables Grass Cutting Work Completed
628 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-19 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4-Inv 4 T106 to T113-8 Tables Grass Cutting Work Completed
629 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-20 | 2 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | G4-Inv 4 T114 to T123-10 Tables Grass Cutting Work Completed
630 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-21 | 2 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | G4-Inv 4 T124 to T133-10 Tables Grass Cutting Work Completed
631 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | 2 | 1 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | G4-Inv 4 T134 to T137-4 Tables Grass Cutting Work Completed
632 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-23 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Non PV Area Grass Cutting Work Completed
633 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-24 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Non PV Area Grass Cutting Work Completed
634 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-25 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Non PV Area Grass Cutting Work Completed
635 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-26 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Non PV Area Grass Cutting Work Completed
636 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Non PV Area Grass Cutting Work Completed
637 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-28 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Non PV Area Grass Cutting Work Completed
638 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-29 | 2 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | G5-Inv1 T37 to T39-3 Tables & G5 Non PV Area Grass Cutting Work Completed
639 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-30 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Non PV Area Grass Cutting Work Completed
640 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-31 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Non PV Area Grass Cutting Work Completed
641 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-01 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Non PV Area Grass Cutting Work Completed
642 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-02 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Non PV Area Grass Cutting Work Completed
643 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-03 | 2 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | G6 Non PV Area & G5-Inv2 TW16 to TW18-3 Tables Grass Cutting Work Completed
644 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-04 | 2 | 1 | 2 | 0 | 0 | 0 | 0 | 6 | 8 | G5-Inv1 & 6 T31 to T38-8 Tables Grass Cutting Work Completed
645 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-05 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 9 | 9 | G5-Inv6 T22 to T30-9 Tables Grass Cutting Work Completed
646 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1 Non PV Area Grass Cutting Work Completed
647 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-07 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G2 Non PV Area Grass Cutting Work Completed
648 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-08 | 2 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | G5-Inv2 TW11 to T15-5 Tables Grass Cutting Work Completed
649 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-09 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G5-Inv6 T21 to T12-10 Tables Grass Cutting Work Completed
650 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-10 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 3 | G5-Inv6 T09 to T-11-2 Tables & Spare Area Surrounding Grass Cutting Work Completed
651 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Spare Area Surrounding Grass Cutting Work Completed
652 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-12 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Store Spare Area & G6 Non PV Area Grass Cutting Work Done
653 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-13 | 2 | 1 | 0 | 0 | 5 | 6 | 0 | 0 | 11 | G5-Inv 3&4 TW 01 to 10 & G6 TW1- 11 Tables Grass Cutting Work Completed
654 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | 2 | 1 | 0 | 3 | 6 | 5 | 0 | 0 | 14 | G6-Inv2, 3&4 TW 02 to 15 - 14 Tables Grass Cutting Work Completed
655 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Due to festival
656 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-16 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ICR2 Surrounding Area Grass Cutting Work Completed
657 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-17 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Manual Tree cutting at grid 5 and fencing side at grid 5 top area
658 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-18 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
659 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-19 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Non PV Area & G2 Non PV Area Grass Cutting Work Completed
660 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-20 | 2 | 1 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | G4 Non PV Area & G4 Inv 5- T04 to T09-6 Tables Grass Cutting Work Completed
661 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-21 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Between G3 &G4 Non PV Area Grass Cutting Work Completed
662 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
663 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-23 | 2 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | G5 Table 119 to table 127
664 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-24 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard & G5 Fench Side Bush Cutting Work Completed
665 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-25 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Fench Side & G1 Fench Side Area Grass Cutting Work Done
666 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
667 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-27 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1 Fench Side Area Grass Cutting Work Done
668 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-28 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G2 Fench Side Area Grass Cutting Work Done
669 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-29 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | B/w G1&2 fencing and Grass cutting work done
670 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-30 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1 Fench Side Area Grass Cutting Work Done
671 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-01 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-02 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1 Fench Side Area Grass Cutting Work Done
674 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-03 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1 Fench Side Manual Grass Cutting Work Done
675 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-04 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1& 2 Fench Side Manual Grass Cutting Work Done
676 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
677 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-06 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
678 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-07 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
679 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-08 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
680 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-09 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
681 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
682 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
683 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
684 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
685 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-14 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
686 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-15 | 2 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G3-Inv 5-Ttw01 to T04-10 Tables Grass Cutting Work Completed
687 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-16 | 2 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G3-Inv 2-Ttw06 toT14-8 Tables Grass Cutting Work Completed
688 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-17 | 2 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 11 | G4-Inv 1-T40 to T51-11 Tables Grass Cutting Work Completed
689 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-18 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G5-inv 4-T140 to T147-8 Tables Grass Cutting Work Completed
690 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
691 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
692 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-21 | 2 | 1 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | G5-Inv 1 T60 to T70-11 tables Grass Cutting work Completed
693 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
694 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-23 | 2 | 1 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | G5-Inv 4 T128 to T139-12 tables Grass Cutting work Completed
695 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
696 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-25 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
697 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
698 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-27 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
699 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-28 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-29 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
701 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-01 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
702 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-02 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
703 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-03 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
704 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-04 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
705 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
706 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Parcel 2 Vegitation Work Completed
707 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-07 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Parcel 2 Manual Grass Cutting Work Done
708 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-08 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
709 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-09 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
710 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
711 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
712 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
713 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-02 | 31 | 2024-03-13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
714 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-03 | 31 | 2024-03-14 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
715 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-04 | 31 | 2024-03-15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
716 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-05 | 31 | 2024-03-16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
717 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
718 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-18 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
718 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-19 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
719 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
720 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-21 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
721 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
722 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-23 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
723 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
724 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-25 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
725 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-26 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
726 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-27 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
727 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-28 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
728 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-29 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
729 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-30 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
730 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-06 | 31 | 2024-03-31 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
731 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-01 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
732 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-02 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ICR1 WMS Surrounding Vegitation Work Completed
733 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-03 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
734 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-04 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
735 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
736 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-02 | 30 | 2024-04-06 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
737 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-07 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
738 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-08 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
739 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-09 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
740 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
741 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-11 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
742 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-12 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
743 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-13 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
744 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-14 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
745 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-15 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Manual Grass Cutting work done
746 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
747 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
748 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-18 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
749 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-19 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
750 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-20 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 & G4 Manual Grass Cutting work done
751 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-21 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Manual Grass Cutting work done
752 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-22 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
753 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-23 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
754 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Manual Grass Cutting work done
755 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-25 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | Switch Yard Vegitation Work Done
755 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-26 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
756 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-27 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard Vegitation Work Done
757 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-28 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard Vegitation Work Done
758 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-29 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard Vegitation Work Done
759 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-03 | 30 | 2024-04-30 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
780 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-01 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
781 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-02 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 & G4 bushes Grass Removal Work Completed
782 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-03 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 & G4 Manual Grass Removal Work Completed
783 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-04 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Manual Grass Cutting work done
784 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
785 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-06 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
786 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-07 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4 Manual Grass Cutting work done
787 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-08 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
788 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-09 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
789 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-10 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Manual Grass Cutting work done
790 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-11 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
791 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-12 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
792 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-13 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Manual Grass Cutting work done
793 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-14 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Manual Grass Cutting Work done
794 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-15 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Manual Grass Cutting Work done
795 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-16 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G1 Manual Grass Cutting Work Done
796 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-17 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
797 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-18 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDT2 Switch Yard Vegitation work done
798 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-19 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
799 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-20 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-21 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDT1 Switch Yard Vegitation work done
801 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-22 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDT2 & WMS Switch Yard Vegitation work done
802 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-23 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Manual Grass Cutting work done
803 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-24 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 Manual Grass Cutting Work done
804 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-25 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Manual Grass Cutting Work Done
805 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-26 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4&G6 Manual Grass Cutting Work Done
806 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-27 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3&G4 Manual Grass Cutting Work Done
807 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-28 | 1 | 1 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | G5-inv 4-T148 to T158-11 Tables & G3,G4&G6 Manual Grass Cutting Work Done
808 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-29 | 1 | 1 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | G5-inv 4-T133 to T147-15 Tables & G3,G4&G6 Manual Grass Cutting Work Done
809 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-30 | 1 | 1 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | G5-inv 4-T119 to T132-14 Tables & G3,G4&G6 Manual Grass Cutting Work Done
810 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-03 | 31 | 2024-05-31 | 1 | 1 | 0 | 0 | 4 | 9 | 0 | 0 | 13 | G5-inv 4 & 3-T107 to T1118-13 Tables &G6 Manual Grass Cutting Work Done
811 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-01 | 1 | 1 | 0 | 0 | 12 | 0 | 0 | 0 | 12 | G5-inv 3-T96 to T106-12 Tables &G6 Manual Grass Cutting Work Done
812 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-02 | 1 | 1 | 0 | 0 | 5 | 6 | 0 | 0 | 11 | G5-inv 3& 4-T85 to T196-11 Tables Grass Cutting Work Done
813 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-03 | 1 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | G5-inv 4-T75 to T84-10 Tables Grass Cutting Work Done
814 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-04 | 1 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | G5-inv 3-T66 to T74-09 Tables Grass Cutting Work Done
815 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-05 | 1 | 1 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | G5-inv 2-T55 to T65-11 Tables Grass Cutting Work Done
816 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-06 | 1 | 1 | 0 | 0 | 11 | 0 | 0 | 0 | 11 | G4-Inv 3 -T88 to T98-11 Tables Grass Cutting Work Done
817 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-07 | 1 | 1 | 0 | 0 | 7 | 3 | 0 | 0 | 10 | G4-Inv 3 &4 -T99 to T108-10 Tables Grass Cutting Work Done
818 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-08 | 1 | 1 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | G4-Inv 4 -T109 to T119-11 Tables Grass Cutting Work Done
819 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-09 | 1 | 1 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | G4-Inv 4 -T120 to T131-12 Tables Grass Cutting Work Done
820 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-10 | 1 | 1 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | G4-Inv 4 -T132 to T143-12 Tables Grass Cutting Work Done
821 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-11 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 10 | 12 | G1-Inv 5& 6 -T41 to T52-12 Tables Grass Cutting Work Done
822 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-12 | 1 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G1-Inv 5 -T30 to T40-12 Tables Grass Cutting Work Done
823 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-13 | 1 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G1-Inv 5 -T20 to T29-10 Tables Grass Cutting Work Done
824 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-14 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
825 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-15 | 1 | 1 | 0 | 0 | 0 | 0 | 11 | 0 | 11 | G1-Inv 5 -T19 to T09-11 Tables Grass Cutting Work Done
826 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-16 | 1 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G1 & G2-Inv 5 -T01 to T08 & G2 TW1& T01 TO T03-12 Tables Grass Cutting Work Done
827 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-17 | 1 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G2-Inv 5-T04 to T15-12 Tables Grass Cutting Work Done
828 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-18 | 1 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G2-Inv 5-T16 to T27-12 Tables Grass Cutting Work Done
829 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-19 | 1 | 1 | 0 | 0 | 0 | 0 | 13 | 0 | 13 | G2-Inv 5-T28 to T40-13 Tables Grass Cutting Work Done
830 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-20 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Due to Rain Grass Cutting Not Done
831 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-21 | 1 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | G5-inv 2-T48 to T54-07 Tables Grass Cutting Work Done
832 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-22 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
833 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-23 | 1 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | G5-inv 2-T42 to T-T47 Tables Grass Cutting Work Done
834 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-24 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 3 | G5-inv 1-T39 to T-T41 Tables Grass Cutting Work Done
835 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-25 | 1 | 1 | 2 | 0 | 0 | 0 | 6 | 0 | 8 | G5-inv 1 &6-T30 to T-T38 Tables Grass Cutting Work Done
836 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-26 | 1 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G5-inv 6-T22 to T-T29-8 Tables Grass Cutting Work Done
837 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-27 | 1 | 1 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | G5-inv 6-T16 to T-T21-6 Tables Grass Cutting Work Done
838 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-28 | 1 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G5-inv 6-T06 to T-T15-10 Tables Grass Cutting Work Done
839 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-29 | 1 | 1 | 0 | 0 | 0 | 0 | 3 | 5 | 8 | G5-inv 6-T01 to T-T05 & G4 T01 TO T03-08 Tables Grass Cutting Work Done
840 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-03 | 30 | 2024-06-30 | 1 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G4-Inv 5- T04 TO T10-07 Tables Grass Cutting Work Done
841 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-01 | 1 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G4-Inv 5- T11 TO T19-09 Tables Grass Cutting Work Done
842 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-02 | 1 | 1 | 3 | 0 | 0 | 0 | 6 | 0 | 9 | G4-Inv 5- T20 TO T28-09 Tables Grass Cutting Work Done
843 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-03 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G4-Inv 1- T29 TO T37-09 Tables Grass Cutting Work Done
844 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-04 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G4-Inv 1- T38 TO T46-09 Tables Grass Cutting Work Done
845 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-05 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G4-Inv 1- T47 TO T55-09 Tables Grass Cutting Work Done
846 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-06 | 1 | 1 | 7 | 1 | 0 | 0 | 0 | 0 | 8 | G4-Inv 1 & 2 - T56 TO T63-08 Tables Grass Cutting Work Done
847 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-07 | 1 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | G4-Inv 2 - T64 TO T72-09 Tables Grass Cutting Work Done
848 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-08 | 1 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 5 | G4-Inv 3 - T73 TO T77-05 Tables Grass Cutting Work Done
849 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-09 | 1 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | G4-Inv 3 - T78 TO T85-09 Tables Grass Cutting Work Done
850 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-10 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard Grass Cutting Work Completed
851 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-11 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Non PV Area & ICR2 Surrounding Area Grass Cutting Work Completed
852 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-12 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Non PV Area Grass Cutting Work Completed
853 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-13 | 1 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G3-Inv 5-Ttw01 to T03-09 Tables Grass Cutting Work Completed
854 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-14 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G3-Inv 1-T04 to T12-09 Tables Grass Cutting Work Completed
855 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-15 | 1 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G3-Inv 1-T13 to T19-07 Tables Grass Cutting Work Completed
856 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-16 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G3-Inv 1-T20 to T28-09 Tables Grass Cutting Work Completed
857 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-17 | 1 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G3-Inv 1-T29 to T37-09 Tables Grass Cutting Work Completed
858 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-18 | 1 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G3-Inv 1-T38 to T44-07 Tables Grass Cutting Work Completed
859 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-19 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Due to Rain Grass Cutting Not Done
860 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-20 | 1 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | G3-Inv 2-T45 to T51-07 Tables Grass Cutting Work Completed
861 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-21 | 1 | 1 | 0 | 2 | 5 | 0 | 0 | 0 | 7 | G3-Inv 2 & 3-T52 to T58-07 Tables Grass Cutting Work Completed
862 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-22 | 1 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | G3-Inv 3-T59 to T68-10 Tables Grass Cutting Work Completed
863 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-23 | 1 | 1 | 0 | 0 | 0 | 5 | 4 | 0 | 9 | G5-Inv 4&3-TW1 to TW9-09 Tables Grass Cutting Work Completed
864 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-24 | 1 | 1 | 0 | 4 | 2 | 0 | 0 | 0 | 6 | G5-Inv 2&3-TW10 to TW15-06 Tables Grass Cutting Work Completed
865 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-25 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Due to Rain Grass Cutting Not Done
866 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-26 | 1 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | G6-Inv 3-T81 to T88-08 Tables Grass Cutting Work Completed
867 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-27 | 1 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | G6-Inv 2-1W 16 to TTW12-08 Tables Grass Cutting Work Completed
868 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-28 | 1 | 1 | 0 | 0 | 4 | 6 | 0 | 0 | 10 | G6-Inv 3&4-TW 01 to TW10-10 Tables Grass Cutting Work Completed
869 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-29 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G6-Inv 6-T 01 to T 10-10 Tables Grass Cutting Work Completed | cycle 3 completed
870 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-30 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
871 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 31 | 2024-07-31 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
872 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-01 | 2 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Fence side area Manual Grass cutting work done
873 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-02 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Additional Parcel Fench side Manual Grass Cutting Work Done
874 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-03 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Additional Parcel Fench side Manual Grass Cutting Work Done
875 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-04 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
876 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-05 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
877 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-06 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDT2 Switch Yard Vegitation work done
878 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Main Switch yard vegitation Work Done
879 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-08 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | IDT1 Switch Yard Vegitation work done
880 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-09 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
881 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
882 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-11 | [8 empty] | 0
883 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | [8 empty] | 0
884 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-13 | [8 empty] | 0
885 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-14 | [8 empty] | 0
886 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-15 | [8 empty] | 0
887 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-16 | [8 empty] | 0
888 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-17 | [8 empty] | 0
889 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-18 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Main gate road side area grass cutting work was completed
890 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard Grass Cutting Work Completed
891 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-20 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Switch Yard Grass Cutting Work Completed
892 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-21 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
893 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-22 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
894 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-23 | [8 empty] | 0
895 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-24 | [8 empty] | 0
896 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-25 | [8 empty] | 0
897 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-26 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G5-Inv 6-T1 to T10-10 Tables Grass Cutting Work Completed
898 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-27 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | G5-Inv 6-T11 to T17-07 Tables Grass Cutting Work Completed
899 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-28 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | G5-Inv 6-T18 to T25-08 Tables Grass Cutting Work Completed
900 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-29 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | G5-Inv 6-T26 to T29-04 Tables Grass Cutting Work Completed
901 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-30 | 2 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | G4-Inv 3-T88 to T89-02 Tables Grass Cutting Work Completed
902 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-31 | 2 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 10 | G4-Inv 3-T90 to T99-10 Tables Grass Cutting Work Completed
903 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-01 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 7 | 7 | G5-Inv 6-T29 to T35-07 Tables Grass Cutting Work Completed
904 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-02 | 2 | 1 | 4 | 2 | 0 | 0 | 0 | 1 | 7 | G5-Inv 6-T36 to T42-07 Tables Grass Cutting Work Completed
905 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-03 | 2 | 1 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | G5-Inv 2-T43 to T52-10 Tables Grass Cutting Work Completed
906 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-04 | 2 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | G5-Inv 2-T53 to T60-08 Tables Grass Cutting Work Completed
907 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-05 | 2 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | G5-Inv 2-T61 to T68-08 Tables Grass Cutting Work Completed
908 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-06 | 2 | 1 | 0 | 7 | 1 | 0 | 0 | 0 | 8 | G5-Inv 2-T69 to T76-08 Tables Grass Cutting Work Completed
909 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-07 | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | G5-Inv 3-T77 to T79-03 Tables & Spare Area Grass Cutting Work Completed
910 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-08 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Spare Area Surrounding Grass Cutting Work Completed
911 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-09 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | spare Area Surrounding & ICR1 Surrounding Grass Cutting Work Completed
912 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-10 | 2 | 1 | 0 | 0 | 4 | 8 | 0 | 0 | 12 | G5-Inv 3 & 4-T81 to T91-12 Tables Grass Cutting Work Completed
913 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-11 | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 3 | G5-Inv 3 -T100 to T102-02 Tables Grass Cutting Work Completed
914 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-12 | 2 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | G5-Inv 3 -T102 to T109-08 Tables Grass Cutting Work Completed
915 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-13 | 2 | 1 | 0 | 0 | 1 | 5 | 0 | 0 | 6 | G5-Inv 3 -T110 to T114-06 Tables Grass Cutting Work Completed
916 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-14 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G5-Inv 4 -T115 to T122-08 Tables Grass Cutting Work Completed
917 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-15 | 2 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | G5-Inv 4 -T123 to T131-09 Tables Grass Cutting Work Completed
918 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-16 | 2 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | G5-Inv 4 -T132 to T141-10 Tables Grass Cutting Work Completed
919 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-17 | 2 | 1 | 0 | 0 | 0 | 0 | 4 | 10 | 14 | G1-Inv 6&5 -T39 to T52-14 Tables Grass Cutting Work Completed
920 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-18 | 2 | 1 | 0 | 0 | 0 | 0 | 13 | 0 | 13 | G1-Inv 5 -T26 to T38-13 Tables Grass Cutting Work Completed
921 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-19 | 2 | 1 | 0 | 0 | 0 | 0 | 6 | 0 | 6 | G4-Inv 5 -T01 to T06-06 Tables Grass Cutting Work Completed
922 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-20 | [8 empty] | 0
923 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-21 | 2 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G4-Inv 5 -T07 to T13-08 Tables Grass Cutting Work Completed
924 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-22 | 2 | 1 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | G4-Inv 5 -T14 to T18-05 Tables Grass Cutting Work Completed
925 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-23 | [8 empty] | 0
926 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-24 | [8 empty] | 0
927 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-25 | 2 | 1 | 1 | 0 | 0 | 0 | 7 | 0 | 8 | G4-Inv 5 -T19 to T26-08 Tables Grass Cutting Work Completed
928 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-26 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G4-Inv 1 -T27 to T32-06 Tables Grass Cutting Work Completed
929 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-27 | 2 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G4-Inv 1 -T33 to T39-07 Tables Grass Cutting Work Completed
930 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-28 | [8 empty] | 0
931 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-29 | 2 | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G4-Inv 1 -T40 to T46-07 Tables Grass Cutting Work Completed
932 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 30 | 2024-09-30 | 2 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G4-Inv 1 -T47 to T52-06 Tables Grass Cutting Work Completed
933 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-01 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-02 | 2 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G4-Inv 1 -T53 to T60-08 Tables Grass Cutting Work Completed
935 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | 2 | 1 | 2 | 6 | 0 | 0 | 0 | 0 | 8 | G4-Inv 1 & Inv 2 -T61 to T68-08 Tables Grass Cutting Work Completed
936 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-04 | 2 | 1 | 0 | 4 | 4 | 0 | 0 | 0 | 8 | G4-Inv 2 & Inv 3 -T69 to T76-08 Tables Grass Cutting Work Completed
937 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-05 | 2 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | G4-Inv 3 -T77 to T85-09 Tables Grass Cutting Work Completed
938 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-06 | 2 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | G4-Inv 3 -T86 to T89 & T101 to 104-08 Tables Grass Cutting Work Completed
939 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-07 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4-Inv 4 -T105 to T112 -08 Tables Grass Cutting Work Completed
940 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-08 | [8 empty] | 0 | Due to Rain Grass Cutting Not Done
941 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-09 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4-Inv 4 -T113 to T119 -08 Tables Grass Cutting Work Completed
942 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-10 | 2 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | G4-Inv 4 -T120 to T129 -09 Tables Grass Cutting Work Completed
943 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-11 | [8 empty] | 0
944 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-12 | 2 | 1 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | G4-Inv 4 -T130 to T134 -04 Tables Grass Cutting Work Completed
945 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-13 | 2 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | G4-Inv 4 -T135 to T140 -06 Tables Grass Cutting Work Completed
946 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-14 | 2 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G1-Inv 5 -T14 to T125 -12 Tables Grass Cutting Work Completed
947 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-15 | [8 empty] | 0 | Due to Rain Grass Cutting Not Done
948 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-16 | 2 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G1-Inv 5 -T06 to T113 -08 Tables Grass Cutting Work Completed
949 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-17 | 2 | 1 | 0 | 0 | 0 | 0 | 10 | 0 | 10 | G1-Inv 5 -T01 to T05 & G2 -T01 TO T05-10 Tables Grass Cutting Work Completed
950 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-18 | 2 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G2-T06 TO T16 -12 Tables Grass Cutting Work Completed
951 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-19 | 2 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 4 | G2-T17 TO T20 -04 Tables Grass Cutting Work Completed
952 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-20 | [8 empty] | 0 | Due to Rain Grass Cutting Not Done
953 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-21 | [8 empty] | 0 | Due to Rain Grass Cutting Not Done
954 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-22 | 2 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G2-T21 TO T29 -09 Tables Grass Cutting Work Completed
955 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-23 | 2 | 1 | 0 | 0 | 0 | 0 | 11 | 0 | 11 | G2-T30 TO T40 -11 Tables Grass Cutting Work Completed
956 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | [8 empty] | 0 | Due to Rain Grass Cutting Not Done
957 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G4-Inv 4 -T141 to T143 & G5-inv4-T -08 Tables Grass Cutting Work Completed
958 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-26 | 2 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G5-Inv 4-T147 TO T154 -08 Tables Grass Cutting Work Completed
959 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-27 | 2 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | G5-Inv 3-T92 TO T99 -08 Tables Grass Cutting Work Completed
960 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-28 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 9 | 9 | G6-Inv 6-T01 TO T09 -09 Tables Grass Cutting Work Completed
961 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | [8 empty] | 0
962 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-30 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | G6-Inv 6-T10 TO T14 -05 Tables Grass Cutting Work Completed
963 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | G6-Inv 6-T15 TO T21 -06 Tables Grass Cutting Work Completed
964 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-01 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | G6-Inv 6-T22 TO T27 -06 Tables Grass Cutting Work Completed
965 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | G6-Inv 6-T28 TO T43 -16 Tables Grass Cutting Work Completed
966 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-03 | 2 | 1 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | G6-Inv 2-T44 TO T55 -12 Tables Grass Cutting Work Completed
967 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-04 | 2 | 1 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | G6-Inv 2-T56 TO T71 -16 Tables Grass Cutting Work Completed
968 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | 2 | 1 | 0 | 8 | 9 | 0 | 0 | 0 | 17 | G6-Inv 2 & 3 -T72 TO T88 -16 Tables Grass Cutting Work Completed
969 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-06 | 2 | 1 | 0 | 0 | 0 | 0 | 12 | 0 | 12 | G3- Inv 5 & 1-T3A-T1 TO T5 & TW1 TO- T6-12 Tables Grass Cutting Work Completed
970 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-07 | 2 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G3- Inv1- T07 TO- T14-8 Tables Grass Cutting Work Completed
971 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-08 | 2 | 1 | 18 | 0 | 0 | 0 | 0 | 0 | 18 | G3- Inv1- T15 TO- T32-18 Tables Grass Cutting Work Completed
972 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-09 | 2 | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 12 | G3- Inv1- T33 TO- T44-18 Tables Grass Cutting Work Completed
973 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-10 | 2 | 1 | 0 | 9 | 1 | 0 | 0 | 0 | 10 | G3- Inv2- T45 TO- T54-10 Tables Grass Cutting Work Completed
974 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-11 | 2 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | G3- Inv3- T55 TO- T63-9 Tables Grass Cutting Work Completed
975 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-12 | 2 | 1 | 0 | 0 | 4 | 5 | 0 | 0 | 9 | G3- Inv3- T64 TO- T68 & TW13 TO 17 -9 Tables Grass Cutting Work Completed
976 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-13 | 2 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | G5- TW09 TO 12 -4 Tables Grass Cutting Work Completed
977 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-14 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
978 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-15 | [8 empty] | 0 | Not done due to Rain
979 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-16 | [8 empty] | 0 | Not done due to Rain
980 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-17 | [8 empty] | 0 | Not done due to Rain
981 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | [8 empty] | 0
982 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-19 | 3 | 1 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | G5- TW01 TO 10 -10 Tables Grass Cutting Work Completed
983 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-20 | 3 | 1 | 0 | 0 | 6 | 6 | 0 | 0 | 12 | G6-TW06 TO TW16-12 Tables Grass Cutting Work Completed
984 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-21 | 3 | 1 | 0 | 0 | 8 | 5 | 0 | 0 | 13 | G6-TW01 TO TW05 & G5 T101 to T108-13 Tables Grass Cutting Work Completed
985 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-22 | 3 | 1 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | G5- T109 & T110A to T113-13 Tables Grass Cutting Work Completed
986 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-23 | 3 | 1 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | G5- TT14 T120-07 Tables Grass Cutting Work Completed
987 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-24 | 3 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | G5- TT121 T129-09 Tables Grass Cutting Work Completed
988 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-25 | 3 | 1 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | G5- TT130 T142-13 Tables Grass Cutting Work Completed
989 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-26 | [8 empty] | 0 | Not done due to helpers taken weekoff
990 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-27 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | G5-T01 TO t05-05 tables Grass Cutting Work Completed
991 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-28 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G5-T06 T15 -10 tables Grass Cutting Work Completed
992 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-29 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | G5-T16 T25 -10 tables Grass Cutting Work Completed
993 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-30 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | G5-T26 T33 -08 tables Grass Cutting Work Completed
994 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-01 | 3 | 1 | [6 empty] | 0 | Due to Rain Grass Cutting Not Done
995 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-02 | 3 | 1 | [6 empty] | 0 | Due to Rain Grass Cutting Not Done
996 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-03 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Non PV area Manual Grass Cutting work done
997 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-04 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Non PV area Manual Grass Cutting work done
998 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-05 | 3 | 1 | 4 | 3 | 0 | 0 | 0 | 3 | 10 | G5-T34 to T43 -10 tables Grass Cutting Work Completed
999 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-06 | 3 | 1 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | G5-T44 to T52 -09 tables & spare Area Grass Cutting Work Completed
1000 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-07 | 3 | 1 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | G5-T53 to T72 -20 tables & spare Area Grass Cutting Work Completed
1001 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-08 | 3 | 1 | 0 | 3 | 2 | 0 | 0 | 0 | 5 | G5-T73 to T77 -5 tables Grass Cutting work completed
1002 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-09 | 3 | 1 | 0 | 0 | 8 | 6 | 5 | 0 | 19 | G5-T78 to T91 & G4-T01 to T05 -19 tables Grass Cutting work completed
1003 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-10 | 3 | 1 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | G4-T06 to T10 -05 tables Grass Cutting work completed
1004 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-11 | [8 empty] | 0
1005 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-12 | 3 | 1 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G4-T11 to T18 -08 tables Grass Cutting work completed
1006 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-13 | 3 | 1 | 2 | 0 | 0 | 0 | 7 | 0 | 9 | G4-T19 to T27 -09 tables Grass Cutting work completed
1007 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-14 | 3 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G4-T28 to T36 -09 tables Grass Cutting work completed
1008 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-15 | 3 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | G4-T37 to T50 -15 tables Grass Cutting work completed
1009 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-16 | 3 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | G4-T51 to T59 -09 tables Grass Cutting work completed
1010 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-17 | [8 empty] | 0
1011 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-18 | 3 | 1 | 2 | 10 | 0 | 0 | 0 | 0 | 12 | G4-T60 to T71 -12 tables Grass Cutting work completed
1012 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-19 | 3 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 9 | G4-T72 to T80 -09 tables Grass Cutting work completed
1013 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-20 | 3 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 7 | G4-T81 to T87 -07 tables Grass Cutting work completed
1014 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-21 | 3 | 1 | 0 | 0 | 18 | 0 | 0 | 0 | 18 | G4-T88 to T105 -18 tables Grass Cutting work completed
1015 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-22 | [8 empty] | 0
1016 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-23 | 3 | 1 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | G4-T106 to T125 -20 tables Grass Cutting work completed
1017 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-24 | 3 | 1 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | G4-T126 to T131 -06 tables Grass Cutting work completed
1018 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-25 | [8 empty] | 0
1019 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-26 | 4 | 1 | 0 | 0 | 0 | 0 | 2 | 10 | 12 | G1- T41 to T52-12 Tables Grass Cutting Work completed
1020 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-27 | 4 | 1 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | G1- T36 to T40-05 Tables Grass Cutting Work completed
1021 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-28 | [8 empty] | 0
1022 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-29 | [8 empty] | 0
1023 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-30 | [8 empty] | 0
1024 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 31 | 2024-12-31 | 4 | 1 | 0 | 0 | 0 | 0 | 9 | 0 | 9 | G1-T26 to T35-09 Tables Grass Cutting Work Completed
1025 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-01 | [8 empty] | 0
1026 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-02 | 4 | 1 | 0 | 0 | 0 | 0 | 14 | 0 | 14 | G1-T12 to T25-14 Tables Grass Cutting Work Completed
1027 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-03 | [8 empty] | 0
1028 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-04 | 4 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G1-T05 to T11-07 Tables Grass Cutting Work Completed
1029 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-05 | 4 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 4 | G1-T01 to T04-04 Tables Grass Cutting Work Completed
1030 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | [8 empty] | 0
1031 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-07 | [8 empty] | 0
1032 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | 4 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G2-T35 to T41-07 Tables Grass Cutting Work Completed
1033 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-09 | [8 empty] | 0
1034 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-10 | 4 | 1 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | G2-T28 to T34-07 Tables Grass Cutting Work Completed
1035 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-11 | 4 | 1 | 0 | 0 | 0 | 0 | 11 | 0 | 11 | G2-T18 to T27-11 Tables Grass Cutting Work Completed
1036 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-12 | 4 | 1 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | G2-T01 to T17-17 Tables Grass Cutting Work Completed
1037 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-13 | [8 empty] | 0
1038 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-14 | [8 empty] | 0
1039 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-15 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Spare Area Grass Cutting Completed
1040 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-16 | [8 empty] | 0
1041 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-17 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G2 Side Non PV Area Grass Cutting Work done
1042 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-18 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Spare Area Grass Cutting Completed
1043 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-19 | [8 empty] | 0
1044 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-20 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Spare Area Grass Cutting Completed
1045 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-21 | [8 empty] | 0
1046 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-22 | [8 empty] | 0
1047 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-23 | [8 empty] | 0
1048 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-24 | [8 empty] | 0
1049 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | [8 empty] | 0
1050 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-26 | [8 empty] | 0
1051 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-27 | [8 empty] | 0
1052 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | [8 empty] | 0
1053 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-29 | [8 empty] | 0
1054 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-30 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Fench Side Grass Cutting Work Done
1055 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-31 | [8 empty] | 0
1056 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-01 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Fench Side Grass Cutting Work Done
1057 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-02 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Fench Side Grass Cutting Work Done
1058 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-03 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Fench Side Grass Cutting Work Done
1059 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-04 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Fence side area Grass cutting work done
1060 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-05 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Fence side area Grass cutting work done
1061 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-06 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 Fench Side Grass Cutting Work Done
1062 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-07 | [8 empty] | 0
1063 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-08 | [8 empty] | 0
1064 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-09 | [8 empty] | 0
1065 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-10 | [8 empty] | 0
1066 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-11 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G3 Fench Side Grass cutting Work Done
1067 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-12 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
1068 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-13 | [8 empty] | 0
1069 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-14 | [8 empty] | 0
1070 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-15 | [8 empty] | 0
1071 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-16 | [8 empty] | 0
1072 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-17 | [8 empty] | 0
1073 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-18 | [8 empty] | 0
1074 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-19 | [8 empty] | 0
1075 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-20 | [8 empty] | 0
1076 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-21 | [8 empty] | 0
1077 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-22 | [8 empty] | 0
1078 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-23 | [8 empty] | 0
1079 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-24 | [8 empty] | 0
1080 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-25 | [8 empty] | 0
1081 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-26 | [8 empty] | 0
1082 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-27 | [8 empty] | 0
1083 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-02-01 | 28 | 2025-02-28 | [8 empty] | 0
1084 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-01 | [8 empty] | 0
1085 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-02 | [8 empty] | 0
1086 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-03 | [8 empty] | 0
1087 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-04 | [8 empty] | 0
1088 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-05 | [8 empty] | 0
1089 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-06 | [8 empty] | 0
1090 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-07 | [8 empty] | 0
1091 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-08 | [8 empty] | 0
1092 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-09 | [8 empty] | 0
1093 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-10 | [8 empty] | 0
1094 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-11 | [8 empty] | 0
1095 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-12 | [8 empty] | 0
1096 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-13 | [8 empty] | 0
1097 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-14 | [8 empty] | 0
1098 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-15 | [8 empty] | 0
1099 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-16 | [8 empty] | 0
1100 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-17 | [8 empty] | 0
1101 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-18 | [8 empty] | 0
1102 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-19 | [8 empty] | 0
1103 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-20 | [8 empty] | 0
1104 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | [8 empty] | 0
1105 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-22 | [8 empty] | 0
1106 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-23 | [8 empty] | 0
1107 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-24 | [8 empty] | 0
1108 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-25 | [8 empty] | 0
1109 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-26 | [8 empty] | 0
1110 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | [8 empty] | 0
1111 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-28 | [8 empty] | 0
1112 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | [8 empty] | 0
1113 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-30 | [8 empty] | 0
1114 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-31 | [8 empty] | 0
1115 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-01 | [8 empty] | 0
1116 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | [8 empty] | 0
1117 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-03 | [8 empty] | 0
1118 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | [8 empty] | 0
1119 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | [8 empty] | 0
1120 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | [8 empty] | 0
1121 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | [8 empty] | 0
1122 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | [8 empty] | 0
1123 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-09 | [8 empty] | 0
1124 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | [8 empty] | 0
1125 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | [8 empty] | 0
1126 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | [8 empty] | 0
1127 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | [8 empty] | 0
1128 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-14 | [8 empty] | 0
1129 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-15 | [8 empty] | 0
1130 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | [8 empty] | 0
1131 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-17 | [8 empty] | 0
1132 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-18 | [8 empty] | 0
1133 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | [8 empty] | 0
1134 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | [8 empty] | 0
1135 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | [8 empty] | 0
1136 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | [8 empty] | 0
1137 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-23 | [8 empty] | 0
1138 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | [8 empty] | 0
1139 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-25 | [8 empty] | 0
1140 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | [8 empty] | 0
1141 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-27 | [8 empty] | 0
1142 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | [8 empty] | 0
1143 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | [8 empty] | 0
1144 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | [8 empty] | 0
1145 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-01 | [8 empty] | 0
1146 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-02 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 T1 TO T10-10 Tab;es Manual Grass Cutting Work Done
1147 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-03 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 T21 TO T42-10 Tab;es Manual Grass Cutting Work Done
1148 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-04 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5 T43 TO T60-17 Tab;es Manual Grass Cutting Work Done
1149 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-05 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 T01 TO T20-20 Tables Manual Grass Cutting Work Done
1150 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-06 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 T21 TO T40-20 Tables Manual Grass Cutting Work Done
1151 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-07 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 T41 TO T60-20 Tables Manual Grass Cutting Work Done
1152 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-08 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 T61 TO T80-20 Tables Manual Grass Cutting Work Done
1153 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-09 | [8 empty] | 0
1154 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-10 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G6 T81 TO T88-08 Tables Manual Grass Cutting Work Done
1155 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-11 | [8 empty] | 0
1156 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-12 | [8 empty] | 0
1157 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-13 | [8 empty] | 0
1158 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-14 | [8 empty] | 0
1159 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-15 | [8 empty] | 0
1160 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-16 | [8 empty] | 0
1161 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-17 | [8 empty] | 0
1162 | FY2024-25 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-18 | [8 empty] | 0
1163 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-19 | [8 empty] | 0
1164 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-20 | [8 empty] | 0
1165 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-21 | [8 empty] | 0
1166 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-22 | [8 empty] | 0
1167 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-23 | [8 empty] | 0
1168 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-24 | [8 empty] | 0
1169 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-25 | [8 empty] | 0
1170 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-26 | [8 empty] | 0
1171 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-27 | [8 empty] | 0
1172 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-28 | [8 empty] | 0
1173 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-29 | [8 empty] | 0
1174 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-30 | [8 empty] | 0
1175 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 2025-05-31 | [8 empty] | 0
1176 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-01 | [8 empty] | 0
1177 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-02 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T01 TO T25 -Manual Grass cutting work completed
1178 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-03 | [8 empty] | 0
1179 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T26 TO T50 -Manual Grass cutting work completed
1180 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T51 TO T70 -Manual Grass cutting work completed
1181 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T71 TO T89 -Manual Grass cutting work completed
1182 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T90 TO T120 -Manual Grass cutting work completed
1183 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-08 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T121 TO T140 -Manual Grass cutting work completed
1184 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G5-T141 TO T155 -Manual Grass cutting work completed
1185 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 1 | 2 | 0 | 0 | 0 | 0 | 4 | 0 | 4 | G4 T01 TO T04 -04 Tables Grass Cutting Work Completed
1186 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 1 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G4 T05 TO T12 -08 Tables Grass Cutting Work Completed
1187 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-12 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | G4-T101 TO T135 -Manual Grass cutting work Completed
1188 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-13 | 1 | 2 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | G4 T13 TO T20 -08 Tables Grass Cutting Work Completed
1189 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 1 | 2 | 3 | 0 | 0 | 0 | 4 | 0 | 7 | G4 T21 TO T27 -07 Tables Grass Cutting Work Completed
1190 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-15 | 1 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 7 | G4 T28 TO T34 -07 Tables Grass Cutting Work Completed
1191 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-16 | 1 | 2 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | G4 T35 TO T49 -15 Tables Grass Cutting Work Completed
1192 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 1 | 2 | 11 | 5 | 0 | 0 | 0 | 0 | 16 | G4 T50 TO T65 -16 Tables Grass Cutting Work Completed
1193 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 1 | 2 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | G4 T66 TO T73 -08 Tables Grass Cutting Work Completed
1194 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 1 | 2 | 0 | 0 | 14 | 0 | 0 | 0 | 14 | G4 T74 TO T87 -14 Tables Grass Cutting Work Completed
1195 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-20 | 1 | 2 | 0 | 0 | 18 | 0 | 0 | 0 | 18 | G4 T88 TO T105 -18 Tables Grass Cutting Work Completed
1196 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-21 | 1 | 2 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | G4-T106 to T114 -09 tables Grass Cutting work completed
1197 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-22 | 1 | 2 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | G4-T115 to T125 -11 tables Grass Cutting work completed
1198 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-23 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
1199 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MCR Surrounding Area Grass Cutting Work Done
1200 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 1 | 2 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | G4-T126 to T140 -15 tables Grass Cutting work completed
1201 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | 1 | 2 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | G4-T141 to T143 & G5-T146 TO T158 -16 tables Grass Cutting work completed
1202 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-27 | 1 | 2 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | G5-T131 TO T145 -15 tables Grass Cutting work completed
1203 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-28 | 1 | 2 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | G5-T118 TO T130 -13 tables Grass Cutting work completed
1204 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 1 | 2 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | G5-T110 TO T117 -08 tables Grass Cutting work completed
1205 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | 1 | 2 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | G5-T105 TO T110A -06 tables Grass Cutting work completed
1206 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-01 | 1 | 2 | 0 | 0 | 0 | 0 | 13 | 0 | 13 | G3 TW1 TO TW5-5 Tables & T1 TO T8-13 Tables Grass Cutting work Completed
1207 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | 1 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | G3 - T9 TO T13-05 Tables Grass Cutting work Completed
1208 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-03 | 1 | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G3 - T14 TO T 21-8 Tables Grass Cutting work Completed
1209 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-04 | 1 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | G3 - T22 TO T 31-10 Tables Grass Cutting work Completed
1210 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-05 | 1 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | G3 - T32 TO T 37-06 Tables Grass Cutting work Completed
1211 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 1 | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | G3 - T38 TO T 45-08 Tables Grass Cutting work Completed
Formulas:
Days = DAY(EOMONTH([Month Year],0))
Date = [Date, row above]+1

## Spare_Consumable
Sr. No. | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Date | Item Consumed | Qty Consumed | Place of Consumption | Ownership of Spare/Consumable | Remarks for the day
1 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | MC4 CONNECTORS | 1 | IC1_Inv4_SCB2_String9
2 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | +VE YCONNECTOR | 1 | IC1_Inv4_SCB3_String14
3 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | +VE YCONNECTOR | 1 | IC1_Inv4_SCB6_String4
4 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | MC4 CONNECTORS | 1 | IC2_Inv1_SCB1_String9
5 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | MC4 CONNECTORS | 1 | IC2_Inv1_SCB2_String1
6 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-05-01 | 31 | 2022-05-06 | +VE YCONNECTOR | 1 | IC2_Inv1_SCB10_String2
7 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-09 | Y CONNECTORS | 1 | IC1_Inv2_SCB1_String14
8 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-09 | No used | 1 | IC1_Inv2_SCB6_String10
9 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-11 | Y CONNECTORS | 1 | IC1_Inv2_SCB8_String5
10 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | Y CONNECTORS | 1 | IC1_Inv2_SCB5_String5
11 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | Mc4 connector Male | 1 | IC1_Inv2_SCB1_String9
12 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | Negative Y connector | 1 | IC1_Inv2_SCB6_String12
13 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | Positive Y connector | 1 | IC1_Inv1_SCB6_String12
14 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-12 | Positive Y connector | 1 | IC1_Inv1_SCB5_String8
15 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | Positive Y connector | 1 | IC1_Inv1_SCB1_String5
16 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | Positive Y connector | 1 | IC1_Inv1_SCB8_String13
17 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | Positive Y connector | 1 | IC1_Inv3_SCB1_String1
18 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | Positive Y connector | 1 | IC1_Inv3_SCB1_String14
19 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-15 | Mc4 connector Male & Female | 1 | IC1_Inv3_SCB7_String9
20 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-19 | Positive Y connector | 1 | IC1_Inv4_SCB4_String13
21 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-29 | Positive Y connector | 1 | IC1_Inv4_SCB6_String10
22 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-07-01 | 31 | 2022-07-29 | Positive Y connector | 1 | IC2_Inv1_SCB1_String1
23 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-02 | Mc4 connector Male & Female | 1 | IC1_Inv4_SCB8_String6
24 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-07 | Positive Y connector | 1 | IC2_Inv6_SCB3_String7
25 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-07 | Positive Y connector | 1 | IC2_Inv5_SCB2_String8
26 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-16 | Tilt sensor add-04 installed | 1 | IC2_Inv1
27 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | pcb board replaced | 1 | IC1_Inv4
28 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
29 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
30 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-19 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
31 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-20 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
32 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-20 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
33 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-21 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
34 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-21 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv1
35 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-22 | Tilt sensor add-02 installed | 2 | IC1_Inv4
36 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-22 | New 2 Nos Battery Replaced | 2 | IC1_Inv4
37 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-23 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
38 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-25 | Positive Y connector | 1 | IC2_Inv5_SCB2_String 1
39 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-25 | Positive Y connector | 1 | IC2_Inv5_SCB4_String 4
40 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-25 | Positive Y connector | 1 | IC1_Inv2_SCB5_String 13
41 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-25 | Positive Y connector | 1 | IC1_Inv1_SCB3_String 6
42 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-25 | Positive Y connector | 1 | IC1_Inv3_SCB3_String 13
43 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-25 | Positive Y connector | 2 | IC1_Inv4_SCB3_String 7 & 14
44 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | New 2 Nos Battery Replaced | 2 | IC2_Inv1
45 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | Pcb board replaced | 1 | IC2_Inv2
46 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-27 | Add 002 tilt sensor installed | 2 | IC2_Inv2
47 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-27 | Y-Connector | 1 | IC1_Inv4_SCB3_String 3
48 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-27 | String Cable | 6 Metre | IC1_Inv4_SCB5_String 2
49 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-28 | Y-Connector | 1 | IC1_Inv4_SCB4_String 12
50 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-01 | 31 | 2022-08-31 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
51 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-08-02 | 31 | 2022-08-31 | MC4 Connector | 1 | IC2_Inv6_SCB4_String 7
52 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
53 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | Actuator 1 small,1 medium gear wheel & Diode 2 Nos was replaced | Each 1 | IC1_Inv4
54 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-03 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Noswas replaced | Each 1 | IC2_Inv2
55 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
56 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC1_Inv2
57 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | Actuator 1 small,1 medium gear wheel & Diode 2 Nos was replaced | Each 1 | IC1_Inv3
58 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-01 | 30 | 2022-09-04 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC1_Inv2
59 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-02 | 30 | 2022-09-07 | MC4 Connector | 1 | IC1_Inv4_SCB4_String 12
60 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-02 | 30 | 2022-09-07 | MC4 Connector | 1 | IC1_Inv4_SCB3_String 7
61 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-02 | 30 | 2022-09-07 | MC4 Connector | 1 | IC1_Inv4_SCB3_String 14
62 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-02 | 30 | 2022-09-07 | Y-Connector | 1 | IC1_Inv1_SCB7_String 9
63 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-02 | 30 | 2022-09-07 | Y-Connector | 1 | IC2_Inv6_SCB1_String 9
64 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-03 | 30 | 2022-09-09 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC1_Inv2
65 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-04 | 30 | 2022-09-09 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv3
66 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-05 | 30 | 2022-09-09 | Actuator 1 small,1 medium gear wheel & Diode 2 Nos was replaced | Each 1 | IC1_Inv 1
67 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-06 | 30 | 2022-09-09 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC1_Inv 4
68 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-07 | 30 | 2022-09-10 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB2_String 7
69 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-08 | 30 | 2022-09-10 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC1_Inv 3
70 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-09 | 30 | 2022-09-10 | Actuator 1 Big gear wheel & 1 motor& Diode 2 Nos was replaced | Each 1 | IC1_Inv 3
71 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-10 | 30 | 2022-09-10 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 3
72 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-11 | 30 | 2022-09-10 | Actuator 1 small,1 medium gear wheel & Diode 2 Nos was replaced | Each 1 | IC2_Inv 5
73 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-12 | 30 | 2022-09-10 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC2_Inv 5
74 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-13 | 30 | 2022-09-11 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC2_Inv 5
75 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-14 | 30 | 2022-09-11 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB2_String 7
76 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-15 | 30 | 2022-09-11 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB3_String 6
77 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-16 | 30 | 2022-09-12 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB3_String 6
78 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-17 | 30 | 2022-09-13 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB1_String 6
79 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-18 | 30 | 2022-09-13 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 5
80 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-19 | 30 | 2022-09-13 | Actuator 1 small,1 medium gear wheel & Diode 2 Nos was replaced | Each 1 | IC1_Inv 1
81 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-20 | 30 | 2022-09-13 | Actuator 1 Big gear wheel & 1 motor & Diode 2 Nos was replaced | Each 1 | IC2_Inv 6
82 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-21 | 30 | 2022-09-13 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 1
83 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-22 | 30 | 2022-09-14 | Actuator 1 small,1 medium gear wheel & Diode 2 Nos was replaced | Each 1 | IC1_Inv 2
84 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-23 | 30 | 2022-09-14 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 2
85 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-24 | 30 | 2022-09-14 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB1_String 6
86 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-25 | 30 | 2022-09-14 | Negative Y connector Replaced | 1 | IC1_Inv2_SCB10_String 7
87 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-25 | 30 | 2022-09-14 | Mc4 Connector replaced | 1 | IC1_Inv1_SCB7_String 13
88 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-25 | 30 | 2022-09-14 | Mc4 Connector replaced | 1 | IC1_Inv4_SCB8_String 9
89 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-26 | 30 | 2022-09-15 | Mc4 Connector replaced | 1 | IC1_Inv4_SCB5_String 14
90 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-27 | 30 | 2022-09-15 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB1_String 4
91 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-28 | 30 | 2022-09-15 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB1_String 3
92 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-29 | 30 | 2022-09-15 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 5
93 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-15 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 5
94 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-15 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 5
95 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-16 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB2_String 6
96 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-16 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB3_String 3
97 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-17 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB2_String 2
98 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-17 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 1
99 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB3_String 1
100 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 320 Watts module(1 No)104110100024 | 1 | IC2_Inv5_SCB7_String 1
101 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110101130 | 1 | IC2_Inv5_SCB7_String 8
102 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110101176 | 1 | IC1_Inv1_SCB3_String 13
103 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110101127 | 1 | IC1_Inv1_SCB4_String 12
104 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100753 | 1 | IC1_Inv1_SCB4_String 13
105 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110101014 | 1 | IC1_Inv1_SCB6_String 13
106 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110101023 | 1 | IC1_Inv1_SCB7_String 10
107 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100881 | 1 | IC1_Inv1_SCB8_String 14
108 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100791 | 1 | IC1_Inv1_SCB8_String 14
109 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100840 | 1 | IC1_Inv2_SCB2_String 13
110 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100877 | 1 | IC1_Inv3_SCB1_String 13
111 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100997 | 1 | IC1_Inv3_SCB1_String 13
112 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100805 | 1 | IC1_Inv3_SCB1_String 13
113 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100965 | 1 | IC1_Inv3_SCB1_String 13
114 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100986 | 1 | IC1_Inv3_SCB1_String 11
115 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-18 | Replaced old PV 325 Watts module(1 No)104110100502 | 1 | IC1_Inv3_SCB8_String 1
116 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB3_String 3
117 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | 21 Nos New (PV 330 W )Module was replaced | 21 | IC1_Inv4_SCB1_String 3
118 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101192 | 1 | IC1_Inv2_SCB3_String 13
119 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101194 | 1 | IC1_Inv2_SCB3_String 13
120 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101198 | 1 | IC1_Inv2_SCB4_String 13
121 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101111 | 1 | IC1_Inv2_SCB7_String 9
122 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101245 | 1 | IC1_Inv2_SCB8_String 3
123 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101257 | 1 | IC1_Inv2_SCB8_String 2
124 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101258 | 1 | IC1_Inv2_SCB9_String 6
125 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101259 | 1 | IC1_Inv1_SCB9_String 7
126 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101290 | 1 | IC2_Inv6_SCB7_String 3
127 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-19 | Replaced old PV 325 Watts module(1 No)104110101253 | 1 | IC2_Inv6_SCB7_String 3
128 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB4_String 1
129 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101123 | 1 | IC1_Inv3_SCB4_String 3
130 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101099 | 1 | IC1_Inv3_SCB4_String 3
131 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101210 | 1 | IC1_Inv3_SCB4_String 4
132 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101124 | 1 | IC1_Inv3_SCB4_String 9
133 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101252 | 1 | IC1_Inv3_SCB4_String 10
134 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101289 | 1 | IC1_Inv3_SCB5_String 10
135 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101097 | 1 | IC1_Inv3_SCB7_String 14
136 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101133 | 1 | IC1_Inv3_SCB5_String 8
137 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101375 | 1 | IC1_Inv3_SCB5_String 8
138 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101491 | 1 | IC1_Inv3_SCB4_String 7
139 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101040 | 1 | IC1_Inv3_SCB3_String 1
140 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101385 | 1 | IC1_Inv3_SCB2_String 2
141 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101342 | 1 | IC1_Inv3_SCB2_String 3
142 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101492 | 1 | IC1_Inv3_SCB1_String 2
143 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110100943 | 1 | IC1_Inv2_SCB2_String 2
144 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110101013 | 1 | IC1_Inv2_SCB2_String 1
145 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-20 | Replaced old PV 325 Watts module(1 No)104110100355 | 1 | IC1_Inv2_SCB1_String 4
146 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB4_String 13
147 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101007 | 1 | IC1_Inv1_SCB8_String 2
148 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101009 | 1 | IC1_Inv1_SCB7_String 4
149 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101079 | 1 | IC1_Inv1_SCB7_String 1
150 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101077 | 1 | IC1_Inv1_SCB4_String 4
151 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101132 | 1 | IC1_Inv1_SCB4_String 5
152 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101246 | 1 | IC1_Inv4_SCB1_String 12
153 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104110101125 | 1 | IC1_Inv4_SCB6_String 2
154 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-21 | Replaced old PV 325 Watts module(1 No)104111000463 | 1 | IC1_Inv4_SCB6_String 4
155 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-22 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB4_String 10
156 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101019 | 1 | IC1_Inv1_SCB6_String 4
157 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101128 | 1 | IC1_Inv1_SCB4_String 2
158 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101037 | 1 | IC1_Inv1_SCB3_String 4
159 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101056 | 1 | IC1_Inv1_SCB2_String 3
160 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101041 | 1 | IC1_Inv3_SCB3_String 9
161 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101044 | 1 | IC1_Inv4_SCB10_String 4
162 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101274 | 1 | IC1_Inv4_SCB10_String 4
163 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101251 | 1 | IC1_Inv4_SCB9_String 1
164 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101304 | 1 | IC1_Inv4_SCB9_String 4
165 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101286 | 1 | IC1_Inv4_SCB8_String 6
166 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101193 | 1 | IC1_Inv4_SCB6_String 13
167 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101195 | 1 | IC1_Inv3_SCB7_String 3
168 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101160 | 1 | IC1_Inv3_SCB6_String 14
169 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-23 | Replaced old PV 325 Watts module(1 No)104110101061 | 1 | IC1_Inv3_SCB3_String 14
170 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110101118 | 1 | IC2_Inv6_SCB5_String 2
171 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110101063 | 1 | IC2_Inv6_SCB5_String 1
172 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110101177 | 1 | IC2_Inv6_SCB4_String 4
173 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 330 Watts module(1 No)104220900182 | 1 | IC2_Inv6_SCB4_String 1
174 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110101042 | 1 | IC2_Inv6_SCB2_String 12
175 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110100942 | 1 | IC2_Inv6_SCB2_String 11
176 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110100806 | 1 | IC2_Inv6_SCB6_String 12
177 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110100807 | 1 | IC2_Inv6_SCB6_String 13
178 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804577 | 1 | IC2_Inv6_SCB6_String 14
179 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804153 | 1 | IC2_Inv6_SCB7_String 12
180 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804766 | 1 | IC2_Inv6_SCB8_String 12
181 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104107202563 | 1 | IC1_Inv2_SCB9_String 4
182 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106605065 | 1 | IC1_Inv2_SCB8_String 9
183 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104107202470 | 1 | IC1_Inv2_SCB8_String 9
184 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804432 | 1 | IC1_Inv2_SCB7_String 7
185 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804315 | 1 | IC1_Inv2_SCB7_String 12
186 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804334 | 1 | IC1_Inv2_SCB7_String 12
187 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804467 | 1 | IC1_Inv2_SCB7_String 12
188 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104106804324 | 1 | IC1_Inv2_SCB7_String 12
189 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104107202533 | 1 | IC1_Inv2_SCB6_String 4
190 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104107201670 | 1 | IC1_Inv2_SCB6_String 4
191 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104110401125 | 1 | IC1_Inv2_SCB6_String 3
192 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-24 | Replaced old PV 325 Watts module(1 No)104107202165 | 1 | IC1_Inv2_SCB4_String 3
193 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-25 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 4
194 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-25 | Tilt sensor add-05 installed 1 No | 1 | IC1_Inv 3
195 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-25 | Tilt sensor add-01 installed 1 No | 1 | IC1_Inv 2
196 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101131 | 1 | IC2_Inv6_SCB9_String 4
197 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101271 | 1 | IC2_Inv5_SCB4_String 9
198 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101275 | 1 | IC2_Inv5_SCB2_String 10
199 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101217 | 1 | IC2_Inv5_SCB2_String 13
200 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101273 | 1 | IC2_Inv5_SCB2_String 13
201 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101276 | 1 | IC2_Inv5_SCB1_String 7
202 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101010 | 1 | IC2_Inv5_SCB1_String 5
203 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101008 | 1 | IC2_Inv5_SCB2_String 2
204 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101302 | 1 | IC2_Inv5_SCB4_String 2
205 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101219 | 1 | IC2_Inv5_SCB4_String 2
206 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-26 | Replaced old PV 325 Watts module(1 No)104110101277 | 1 | IC2_Inv5_SCB4_String 2
207 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-27 | New 2 Nos Battery Replaced | 2 | IC2_Inv 5
208 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-27 | Tilt sensor add-01 installed 1 No | 1 | IC1_Inv 3
209 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-27 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 1
210 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-27 | Replaced old PV 325 Watts module(1 No)104110101163 | 1 | IC1_Inv2_SCB3_String 8
211 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-27 | Replaced New PV 330 Watts module(1 No)104249300044 | 1 | IC2_Inv6_SCB3_String 3
212 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-28 | Tilt sensor add-04 installed 1 No | 1 | IC1_Inv 4
213 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-28 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 2
214 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-29 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 1
215 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-30 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 1
216 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-09-30 | 30 | 2022-09-30 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 6
217 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-01 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 1
218 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-03 | 1 No PCB Replaced | 1 | IC2_Inv 1
219 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-03 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 4
220 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv 1
221 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 2
222 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 3
223 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-07 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 3
224 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-09 | Positive Y-Connector | 1 | IC2_Inv6_SCB1_String 7
225 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-09 | Positive Y-Connector | 1 | IC2_Inv5_SCB2_String 1
226 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-10 | Positive Y-Connector | 1 | IC2_Inv5_SCB8_String 10
227 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv 1
228 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv 1
229 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 1
230 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 2
231 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | Tilt sensor add-03 installed 1 No | 1 | IC2_Inv 1
232 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | New 2 Nos Batteries Replaced | 2 | IC1_Inv 1
233 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-11 | 42 Nos New (PV 330 W )Module was replaced | 42 | IC1_Inv4_SCB1_String 1
234 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-12 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv 4
235 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-12 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv 3
236 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-15 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
237 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-15 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
238 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-18 | Charge control unit replaced | 1 | IC1_Inv2
239 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-21 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
240 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-21 | Actuator 1 No Motor was replaced | 1 | IC1_Inv3
241 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-23 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
242 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-24 | MC4 Connector(Male & Female) | 1 | IC2_Inv 1
243 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-26 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv3
244 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv 4
245 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv 4
246 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-28 | 1 no. Actuator Nylon Brass Bush replaced | 1 | IC1_Inv2
247 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-10-01 | 31 | 2022-10-31 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv 1
248 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-02 | 1 no. Actuator Nylon Brass Bush replaced | 1 | IC2_Inv 1
249 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-03 | New 2 Nos Batteries Replaced | 2 | IC2_Inv2
250 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-07 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
251 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-10 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
252 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-10 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv1
253 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-10 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv1
254 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-12 | New 2 Nos Batteries Replaced | 2 | IC1_Inv3
255 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-12 | New 2 Nos Batteries Replaced | 2 | IC1_Inv4
256 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-18 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
257 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-18 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv1
258 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-22 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv1
259 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-24 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv1
260 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-27 | New 2 Nos Batteries Replaced | 2 | IC2_Inv1
261 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-30 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
262 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-30 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
263 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-30 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv4
264 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-11-01 | 31 | 2022-11-30 | New 2 Nos Batteries Replaced | 2 | IC1_Inv4
265 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
266 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
267 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-06 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv1
268 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
269 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv1
270 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-11 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
271 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv1
272 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
273 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-15 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
274 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-16 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
275 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-17 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
276 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-17 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
277 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
278 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-24 | Positive Y-Connector | 1 | IC1_Inv2_SCB5_String 1
279 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | MC4 Connector(Male & Female) | 1 | IC1_Inv4_SCB3_String 9
280 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | Positive Y-Connector | 1 | IC1_Inv4_SCB3_String 5
281 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-25 | Positive Y-Connector | 1 | IC1_Inv4_SCB4_String 9
282 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | Positive Y-Connector | 1 | IC1_Inv4_SCB2_String 2
283 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | Positive & Negative Y-Connector | 1 | IC1_Inv4_SCB2_String 11
284 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-26 | MC4 Connector(Male & Female) | 1 | IC1_Inv4_SCB4_String 12
285 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv1
286 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
287 | FY2022-23 | 2022 | Year_1 | Year_1 | 2022-12-01 | 31 | 2022-12-29 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
288 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-03 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv2
289 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-03 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
290 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-04 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv2
291 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
292 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv2
293 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-05 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
294 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-06 | 1 no. Actuator Motor replaced | 1 | IC2_Inv2
295 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-07 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
296 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-07 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
297 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-08 | Y Connector(+ve & -ve) | 1 | IC1_Inv4_SCB4_String 11
298 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-08 | MC4 Connector(Male & Female) | 1 | IC1_Inv4_SCB4_String 11
299 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv2
300 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv2
301 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv2
302 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 2 Nos MSAT box Batteries Replaced | 2 | IC1_Inv2
303 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-15 | 2 Nos MSAT box Batteries Replaced | 2 | IC1_Inv2
304 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
305 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
306 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 2 Nos MSAT box Batteries Replaced | 2 | IC1_Inv2
307 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 2 Nos MSAT box Batteries Replaced | 2 | IC1_Inv2
308 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-16 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv2
309 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-17 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
310 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-18 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv2
311 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
312 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
313 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-20 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv4
314 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-21 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
315 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-22 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
316 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-22 | 1 No Actuator Small Gear Replaced | 1 | IC1_Inv2
317 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-23 | 1 No Actuator Motor Replaced | 1 | IC2_Inv2
318 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-23 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv1
319 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-24 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
320 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-25 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
321 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-26 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
322 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
323 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
324 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
325 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-28 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
326 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-29 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
327 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-29 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
328 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-30 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
329 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-30 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
330 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-01-01 | 31 | 2023-01-31 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
331 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
332 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
333 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-02 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
334 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-03 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
335 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-03 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv1
336 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | 1 No Actuator Motor Replaced | 1 | IC1_Inv2
337 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
338 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
339 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-05 | MC4 Connector(Male & Female) | 1 | IC1_Inv4_SCB4_String 10
340 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
341 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
342 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-07 | 1 No Medium Gear Replaced | 1 | IC1_Inv4
343 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-08 | 1 No Actuator Bearing Replaced | 1 | IC2_Inv2
344 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-08 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
345 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | 2 Nos MSAT box Batteries Replaced | 2 | IC1_Inv1
346 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv2
347 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
348 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-09 | 1 No Actuator Bearing Replaced | 1 | IC1_Inv2
349 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-10 | 1 No Actuator Bearing Replaced | 1 | IC1_Inv4
350 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-10 | 1 No Actuator Motor Replaced | 1 | IC1_Inv2
351 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-11 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
352 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-11 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
353 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-12 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
354 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-12 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
355 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-13 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
356 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | 2 Nos MSAT box Batteries Replaced | 2 | IC2_Inv1
357 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
358 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-14 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
359 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-15 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
360 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-16 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
361 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | Positive Y-Connector | 1 | IC1_Inv4_SCB4_String 5
362 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | Positive Y-Connector | 1 | IC1_Inv4_SCB4_String 13
363 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
364 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
365 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-17 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv1
366 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-18 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
367 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-19 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
368 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-19 | 1 No Actuator Bearing Replaced | 1 | IC2_Inv2
369 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-20 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
370 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
371 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
372 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-21 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
373 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
374 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
375 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-22 | Positive Y-Connector | 1 | IC1_Inv1_SCB2_String 1
376 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-23 | 1 No Actuator Motor Replaced | 1 | IC2_Inv2
377 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
378 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
379 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-24 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
380 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
381 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
382 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-25 | 1 No Big Gear Replaced | 1 | IC1_Inv4
383 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
384 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | 1 No Big Gear Replaced | 1 | IC2_Inv2
385 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-26 | Charge control unit replaced | 1 | IC2_Inv1
386 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-02-01 | 28 | 2023-02-27 | Charge control unit replaced | 1 | IC2_Inv1
387 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-01 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
388 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
389 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | 1 No Actuator Motor Replaced | 1 | IC1_Inv2
390 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-02 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
391 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
392 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | 1 No Actuator Motor Replaced | 1 | IC2_Inv1
393 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
394 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-04 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
395 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
396 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
397 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-05 | 1 No Actuator Small Gear Replaced | 1 | IC2_Inv2
398 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
399 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | 1 No Actuator Motor Replaced | 1 | IC1_Inv2
400 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-09 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv2
401 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-10 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv2
402 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-12 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
403 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-12 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
404 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-13 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv2
405 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-16 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
406 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-16 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
407 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-18 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
408 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-18 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv2
409 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-19 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv3
410 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-22 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
411 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-23 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
412 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv1
413 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
414 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-24 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
415 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | Negative Y connector Replaced | 1 | IC2_Inv5_SCB1_String 1
416 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | Negative Y connector Replaced | 1 | IC2_Inv5_SCB1_String 2
417 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-25 | MC4 Connector(Male & Female) | 1 | IC2_Inv5_SCB2_String 2
418 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
419 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
420 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-26 | Charge control unit replaced | 1 | IC1_Inv4
421 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-27 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
422 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-30 | MC4 Connector(Male & Female) | 1 | IC1_Inv4_SCB3_String 7
423 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-30 | Positive Y-Connector | 1 | IC1_Inv4_SCB1_String 3
424 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | Positive Y-Connector | 1 | IC1_Inv2_SCB6_String 14
425 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | MC4 Connector(Male & Female) | 1 | IC1_Inv2_SCB7_String 12
426 | FY2022-23 | 2023 | Year_1 | Year_1 | 2023-03-01 | 31 | 2023-03-31 | Positive Y-Connector | 1 | IC1_Inv2_SCB3_String 10
427 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-07 | Charge control unit replaced | 1 | IC2_Inv2
428 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | MC4 Connector(Male & Female) | 1 | IC2_Inv2_SCB1_String 1
429 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | Positive Y-Connector | 1 | IC2_Inv2_SCB6_String 6
430 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | Positive Y-Connector | 1 | IC1_Inv4_SCB4_String 9
431 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-09 | Negative Y connector Replaced | 1 | IC1_Inv4_SCB4_String 9
432 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv2
433 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
434 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
435 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-10 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv3
436 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
437 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
438 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
439 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-11 | 1 No Actuator Motor Replaced | 1 | IC1_Inv2
440 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
441 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | 1 No Actuator Motor Replaced | 1 | IC1_Inv3
442 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | MC4 Connector(Male & Female) | 1 | IC1_Inv1_SCB7_String 10
443 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | Positive Y-Connector | 1 | IC1_Inv1_SCB7_String 5
444 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | SCB 30A Fuse | 1 | IC1_Inv4_SCB2_String 2
445 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-12 | Positive Y-Connector | 1 | IC1_Inv4_SCB5_String 13
446 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-14 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv1
447 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-17 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
448 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-17 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
449 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
450 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
451 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
452 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-18 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv2
453 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-19 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
454 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-19 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
455 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
456 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-20 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
457 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-21 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv2
458 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-21 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv3
459 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-21 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
460 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-23 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
461 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | 1 No Actuator Motor Replaced | 1 | IC2_Inv1
462 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
463 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | Actuator motor 2 no.s Carbon brushes are replaced | 2 | IC1_Inv2
464 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | 1 no Circlip replaced | 1 | IC1_Inv2
465 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-24 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
466 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-25 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
467 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-25 | 1 No Actuator Motor Replaced | 1 | IC1_Inv4
468 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-25 | 1 No Circlip Replaced | 1 | IC1_Inv4
469 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
470 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | 1 No Circlip Replaced | 1 | IC2_Inv2
471 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
472 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
473 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-26 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
474 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
475 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv2
476 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
477 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-27 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv2
478 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-28 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
479 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-28 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv4
480 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-29 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
481 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-04-01 | 30 | 2023-04-29 | 1 No Circlip Replaced | 1 | IC2_Inv1
482 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-02 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
483 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-04 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
484 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-04 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
485 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-05 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
486 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-06 | 1 No Actuator Bearing Replaced | 1 | IC2_Inv1
487 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-06 | 1 No Circlip Replaced | 1 | IC2_Inv1
488 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-08 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
489 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-09 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
490 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-12 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
491 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-14 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
492 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-14 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv1
493 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-18 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
494 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-18 | 1 No Actuator Motor Replaced | 1 | IC1_Inv4
495 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-18 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
496 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | Positive Y-Connector | 1 | IC1_Inv1_SCB4_String 2
497 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | Positive Y-Connector | 1 | IC1_Inv3_SCB3_String 15
498 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | MC4 Connector(Male & Female) | 1 | IC1_Inv4_SCB1_String 8
499 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | Positive Y-Connector | 1 | IC1_Inv4_SCB1_String 10
500 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | MC4 Connector(Male & Female) | 2 | IC1_Inv3_SCB9_String 4
501 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-20 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
502 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-21 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
503 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-22 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv1
504 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Main Moving Contact | 3 | MCR Power Trafo OLTC
505 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Resistor Moving Contact Assembly | 3 | MCR Power Trafo OLTC
506 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Fixed Contact Assembly | 15 | MCR Power Trafo OLTC
507 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Copper Braided Wire | 4 | MCR Power Trafo OLTC
508 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Top Cover Gasket | 1 | MCR Power Trafo OLTC
509 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Transformer Mineral Oil | 210 | MCR Power Trafo OLTC
510 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-25 | Transformer Mineral Oil | 105 | MCR Power Trafo OLTC
511 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC1_Inv4
512 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
513 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
514 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-26 | Charge control unit replaced | 1 | IC1_Inv3
515 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-27 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
516 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-27 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
517 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-28 | 1 No MSAT 12V 65Ah Battery replaced | 1 | IC1_Inv3
518 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-30 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
519 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-05-01 | 31 | 2023-05-31 | Replaced New PV 330 Watts module(1 No)104249300044 | 1 | IC1_Inv4_SCB3_String 6
520 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-02 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
521 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-03 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
522 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-04 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
523 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | Tracker Relay & Relay Base | 10 | IC2_Inv2
524 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
525 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
526 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-08 | Charge control unit replaced | 1 | IC2_Inv1
527 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-09 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
528 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-11 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
529 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-12 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
530 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-14 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
531 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-16 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
532 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-18 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv3
533 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-18 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
534 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-21 | 1 No Actuator Motor Replaced | 1 | IC1_Inv3
535 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-21 | 1 No Actuator Small Gear Replaced | 1 | IC1_Inv3
536 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-21 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv3
537 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-26 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
538 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-26 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
539 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-26 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
540 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-27 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv1
541 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-06-01 | 30 | 2023-06-29 | MICOM Relay (Line Differential Protection Relay) - GE(Alstom) make | 1 | Line CRP Solar Panel, 66/11 kV KPTCL Substation Chowdanakuppe
542 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-01 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
543 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-01 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv1
544 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | Positive Y-Connector | 1 | IC1_Inv3_SCB6_String 6
545 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | Positive Y-Connector | 1 | IC1_Inv3_SCB6_String 9
546 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | Positive Y-Connector | 1 | IC1_Inv3_SCB6_String 13
547 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | Positive Y-Connector | 1 | IC1_Inv1_SCB7_String 1
548 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | Positive Y-Connector | 1 | IC2_Inv5_SCB9_String 6
549 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-02 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
550 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-05 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
551 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-05 | 1 No Actuator Motor Replaced | 1 | IC1_Inv3
552 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-05 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
553 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-06 | Actuator 2 Nos Diode was replaced | 2 | IC1_Inv3
554 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-06 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
555 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-09 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
556 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-09 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
557 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-11 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
558 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-12 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
559 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-14 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
560 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-15 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
561 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-15 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
562 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-16 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
563 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-17 | 1 No Actuator Motor Replaced | 1 | IC2_Inv1
564 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-18 | 1 No Actuator Motor Replaced | 1 | IC2_Inv1
565 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-19 | PCB_100 Type | 1 | IC2_Inv2
566 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | PCB_100 Type | 1 | IC2_Inv2
567 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | PCB_100 Type | 1 | IC1_Inv3
568 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | PCB_100 Type | 1 | IC2_Inv1
569 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
570 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-21 | PCB_100 Type | 1 | IC1_Inv2
571 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-22 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
572 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | 1 No Limit Switch was replaced | 1 | IC2_Inv2
573 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | Actuator 2 Nos Diode was replaced | 2 | IC2_Inv2
574 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
575 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
576 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-25 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
577 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | Memory unit | 1 | IC2_Inv2
578 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
579 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
580 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-27 | PCB_100 Type | 1 | IC2_Inv2
581 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
582 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
583 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | 1 No Limit Switch was replaced | 1 | IC1_Inv4
584 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | Charge control unit replaced | 1 | IC2_Inv2
585 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-29 | 1 no 25v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv2
586 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-30 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
587 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-31 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
588 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-31 | PCB_100 Type | 1 | IC2_Inv2
589 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-07-01 | 31 | 2023-07-31 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
590 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-04 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
591 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-04 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
592 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-04 | 1 N0. 2000A Fuse Replaced | 1 | IC1_Inv1
593 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-07 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
594 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-08 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
595 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-08 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv2
596 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-09 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
597 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-11 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv1
598 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-12 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
599 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-13 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
600 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-13 | 1 No Limit Switch was replaced | 1 | IC1_Inv4
601 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-14 | 2 Nos Actuator carbon brush replaced | 2 | IC1_Inv1
602 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-14 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
603 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-15 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
604 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-16 | 1 No Limit Switch was replaced | 1 | IC1_Inv1
605 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-21 | 1 No Limit Switch was replaced | 1 | IC1_Inv2
606 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-23 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
607 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-24 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
608 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-25 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
609 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-26 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
610 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-27 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
611 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-27 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
612 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-28 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
613 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-30 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
614 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-30 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
615 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-31 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
616 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-31 | Charge control unit replaced | 1 | IC2_Inv1
617 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-08-01 | 31 | 2023-08-31 | 1 No Limit Switch was replaced | 1 | IC1_Inv4
618 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-04 | 1 No Limit Switch was replaced | 1 | IC2_Inv1
619 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-05 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
620 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-05 | 1 No Limit Switch was replaced | 1 | IC2_Inv1
621 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-05 | PCB_100 Type | 1 | IC1_Inv1
622 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-05 | PCB_100 Type | 1 | IC1_Inv2
623 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-07 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
624 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-07 | 1 No Actuator Motor Replaced | 1 | IC2_Inv2
625 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-07 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
626 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-08 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
627 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-10 | Charge control unit replaced | 1 | IC1_Inv4
628 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-11 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
629 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-12 | 1 No Actuator Motor Replaced | 1 | IC2_Inv2
630 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-13 | PCB_100 Type | 1 | IC2_Inv2
631 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-13 | PCB_100 Type | 1 | IC2_Inv2
632 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-13 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
633 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-13 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
634 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-13 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC2_Inv2
635 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-13 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
636 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | PCB_100 Type | 1 | IC2_Inv2
637 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | PCB_100 Type | 1 | IC2_Inv2
638 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | PCB_100 Type | 1 | IC2_Inv2
639 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | PCB_100 Type | 1 | IC2_Inv2
640 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC2_Inv2
641 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
642 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
643 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC2_Inv2
644 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
645 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
646 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC2_Inv2
647 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
648 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC2_Inv2
649 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
650 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
651 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
652 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-14 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
653 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | PCB_100 Type | 1 | IC2_Inv2
654 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | PCB_100 Type | 1 | IC2_Inv2
655 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC2_Inv2
656 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
657 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
658 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC2_Inv2
659 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-15 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
660 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-17 | 1 No Actuator Carbon Brush Replaced | 1 | IC1_Inv2
661 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-17 | PCB_100 Type | 1 | IC1_Inv1
662 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-18 | 1 No Limit Switch was replaced | 1 | IC2_Inv2
663 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
664 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
665 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | 1 No Actuator Motor Replaced | 1 | IC2_Inv1
666 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | Positive Y-Connector Replaced | 1 | IC1_Inv4
667 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | Positive Y-Connector Replaced | 1 | IC1_Inv4
668 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | Positive Y-Connector Replaced | 1 | IC1_Inv4
669 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-19 | MC4 Connector Replaced | 1 | IC1_Inv4
670 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-22 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
671 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-23 | 1 No Actuator Carbon Brush Replaced | 1 | IC1_Inv3
672 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-23 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC2_Inv2
673 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-24 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
674 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-24 | Actuator motor 2 no.s Carbon brushes was replaced | 2 | IC2_Inv2
675 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-25 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
676 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-25 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
677 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-26 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC2_Inv2
678 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-26 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
679 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-26 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
680 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-26 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
681 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-26 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv1
682 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
683 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
684 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
685 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
686 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
687 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
688 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
689 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
690 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
691 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
692 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-27 | 1 No Actuator Carbon Brush Replaced | 1 | IC2_Inv1
693 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv1
694 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
695 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
696 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
697 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
698 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
699 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
700 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv2
701 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | PCB_200 Type | 1 | IC1_Inv3
702 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv1
703 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
704 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
705 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv3
706 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv3
707 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-28 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
708 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv1
709 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv1
710 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv1
711 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv1
712 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv2
713 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv2
714 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv2
715 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv2
716 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv2
717 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
718 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv2
719 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv2
720 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
721 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv2
722 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
723 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv2
724 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
725 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv2
726 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
727 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv2
728 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv2
729 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv2
730 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | PCB_100 Type | 1 | IC1_Inv4
731 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No Actuator Carbon Brush Replaced | 1 | IC1_Inv2
732 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-29 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv2
733 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
734 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv2
735 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv2
736 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv3
737 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
738 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv3
739 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv3
740 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv3
741 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
742 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | PCB_200 Type | 1 | IC1_Inv3
743 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | New Actuator HB-DJ828 Installed | 1 | IC1_Inv2
744 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | New Actuator HB-DJ828 Installed | 1 | IC1_Inv3
745 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-09-01 | 31 | 2023-09-30 | New Actuator HB-DJ828 Installed | 1 | IC1_Inv3
746 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
747 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
748 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC2_Inv2
749 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv4
750 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
751 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | New Actuator HB-DJ828 Installed | 1 | IC2_Inv1
752 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-01 | New Actuator HB-DJ828 Installed | 1 | IC1_Inv4
753 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | New Actuator HB-DJ828 Installed | 1 | IC2_Inv1
754 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | New Actuator HB-DJ828 Installed | 1 | IC2_Inv1
755 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | New Actuator HB-DJ828 Installed | 1 | IC2_Inv1
756 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | Charge control unit replaced | 1 | IC2_Inv1
757 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
758 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
759 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-02 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
760 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
761 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | 1 No Actuator Big Gear Replaced | 1 | IC2_Inv1
762 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
763 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-03 | Charge control unit replaced | 1 | IC1_Inv3
764 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | New Actuator HB-DJ828 Installed | 1 | IC1_Inv2
765 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | Actuator 1 No Diode was replaced | 1 | IC2_Inv2
766 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | 1 No Actuator Big Gear Replaced | 1 | IC2_Inv2
767 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
768 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | Positive Y-Connector Replaced | 1 | IC1_Inv4
769 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-04 | Positive Y-Connector Replaced | 1 | IC1_Inv2
770 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | Positive Y-Connector Replaced | 1 | IC1_Inv1_SCB2_String 1
771 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB5_String 11
772 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB9_String 9
773 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv1
774 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
775 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | Actuator motor 2 no.s Carbon brushes replaced | 2 | IC2_Inv2
776 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | Actuator Motor 1 no Circlip replaced | 1 | IC2_Inv2
777 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | Actuator 2 No.s Bearings replaced | 2 | IC2_Inv2
778 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | 1 No Limit Switch replaced | 1 | IC2_Inv2
779 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-05 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv3
780 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv4
781 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
782 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
783 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-06 | PCB_100 Type | 1 | IC1_Inv4
784 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv2
785 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | Charge control unit replaced | 1 | IC2_Inv1
786 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-07 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB1_String 8
787 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
788 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv3
789 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-08 | Positive Y-Connector Replaced | 1 | IC2_Inv1
790 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | Actuator 1 No Diode was replaced | 1 | IC2_Inv1
791 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
792 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
793 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv2
794 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC2_Inv1
795 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv3
796 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv2
797 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-10 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv2
798 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-11 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
799 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-12 | PCB_100 Type | 1 | IC1_Inv1
800 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-12 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
801 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-13 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
802 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-13 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv1
803 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | Actuator 2 No.s Bearings replaced | 2 | IC1_Inv1
804 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
805 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-14 | MC4 Connector(Male & Female) | 1 | IC2_Inv2_SCB9_String 10
806 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | 1 No Limit Switch replaced | 1 | IC1_Inv2
807 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
808 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-15 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB4_String 1
809 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv3
810 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
811 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv3
812 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
813 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-16 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB3_String 10
814 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | Actuator 2 No.s Bearings replaced | 2 | IC1_Inv4
815 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
816 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | Actuator motor 2 no.s Carbon brushes replaced | 2 | IC1_Inv1
817 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-17 | Actuator Motor 1 no Circlip replaced | 1 | IC1_Inv1
818 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv3
819 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
820 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
821 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-18 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
822 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-19 | MC4 Connector Replaced | 1 | IC2_Inv2_SCB9_String 10
823 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-19 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB4_String 12
824 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-20 | Negative Y-Connector Replaced | 1 | IC2_Inv1_SCB5_String 3
825 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-20 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB3_String 14
826 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | Actuator motor 1 no.s Carbon brushes replaced | 1 | IC2_Inv1
827 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
828 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-21 | Actuator 2 No.s Bearings replaced | 2 | IC1_Inv2
829 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-22 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
830 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-22 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv4
831 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB4_String 13
832 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | Negative Y-Connector Replaced | 1 | IC1_Inv4_SCB4_String 13
833 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | Negative Y-Connector Replaced | 1 | IC1_Inv4_SCB4_String 10
834 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-23 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
835 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-24 | MC4 Connector Replaced | 1 | IC1_Inv4_SCB4_String 13
836 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-25 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB9_String 10
837 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-25 | Actuator 1 No Diode was replaced | 1 | IC1_Inv4
838 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-26 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
839 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-26 | Negative Y-Connector Replaced | 1 | IC2_Inv1_SCB5_String 2
840 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-27 | Actuator motor 2 no.s Carbon brushes replaced | 2 | IC2_Inv1
841 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-27 | Actuator Motor 1 no Circlip replaced | 1 | IC2_Inv1
842 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
843 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
844 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-28 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
845 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
846 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv3
847 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-29 | New Actuator HB-DJ8289824-700 Installed | 1 | IC1_Inv1
848 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | PCB_100 Type | 1 | IC2_Inv1
849 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
850 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
851 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-30 | Actuator 1 No Diode was replaced | 1 | IC1_Inv2
852 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-10-01 | 31 | 2023-10-31 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
853 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-01 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
854 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-01 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
855 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-03 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
856 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-05 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
857 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-05 | PCB_100 Type | 1 | IC1_Inv1
858 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-06 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
859 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-06 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
860 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-07 | MC4 Connector Replaced | 1 | IC2_Inv2_SCB1_String 13
861 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-07 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB3_String 7
862 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-07 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
863 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-07 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
864 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-08 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB5_String 5
865 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-09 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
866 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-09 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
867 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-09 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
868 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-10 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
869 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-10 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv2
870 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-11 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
871 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-11 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC1_Inv2
872 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-12 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
873 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-13 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
874 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-14 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
875 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-14 | Actuator 1 No Diode was replaced | 1 | IC1_Inv3
876 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-15 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
877 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-15 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
878 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-15 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
879 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-16 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv2
880 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-17 | Negative Y-Connector Replaced | 1 | IC2_Inv2_SCB1_String 13
881 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-18 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
882 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-18 | Negative Y-Connector Replaced | 1 | IC2_Inv2_SCB1_String 5
883 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-19 | Negative Y-Connector Replaced | 1 | IC1_Inv3_SCB7_String 5
884 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-20 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
885 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-20 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB8_String 11
886 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-20 | Negative Y-Connector Replaced | 1 | IC2_Inv1_SCB1_String 5
887 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-21 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv4
888 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-21 | 1 No. Tilt Sensor ADD 5 installed | 1 | IC2_Inv2
889 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-22 | Positive Y-Connector Replaced | 1 | IC2_Inv1_SCB2_String 7
890 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-22 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
891 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-23 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
892 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-24 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
893 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-26 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
894 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-27 | Positive Y-Connector Replaced | 1 | IC1_Inv1_SCB4_String 5
895 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-27 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
896 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-28 | MC4 Connector Replaced | 1 | IC1_Inv4_SCB8_String 7
897 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-28 | Negative Y-Connector Replaced | 1 | IC1_Inv1_SCB8_String 6
898 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-11-01 | 31 | 2023-11-29 | Actuator 2 No.s Diode was replaced | 2 | IC1_Inv2
899 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
900 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
901 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-04 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
902 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-05 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
903 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-06 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB10_String 4
904 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-06 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
905 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-08 | Negative Y-Connector Replaced | 1 | IC1_Inv4_SCB1_String 9
906 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-08 | Negative Y-Connector Replaced | 1 | IC1_Inv4_SCB4_String 1
907 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-09 | MC4 Connector Replaced | 1 | IC1_Inv1_SCB3_String 12
908 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-10 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
909 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-10 | MC4 Connector Replaced | 1 | IC2_Inv2_SCB1_String 13
910 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
911 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
912 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-11 | MC4 Connector Replaced | 1 | IC2_Inv1_SCB8_String 9
913 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-12 | MC4 Connector Replaced | 1 | IC1_Inv1_SCB1_String 1
914 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-12 | Negative Y-Connector Replaced | 1 | IC1_Inv1_SCB1_String 3
915 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-14 | MC4 Connector Replaced | 2 | IC1_Inv2_SCB10_String 5
916 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB5_String 8
917 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | MC4 Connector Replaced | 1 | IC1_Inv1_SCB3_String 13
918 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
919 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-15 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
920 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-16 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
921 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-16 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
922 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-18 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
923 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-18 | Negative Y-Connector Replaced | 1 | IC1_Inv2_SCB8_String 8
924 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-19 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
925 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
926 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-20 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
927 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-21 | MC4 Connector Replaced | 1 | IC1_Inv3_SCB10_String 5
928 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB7_String 5
929 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | Positive Y-Connector Replaced | 1 | IC2_Inv1_SCB4_String 4
930 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
931 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-22 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
932 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-23 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv4
933 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-23 | PCB_100 Type | 1 | IC1_Inv4
934 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-26 | Charge control unit replaced | 1 | IC1_Inv4
935 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | MC4 Connector Replaced | 1 | IC1_Inv4_SCB6_String 9
936 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
937 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-27 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
938 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-28 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB6_String 1
939 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-28 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
940 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-29 | MC4 Connector Replaced | 1 | IC2_Inv2_SCB5_String 5
941 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-29 | Charge control unit replaced | 1 | IC1_Inv4
942 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-30 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
943 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-30 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
944 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-31 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
945 | FY2023-24 | 2023 | Year_2 | Year_2 | 2023-12-01 | 31 | 2023-12-31 | PCB_200 Type | 1 | IC2_Inv1
946 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-01 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
947 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-01 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
948 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-02 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB6_String 5
949 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-02 | Positive Y-Connector Replaced | 1 | IC2_Inv1_SCB6_String 7
950 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-03 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
951 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-04 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
952 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-05 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv4
953 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | Actuator motor 2 no.s Carbon brushes | 1 | IC2_Inv1
954 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
955 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-06 | Replaced old PV 325 Watts module(1 No)104111000743 | 1 | IC1_Inv1
956 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-08 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
957 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-09 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
958 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-10 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
959 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-10 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
960 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv1
961 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
962 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
963 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | Actuator motor Bearing | 1 | IC2_Inv1
964 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-11 | Actuator motor Bearing | 1 | IC1_Inv2
965 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-13 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB10_String 11
966 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
967 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
968 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-14 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
969 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-16 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
970 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-16 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
971 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-17 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
972 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-17 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
973 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-19 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv4
974 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-20 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
975 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-20 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
976 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-24 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
977 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-25 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB3_String 9
978 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-25 | MC4 Connector Replaced | 1 | IC1_Inv4_SCB6_String 12
979 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
980 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
981 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-26 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv1
982 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-27 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
983 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-27 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
984 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-28 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB7_String 14
985 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-29 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
986 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-29 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv2
987 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-30 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
988 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | Positive Y-Connector Replaced | 1 | IC2_Inv2_SCB2_String 13
989 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB1_String 7
990 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB5_String 14
991 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-01-01 | 31 | 2024-01-31 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv1
992 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-01 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
993 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-01 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
994 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-02 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
995 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-03 | Positive Y-Connector Replaced | 1 | IC1_Inv4
996 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-03 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
997 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-05 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv1
998 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-05 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv1
999 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-06 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
1000 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-06 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1001 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-08 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
1002 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-09 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1003 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-09 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1004 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1005 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | Positive Y-Connector Replaced | 1 | IC2_Inv2
1006 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | Positive Y-Connector Replaced | 1 | IC2_Inv2
1007 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | Positive Y-Connector Replaced | 1 | IC1_Inv4
1008 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-11 | Positive Y-Connector Replaced | 1 | IC1_Inv4
1009 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
1010 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1011 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-12 | Positive Y-Connector Replaced | 1 | IC1_Inv4
1012 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | PCB_100 Type | 1 | IC1_Inv2
1013 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | PCB_100 Type | 1 | IC1_Inv4
1014 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | PCB_100 Type | 1 | IC1_Inv3
1015 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | PCB_100 Type | 1 | IC2_Inv2
1016 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | PCB_100 Type | 1 | IC2_Inv2
1017 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | PCB_100 Type | 1 | IC2_Inv2
1018 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-13 | IC1_Inv4_SCB3_String 3 | 1 | IC1_Inv1_SCB1_String 12
1019 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-14 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv1
1020 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-16 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1021 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-16 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
1022 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-17 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1023 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-17 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
1024 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
1025 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
1026 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-19 | IC1_Inv4_SCB3_String 3 | 1 | IC1_Inv4_SCB3_String 3
1027 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-20 | IC1_Inv4_SCB10_String 5 | 1 | IC1_Inv4_SCB10_String 5
1028 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-21 | Positive Y-Connector Replaced | 1 | IC2_Inv2_SCB3_String 7
1029 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-21 | MC4 Connector Replaced | 1 | IC1_Inv2_SCB10_String 1
1030 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-22 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv2
1031 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-22 | Charge control unit replaced | 1 | IC1_Inv2
1032 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-23 | Positive Y-Connector Replaced | 1 | IC2_Inv1_SCB2_String 1
1033 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB1_String 3
1034 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB10_String 11
1035 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB10_String 04
1036 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-24 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB6_String 05
1037 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB5_String 5
1038 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB5_String 9
1039 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB7_String 5
1040 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | PCB_100 Type | 1 | PCB_100 Type
1041 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1042 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-26 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1043 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-02-01 | 29 | 2024-02-28 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1044 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-01 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB10_String 1
1045 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-01 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB6_String 6
1046 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-01 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB9_String 10
1047 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-02 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB7_String 3
1048 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB6_String 10
1049 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB6_String 11
1050 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB2_String 8
1051 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-06 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB2_String 11
1052 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-08 | Positive Y-Connector Replaced | 1 | IC2_Inv5_SCB2_String 7
1053 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
1054 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | 1 No Actuator Medium Gear Replaced | 1 | IC2_Inv2
1055 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-11 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC2_Inv2
1056 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1057 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv3
1058 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB5_String 5
1059 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB5_String 8
1060 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB4_String 11
1061 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-12 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB9_String 5
1062 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-13 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB4_String 10
1063 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-13 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB6_String 11
1064 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-13 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB1_String 3
1065 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-15 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1066 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-16 | 1 Nos Actuator Bearing Replaced | 1 | IC2_Inv2
1067 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-17 | Actuator motor 1 no.s Carbon brushes | 1 | IC2_Inv2
1068 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-18 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB3_String 13
1069 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-18 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB3_String 10
1070 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-20 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1071 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1072 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-20 | 1 No Actuator Medium Gear Replaced | 1 | IC1_Inv3
1073 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-24 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1074 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-24 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1075 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-25 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1076 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-25 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1077 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-25 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1078 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-26 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB1_String 3
1079 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-26 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB9_String 12
1080 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-26 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB9_String 5
1081 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-26 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB6_String 5
1082 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-27 | PCB_200 Type | 1 | IC1_Inv2
1083 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-28 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB10_String 6
1084 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-28 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB10_String 8
1085 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-28 | PCB_100 Type | 1 | IC2_Inv1
1086 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-29 | PCB_200 Type | 1 | IC2_Inv2
1087 | FY2023-24 | 2024 | Year_2 | Year_2 | 2024-03-01 | 31 | 2024-03-29 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
1088 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-01 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
1089 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-04 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
1090 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-05 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
1091 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-05 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1092 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-06 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1093 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-07 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1094 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-10 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1095 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-10 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1096 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-12 | Actuator motor 2 no.s Carbon brush | 2 | IC2_Inv2
1097 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-19 | Positive Y-Connector Replaced | 1 | IC1_Inv2_SCB1_String 10
1098 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-20 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC2_Inv1
1099 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-21 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1100 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-21 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1101 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-22 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1102 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-22 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1103 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-22 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1104 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-24 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1105 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-24 | Positive Y-Connector Replaced | 1 | IC2_Inv1
1106 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-25 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
1107 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-26 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1108 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-26 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1109 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-04-01 | 30 | 2024-04-26 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1110 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-02 | 1 No Actuator Big Gear Replaced | 1 | IC2_Inv1
1111 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-03 | Replaced old PV 325 Watts module(1 No)104249300393 | 1 | IC1_Inv4_SCB1_String 6
1112 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-03 | Replaced old PV 325 Watts module(1 No)104249300498 | 1 | IC1_Inv4_SCB1_String 6
1113 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-06 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
1114 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-07 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB2_String 11
1115 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-07 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB1_String 9
1116 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv2
1117 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104107202941 | 1 | IC1_Inv1_SCB1_String 2
1118 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104107204308 | 1 | IC1_Inv1_SCB2_String 2
1119 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104107204320 | 1 | IC1_Inv1_SCB6_String 3
1120 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104107204305 | 1 | IC1_Inv2_SCB1_String 2
1121 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)1041929035529 | 1 | IC1_Inv3_SCB3_String 5
1122 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000393 | 1 | IC1_Inv3_SCB3_String 15
1123 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000798 | 1 | IC2_Inv5_SCB8_String 11
1124 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000519 | 1 | IC1_Inv1_SCB1_String 13
1125 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000110 | 1 | IC1_Inv1_SCB5_String 13
1126 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000610 | 1 | IC1_Inv1_SCB7_String 11
1127 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000002 | 1 | IC1_Inv1_SCB8_String 13
1128 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104110401582 | 1 | IC1_Inv1_SCB8_String 13
1129 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000003 | 1 | IC1_Inv2_SCB2_String 11
1130 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000807 | 1 | IC1_Inv3_SCB3_String 13
1131 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104110101089 | 1 | IC2_Inv6_SCB6_String 1
1132 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000441 | 1 | IC2_Inv6_SCB8_String 1
1133 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000714 | 1 | IC2_Inv6_SCB8_String 2
1134 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000571 | 1 | IC1_Inv1_SCB9_String 12
1135 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000674 | 1 | IC1_Inv3_SCB8_String 11
1136 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-08 | Replaced old PV 325 Watts module(1 No)104111000722 | 1 | IC1_Inv4_SCB9_String 1
1137 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv3
1138 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204503 | 1 | IC1_Inv3_SCB4_String 3
1139 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204719 | 1 | IC1_Inv3_SCB6_String 10
1140 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204634 | 1 | IC1_Inv3_SCB7_String 11
1141 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204717 | 1 | IC1_Inv3_SCB7_String 12
1142 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204716 | 1 | IC1_Inv3_SCB7_String 14
1143 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204718 | 1 | IC1_Inv4_SCB2_String 11
1144 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204651 | 1 | IC1_Inv4_SCB6_String 1
1145 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104107204586 | 1 | IC1_Inv4_SCB6_String 2
1146 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104110101114 | 1 | IC1_Inv4_SCB8_String 7
1147 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-09 | Replaced old PV 325 Watts module(1 No)104110101200 | 1 | IC1_Inv4_SCB8_String 8
1148 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101712 | 1 | IC2_Inv5_SCB9_String 2
1149 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101708 | 1 | IC2_Inv5_SCB9_String 2
1150 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104111500999 | 1 | IC2_Inv5_SCB9_String 2
1151 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104111000432 | 1 | IC2_Inv5_SCB9_String 12
1152 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101709 | 1 | IC2_Inv5_SCB4_String 9
1153 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101737 | 1 | IC2_Inv5_SCB4_String 11
1154 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101621 | 1 | IC2_Inv5_SCB3_String 8
1155 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104111000309 | 1 | IC1_Inv2_SCB8_String 7
1156 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104111000433 | 1 | IC2_Inv6_SCB2_String 14
1157 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101108 | 1 | IC2_Inv6_SCB1_String 12
1158 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101135 | 1 | IC2_Inv6_SCB1_String 10
1159 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101445 | 1 | IC1_Inv1_SCB2_String 2
1160 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101774 | 1 | IC1_Inv3_SCB1_String 3
1161 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101475 | 1 | IC2_Inv5_SCB7_String 7
1162 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101623 | 1 | IC1_Inv1_SCB8_String 14
1163 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101729 | 1 | IC1_Inv2_SCB1_String 10
1164 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101736 | 1 | IC1_Inv2_SCB7_String 3
1165 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-10 | Replaced old PV 325 Watts module(1 No)104110101691 | 1 | IC1_Inv2_SCB6_String 5
1166 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-11 | Positive Y-Connector Replaced | 1 | IC1_Inv4_SCB3_String 8
1167 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-13 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
1168 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-13 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1169 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-14 | 1 No Actuator Big Gear Replaced | 1 | IC1_Inv2
1170 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-15 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1171 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-19 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
1172 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-20 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1173 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-21 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv1
1174 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-22 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
1175 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-22 | Iron Nut Replaced | 1 | IC1_Inv4
1176 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-22 | Vthread Rod Replaced | 1 | IC1_Inv4
1177 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-23 | Actuator Big Gear Replaced | 1 | IC1_Inv3
1178 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-24 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv1
1179 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-26 | Actuator motor 2 no.s Carbon brush | 2 | IC1_Inv1
1180 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-26 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1181 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-30 | Positive Y Connector Failure | 1 | IC1_Inv1_SCB4_String 7
1182 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-30 | Positive Y Connector Failure | 1 | IC1_Inv1_SCB2_String 1
1183 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | Actuator motor 2 no.s Carbon brush | 2 | IC1_Inv4
1184 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | PCB_100 Type | 1 | IC1_Inv4
1185 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | PCB_100 Type | 1 | IC1_Inv2
1186 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-05-01 | 31 | 2024-05-31 | PCB_100 Type | 1 | IC1_Inv2
1187 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 30 | 2024-06-03 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1188 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-04 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv4
1189 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-05 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv4
1190 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-05 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv1
1191 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-05 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1192 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-05 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
1193 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-06 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv4
1194 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-07 | PCB_100 Type | 1 | IC1_Inv3
1195 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-07 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1196 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-07 | Actuator motor 2 no.s Carbon brush | 2 | IC1_Inv3
1197 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-08 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1198 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-08 | Actuator Big Gear Replaced | 1 | IC2_Inv1
1199 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-08 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1200 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-10 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
1201 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-10 | Iron Nut Replaced | 1 | IC2_Inv2
1202 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-10 | Vthread Rod Replaced | 1 | IC1_Inv4
1203 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-11 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1204 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-11 | 1 No Actuator Motor | 1 | IC1_Inv4
1205 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-13 | 1 No Actuator Motor | 1 | IC2_Inv1
1206 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-13 | Memory Unit Replaced | 1 | IC2_Inv1
1207 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-17 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv1
1208 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-18 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
1209 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-18 | 1 No Actuator Motor | 1 | IC1_Inv2
1210 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-19 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1211 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-22 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv4
1212 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-22 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv4
1213 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-23 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
1214 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-25 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1215 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-28 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1216 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-28 | Iron Nut Replaced | 1 | IC1_Inv1
1217 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-28 | Vthread Rod Replaced | 1 | IC1_Inv1
1218 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-28 | 2 No Battaries Replaced | 2 | IC1_Inv2
1219 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-28 | 2 No Battaries Replaced | 2 | IC1_Inv1
1220 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-28 | 2 No Battaries Replaced | 2 | IC1_Inv1
1221 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-06-01 | 31 | 2024-06-29 | 2 No Battaries Replaced | 2 | IC2_Inv1
1222 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | 2 No Battaries Replaced | 2 | IC1_Inv4
1223 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | 2 No Battaries Replaced | 2 | IC1_Inv1
1224 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | 2 No Battaries Replaced | 2 | IC1_Inv1
1225 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | PCB_100 Type | 1 | IC1_Inv4
1226 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | PCB_100 Type | 1 | IC1_Inv1
1227 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | PCB_100 Type | 1 | IC1_Inv3
1228 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | Iron Nut & Vthread Rod Replaced | 1 | IC1_Inv3
1229 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv3
1230 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-01 | Actuator Big Gear Replaced | 1 | IC1_Inv3
1231 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-02 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv3
1232 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-02 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1233 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-03 | 2 No Battaries Replaced | 2 | IC2_Inv1
1234 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-03 | 2 No Battaries Replaced | 2 | IC2_Inv1
1235 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-03 | PCB_100 Type | 1 | IC2_Inv1
1236 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-04 | 1 No Actuator Motor | 1 | IC2_Inv1
1237 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-07 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
1238 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-07 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv3
1239 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-07 | 2 No Battaries Replaced | 2 | IC1_Inv2
1240 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-09 | 1 No. Tilt Sensor ADD 3 installed | 1 | IC1_Inv4
1241 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-09 | 1 No Battaries Replaced | 1 | IC1_Inv1
1242 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-10 | Actuator 1 No Limit Switch was replaced | 1 | IC1_Inv2
1243 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-10 | 1 No Actuator Motor | 1 | IC2_Inv1
1244 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-10 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1245 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-12 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
1246 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-12 | Actuator 1 No Limit Switch was replaced | 1 | IC2_Inv2
1247 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-13 | 2 Nos Actuator Bearing Replaced | 1 | IC2_Inv2
1248 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-14 | 1 No Medium Gear Replaced | 1 | IC1_Inv3
1249 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-14 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
1250 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-16 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1251 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-16 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1252 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-16 | 1 No Medium Gear Replaced | 1 | IC1_Inv1
1253 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-21 | 1 No Actuator Motor | 1 | IC2_Inv1
1254 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-22 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1255 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-22 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1256 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-23 | 2 No Battaries Replaced | 2 | IC2_Inv1
1257 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-24 | Iron Nut & Vthread Rod Replaced | 1 | IC1_Inv2
1258 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-25 | 2 No Battaries Replaced | 2 | IC1_Inv4
1259 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-25 | 1 No. Tilt Sensor ADD 1 installed | 1 | IC1_Inv4
1260 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-25 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC1_Inv4
1261 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-26 | 1 No. Tilt Sensor ADD 4 installed | 1 | IC1_Inv4
1262 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-26 | 1 No Actuator Motor | 1 | IC1_Inv3
1263 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-26 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1264 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-26 | 1 No. Tilt Sensor ADD 2 installed | 1 | IC2_Inv2
1265 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-27 | Iron Nut & Vthread Rod Replaced | 1 | IC2_Inv1
1266 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-27 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1267 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-29 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1268 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-30 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1269 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-30 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1270 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-07-01 | 30 | 2024-07-30 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1271 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-01 | Iron Nut & Vthread Rod Replaced | 1 | IC1_Inv1
1272 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-01 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1273 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-02 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1274 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-02 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1275 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-03 | 1 No Actuator Motor | 1 | IC1_Inv2
1276 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-04 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1277 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
1278 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | 1 No Actuator Motor | 1 | IC2_Inv1
1279 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-07 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1280 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-09 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1281 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-09 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1282 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1283 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | Iron Nut Replaced | 1 | IC1_Inv3
1284 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-12 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1285 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-13 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1286 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-13 | 1 No Medium Gear Replaced | 1 | IC1_Inv2
1287 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-14 | Iron Nut Replaced | 1 | IC2_Inv1
1288 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-16 | 1 No Actuator Motor | 1 | IC1_Inv2
1289 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-17 | Iron Nut Replaced | 1 | IC1_Inv3
1290 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-18 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1291 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1292 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | Iron Nut Replaced | 1 | IC1_Inv2
1293 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-19 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
1294 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-22 | Iron Nut Replaced | 1 | IC1_Inv2
1295 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-23 | 1 No Actuator Motor | 1 | IC2_Inv1
1296 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-24 | 1 No Medium Gear Replaced | 1 | IC1_Inv2
1297 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-24 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
1298 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-25 | Iron Nut Replaced | 1 | IC2_Inv2
1299 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-25 | 1 No Actuator Motor | 1 | IC1_Inv2
1300 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-08-01 | 31 | 2024-08-28 | PCB_200 Type | 1 | IC2_Inv1
1301 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-03 | 1 No Actuator Motor | 1 | IC1_Inv2
1302 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-03 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1303 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-03 | 1 No Actuator Motor | 1 | IC1_Inv3
1304 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-03 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1305 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-04 | 1 No Actuator Motor | 1 | IC1_Inv2
1306 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-05 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1307 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-05 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
1308 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-05 | Charge control unit replaced | 1 | IC1_Inv2
1309 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-06 | Iron Nut Replaced | 1 | IC2_Inv1
1310 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-08 | PCB_200 Type | 1 | IC2_Inv2
1311 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-09 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1312 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-11 | Iron Nut Replaced | 1 | IC1_Inv4
1313 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-11 | 1 No Actuator Motor | 1 | IC1_Inv4
1314 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-12 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1315 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-14 | PCB_200 Type | 1 | IC2_Inv2
1316 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-16 | PCB_200 Type | 1 | IC1_Inv2
1317 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-16 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1318 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-18 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1319 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-19 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1320 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-20 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1321 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-20 | PCB_200 Type | 1 | IC2_Inv2
1322 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-20 | PCB_200 Type | 1 | IC2_Inv1
1323 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-22 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1324 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-24 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv4
1325 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-25 | 1 No Actuator Motor | 1 | IC2_Inv1
1326 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-26 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1327 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-27 | Iron Nut Replaced | 1 | IC2_Inv1
1328 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-29 | 1 No Big Gear Replaced | 1 | IC1_Inv3
1329 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-30 | Negative Y connector Replaced | 1 | IC1_Inv3_SCB9_String 7
1330 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-09-01 | 31 | 2024-09-30 | Positive Y-Connector Replaced | 1 | IC2_Inv6_SCB7_String 13
1331 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | Iron Nut Replaced | 1 | IC1_Inv2
1332 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv3
1333 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-03 | PCB_200 Type | 1 | IC1_Inv2
1334 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-04 | Actuator motor 2 no.s Carbon brushes | 1 | IC1_Inv3
1335 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-05 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1336 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-05 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
1337 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-07 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1338 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-07 | 1 No Actuator Motor | 1 | IC1_Inv2
1339 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-09 | 1 No Big Gear Replaced | 1 | IC2_Inv2
1340 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-10 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1341 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-12 | MC4 Connector Replaced | 1 | IC1_Inv4_SCB8_String 5
1342 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-16 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1343 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-16 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1344 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-18 | 1 No Big Gear Replaced | 1 | IC2_Inv2
1345 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-20 | 1 No Actuator Motor | 1 | IC2_Inv1
1346 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1347 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1348 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1349 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1350 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1351 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1352 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-24 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1353 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1354 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1355 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-25 | 1 No Big Gear Replaced | 1 | IC1_Inv4
1356 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-26 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1357 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-26 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1358 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1359 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1360 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-29 | 2 NO Diode Replaced | 2 | IC1_Inv1
1361 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-30 | Iron Rod Replaced | 1 | IC2_Inv1
1362 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-30 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1363 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | 1 No Actuator Motor | 1 | IC1_Inv1
1364 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | 1 No Actuator Motor | 1 | IC1_Inv1
1365 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-10-01 | 31 | 2024-10-31 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1366 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-01 | 1 No Actuator Motor | 1 | IC1_Inv1
1367 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
1368 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1369 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-02 | 1 No Actuator Motor | 1 | IC1_Inv1
1370 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-03 | Iron Rod Replaced | 1 | IC2_Inv2
1371 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-04 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1372 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-04 | 1 No Actuator Motor | 1 | IC2_Inv1
1373 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | Iron Nut Replaced | 1 | IC1_Inv1
1374 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | Positive Y-Connector Replaced | 1 | IC1_Inv1_SCB8_String 3
1375 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-05 | Positive Y-Connector Replaced | 1 | IC1_Inv3_SCB6_String 8
1376 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-06 | 1 No Actuator Motor | 1 | IC2_Inv2
1377 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-07 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
1378 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-08 | Actuator 2 No Limit Switch was replaced | 1 | IC1_Inv1
1379 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-08 | V thread Rod | 1 | IC1_Inv2
1380 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-10 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1381 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-10 | 1 No Actuator Motor | 1 | IC2_Inv2
1382 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-12 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
1383 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-13 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1384 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv4
1385 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | 1 No Actuator Motor | 1 | IC1_Inv2
1386 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-18 | Iron Rod Replaced | 1 | IC1_Inv1
1387 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-22 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1388 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-11-01 | 30 | 2024-11-27 | Iron Nut Replaced | 1 | IC2_Inv2
1389 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-01 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1390 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-04 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1391 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-04 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1392 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-05 | 1 No Actuator Motor | 1 | IC1_Inv2
1393 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-05 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1394 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-05 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1395 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-06 | Iron Rod Replaced | 1 | IC1_Inv4
1396 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-06 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
1397 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-07 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
1398 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-10 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1399 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-10 | 1 No Actuator Motor | 1 | IC1_Inv3
1400 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-13 | Iron Nut Replaced | 1 | IC1_Inv2
1401 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-13 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1402 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-15 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1403 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-16 | 1 No Actuator Motor | 1 | IC2_Inv2
1404 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-16 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1405 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-17 | Iron Nut Replaced | 1 | IC1_Inv3
1406 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-18 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1407 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-18 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv3
1408 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-20 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1409 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-21 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
1410 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-22 | Iron Nut Replaced | 1 | IC1_Inv4
1411 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-22 | 1 No Medium Gear Replaced | 1 | IC1_Inv4
1412 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-26 | 1 No Actuator Bearing Replaced | 1 | IC1_Inv1
1413 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-26 | 1 No Big Gear Replaced | 1 | IC2_Inv2
1414 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-28 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1415 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-28 | Iron nut Replaced | 1 | IC1_Inv1
1416 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-28 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1417 | FY2024-25 | 2024 | Year_2 | Year_2 | 2024-12-01 | 30 | 2024-12-30 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1418 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-05 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1419 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | PCB_100 Type | 1 | IC2_Inv1
1420 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | PCB_100 Type | 1 | IC1_Inv2
1421 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-06 | PCB_100 Type | 1 | IC1_Inv3
1422 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-07 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1423 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1424 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | PCB_100 Type | 1 | IC1_Inv4
1425 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | CCU Replaced | 1 | IC1_Inv3
1426 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | CCU Replaced | 1 | IC1_Inv4
1427 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-08 | Add 2 Tilt Sensor Replaced | 1 | IC1_Inv4
1428 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-09 | PCB_100 Type | 1 | IC1_Inv3
1429 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-09 | CCU Replaced | 1 | IC1_Inv3
1430 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-10 | Add 1 Tilt Sensor Replaced | 1 | IC2_Inv2
1431 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-10 | Add 1 Tilt Sensor Replaced | 1 | IC1_Inv3
1432 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-11 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1433 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-12 | 1 No Actuator Motor | 1 | IC1_Inv4
1434 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-12 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1435 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-14 | 1 No Big Gear Replaced | 1 | IC1_Inv3
1436 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-15 | Add 1 Tilt Sensor Replaced | 1 | IC1_Inv3
1437 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-16 | Add 1 Tilt Sensor Replaced | 1 | IC1_Inv4
1438 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-16 | Add 4 Tilt Sensor Replaced | 1 | IC1_Inv4
1439 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-18 | 1 No Actuator Bearing Replaced | 1 | IC1_Inv3
1440 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-19 | Add 5 Tilt Sensor Replaced | 1 | IC2_Inv2
1441 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-21 | Actuator 2 No Limit Switch was replaced | 1 | IC1_Inv1
1442 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-21 | 1 No Medium Gear Replaced | 1 | IC1_Inv3
1443 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-23 | 1 No Actuator Motor | 1 | IC1_Inv1
1444 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-23 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1445 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-24 | 1 No Medium Gear Replaced | 1 | IC1_Inv2
1446 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-24 | 1 No Big Gear Replaced | 1 | IC1_Inv2
1447 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1448 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | Iron nut Replaced | 1 | IC1_Inv3
1449 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | PCB_100 Type | 1 | IC1_Inv4
1450 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-25 | PCB_100 Type | 1 | IC1_Inv3
1451 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-26 | Iron nut Replaced | 1 | IC1_Inv3
1452 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv4
1453 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | 1 No Actuator Motor | 1 | IC1_Inv4
1454 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv4
1455 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-28 | 1 No Big Gear Replaced | 1 | IC1_Inv4
1456 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-29 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1457 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-29 | 1 No Actuator Motor | 1 | IC1_Inv3
1458 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-01-01 | 31 | 2025-01-30 | PCB_100 Type | 1 | IC1_Inv2
1459 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-03 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv2
1460 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-06 | PCB_100 Type | 1 | IC1_Inv3
1461 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-11 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1462 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-12 | 1 No Big Gear Replaced | 1 | IC2_Inv2
1463 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-13 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
1464 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-13 | 1 No Big Gear Replaced | 1 | IC1_Inv2
1465 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-14 | Iron nut Replaced | 1 | IC1_Inv2
1466 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-14 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1467 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-15 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1468 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-18 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1469 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-18 | Iron nut Replaced | 1 | IC2_Inv2
1470 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-18 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1471 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-18 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1472 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-19 | 1 No Big Gear Replaced | 1 | IC2_Inv2
1473 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-21 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1474 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-22 | Actuator Limit Board Replaced | 1 | IC2_Inv1
1475 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-22 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
1476 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-25 | 1 No Actuator Motor Replaced | 2 | IC2_Inv1
1477 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-25 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1478 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-26 | 1 No Actuator Motor Replaced | 1 | IC1_Inv2
1479 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-02-01 | 31 | 2025-02-26 | 1 No Big Gear Replaced | 1 | IC1_Inv3
1480 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-03 | 1 No Actuator Motor Replaced | 1 | IC1_Inv3
1481 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-04 | 1 No Actuator Motor Replaced | 1 | IC1_Inv3
1482 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-07 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1483 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-07 | Iron Nut Replaced | 1 | IC2_Inv1
1484 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-08 | 1 No Big Gear Replaced | 1 | IC2_Inv1
1485 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-08 | 1 No Actuator Motor Replaced | 1 | IC1_Inv3
1486 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-10 | Iron Nut Replaced | 1 | IC1_Inv3
1487 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-11 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1488 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-11 | 1 No Actuator Motor Replaced | 1 | IC1_Inv4
1489 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-15 | Iron nut Replaced | 1 | IC1_Inv1
1490 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-15 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1491 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-17 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1492 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-17 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1493 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-19 | EMC Filter | 1 | IC1_Inv1
1494 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-19 | 1 No Actuator Motor Replaced | 1 | IC1_Inv1
1495 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-20 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1496 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-20 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1497 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1498 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1499 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 1 No Actuator Motor | 1 | IC2_Inv1
1500 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1501 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | Iron Nut Replaced | 1 | IC2_Inv1
1502 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-21 | 1 No Big Gear Replaced | 1 | IC2_Inv1
1503 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-22 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1504 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-22 | 1 No Actuator Motor Replaced | 1 | IC2_Inv2
1505 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-26 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1506 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-26 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1507 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1508 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1509 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-27 | 1 No Big Gear Replaced | 1 | IC2_Inv1
1510 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv4
1511 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 1 No Medium Gear Replaced | 1 | IC1_Inv3
1512 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | 1 No Actuator Motor | 1 | IC1_Inv2
1513 | FY2024-25 | 2024 | Year_2 | Year_2 | 2025-03-01 | 31 | 2025-03-29 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1514 | FY2025-26 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv3
1515 | FY2025-26 | 2024 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | 1 No Actuator Motor | 1 | IC1_Inv1
1516 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-02 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1517 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv2
1518 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 1 No Big Gear Replaced | 1 | IC1_Inv1
1519 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-04 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1520 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 1 No Big Gear Replaced | 1 | IC2_Inv1
1521 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv4
1522 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-05 | 1 No Actuator Motor | 1 | IC1_Inv4
1523 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 1 No Actuator Motor | 1 | IC2_Inv1
1524 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1525 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1526 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-06 | 2000A Replaced | 1 | IC1_Inv4
1527 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-07 | LCL Filter Replaced | 1 | IC1_Inv4
1528 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC1_Inv3
1529 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC2_Inv2
1530 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC2_Inv2
1531 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC2_Inv2
1532 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC2_Inv2
1533 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC2_Inv2
1534 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC1_Inv4
1535 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC1_Inv1
1536 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-08 | PCB_100 Type | 1 | IC1_Inv4
1537 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 1 No Big Gear Replaced | 1 | IC1_Inv4
1538 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-10 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1539 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1540 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1541 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | Actuator 2 No Limit Switch was replaced | 2 | IC2_Inv1
1542 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-11 | PCB_100 Type | 1 | IC2_Inv1
1543 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-12 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1544 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 1 No Medium Gear Replaced | 1 | IC1_Inv1
1545 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-13 | 1 No Big Gear Replaced | 1 | IC1_Inv1
1546 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-16 | Actuator 2 No Limit Switch was replaced | 1 | IC1_Inv3
1547 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 1 No Medium Gear Replaced | 1 | IC1_Inv4
1548 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | 1 No Actuator Motor | 1 | IC1_Inv4
1549 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-19 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1550 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-20 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1551 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 1 No Medium Gear Replaced | 1 | IC1_Inv3
1552 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1553 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 1 No Medium Gear Replaced | 1 | IC1_Inv1
1554 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | 2000A Fuse | 1 | IC1_Inv4
1555 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-21 | CL18 Connector | 1 | IC1_Inv4
1556 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1557 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-22 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1558 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1559 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-24 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
1560 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1561 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-26 | 1 No Small Gear Replaced | 1 | IC2_Inv2
1562 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1563 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-28 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv2
1564 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-29 | 1 No Medium Gear Replaced | 1 | IC1_Inv1
1565 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1566 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1567 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 2025-04-30 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1568 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-03 | 1 No Actuator Motor | 1 | IC1_Inv1
1569 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-03 | 1 No Medium Gear Replaced | 1 | IC1_Inv2
1570 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-07 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv1
1571 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-10 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1572 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-10 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv2
1573 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-11 | 1 No Actuator Motor | 1 | IC1_Inv1
1574 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-11 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1575 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-12 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1576 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-13 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1577 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-13 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1578 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-14 | 1 No Actuator Motor | 1 | IC2_Inv2
1579 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-18 | 1 No Medium Gear Replaced | 1 | IC1_Inv2
1580 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-20 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1581 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-20 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1582 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-21 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1583 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-22 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1584 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-23 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv4
1585 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-23 | 1 No. Nylon brass bush replaced | 1 | IC2_Inv2
1586 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-24 | AC Contactor | 1 | IC1_Inv4
1587 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-24 | AC Contactor Busbar | 1 | IC1_Inv4
1588 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-26 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv2
1589 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-28 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
1590 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-28 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv3
1591 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-30 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv4
1592 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-05-01 | 30 | 2025-05-30 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1593 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-04 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv3
1594 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 1 No. Nylon brass bush replaced | 1 | IC1_Inv2
1595 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1596 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-05 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
1597 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1598 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-06 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv1
1599 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1600 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-07 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1601 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-09 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv1
1602 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-10 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv2
1603 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-11 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv2
1604 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1605 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-14 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv3
1606 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 2 Nos Actuator Bearing Replaced | 2 | IC2_Inv1
1607 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | 1 No Actuator Motor | 1 | IC2_Inv1
1608 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-17 | Actuator 2 No Limit Switch was replaced | 2 | IC1_Inv3
1609 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
1610 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-18 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC2_Inv1
1611 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-19 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv1
1612 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-24 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv3
1613 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 1 No Medium Gear Replaced | 1 | IC1_Inv1
1614 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | Actuator motor 2 no.s Carbon brushes | 2 | IC1_Inv1
1615 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-25 | 2 Nos Actuator Bearing Replaced | 1 | IC1_Inv1
1616 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-26 | Actuator motor 2 no.s Carbon brushes | 1 | IC1_Inv2
1617 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 1 No Medium Gear Replaced | 1 | IC2_Inv2
1618 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 2 Nos Actuator Bearing Replaced | 2 | IC1_Inv1
1619 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-29 | 1 no 25.6v 24Ah Li-ion Battery Replaced | 1 | IC1_Inv4
1620 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 2025-06-30 | Actuator motor 2 no.s Carbon brushes | 2 | IC2_Inv2
1621 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-02 | Actuator motor 2 no.s Carbon brushes | 1 | IC1_Inv2
1622 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 1 No Medium Gear Replaced | 1 | IC2_Inv1
1623 | FY2025-26 | 2025 | Year_2 | Year_2 | 2025-07-01 | 31 | 2025-07-06 | 2 Nos Actuator Bearing Replaced | 1 | IC2_Inv1
Formulas:
Days = DAY(EOMONTH([Month Year],0))

## Basic Data (hidden)
Equipment | Affected DC Capacity | Plant Equivalent Weightage | Fault Category Plant BD sheet | Fault Category Tracker BD sheet | Tracker Equipment | Weightage of BD | Plant Equivalent Weightage | Status
IC1_Inv1 | 1669.29 | 15.89% | Module | MSAT100_PCB | MSAT_Type1 | 315 | 0.9665% | Open
IC1_Inv2 | 1833.3 | 17.45% | String Cable | MSAT200_PCB | MSAT_Type2 | 252 | 0.7732% | Close
IC1_Inv3 | 1785.84 | 17% | String Fuse | Tilt Sensor | MSAT_Type3 | 189 | 0.5799%
IC1_Inv4 | 1785.42 | 16.99% | SCB | Actuator | MSAT_Type4 | 210 | 0.6443%
IC2_Inv1 | 1763.16 | 16.78% | SCB Cable | Battery | MSAT_Type5 | 168 | 0.5155%
IC2_Inv2 | 1669.29 | 15.89% | SCB Fuse | Charge Controller | MSAT_Type6 | 126 | 0.3866%
IC1_Inv1_CB1 | 188.16 | 1.791% | Inverter | RTC | Tilt Sensor_Type1 | 63 | 0.1933%
IC1_Inv1_CB2 | 188.58 | 1.795% | InverterAC Cable | Gateway | Tilt Sensor_Type2 | 42 | 0.1289%
IC1_Inv1_CB3 | 188.79 | 1.797% | IDT | MMS | Baatery_Type1 | 315 | 0.9665%
IC1_Inv1_CB4 | 188.37 | 1.793% | IDT MV Cable |  | Baatery_Type2 | 252 | 0.7732%
IC1_Inv1_CB5 | 188.37 | 1.793% | IC MV Panel |  | Baatery_Type3 | 189 | 0.5799%
IC1_Inv1_CB6 | 188.16 | 1.791% | Incomer MV Cable |  | Baatery_Type4 | 210 | 0.6443%
IC1_Inv1_CB7 | 188.16 | 1.791% | Incomer MV Panel |  | Baatery_Type5 | 168 | 0.5155%
IC1_Inv1_CB8 | 188.16 | 1.791% | Metering System Plant |  | Baatery_Type6 | 126 | 0.3866%
IC1_Inv1_CB9 | 162.54 | 1.547% | Grid System |  | CCU_Type1 | 315 | 0.9665%
IC1_Inv1_CB10 | NA |  | Metering System Grid |  | CCU_Type2 | 252 | 0.7732%
IC1_Inv2_CB11 | NA |  | WMS |  | CCU_Type3 | 189 | 0.5799%
IC1_Inv2_CB1 | 188.16 | 1.791% | MMS |  | CCU_Type4 | 210 | 0.6443%
IC1_Inv2_CB2 | 188.16 | 1.791% | Battery Charger_MCR |  | CCU_Type5 | 168 | 0.5155%
IC1_Inv2_CB3 | 188.37 | 1.793% | IC_UPS |  | CCU_Type6 | 126 | 0.3866%
IC1_Inv2_CB4 | 188.37 | 1.793% | IC_Auxiliary Tranformer |  | Actuator Type1 | 63 | 0.1933%
IC1_Inv2_CB5 | 188.16 | 1.791% | IC_Auxiliary DB |  | Actuator Type2 | 42 | 0.1289%
IC1_Inv2_CB6 | 188.16 | 1.791% | IC_SCADA Panel |  | RTC
IC1_Inv2_CB7 | 190.05 | 1.809% | MC4 Connector |  | Gateway
IC1_Inv2_CB8 | 189.84 | 1.807% | Y-Connector |  | Repeater
IC1_Inv2_CB9 | 162.75 | 1.549% |  |  | Switch
IC1_Inv2_CB10 | 161.28 | 1.535%
IC1_Inv2_CB11 | NA
IC1_Inv3_CB1 | 188.16 | 1.791%
IC1_Inv3_CB2 | 188.16 | 1.791%
IC1_Inv3_CB3 | 201.81 | 1.921%
IC1_Inv3_CB4 | 189.21 | 1.801%
IC1_Inv3_CB5 | 190.05 | 1.809%
IC1_Inv3_CB6 | 190.47 | 1.813%
IC1_Inv3_CB7 | 190.26 | 1.811%
IC1_Inv3_CB8 | 191.1 | 1.819%
IC1_Inv3_CB9 | 95.34 | 0.9075%
IC1_Inv3_CB10 | 161.28 | 1.535%
IC1_Inv3_CB11 | NA
IC1_Inv4_CB1 | 204.54 | 1.947%
IC1_Inv4_CB2 | 191.1 | 1.819%
IC1_Inv4_CB3 | 191.1 | 1.819%
IC1_Inv4_CB4 | 191.1 | 1.819%
IC1_Inv4_CB5 | 191.1 | 1.819%
IC1_Inv4_CB6 | 191.1 | 1.819%
IC1_Inv4_CB7 | 204.54 | 1.947%
IC1_Inv4_CB8 | 191.1 | 1.819%
IC1_Inv4_CB9 | 81.9 | 0.7795%
IC1_Inv4_CB10 | 147.84 | 1.407%
IC1_Inv4_CB11 | NA
IC2_Inv1_CB1 | 201.6 | 1.919%
IC2_Inv1_CB2 | 188.16 | 1.791%
IC2_Inv1_CB3 | 188.16 | 1.791%
IC2_Inv1_CB4 | 188.16 | 1.791%
IC2_Inv1_CB5 | 188.37 | 1.793%
IC2_Inv1_CB6 | 188.58 | 1.795%
IC2_Inv1_CB7 | 188.16 | 1.791%
IC2_Inv1_CB8 | 190.05 | 1.809%
IC2_Inv1_CB9 | 161.28 | 1.535%
IC2_Inv1_CB10 | 80.64 | 0.7675%
IC2_Inv1_CB11 | NA
IC2_Inv2_CB1 | 191.73 | 1.825%
IC2_Inv2_CB2 | 192.57 | 1.833%
IC2_Inv2_CB3 | 192.57 | 1.833%
IC2_Inv2_CB4 | 191.94 | 1.827%
IC2_Inv2_CB5 | 191.1 | 1.819%
IC2_Inv2_CB6 | 191.1 | 1.819%
IC2_Inv2_CB7 | 191.1 | 1.819%
IC2_Inv2_CB8 | 191.1 | 1.819%
IC2_Inv2_CB9 | 136.08 | 1.295%
IC2_Inv2_CB10 | NA
IC2_Inv2_CB11 | NA
IC1_IDT | 7073.85 | 67.33%
IC2_IDT | 3432.45 | 32.67%
ICOG1_IC1 | 7073.85 | 67.33%
Incomer1 | 7073.85 | 67.33%
Incomer2 | 3432.45 | 32.67%
Outgoing1 | 10506.3 | 100%
Grid CB | 10506.3 | 100%
MV Cable_Incomer1 | 7073.85 | 67.33%
MV Cable INcomer2 | 3432.45 | 32.67%
MV Cable_IC1_IDT | 7073.85 | 67.33%
MV Cable_IC2_IDT | 3432.45 | 32.67%
IC1_UPS | 7073.85 | 67.33%
IC2_UPS | 3432.45 | 32.67%
IC1_Aux Tranfo. | 7073.85 | 67.33%
IC2_Aux Tranfo. | 3432.45 | 32.67%
IC1_AUX. DB | 7073.85 | 67.33%
IC2_AUX. DB | 3432.45 | 32.67%
IC1_SCADA Panel | 0 | 0%
IC2_SCADA Panel | 0 | 0%
MCR SCADA Panel | 0 | 0%
MCR_Aux Transfo. | 10506.3 | 100%
MCR_Battery Charger | 10506.3 | 100%
String_Type1_310 | 13.02 | 0.1239%
String_Type2_315 | 13.23 | 0.1259%
String_Type3_320 | 13.44 | 0.1279%
String_Type4_325 | 13.65 | 0.1299%
String_Type5_330 | 13.86 | 0.1319%
String_Type6_310/2 | 6.51 | 0.06196%
String_Type7_315/2 | 6.615 | 0.06296%
String_Type8_320/2 | 6.72 | 0.06396%
String_Type9_325/2 | 6.825 | 0.06496%
String_Type10_330/2 | 6.93 | 0.06596%