## Dashboard
Performance Summary of JPPL 50 MW Agra as on date and YTD
Month | 2025-07-01
Date | 2025-07-06
Operation Year | FY26
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 224.1121 | 232.1705 | 3.596%
| E_Grid MTD(MWh) | 1344.6724 | 1293.2624 | -3.823%
| E_Grid YTD (MWh) | 29500.5269 | 27836.6808 | -5.64%
2 | CUF Daily(%) | 13.99% | 14.49% | 3.603%
| CUF MTD(%) | 13.99% | 13.45% | -3.823%
| CUF YTD(%) | 18.98% | 17.91% | -5.64%
3 | PR_Daily (%) | 77.09% | 77.29% | 0.2614%
| PR_MTD (%) | 77.09% | 78.06% | 1.249%
| PR_YTD (%) | 75.99% | 75.97% | -0.03639%
4 | POA Daily (KWh/m2) | 4.3548 | 4.5 | 3.333%
| POA MTD(KWh/m2) | 26.129 | 24.82 | -5.01%
| POA YTD(KWh/m2) | 581.529 | 548.9302 | -5.606%
5 | PA Daily | 99.5% | 99.97% | 0.4712%
| PA MTD | 99.5% | 99.46% | -0.03543%
| PA YTD | 99.5% | 98.75% | -0.7542%
6 | GA Daily | 99.5% | 100% | 0.5025%
| GA MTD | 99.5% | 100% | 0.5025%
| GA YTD | 99.5% | 100% | 0.5025%

## Annual_KPI
Till Date | 2025-07-06 | 2025-07-01
JPPL 50 MW Performance Summary-YTD
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2026 | 97 | 581.529 | 548.9302 | 29500.5269 | 27836.6808 | 75.99% | 75.97% | 18.98% | 17.91% | 99.5% | 100% | 99.5% | 98.75% | 0 | 0
JPPL 50 MW Performance Summary-Monthwise
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-04-01 | 30 | 206.6 | 181.3903 | 10495.2627 | 9324.465 | 76.1% | 77.01% | 21.84% | 19.4% | 99.5% | 100% | 99.5% | 99.69% | 0 | 0
2025-05-01 | 31 | 191.7 | 182.72 | 9688.8168 | 8998.9708 | 75.71% | 73.78% | 19.51% | 18.12% | 99.5% | 100% | 99.5% | 97.38% | 0 | 0
2025-06-01 | 30 | 157.1 | 160 | 7971.775 | 8219.9827 | 76.01% | 76.96% | 16.59% | 17.1% | 99.5% | 100% | 99.5% | 99.09% | 0 | 0
2025-07-01 | 6 | 26.129 | 24.82 | 1344.6724 | 1293.2624 | 77.09% | 78.06% | 13.99% | 13.45% | 99.5% | 100% | 99.5% | 99.46% | 0 | 0
2025-08-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2025-09-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2025-10-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2025-11-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2025-12-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2026-01-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2026-02-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2026-03-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0

## Monthly_KPI
Till Date | 2025-07-06
JPPL 50 MW Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-07-01 | 6 | 26.129 | 24.82 | 1344.6724 | 1293.2624 | 77.09% | 78.06% | 13.99% | 13.45% | 99.5% | 100% | 99.5% | 99.46% | 0 | 0
Start Date | 2025-06-30
End Date | 2025-07-06
JPPL50 MW Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-07-01 | 7 | 31.3657 | 27.85 | 1610.3982 | 1458.5678 | 76.91% | 78.45% | 14.36% | 13.01% | 99.5% | 100% | 99.5% | 99.44% | 0 | 0
Formulas:
Days = [Days, row below]-6

## Grass_Ct
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | Blk1 | Blk2 | Blk3 | Blk4 | Blk5 | Blk6 | Blk7 | Blk8 | Total No.Table GC done | Mrthod of Cutting | Remarks for the day
1 | 2023-10-01 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
2 | 2023-10-02 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
3 | 2023-10-03 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
4 | 2023-10-04 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
5 | 2023-10-05 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
6 | 2023-10-06 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
7 | 2023-10-07 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
8 | 2023-10-08 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
9 | 2023-10-09 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
10 | 2023-10-10 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
11 | 2023-10-11 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
12 | 2023-10-12 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
13 | 2023-10-13 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
14 | 2023-10-14 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
15 | 2023-10-15 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
16 | 2023-10-16 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
17 | 2023-10-17 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
18 | 2023-10-18 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
19 | 2023-10-19 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
20 | 2023-10-20 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
21 | 2023-10-21 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
22 | 2023-10-22 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
23 | 2023-10-23 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
24 | 2023-10-24 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
25 | 2023-10-25 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
26 | 2023-10-26 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
27 | 2023-10-27 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
28 | 2023-10-28 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
29 | 2023-10-29 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
30 | 2023-10-30 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
31 | 2023-10-31 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
32 | 2023-11-01 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
33 | 2023-11-02 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
34 | 2023-11-03 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
35 | 2023-11-04 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
36 | 2023-11-05 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
37 | 2023-11-06 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
38 | 2023-11-07 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
39 | 2023-11-08 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
40 | 2023-11-09 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
41 | 2023-11-10 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
42 | 2023-11-11 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
43 | 2023-11-12 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
44 | 2023-11-13 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
45 | 2023-11-14 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
46 | 2023-11-15 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
47 | 2023-11-16 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
48 | 2023-11-17 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
49 | 2023-11-18 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
50 | 2023-11-19 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
51 | 2023-11-20 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
52 | 2023-11-21 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
53 | 2023-11-22 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
54 | 2023-11-23 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
55 | 2023-11-24 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
56 | 2023-11-25 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
57 | 2023-11-26 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
58 | 2023-11-27 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
59 | 2023-11-28 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
60 | 2023-11-29 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
61 | 2023-11-30 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
62 | 2023-12-01 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
63 | 2023-12-02 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
64 | 2023-12-03 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
65 | 2023-12-04 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
66 | 2023-12-05 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
67 | 2023-12-06 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
68 | 2023-12-07 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
69 | 2023-12-08 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
70 | 2023-12-09 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
71 | 2023-12-10 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
72 | 2023-12-11 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
73 | 2023-12-12 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
74 | 2023-12-13 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
75 | 2023-12-14 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
76 | 2023-12-15 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
77 | 2023-12-16 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
78 | 2023-12-17 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
79 | 2023-12-18 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
80 | 2023-12-19 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
81 | 2023-12-20 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
82 | 2023-12-21 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
83 | 2023-12-22 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
84 | 2023-12-23 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
85 | 2023-12-24 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
86 | 2023-12-25 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
87 | 2023-12-26 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
88 | 2023-12-27 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
89 | 2023-12-28 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
90 | 2023-12-29 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
91 | 2023-12-30 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
92 | 2023-12-31 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
93 | 2024-01-01 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
94 | 2024-01-02 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
95 | 2024-01-03 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
96 | 2024-01-04 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
97 | 2024-01-05 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
98 | 2024-01-06 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
99 | 2024-01-07 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
100 | 2024-01-08 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
101 | 2024-01-09 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
102 | 2024-01-10 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
103 | 2024-01-11 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
104 | 2024-01-12 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
105 | 2024-01-13 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
106 | 2024-01-14 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
107 | 2024-01-15 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
108 | 2024-01-16 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
109 | 2024-01-17 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
110 | 2024-01-18 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
111 | 2024-01-19 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
112 | 2024-01-20 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
113 | 2024-01-21 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
114 | 2024-01-22 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
115 | 2024-01-23 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
116 | 2024-01-24 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
117 | 2024-01-25 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
118 | 2024-01-26 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
119 | 2024-01-27 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
120 | 2024-01-28 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
120 | 2024-01-29 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
122 | 2024-01-30 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
123 | 2024-01-31 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
124 | 2024-02-01 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
125 | 2024-02-02 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
126 | 2024-02-03 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-04 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-05 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-06 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-07 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-08 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-09 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-10 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-11 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-12 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-13 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-14 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-15 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
139 | 2024-02-16 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
140 | 2024-02-17 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
141 | 2024-02-18 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
142 | 2024-02-19 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
143 | 2024-02-20 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
144 | 2024-02-21 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
145 | 2024-02-22 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
146 | 2024-02-23 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
147 | 2024-02-24 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
148 | 2024-02-25 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
149 | 2024-02-26 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
150 | 2024-02-27 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
151 | 2024-02-28 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
152 | 2024-02-29 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
153 | 2024-03-01 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
154 | 2024-03-02 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
155 | 2024-03-03 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
156 | 2024-03-04 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
157 | 2024-03-05 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
158 | 2024-03-06 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
159 | 2024-03-07 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
160 | 2024-03-08 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
161 | 2024-03-09 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
162 | 2024-03-10 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
163 | 2024-03-11 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
164 | 2024-03-12 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
165 | 2024-03-13 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
166 | 2024-03-14 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
167 | 2024-03-15 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
168 | 2024-03-16 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
169 | 2024-03-17 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
170 | 2024-03-18 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
171 | 2024-03-19 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
172 | 2024-03-20 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
173 | 2024-03-21 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
174 | 2024-03-22 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
175 | 2024-03-23 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
176 | 2024-03-24 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
177 | 2024-03-25 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
177 | 2024-03-26 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
179 | 2024-03-27 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
180 | 2024-03-28 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
181 | 2024-03-29 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
182 | 2024-03-30 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
183 | 2024-03-31 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
184 | 2024-04-01 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
185 | 2024-04-02 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
186 | 2024-04-03 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
187 | 2024-04-04 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
188 | 2024-04-05 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
189 | 2024-04-06 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
190 | 2024-04-07 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
191 | 2024-04-08 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
192 | 2024-04-09 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
193 | 2024-04-10 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
194 | 2024-04-11 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
195 | 2024-04-12 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
196 | 2024-04-13 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
197 | 2024-04-14 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
198 | 2024-04-15 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
199 | 2024-04-16 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
200 | 2024-04-17 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
201 | 2024-04-18 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
202 | 2024-04-19 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
203 | 2024-04-20 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
204 | 2024-04-21 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
205 | 2024-04-22 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
206 | 2024-04-23 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
207 | 2024-04-24 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
208 | 2024-04-25 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
209 | 2024-04-26 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
210 | 2024-04-27 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
211 | 2024-04-28 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
212 | 2024-04-29 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
213 | 2024-04-30 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
214 | 2024-05-01 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
215 | 2024-05-02 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
216 | 2024-05-03 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
217 | 2024-05-04 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
218 | 2024-05-05 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
219 | 2024-05-06 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
220 | 2024-05-07 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
221 | 2024-05-08 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
222 | 2024-05-09 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
223 | 2024-05-10 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
224 | 2024-05-11 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
225 | 2024-05-12 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
226 | 2024-05-13 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
227 | 2024-05-14 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
228 | 2024-05-15 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
229 | 2024-05-16 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
230 | 2024-05-17 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 130
231 | 2024-05-18 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
232 | 2024-05-19 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
233 | 2024-05-20 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
234 | 2024-05-21 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
235 | 2024-05-22 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
236 | 2024-05-23 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
237 | 2024-05-24 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
238 | 2024-05-25 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
239 | 2024-05-26 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
240 | 2024-05-27 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
241 | 2024-05-28 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
242 | 2024-05-29 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
243 | 2024-05-30 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
244 | 2024-05-31 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
245 | 2024-06-01 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
246 | 2024-06-02 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
247 | 2024-06-03 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
248 | 2024-06-04 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
249 | 2024-06-05 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
250 | 2024-06-06 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
251 | 2024-06-07 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
252 | 2024-06-08 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
253 | 2024-06-09 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
254 | 2024-06-10 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
255 | 2024-06-11 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
256 | 2024-06-12 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
257 | 2024-06-13 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
258 | 2024-06-14 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
259 | 2024-06-15 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
260 | 2024-06-16 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
261 | 2024-06-17 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
262 | 2024-06-18 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
263 | 2024-06-19 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
264 | 2024-06-20 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
265 | 2024-06-21 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
266 | 2024-06-22 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
267 | 2024-06-23 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
268 | 2024-06-24 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
269 | 2024-06-25 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
270 | 2024-06-26 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
271 | 2024-06-27 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
272 | 2024-06-28 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
273 | 2024-06-29 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
274 | 2024-06-30 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
275 | 2024-07-01 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
276 | 2024-07-02 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
277 | 2024-07-03 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
278 | 2024-07-04 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
279 | 2024-07-05 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
280 | 2024-07-06 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0 |  | It was raining so grass could not be harvested
281 | 2024-07-07 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0 |  | It was raining so grass could not be harvested
282 | 2024-07-08 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0 |  | It was raining so grass could not be harvested
283 | 2024-07-09 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
284 | 2024-07-10 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
285 | 2024-07-11 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
286 | 2024-07-12 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
287 | 2024-07-13 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
288 | 2024-07-14 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
289 | 2024-07-15 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
290 | 2024-07-16 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
291 | 2024-07-17 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
292 | 2024-07-18 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
293 | 2024-07-19 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
294 | 2024-07-20 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
295 | 2024-07-21 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
296 | 2024-07-22 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
297 | 2024-07-23 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
298 | 2024-07-24 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
299 | 2024-07-25 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
300 | 2024-07-26 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
301 | 2024-07-27 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
302 | 2024-07-28 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
303 | 2024-07-29 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
304 | 2024-07-30 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
305 | 2024-07-31 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
306 | 2024-08-01 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
307 | 2024-08-02 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
308 | 2024-08-03 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
309 | 2024-08-04 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
310 | 2024-08-05 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
311 | 2024-08-06 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
312 | 2024-08-07 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
313 | 2024-08-08 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
314 | 2024-08-09 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
315 | 2024-08-10 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
316 | 2024-08-11 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
317 | 2024-08-12 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
318 | 2024-08-13 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
319 | 2024-08-14 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
320 | 2024-08-15 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
321 | 2024-08-16 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
322 | 2024-08-17 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
323 | 2024-08-18 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
324 | 2024-08-19 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
325 | 2024-08-20 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
326 | 2024-08-21 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
327 | 2024-08-22 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
328 | 2024-08-23 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
329 | 2024-08-24 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
330 | 2024-08-25 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
331 | 2024-08-26 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
332 | 2024-08-27 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
333 | 2024-08-28 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
334 | 2024-08-29 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
335 | 2024-08-30 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
336 | 2024-08-31 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
337 | 2024-09-01 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
338 | 2024-09-02 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
339 | 2024-09-03 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
340 | 2024-09-04 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
341 | 2024-09-05 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
342 | 2024-09-06 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
343 | 2024-09-07 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
344 | 2024-09-08 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
345 | 2024-09-09 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
346 | 2024-09-10 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
347 | 2024-09-11 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
348 | 2024-09-12 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
349 | 2024-09-13 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
350 | 2024-09-14 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
351 | 2024-09-15 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
352 | 2024-09-16 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
353 | 2024-09-17 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
354 | 2024-09-18 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
355 | 2024-09-19 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
356 | 2024-09-20 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
357 | 2024-09-21 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
358 | 2024-09-22 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
359 | 2024-09-23 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
360 | 2024-09-24 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
361 | 2024-09-25 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
362 | 2024-09-26 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
363 | 2024-09-27 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
364 | 2024-09-28 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
365 | 2024-09-29 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
366 | 2024-09-30 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
367 | 2024-10-01 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
368 | 2024-10-02 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
369 | 2024-10-03 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
370 | 2024-10-04 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
371 | 2024-10-05 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
372 | 2024-10-06 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
373 | 2024-10-07 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
374 | 2024-10-08 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
375 | 2024-10-09 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
376 | 2024-10-10 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
377 | 2024-10-11 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
378 | 2024-10-12 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
379 | 2024-10-13 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
380 | 2024-10-14 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
381 | 2024-10-15 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
382 | 2024-10-16 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
383 | 2024-10-17 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
384 | 2024-10-18 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
385 | 2024-10-19 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
386 | 2024-10-20 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
387 | 2024-10-21 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
388 | 2024-10-22 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
389 | 2024-10-23 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
390 | 2024-10-24 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
391 | 2024-10-25 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
392 | 2024-10-26 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
393 | 2024-10-27 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
394 | 2024-10-28 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
395 | 2024-10-29 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
396 | 2024-10-30 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
397 | 2024-10-31 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
398 | 2024-11-01 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
399 | 2024-11-02 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
400 | 2024-11-03 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
401 | 2024-11-04 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
402 | 2024-11-05 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
403 | 2024-11-06 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
404 | 2024-11-07 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
405 | 2024-11-08 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
406 | 2024-11-09 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
407 | 2024-11-10 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
408 | 2024-11-11 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
409 | 2024-11-12 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
410 | 2024-11-13 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
411 | 2024-11-14 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
412 | 2024-11-15 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
413 | 2024-11-16 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
414 | 2024-11-17 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
415 | 2024-11-18 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
416 | 2024-11-19 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
417 | 2024-11-20 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
418 | 2024-11-21 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
419 | 2024-11-22 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
420 | 2024-11-23 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
421 | 2024-11-24 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
422 | 2024-11-25 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
423 | 2024-11-26 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
424 | 2024-11-27 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
425 | 2024-11-28 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
426 | 2024-11-29 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
427 | 2024-11-30 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
428 | 2024-12-01 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
429 | 2024-12-02 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
430 | 2024-12-03 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
431 | 2024-12-04 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
432 | 2024-12-05 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
433 | 2024-12-06 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
434 | 2024-12-07 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
435 | 2024-12-08 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
436 | 2024-12-09 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
437 | 2024-12-10 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
438 | 2024-12-11 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
439 | 2024-12-12 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
440 | 2024-12-13 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
441 | 2024-12-14 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
442 | 2024-12-15 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
443 | 2024-12-16 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
444 | 2024-12-17 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
445 | 2024-12-18 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
446 | 2024-12-19 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
447 | 2024-12-20 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
448 | 2024-12-21 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
449 | 2024-12-22 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
450 | 2024-12-23 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
451 | 2024-12-24 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
452 | 2024-12-25 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
453 | 2024-12-26 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
454 | 2024-12-27 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
455 | 2024-12-28 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
456 | 2024-12-29 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
457 | 2024-12-30 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
458 | 2024-12-31 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
459 | 2025-01-01 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
460 | 2025-01-02 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
461 | 2025-01-03 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
462 | 2025-01-04 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
463 | 2025-01-05 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
464 | 2025-01-06 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
465 | 2025-01-07 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
466 | 2025-01-08 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
467 | 2025-01-09 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
468 | 2025-01-10 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
469 | 2025-01-11 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
470 | 2025-01-12 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
471 | 2025-01-13 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
472 | 2025-01-14 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
473 | 2025-01-15 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
474 | 2025-01-16 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
475 | 2025-01-17 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
476 | 2025-01-18 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
477 | 2025-01-19 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
478 | 2025-01-20 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
479 | 2025-01-21 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
480 | 2025-01-22 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
481 | 2025-01-23 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting happened near MCR area.
482 | 2025-01-24 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting happened near MCR area.
483 | 2025-01-25 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
484 | 2025-01-26 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
485 | 2025-01-27 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
486 | 2025-01-28 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
487 | 2025-01-29 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
488 | 2025-01-30 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
489 | 2025-01-31 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
490 | 2025-02-01 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
491 | 2025-02-02 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
492 | 2025-02-03 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
493 | 2025-02-04 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
494 | 2025-02-05 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
495 | 2025-02-06 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
496 | 2025-02-07 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
497 | 2025-02-08 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
498 | 2025-02-09 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
499 | 2025-02-10 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
500 | 2025-02-11 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
501 | 2025-02-12 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
502 | 2025-02-13 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
503 | 2025-02-14 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
504 | 2025-02-15 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
505 | 2025-02-16 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
506 | 2025-02-17 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
507 | 2025-02-18 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
508 | 2025-02-19 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
509 | 2025-02-20 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
510 | 2025-02-21 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
511 | 2025-02-22 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
512 | 2025-02-23 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
513 | 2025-02-24 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
514 | 2025-02-25 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
515 | 2025-02-26 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
516 | 2025-02-27 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
517 | 2025-02-28 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
518 | 2025-03-01 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
519 | 2025-03-02 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
520 | 2025-03-03 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
521 | 2025-03-04 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
522 | 2025-03-05 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
523 | 2025-03-06 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
524 | 2025-03-07 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
525 | 2025-03-08 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
527 | 2025-03-09 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
528 | 2025-03-10 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
529 | 2025-03-11 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
530 | 2025-03-12 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
531 | 2025-03-13 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
532 | 2025-03-14 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
533 | 2025-03-15 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
534 | 2025-03-16 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
535 | 2025-03-17 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
536 | 2025-03-18 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
537 | 2025-03-19 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
538 | 2025-03-20 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
539 | 2025-03-21 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
540 | 2025-03-22 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
541 | 2025-03-23 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
542 | 2025-03-24 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
543 | 2025-03-25 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
544 | 2025-03-26 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
545 | 2025-03-27 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
546 | 2025-03-28 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
547 | 2025-03-29 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
548 | 2025-03-30 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
549 | 2025-03-31 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
550 | 2025-04-01 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | [10 empty] | 0
551 | 2025-04-02 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk5: 90 | 90 | Tractor Based Rotavetor
552 | 2025-04-03 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk5: 118 | 118 | Tractor Based Rotavetor
553 | 2025-04-04 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk5: 112 | 112 | Tractor Based Rotavetor
554 | 2025-04-05 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | [8 empty] | 0 | Tractor Based Rotavetor
555 | 2025-04-06 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 120 | 120 | Tractor Based Rotavetor
556 | 2025-04-07 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 50 | 50 | Tractor Based Rotavetor
557 | 2025-04-08 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 20 | 20 | Tractor Based Rotavetor
558 | 2025-04-09 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | [8 empty] | 0 | Tractor Based Rotavetor
559 | 2025-04-10 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 24 | 24 | Tractor Based Rotavetor
560 | 2025-04-11 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Honda Machine | Blk5: 50; Blk6: 49 | 99 | Honda Machine
561 | 2025-04-12 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Honda Machine | Blk5: 45; Blk6: 50 | 95 | Honda Machine
562 | 2025-04-13 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Honda Machine | [8 empty] | 0 | Honda Machine
563 | 2025-04-14 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Honda Machine | Blk5: 65 | 65 | Honda Machine
564 | 2025-04-15 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 82 | 82 | Tractor Based Rotavetor
565 | 2025-04-16 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 60 | 60 | Tractor Based Rotavetor
566 | 2025-04-17 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 130 | 130 | Tractor Based Rotavetor
567 | 2025-04-18 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 40; Blk2: 80; Blk3: 80 | 200 | Tractor Based Rotavetor
568 | 2025-04-19 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 95; Blk2: 95; Blk3: 130 | 320 | Tractor Based Rotavetor
569 | 2025-04-21 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 30; Blk2: 35; Blk3: 25 | 90 | Tractor Based Rotavetor
570 | 2025-04-22 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk2: 40; Blk3: 40 | 80 | Tractor Based Rotavetor
571 | 2025-04-23 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk2: 40 | 40 | Tractor Based Rotavetor
572 | 2025-04-24 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk4: 140 | 140 | Tractor Based Rotavetor
573 | 2025-04-25 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk7: 80 | 80 | Tractor Based Rotavetor
574 | 2025-04-26 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk7: 120 | 120 | Tractor Based Rotavetor
575 | 2025-04-27 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk7: 80 | 80 | Tractor Based Rotavetor
576 | 2025-04-28 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk7: 70 | 70 | Tractor Based Rotavetor
577 | 2025-04-29 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Honda Machine | Blk1: 40; Blk2: 40 | 80 | Honda Machine
578 | 2025-04-30 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 80 | 80
579 | 2025-05-01 | 2026 | 2025 |  |  | May-25 | 31 |  |  | Blk8: 40 | 40
580 | 2025-05-02 | 2026 | 2025 |  |  | May-25 | 31 | [10 empty] | 0
581 | 2025-05-03 | 2026 | 2025 |  |  | May-25 | 31 |  |  | Blk8: 100 | 100 | Tractor Based Rotavetor & Honda Machine
582 | 2025-05-04 | 2026 | 2025 |  |  | May-25 | 31 |  | Honda Machine | Blk8: 90 | 90 | Honda Machine
583 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
584 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
585 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
586 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
587 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
588 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
589 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
590 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
591 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
592 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
593 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
594 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
595 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
596 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
597 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
598 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
599 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
600 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
601 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
602 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
603 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
604 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
605 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
606 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
607 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
608 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
609 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
610 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
611 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
612 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
613 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
614 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
615 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
616 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
617 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
618 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
619 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
620 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
621 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
622 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
623 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
624 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
625 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
626 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
627 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
628 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
629 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
630 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
631 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
632 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
633 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
634 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
635 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
636 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
637 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
638 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
639 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
640 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
641 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
642 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
Formulas:
Days = DAY(EOMONTH(GC[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Mod_CL
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | Blk1 | Blk2 | Blk3 | Blk4 | Blk5 | Blk6 | Blk7 | Blk8 | Total NO. Module cleaned | Morning Start Time | Morning End Time | Evening Start Time | Evening End time | Brush/MOP Replcemnet | Water Test Report | Remarks for the day
1 | 2023-10-01 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
2 | 2023-10-02 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
3 | 2023-10-03 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
4 | 2023-10-04 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
5 | 2023-10-05 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
6 | 2023-10-06 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
7 | 2023-10-07 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
8 | 2023-10-08 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
9 | 2023-10-09 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
10 | 2023-10-10 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
11 | 2023-10-11 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
12 | 2023-10-12 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
13 | 2023-10-13 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
14 | 2023-10-14 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
15 | 2023-10-15 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
16 | 2023-10-16 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
17 | 2023-10-17 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
18 | 2023-10-18 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
19 | 2023-10-19 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
20 | 2023-10-20 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
21 | 2023-10-21 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
22 | 2023-10-22 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
23 | 2023-10-23 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
24 | 2023-10-24 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
25 | 2023-10-25 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
26 | 2023-10-26 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
27 | 2023-10-27 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
28 | 2023-10-28 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
29 | 2023-10-29 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
30 | 2023-10-30 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
31 | 2023-10-31 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
32 | 2023-11-01 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
33 | 2023-11-02 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
34 | 2023-11-03 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
35 | 2023-11-04 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
36 | 2023-11-05 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
37 | 2023-11-06 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
38 | 2023-11-07 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
39 | 2023-11-08 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
40 | 2023-11-09 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
41 | 2023-11-10 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
42 | 2023-11-11 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
43 | 2023-11-12 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
44 | 2023-11-13 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
45 | 2023-11-14 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
46 | 2023-11-15 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
47 | 2023-11-16 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
48 | 2023-11-17 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
49 | 2023-11-18 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
50 | 2023-11-19 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
51 | 2023-11-20 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
52 | 2023-11-21 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
53 | 2023-11-22 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
54 | 2023-11-23 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
55 | 2023-11-24 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
56 | 2023-11-25 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
57 | 2023-11-26 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
58 | 2023-11-27 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
59 | 2023-11-28 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
60 | 2023-11-29 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
61 | 2023-11-30 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
62 | 2023-12-01 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
63 | 2023-12-02 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
64 | 2023-12-03 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
65 | 2023-12-04 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
66 | 2023-12-05 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
67 | 2023-12-06 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
68 | 2023-12-07 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
69 | 2023-12-08 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
70 | 2023-12-09 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
71 | 2023-12-10 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
72 | 2023-12-11 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
73 | 2023-12-12 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
74 | 2023-12-13 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
75 | 2023-12-14 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
76 | 2023-12-15 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
77 | 2023-12-16 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
78 | 2023-12-17 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
79 | 2023-12-18 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
80 | 2023-12-19 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
81 | 2023-12-20 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
82 | 2023-12-21 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
83 | 2023-12-22 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
84 | 2023-12-23 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
85 | 2023-12-24 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
86 | 2023-12-25 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
87 | 2023-12-26 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
88 | 2023-12-27 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
89 | 2023-12-28 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
90 | 2023-12-29 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
91 | 2023-12-30 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
92 | 2023-12-31 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
93 | 2024-01-01 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
94 | 2024-01-02 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
95 | 2024-01-03 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
96 | 2024-01-04 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
97 | 2024-01-05 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
98 | 2024-01-06 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
99 | 2024-01-07 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
100 | 2024-01-08 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
101 | 2024-01-09 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
102 | 2024-01-10 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
103 | 2024-01-11 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
104 | 2024-01-12 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
105 | 2024-01-13 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
106 | 2024-01-14 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
107 | 2024-01-15 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
108 | 2024-01-16 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
109 | 2024-01-17 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
110 | 2024-01-18 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
111 | 2024-01-19 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
112 | 2024-01-20 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
113 | 2024-01-21 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
114 | 2024-01-22 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
115 | 2024-01-23 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
116 | 2024-01-24 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
117 | 2024-01-25 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
118 | 2024-01-26 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
119 | 2024-01-27 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
120 | 2024-01-28 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
120 | 2024-01-29 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
122 | 2024-01-30 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
123 | 2024-01-31 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
124 | 2024-02-01 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000
125 | 2024-02-02 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000
126 | 2024-02-03 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000
127 | 2024-02-04 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000
127 | 2024-02-05 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-02-06 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-02-07 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-02-08 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-02-09 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-02-10 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-02-11 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 0.16667 | 0.375 | MOP |  | Cleaning Stop due to Fanbalt Broken
127 | 2024-02-12 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-02-13 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 0.16667 | 0.375 | MOP
127 | 2024-02-14 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning not done due to marriage in vendor's family
127 | 2024-02-15 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning not done due to marriage in vendor's family
139 | 2024-02-16 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 0.16667 | 0.375 | MOP |  | Cleaning stop due to Tractor pulli Broken
140 | 2024-02-17 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning Stop due to Tractor under breakdown
141 | 2024-02-18 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning Stop due to Tractor under breakdown
142 | 2024-02-19 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 0.16667 | 0.375 | MOP
143 | 2024-02-20 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 0.20833 | 0.45833 | MOP
144 | 2024-02-21 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
145 | 2024-02-22 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
146 | 2024-02-23 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
147 | 2024-02-24 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
148 | 2024-02-25 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
149 | 2024-02-26 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
150 | 2024-02-27 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
151 | 2024-02-28 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
152 | 2024-02-29 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
153 | 2024-03-01 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
154 | 2024-03-02 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
155 | 2024-03-03 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
156 | 2024-03-04 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
157 | 2024-03-05 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
158 | 2024-03-06 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
159 | 2024-03-07 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
160 | 2024-03-08 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Module cleaning stopped by vendor due to festival yesterday.
161 | 2024-03-09 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP |  | Venders absent
162 | 2024-03-10 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP |  | Venders absent
163 | 2024-03-11 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP |  | Venders absent
164 | 2024-03-12 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP |  | Venders absent
165 | 2024-03-13 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP |  | Venders absent
166 | 2024-03-14 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
167 | 2024-03-15 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
168 | 2024-03-16 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
169 | 2024-03-17 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
170 | 2024-03-18 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
171 | 2024-03-19 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
172 | 2024-03-20 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
173 | 2024-03-21 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
174 | 2024-03-22 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
175 | 2024-03-23 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
176 | 2024-03-24 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning Stop due to Festival
177 | 2024-03-25 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning Stop due to Festival
177 | 2024-03-26 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
179 | 2024-03-27 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP |  | Cleaning happed only evening due to tractor breadown on 26 March night.
180 | 2024-03-28 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
181 | 2024-03-29 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
182 | 2024-03-30 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
183 | 2024-03-31 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
184 | 2024-04-01 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
185 | 2024-04-02 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
186 | 2024-04-03 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
187 | 2024-04-04 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
188 | 2024-04-05 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
189 | 2024-04-06 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
190 | 2024-04-07 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
191 | 2024-04-08 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
192 | 2024-04-09 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
193 | 2024-04-10 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
194 | 2024-04-11 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
195 | 2024-04-12 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
196 | 2024-04-13 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
197 | 2024-04-14 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
198 | 2024-04-15 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
199 | 2024-04-16 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
200 | 2024-04-17 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
201 | 2024-04-18 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
202 | 2024-04-19 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
203 | 2024-04-20 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
204 | 2024-04-21 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
205 | 2024-04-22 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
206 | 2024-04-23 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
207 | 2024-04-24 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
208 | 2024-04-25 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
209 | 2024-04-26 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
210 | 2024-04-27 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
211 | 2024-04-28 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
212 | 2024-04-29 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
213 | 2024-04-30 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
214 | 2024-05-01 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
215 | 2024-05-02 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 |  |  | MOP |  | One tractor breakdown
216 | 2024-05-03 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
217 | 2024-05-04 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
218 | 2024-05-05 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 |  |  | MOP |  | One tractor breakdown
219 | 2024-05-06 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
220 | 2024-05-07 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
221 | 2024-05-08 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
222 | 2024-05-09 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 |  |  | MOP |  | One tractor breakdown
223 | 2024-05-10 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 14950 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
224 | 2024-05-11 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
225 | 2024-05-12 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
226 | 2024-05-13 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
227 | 2024-05-14 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
228 | 2024-05-15 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
229 | 2024-05-16 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
230 | 2024-05-17 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
231 | 2024-05-18 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
232 | 2024-05-19 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
233 | 2024-05-20 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
234 | 2024-05-21 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
235 | 2024-05-22 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
236 | 2024-05-23 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 |  |  | MOP |  | One tractor breakdown
237 | 2024-05-24 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
238 | 2024-05-25 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
239 | 2024-05-26 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
240 | 2024-05-27 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
241 | 2024-05-28 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 |  |  | MOP |  | One tractor breakdown
242 | 2024-05-29 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 |  |  | MOP |  | One tractor breakdown
243 | 2024-05-30 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
244 | 2024-05-31 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
245 | 2024-06-01 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
246 | 2024-06-02 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
247 | 2024-06-03 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
248 | 2024-06-04 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 | 0.6875 | 0.95833 | MOP
249 | 2024-06-05 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.22917 | 0.39583 |  |  | MOP |  | One tractor breakdown
250 | 2024-06-06 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
251 | 2024-06-07 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
252 | 2024-06-08 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
253 | 2024-06-09 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
254 | 2024-06-10 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
255 | 2024-06-11 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
256 | 2024-06-12 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP |  | One tractor breakdown
257 | 2024-06-13 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
258 | 2024-06-14 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
259 | 2024-06-15 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
260 | 2024-06-16 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
261 | 2024-06-17 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
262 | 2024-06-18 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
263 | 2024-06-19 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
264 | 2024-06-20 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
265 | 2024-06-21 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
266 | 2024-06-22 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
267 | 2024-06-23 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
268 | 2024-06-24 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
269 | 2024-06-25 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
270 | 2024-06-26 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning was stopped at the site yesterday because module cleaning was done by rain.
271 | 2024-06-27 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
272 | 2024-06-28 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
273 | 2024-06-29 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning was stopped at the site yesterday because module cleaning was done by rain.
274 | 2024-06-30 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
275 | 2024-07-01 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
276 | 2024-07-02 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
277 | 2024-07-03 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
278 | 2024-07-04 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning was stopped at the site yesterday due to heavy rain
279 | 2024-07-05 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 13.40mm Rain fall at Site
280 | 2024-07-06 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 53.40mm Rain fall at Site
281 | 2024-07-07 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 180.20mm Rain fall at Site
282 | 2024-07-08 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
283 | 2024-07-09 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
284 | 2024-07-10 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
285 | 2024-07-11 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 111.20mm Rain fall at Site
286 | 2024-07-12 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
287 | 2024-07-13 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 36.0mm rainfall at site
288 | 2024-07-14 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
289 | 2024-07-15 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
290 | 2024-07-16 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 10250 |  |  | 0.6875 | 0.95833 | MOP
291 | 2024-07-17 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
292 | 2024-07-18 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
293 | 2024-07-19 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 15.2mm rainfall at site
294 | 2024-07-20 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
295 | 2024-07-21 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
296 | 2024-07-22 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
297 | 2024-07-23 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 3.20mm rainfall at site
298 | 2024-07-24 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | light Rain at Site
299 | 2024-07-25 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
300 | 2024-07-26 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 2.2mm rainfall at site
301 | 2024-07-27 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 22.2mm rainfall at site
302 | 2024-07-28 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
303 | 2024-07-29 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
304 | 2024-07-30 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
305 | 2024-07-31 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 7.80mm rainfall at site
306 | 2024-08-01 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | light Rain at Site
307 | 2024-08-02 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
308 | 2024-08-03 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
309 | 2024-08-04 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 12.2 mm rainfall at Site
310 | 2024-08-05 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 9.20mm rainfall at site
311 | 2024-08-06 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
312 | 2024-08-07 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 6.60mm rainfall at site
313 | 2024-08-08 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 27.60mm rainfall at site
314 | 2024-08-09 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 6.8mm rainfall at site
315 | 2024-08-10 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 4.5mm rainfall at site
316 | 2024-08-11 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 12.6mm rainfall at site
317 | 2024-08-12 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 38.2mm rainfall at site
318 | 2024-08-13 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 6.8mm rainfall at site
319 | 2024-08-14 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 13.6mm rainfall at site
320 | 2024-08-15 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 8.2mm rainfall at site
321 | 2024-08-16 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000
322 | 2024-08-17 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.8 mm rainfall at site
323 | 2024-08-18 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.9 mm rainfall at site
324 | 2024-08-19 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 15.8mm rainfall at site
325 | 2024-08-20 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.6mm rainfall at site
326 | 2024-08-21 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
327 | 2024-08-22 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000
328 | 2024-08-23 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 14.6mm rainfall at site
329 | 2024-08-24 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000
330 | 2024-08-25 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 7mm rainfall at site
331 | 2024-08-26 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.2mm rainfall at site
332 | 2024-08-27 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 4.2mm rainfall at site
333 | 2024-08-28 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 8.0mm rainfall at site
334 | 2024-08-29 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.2mm rainfall at site
335 | 2024-08-30 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 8.4mm rainfall at site
336 | 2024-08-31 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000
337 | 2024-09-01 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
338 | 2024-09-02 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.6875 | 0.95833 | MOP
339 | 2024-09-03 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | 23.20mm rainfall at site
340 | 2024-09-04 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | 42.40mm rainfall at site
341 | 2024-09-05 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | 2.6mm rainfall at site
342 | 2024-09-06 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | 144.4mm rainfall at site
343 | 2024-09-07 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
344 | 2024-09-08 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
345 | 2024-09-09 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
346 | 2024-09-10 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
347 | 2024-09-11 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
348 | 2024-09-12 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
349 | 2024-09-13 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
350 | 2024-09-14 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
351 | 2024-09-15 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
352 | 2024-09-16 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
353 | 2024-09-17 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
354 | 2024-09-18 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
355 | 2024-09-19 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
356 | 2024-09-20 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
357 | 2024-09-21 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
358 | 2024-09-22 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
359 | 2024-09-23 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
360 | 2024-09-24 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
361 | 2024-09-25 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
362 | 2024-09-26 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
363 | 2024-09-27 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
364 | 2024-09-28 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
365 | 2024-09-29 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
366 | 2024-09-30 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
367 | 2024-10-01 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
368 | 2024-10-02 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
369 | 2024-10-03 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
370 | 2024-10-04 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
371 | 2024-10-05 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
372 | 2024-10-06 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
373 | 2024-10-07 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
374 | 2024-10-08 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
375 | 2024-10-09 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
376 | 2024-10-10 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
377 | 2024-10-11 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
378 | 2024-10-12 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
379 | 2024-10-13 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
380 | 2024-10-14 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
381 | 2024-10-15 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
382 | 2024-10-16 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
383 | 2024-10-17 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
384 | 2024-10-18 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
385 | 2024-10-19 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
386 | 2024-10-20 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
387 | 2024-10-21 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
388 | 2024-10-22 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
389 | 2024-10-23 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
390 | 2024-10-24 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
391 | 2024-10-25 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
392 | 2024-10-26 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
393 | 2024-10-27 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
394 | 2024-10-28 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
395 | 2024-10-29 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
396 | 2024-10-30 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
397 | 2024-10-31 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
398 | 2024-11-01 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
399 | 2024-11-02 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
400 | 2024-11-03 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
401 | 2024-11-04 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
402 | 2024-11-05 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
403 | 2024-11-06 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
404 | 2024-11-07 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
405 | 2024-11-08 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
406 | 2024-11-09 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
407 | 2024-11-10 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
408 | 2024-11-11 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP |  | Tractor breakdown
409 | 2024-11-12 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
410 | 2024-11-13 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
411 | 2024-11-14 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
412 | 2024-11-15 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
413 | 2024-11-16 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP |  | one tractor breakdown
414 | 2024-11-17 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP |  | one tractor breakdown
415 | 2024-11-18 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP |  | one tractor breakdown
416 | 2024-11-19 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP |  | one tractor breakdown
417 | 2024-11-20 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
418 | 2024-11-21 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
419 | 2024-11-22 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 0.66667 | 0.79167 | MOP
420 | 2024-11-23 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
421 | 2024-11-24 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
422 | 2024-11-25 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
423 | 2024-11-26 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
424 | 2024-11-27 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
425 | 2024-11-28 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
426 | 2024-11-29 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
427 | 2024-11-30 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
428 | 2024-12-01 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
429 | 2024-12-02 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
430 | 2024-12-03 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
431 | 2024-12-04 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
432 | 2024-12-05 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
433 | 2024-12-06 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
434 | 2024-12-07 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
435 | 2024-12-08 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
436 | 2024-12-09 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
437 | 2024-12-10 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
438 | 2024-12-11 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
439 | 2024-12-12 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
440 | 2024-12-13 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
441 | 2024-12-14 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
442 | 2024-12-15 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
443 | 2024-12-16 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
444 | 2024-12-17 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
445 | 2024-12-18 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
446 | 2024-12-19 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
447 | 2024-12-20 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
448 | 2024-12-21 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
449 | 2024-12-22 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
450 | 2024-12-23 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
451 | 2024-12-24 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
452 | 2024-12-25 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
453 | 2024-12-26 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
454 | 2024-12-27 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
455 | 2024-12-28 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
456 | 2024-12-29 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
457 | 2024-12-30 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
458 | 2024-12-31 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 17250 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
459 | 2025-01-01 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Yesterday module cleaning stopped because the vendor did not come due to the New Year.
460 | 2025-01-02 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
461 | 2025-01-03 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 14250 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
462 | 2025-01-04 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
463 | 2025-01-05 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
464 | 2025-01-06 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
465 | 2025-01-07 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
466 | 2025-01-08 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
467 | 2025-01-09 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
468 | 2025-01-10 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
469 | 2025-01-11 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
470 | 2025-01-12 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
471 | 2025-01-13 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
472 | 2025-01-14 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
473 | 2025-01-15 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
474 | 2025-01-16 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
475 | 2025-01-17 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
476 | 2025-01-18 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
477 | 2025-01-19 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
478 | 2025-01-20 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
479 | 2025-01-21 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
480 | 2025-01-22 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
481 | 2025-01-23 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning stopped that day due to bad weather.
482 | 2025-01-24 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
483 | 2025-01-25 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
484 | 2025-01-26 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
485 | 2025-01-27 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
486 | 2025-01-28 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
487 | 2025-01-29 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
488 | 2025-01-30 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
489 | 2025-01-31 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
490 | 2025-02-01 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
491 | 2025-02-02 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
492 | 2025-02-03 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
493 | 2025-02-04 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
494 | 2025-02-05 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
495 | 2025-02-06 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
496 | 2025-02-07 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
497 | 2025-02-08 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
498 | 2025-02-09 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning stopped that day due to vendor home family function.
499 | 2025-02-10 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
500 | 2025-02-11 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning stopped that day due to vendor home family function.
501 | 2025-02-12 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000
502 | 2025-02-13 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
503 | 2025-02-14 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
504 | 2025-02-15 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
505 | 2025-02-16 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
506 | 2025-02-17 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
507 | 2025-02-18 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
508 | 2025-02-19 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
509 | 2025-02-20 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
510 | 2025-02-21 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
511 | 2025-02-22 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
512 | 2025-02-23 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
513 | 2025-02-24 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
514 | 2025-02-25 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
515 | 2025-02-26 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
516 | 2025-02-27 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
517 | 2025-02-28 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000
518 | 2025-03-01 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
519 | 2025-03-02 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
520 | 2025-03-03 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
521 | 2025-03-04 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
522 | 2025-03-05 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
523 | 2025-03-06 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
524 | 2025-03-07 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Function at vendor's home
525 | 2025-03-08 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
526 | 2025-03-09 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
527 | 2025-03-10 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
528 | 2025-03-11 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
529 | 2025-03-12 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
530 | 2025-03-13 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
531 | 2025-03-14 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
532 | 2025-03-15 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
533 | 2025-03-16 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
534 | 2025-03-17 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
535 | 2025-03-18 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
536 | 2025-03-19 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
537 | 2025-03-20 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
538 | 2025-03-21 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
539 | 2025-03-22 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
540 | 2025-03-23 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
541 | 2025-03-24 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
542 | 2025-03-25 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 0.29167 | 0.41667 | 0.66667 | 0.79167 | MOP
543 | 2025-03-26 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
544 | 2025-03-27 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
545 | 2025-03-28 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
546 | 2025-03-29 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
547 | 2025-03-30 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
548 | 2025-03-31 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
549 | 2025-04-01 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
550 | 2025-04-02 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
551 | 2025-04-03 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
552 | 2025-04-04 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
553 | 2025-04-05 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
554 | 2025-04-06 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
555 | 2025-04-07 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
556 | 2025-04-08 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
557 | 2025-04-09 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk8: 6000 | 6000
558 | 2025-04-10 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk4: 4200; Blk6: 6600; Blk7: 6000; Blk8: 6000 | 22800 | 0.375 | 0.5 | 0.58333 | 0.75
559 | 2025-04-11 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7200 | 7450 | 7800 | 7250 |  | 7200 |  | 6000 | 42900 | 0.375 | 0.5 | 0.58333 | 0.75
560 | 2025-04-12 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 6500 | 7550 | 7100 | 7300 | 6900 |  |  | 6000 | 41350 | 0.375 | 0.5 | 0.58333 | 0.75
561 | 2025-04-13 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7100 | 7200 | 6000 |  | 7500 | 7700 | 7800 | 6000 | 49300 | 0.375 | 0.5 | 0.58333 | 0.75
562 | 2025-04-14 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 | 7800 |  |  | 9000 | 6500 | 7250 | 5500 | 43650 | 0.375 | 0.5 | 0.58333 | 0.75
563 | 2025-04-15 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 | 7450 | 5600 | 7250 | 6300 | 5000 | 0 | 4100 | 43300 | 0.375 | 0.5 | 0.58333 | 0.75
564 | 2025-04-16 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 | 6750 | 7800 | 6500 | 7600 |  |  | 7600 | 49200 | 0.375 | 0.5 | 0.58333 | 0.75
565 | 2025-04-17 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning |  | 7600 | 7600 | 6300 | 6300 |  |  | 7000 | 34800 | 0.375 | 0.5 | 0.58333 | 0.75
566 | 2025-04-18 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7800 | 7600 | 7500 | 6500 | 7100 |  |  | 6000 | 42500 | 0.375 | 0.5 | 0.58333 | 0.75
567 | 2025-04-19 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 8580 | 8640 | 10080 |  | 8880 | 9240 | 8700 | 6000 | 45100 | 0.375 | 0.5 | 0.58333 | 0.75
568 | 2025-04-20 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 |  | 9360 |  | 9180 | 9360 | 9360 | 6000 | 38650 | 0.375 | 0.5 | 0.58333 | 0.75
569 | 2025-04-21 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 5760 | 9360 | 10080 |  | 9360 | 9120 | 9000 | 6000 | 46300 | 0.375 | 0.5 | 0.58333 | 0.75
570 | 2025-04-22 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 | 6000 | 7600 | 7250 | 7200 | 7600 |  | 6000 | 49250 | 0.375 | 0.5 | 0.58333 | 0.75
571 | 2025-04-23 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 6200 | 6000 | 6000 | 8640 | 7500 | 7920 | 7000 | 0 | 49260 | 0.375 | 0.5 | 0.58333 | 0.75
572 | 2025-04-24 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7200 | 6000 | 5500 | 9900 | 7200 | 8640 |  | 0 | 44440 | 0.375 | 0.5 | 0.58333 | 0.75
573 | 2025-04-25 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7200 | 6000 | 6800 | 7500 | 7400 | 6200 | 6800 | 0 | 47900 | 0.375 | 0.5 | 0.58333 | 0.75
574 | 2025-04-26 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 6200 | 6800 | 5750 | 6200 | 6900 | 6200 | 5100 | 0 | 43150 | 0.375 | 0.5 | 0.58333 | 0.75
575 | 2025-04-27 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7200 | 7200 | 6000 | 7400 | 7200 | 6600 | 7200 | 0 | 48800 | 0.375 | 0.5 | 0.58333 | 0.75
576 | 2025-04-28 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk2: 0; Blk3: 0 | 0 | 0.375 | 0.5 | 0.58333 | 0.75
577 | 2025-04-29 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk2: 3600; Blk3: 4800; Blk8: 6000 | 14400
578 | 2025-04-30 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk2: 3250; Blk6: 7200; Blk8: 110 | 10560 | 0.375 | 0.5 | 0.58333 | 0.75
579 | 2025-05-01 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | 7200 |  |  | 3600 | 7200 | 2500 | 6600 |  | 27100 | 0.375 | 0.5 | 0.58333 | 0.75
580 | 2025-05-02 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7500; Blk4: 5450; Blk5: 6250; Blk6: 6600 | 25800 | [6 empty] | RO
581 | 2025-05-03 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7050; Blk4: 6600; Blk5: 7150; Blk7: 5500 | 26300
582 | 2025-05-04 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (1 to 11),Robot2 (73 to 79),Robot 3(80 to 86) & Robot 4 (87 to 92)
583 | 2025-05-05 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (12 to 18),Robot2 (70 to 73),Robot 3(93 to 98) & Robot 4 (99 to104)
584 | 2025-05-06 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (19 to 33),Robot2 (81 to 86),Robot 3(105 to 112) & Robot 4 (113 to126)
585 | 2025-05-07 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (22 to 33),Robot2 (34 to 40),Robot 3(80 to 92) & Robot 4 (127 to144)
586 | 2025-05-08 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (40 to 55),Robot2 (73 to 77),Robot 3(93 to 98) & Robot 4 (137 to 166)
587 | 2025-05-09 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (132 to 152),Robot2 (56 to 64),Robot 3(68 to 72) & Robot 4 (99 to 104)
588 | 2025-05-10 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (57 to 63),Robot2 (64 to 67),Robot 3(95 to 111) & Robot 4 (172 to 185)
589 | 2025-05-11 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (50 to 56),Robot2 (68to 74),Robot 3(123 to 131) & Robot 4 (110 to 116)
590 | 2025-05-12 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (26 to 49),Robot2 (2 to 17),Robot 3(103 to 110) & Robot 4 (64 to 69)
591 | 2025-05-13 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (44 to 59),Robot2 (17 to 34),Robot 3(67 to 70) & Robot 4 (97 to 102)
592 | 2025-05-14 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (40 to 55),Robot2 (76 to 79),Robot 3(87 to 91) & Robot 4 (104 to 113)
593 | 2025-05-15 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (62 to 65),Robot2 (81 to 84),Robot 3(87 to 90) & Robot 4 (98 to 102)
594 | 2025-05-16 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (01 to 08),Robot2 (158 to165),Robot 3(148 to 157) & Robot 4 (104 to 110)
595 | 2025-05-17 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 5500; Blk4: 3250; Blk6: 4000; Blk8: 2250 | 15000 | 0.375 | 0.5 | 0.58333 | 0.75
596 | 2025-05-18 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7750; Blk4: 7250; Blk6: 7450; Blk8: 3750 | 26200 | 0.375 | 0.5 | 0.58333 | 0.75
597 | 2025-05-19 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7450; Blk4: 7550; Blk6: 7250; Blk8: 5250 | 27500 | 0.375 | 0.5 | 0.58333 | 0.75
598 | 2025-05-20 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 7650; Blk4: 1400; Blk5: 5400; Blk8: 5100 | 19550 | 0.375 | 0.5 | 0.58333 | 0.75
599 | 2025-05-21 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning |  | 7400 | 7700 |  | 5400 | 1700 | 7750 |  | 29950 | 0.375 | 0.5 | 0.58333 | 0.75
600 | 2025-05-22 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 4600; Blk3: 5950; Blk5: 7000; Blk7: 5100 | 22650 | 0.375 | 0.5 | 0.58333 | 0.75
601 | 2025-05-23 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk5: 3900; Blk7: 3250; Blk8: 3500 | 10650 | 0.375 | 0.5 | 0.58333 | 0.75
602 | 2025-05-24 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk4: 3000; Blk5: 3650; Blk8: 3400 | 10050 | 0.375 | 0.5 | 0.58333 | 0.75
603 | 2025-05-25 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7600; Blk4: 7600; Blk8: 7550 | 22750 | 0.375 | 0.5 | 0.58333 | 0.75
604 | 2025-05-26 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0
605 | 2025-05-27 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0
606 | 2025-05-28 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 7000; Blk3: 3500; Blk5: 5250; Blk7: 4000 | 19750 | 0.375 | 0.5 | 0.58333 | 0.75
607 | 2025-05-29 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0
608 | 2025-05-30 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 4400; Blk6: 6900 | 11300 | 0.375 | 0.5 | 0.58333 | 0.75
609 | 2025-05-31 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 7000; Blk3: 7250; Blk6: 7000; Blk7: 8250 | 29500 | 0.375 | 0.5 | 0.58333 | 0.75
610 | 2025-06-01 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 8250; Blk3: 7250; Blk6: 5400; Blk7: 6600 | 27500 | 0.375 | 0.5 | 0.58333 | 0.75
611 | 2025-06-02 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 6000 |  | 6400 | 2400 |  | 6050 | 1100 | 4500 | 26450 | 0.375 | 0.5 | 0.58333 | 0.75
612 | 2025-06-03 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk1: 6600; Blk4: 7800; Blk5: 7250; Blk8: 5500 | 27150 | 0.375 | 0.5 | 0.58333 | 0.75
613 | 2025-06-04 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk1: 7500; Blk4: 7500; Blk5: 7800; Blk8: 6600 | 29400 | 0.375 | 0.5 | 0.58333 | 0.75
614 | 2025-06-05 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 4500 | 7250 | 7200 | 1850 |  | 7800 | 7750 |  | 36350 | 0.375 | 0.5 | 0.58333 | 0.75
615 | 2025-06-06 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | [8 empty] | 0
616 | 2025-06-07 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 7800; Blk3: 7200; Blk6: 6500; Blk7: 7200 | 28700 | 0.375 | 0.5 | 0.58333 | 0.75
617 | 2025-06-08 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 1300 | 2650 |  |  |  | 6100 | 1100 | 4900 | 16050 | 0.375 | 0.5 | 0.58333 | 0.75
618 | 2025-06-09 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 7300 |  | 4800 | 3250 | 8600 |  |  | 5000 | 28950 | 0.375 | 0.5 | 0.58333 | 0.75
619 | 2025-06-10 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk1: 5800; Blk4: 7300; Blk5: 8000; Blk8: 6750 | 27850 | 0.375 | 0.5 | 0.58333 | 0.75
620 | 2025-06-11 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 5700 | 2000 | 4050 | 7200 | 3900 |  |  |  | 22850 | 0.375 | 0.5 | 0.58333 | 0.75
621 | 2025-06-12 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning |  | 7200 | 7700 | 1800 |  | 5450 | 7000 |  | 29150 | 0.375 | 0.5 | 0.58333 | 0.75
622 | 2025-06-13 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 7500; Blk3: 7600; Blk6: 7700; Blk7: 7250 | 30050 | 0.375 | 0.5 | 0.58333 | 0.75
623 | 2025-06-14 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 4000 | 3000 |  | 7500 |  | 7700 | 2300 | 6300 | 30800 | 0.375 | 0.5 | 0.58333 | 0.75
624 | 2025-06-15 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk1: 8000; Blk4: 9700; Blk5: 7750; Blk8: 6000 | 31450 | 0.375 | 0.5 | 0.58333 | 0.75
625 | 2025-06-16 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 8000 |  |  | 3150 | 6050 | 4500 |  | 6500 | 28200 | 0.375 | 0.5 | 0.58333 | 0.75
626 | 2025-06-17 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 7500; Blk5: 6800; Blk6: 7550; Blk7: 7100 | 28950 | 0.375 | 0.5 | 0.58333 | 0.75
627 | 2025-06-18 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 7500; Blk3: 7400; Blk6: 7600; Blk7: 7150 | 29650 | 0.375 | 0.5 | 0.58333 | 0.75
628 | 2025-06-19 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 2500 | 4500 |  |  | 6600 | 1100 | 6500 |  | 21200 | 0.375 | 0.5 | 0.58333 | 0.75
Formulas:
Days = DAY(EOMONTH(MC[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 12 | 0 |  | 0 |  | 35.4677 | 50.0389 | 2.5105 | 5.7 | [9 empty] | 0 |  |  |  | 66.75 | 6.6839 | 346441.9355 | 77.65% | 21.62% | 99.5% | 99.5%
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 12 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 100% |  |  | 100% |  |  |  |  | 21.45% | 0 | 343623.8886 | 61.9293 | 343561.9593 | 66.75 | 6.6839 | 346441.9355 | 77.65% | 21.62% | 99.5% | 99.5% | [9 empty] | 66.755
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 12 | 0 |  | 7.31 |  | 30.32 | 40.28 | 1.71 | 6.3 | 100% |  |  | 100% |  |  | 70.41% |  | 21.45% | 364093.2 | 343623.8886 | 61.9293 | 343561.9593 | 66.75 | 6.6839 | 346441.9355 | 77.65% | 21.62% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.18 |  | 25.08 | 40.95 | 1.76 | 5.3 | 99.99% |  |  | 100% |  |  | 71.69% |  | 21.45% | 354559 | 343623.8886 | 61.9293 | 343561.9593 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.87 |  | 26.5 | 39.7 | 1.9 | 5.9 | 99.79% |  |  | 100% |  |  | 72.98% |  | 20.89% | 341179 | 334708.37 | 58.016 | 334650.354 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 0 |  | 25.78 | 32 | 2.63 | 5.3 | 99.56% |  |  | 100% |  |  |  |  | 18.92% | 305040 | 303117.53 | 59.618 | 303057.912 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.1 |  | 35.1 | 50.1 | 1.5 | 4.3 | 100% |  |  | 100% |  |  | 77.97% |  | 19.82% | 318035 | 317553.665 | 61.857 | 317491.808 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.9 |  | 37.8 | 58.63 | 1.48 | 7.5 | 100% |  |  | 100% |  |  | 84.59% |  | 20.79% | 336772.2 | 333180.32 | 55.638 | 333124.682 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.92 |  | 39.3 | 47.4 | 1.2 | 5.33 | 100% |  |  | 100% |  |  | 71.24% |  | 20.54% | 331522.2 | 329112.576 | 55.361 | 329057.215 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.5257 |  | 41.9 | 51.1 | 1.1 | 3.13 | 99.98% |  |  | 100% |  |  | 72.85% |  | 19.81% | 324271 | 317387.001 | 54.398 | 317332.603 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.0578 |  | 43.9 | 51.1 | 1.1 | 3.13 | 99.72% |  |  | 100% |  |  | 73.87% |  | 18.65% | 315636 | 298762.742 | 57.574 | 298705.168 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.6268 |  | 39.9 | 50.1 | 1.1 | 3.4 | 100% |  |  | 100% |  |  | 75.08% |  | 17.6% | 289705 | 282018.859 | 38.081 | 281980.778 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 4.36 |  | 34.9 | 49 | 3 | 5 | 99.96% |  |  | 100% |  |  | 75.19% |  | 13.66% | 223694 | 218866.4 | 30.36 | 218836.04 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 4.88 |  | 36.6 | 55.86 | 2.52 | 13.1 | 100% |  |  | 100% |  |  | 78.29% |  | 15.92% | 257651 | 255074.896 | 62.053 | 255012.843 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.15 |  | 29.88 | 43.21 | 1.3 | 6.1 | 99.74% |  |  | 100% |  |  | 77.44% |  | 19.84% | 321089 | 317952.483 | 55.075 | 317897.408 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.14 |  | 31.82 | 40.8 | 3.02 | 7.1 | 99.85% |  |  | 100% |  |  | 81.2% |  | 20.77% | 335292 | 332864.4 | 60.962 | 332803.438 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.51 |  | 32.37 | 45.01 | 1.79 | 6.1 | 99.73% |  |  | 100% |  |  | 76.08% |  | 20.64% | 333086 | 330638.835 | 55.409 | 330583.426 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.23 |  | 32.7 | 43.6 | 1.6 | 6.5 | 99.99% |  |  | 100% |  |  | 76.67% |  | 19.9% | 326506 | 318888.957 | 53.177 | 318835.78 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.27 |  | 34.09 | 46.02 | 1.33 | 6.1 | 100% |  |  | 100% |  |  | 76.29% |  | 19.93% | 323020 | 319338.93 | 54.629 | 319284.301 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.11 |  | 35.7 | 46 | 0.6 | 6.78 | 100% |  |  | 100% |  |  | 75.56% |  | 19.24% | 314197 | 308209.27 | 60.571 | 308148.699 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.95 |  | 35.61 | 47.4 | 1.3 | 5.1 | 100% |  |  | 100% |  |  | 75.62% |  | 18.75% | 305558 | 300377.401 | 57.568 | 300319.833 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.87 |  | 35.4 | 46.4 | 1.2 | 5.3 | 99.63% |  |  | 100% |  |  | 75.46% | 0% | 18.46% | 312642 | 295745.199 | 72.432 | 295672.767 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.7 |  | 35.9 | 47.6 | 1.6 | 5.1 | 100% |  |  | 100% |  |  | 72.02% |  | 20.11% | 327345 | 322154.968 | 55.847 | 322099.121 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.75 |  | 37.4 | 47.37 | 2.08 | 5.4 | 99.65% |  |  | 100% |  |  | 71.15% |  | 20.01% | 328589 | 320631.049 | 59.061 | 320571.988 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.08 |  | 37.9 | 46.08 | 1.93 | 5.1 | 99.68% |  |  | 100% |  |  | 72.39% |  | 21.36% | 347261 | 342184.731 | 53.875 | 342130.856 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.22 |  | 38 | 46.1 | 2 | 5.3 | 99.68% |  |  | 100% |  |  | 72.85% |  | 21.92% | 355743 | 351160.163 | 54.826 | 351105.337 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.18 |  | 36.5 | 45.1 | 2.47 | 8.3 | 99.54% |  |  | 100% |  |  | 72.38% |  | 21.65% | 351420 | 346943.965 | 58.132 | 346885.833 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.1 |  | 37.08 | 47.02 | 1.4 | 6.5 | 99.47% |  |  | 100% |  |  | 69.54% |  | 20.57% | 335649 | 329619.258 | 51.72 | 329567.538 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.34 |  | 36.9 | 43.37 | 1.8 | 9.9 | 100% |  |  | 100% |  |  | 73.1% |  | 16.27% | 266123 | 260616.1 | 41.865 | 260574.235 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.5 |  | 38 | 45.8 | 1.9 | 6.1 | 94.93% |  |  | 100% |  |  | 73.17% |  | 16.77% | 274076 | 268672.384 | 58.871 | 268613.513 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.2 |  | 38.9724 | 45.8338 | 2.2649 | 5.9 | 99.92% |  |  | 100% |  |  | 73.78% |  | 19.06% | 306127.9 | 305402.761 | 61 | 305341.761 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.38 |  | 40 | 46 | 2.1 | 5.1 | 99.9% |  |  | 100% |  |  | 73.79% |  | 19.62% | 316090 | 314307.9307 | 54.003 | 314253.9277 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.29 |  | 35.51 | 43.47 | 2.54 | 6.7 | 99.9% |  |  | 100% |  |  | 73.11% |  | 19.16% | 308834.9 | 307007.4493 | 43.615 | 306963.8343 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 6.3 |  | 34.64 | 42.7 | 3.78 | 7.5 | 100% |  |  | 100% |  |  | 70.46% |  | 18.5% | 298175.2 | 296343.885 | 22.985 | 296320.9 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 4.16 |  | 26.59 | 33.02 | 3.03 | 7.7 | 99.95% |  |  | 100% |  |  | 75.68% |  | 13.12% | 211112 | 210230.583 | 81.52 | 210149.063 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 5.85 |  | 27 | 31 | 3.1 | 5.9 | 99.84% |  |  | 100% |  |  | 74.98% |  | 18.28% | 293330 | 292856.136 | 59.17 | 292796.966 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 6.49 |  | 33.65 | 43.22 | 1.9 | 7.5 | 99.87% |  |  | 100% |  |  | 74.05% |  | 20.02% | 322757 | 320844.417 | 64.162 | 320780.255 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 4.14 |  | 27.91 | 34.01 | 2.69 | 9.1 | 99.71% |  |  | 100% |  |  | 76.47% |  | 13.19% | 212087.7 | 211396.792 | 63.762 | 211333.03 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 12.25 | 0 |  | 6.31 |  | 30.59 | 43.32 | 1.89 | 5.1 | 99.57% |  |  | 100% |  |  | 75.86% |  | 19.95% | 321279.5 | 319633.678 | 103.308 | 319530.37 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 12.5667 | 0 |  | 5.46 |  | 26.11 | 40.91 | 2.1 | 4.9 | 73.28% |  |  | 100% |  |  | 55.99% |  | 12.74% | 213164.2 | 204058.977 | 2.116 | 204056.861 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 12.45 | 0 |  | 6.54 |  | 31.23 | 40.22 | 2.05 | 7.9 | 98.05% |  |  | 100% |  |  | 69.67% |  | 18.99% | 302578 | 304228.486 | 66.532 | 304161.954 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 12.15 | 0 |  | 6.68 |  | 32.39 | 43.99 | 1.81 | 7.1 | 99.59% |  |  | 100% |  |  | 73.52% |  | 20.46% | 328786 | 327888.986 | 53.566 | 327835.42 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 12.0833 | 0 |  | 5.78 |  | 29.02 | 40.1 | 1.6 | 5.4 | 99.62% |  |  | 100% |  |  | 73.67% |  | 17.74% | 283650.6625 | 284293.991 | 47.886 | 284246.105 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 12.45 | 0 |  | 6.7 |  | 31.8 | 43.4 | 1.5 | 4.8 | 99.89% |  |  | 100% |  |  | 75.16% |  | 20.98% | 338732 | 336183.752 | 63.231 | 336120.521 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 12.3167 | 0 |  | 6.85 |  | 35.13 | 43.88 | 1.88 | 7.3 | 99.98% |  |  | 100% |  |  | 75.16% |  | 21.45% | 345699 | 343701.784 | 61.428 | 343640.356 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 12.45 | 0 |  | 5.73 |  | 34.36 | 42.16 | 1.65 | 11.7 | 99.49% |  |  | 100% |  |  | 75.05% |  | 17.92% | 286967.7 | 287098.603 | 65.958 | 287032.645 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 12.9167 | 0 |  | 6.95 |  | 38.2 | 45.38 | 2.6 | 7.1 | 99.64% |  |  | 100% |  |  | 75.03% |  | 21.73% | 201945 | 348122.386 | 66.671 | 348055.715 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 0 |  | 6.81 |  | 38.52 | 46.82 | 2.05 | 5.8 | 99.94% |  |  | 100% |  |  | 74.49% |  | 21.14% | 334705.4 | 338665.544 | 60.012 | 338605.532 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 13.15 | 0 |  | 5.56 |  | 37.78 | 42.3 | 2.3 | 11.3 | 99.97% |  |  | 100% |  |  | 75.32% |  | 17.45% | 292468 | 279612.765 | 60.495 | 279552.27 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 12.9667 | 0 |  | 4.84 |  | 34.4 | 42 | 2.7 | 19.29 | 99.96% |  |  | 100% |  |  | 76.27% |  | 15.38% | 254893 | 246466.213 | 72.164 | 246394.049 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 13.15 | 0 |  | 6.4 |  | 32.3 | 41.68 | 1.14 | 4.7 | 99.66% |  |  | 100% |  |  | 76.6% |  | 20.43% | 332920 | 327298.332 | 54.8 | 327243.532 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 13.2167 | 0 |  | 6.27 |  | 36.2 | 40 | 1.1 | 4.2 | 99.62% |  |  | 100% |  |  | 77.25% |  | 20.18% | 324288 | 323348.624 | 55.371 | 323293.253 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 13.2 | 0 |  | 6.27 |  | 36.2 | 38.23 | 1.3 | 6.3 | 99.94% |  |  | 100% |  |  | 76.72% |  | 20.04% | 323147 | 321187.681 | 90.846 | 321096.835 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 13.1833 | 0 |  | 5.79 |  | 35.5 | 28 | 1.1 | 4.3 | 99.99% |  |  | 100% |  |  | 76.26% |  | 18.4% | 297837.6 | 294810.933 | 87.974 | 294722.959 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 13.2167 | 6.88 |  | 6.41 |  | 33.8 | 43.42 | 3.64 | 8.3 | 99.96% |  |  | 100% |  |  | 75.84% |  | 20.26% | 327534.8 | 324586.013 | 90.849 | 324495.164 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 13.2667 | 6.9 |  | 6.38 |  | 34.93 | 46.23 | 3.32 | 7.1 | 99.98% |  |  | 100% |  |  | 75.88% |  | 20.17% | 326090.97 | 323230.815 | 100.849 | 323129.966 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 13.2333 | 6.17 |  | 5.67 |  | 35.89 | 44.51 | 4.63 | 7.7 | 99.77% |  |  | 100% |  |  | 76.14% |  | 17.99% | 290997.7 | 288274.486 | 120.849 | 288153.637 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 12.7667 | 6.76 |  | 6.25 |  | 36.28 | 44.75 | 2.4 | 6.5 | 99.87% |  |  | 100% |  |  | 79.48% |  | 20.7% | 333824.3 | 331724.974 | 160.849 | 331564.125 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 13.2833 | 5.25 |  | 4.81 |  | 32.47 | 39.01 | 3.18 | 8.3 | 99.66% |  |  | 100% |  |  | 79.8% |  | 15.99% | 258237.06 | 256383.486 | 160.849 | 256222.637 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 13.35 | 6.45 |  | 5.98 |  | 34.17 | 39.27 | 1.95 | 5.7 | 99.93% |  |  | 100% |  |  | 77.18% |  | 19.23% | 311840.2 | 308223.809 | 158.849 | 308064.96 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 13.4167 | 6.79 |  | 6.28 |  | 36.79 | 48.09 | 1.97 | 4.9 | 65.94% |  |  | 100% |  |  | 50.45% |  | 13.2% | 212537.6 | 211625.783 | 159.849 | 211465.934 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 13.1667 | 5.38 |  | 4.87 |  | 35.73 | 41.95 | 2.07 | 9.69 | 86.27% |  |  | 100% |  |  | 66.65% |  | 13.53% | 218430.9 | 216832.746 | 161.849 | 216670.897 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 13.0167 | 5.85 |  | 5.34 |  | 36.45 | 45.55 | 2.33 | 7.9 | 100% |  |  | 100% |  |  | 77.05% |  | 17.14% | 277904.9 | 274797.158 | 161.849 | 274635.309 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 13.1833 | 5.3 |  | 4.85 |  | 33.5 | 42 | 3.1 | 8.3 | 99.72% |  |  | 100% |  |  | 76.48% |  | 15.46% | 251303.79 | 247759.346 | 159.812 | 247599.534 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 13.3167 | 4.91 |  | 4.4 |  | 31.9 | 40.8 | 3.4 | 6.2 | 99.77% |  |  | 100% |  |  | 77.97% |  | 14.29% | 229035.1 | 229145.811 | 156.812 | 228988.999 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 12.6833 | 5.82 |  | 5.25 |  | 32.2 | 41.3 | 3.2 | 4.8 | 94.53% |  |  | 100% |  |  | 73.47% |  | 16.07% | 259288.99 | 257628.344 | 156.812 | 257471.532 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 13.2333 | 5.12 |  | 4.62 |  | 32.1 | 40.8 | 2.8 | 7.1 | 94.13% |  |  | 100% |  |  | 74.85% |  | 14.41% | 231929.06 | 230994.357 | 156.812 | 230837.545 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 13.3833 | 5.74 |  | 5.18 |  | 36.4 | 48 | 3.1 | 6.3 | 99.5% |  |  | 100% |  |  | 78.8% |  | 17.01% | 273632.5 | 272636.06 | 156.812 | 272479.248 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 13.5 | 6.7 |  | 6.3 |  | 36.8 | 52.03 | 3.2 | 8.3 | 95.71% |  |  | 100% |  |  | 74.99% |  | 19.69% | 317965 | 315512.697 | 154.875 | 315357.822 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 13.45 | 6.6 |  | 6.32 |  | 30.8 | 50.3 | 31.1 | 8.5 | 100% |  |  | 100% |  |  | 75.41% |  | 19.86% | 319248 | 318269.456 | 156.271 | 318113.185 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 13.4833 | 6.98 |  | 6.78 |  | 31.9 | 52.8 | 3.9 | 6.4 | 99.74% |  |  | 100% |  |  | 74.75% |  | 21.12% | 340883 | 338445.266 | 155.681 | 338289.585 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 13.4667 | 6.9 |  | 6.38 |  | 38.8 | 45.5 | 1.23 | 6.3 | 99.89% |  |  | 100% |  |  | 77.59% |  | 20.63% | 332985.59 | 330587.652 | 155.681 | 330431.971 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 13.4667 | 7.2 |  | 6.66 |  | 40.38 | 45.99 | 2.41 | 7.7 | 99.85% |  |  | 100% |  |  | 75.64% |  | 20.99% | 338140.4 | 336393.986 | 146.681 | 336247.305 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 13.4833 | 7.54 |  | 7.03 |  | 41.33 | 46.5 | 3.21 | 8.7 | 99.96% |  |  | 100% |  |  | 76.27% |  | 22.34% | 359956.5 | 358052.207 | 146.681 | 357905.526 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 13.45 | 7.17 |  | 6.59 |  | 40.35 | 47.76 | 2.22 | 5.5 | 100% |  |  | 100% |  |  | 76.48% |  | 21% | 338030.77 | 336579.164 | 146.681 | 336432.483 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 13.4333 | 6.58 |  | 6.05 |  | 39.97 | 49.84 | 2.3 | 5.5 | 100% |  |  | 100% |  |  | 76.02% |  | 19.16% | 309854.97 | 307152.908 | 146.681 | 307006.227 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 11.3833 | 5.96 |  | 5.45 |  | 39.42 | 48.96 | 3.4 | 12.9 | 100% |  |  | 100% |  |  | 76.09% |  | 17.28% | 279024.1 | 276945.719 | 146.681 | 276799.038 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 13.5833 | 6.54 |  | 6.01 |  | 37.79 | 49.04 | 1.63 | 4.9 | 99.99% |  |  | 100% |  |  | 76.05% |  | 19.04% | 307007.4 | 305232.082 | 146.681 | 305085.401 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 13.2333 | 4.87 |  | 4.49 |  | 34.83 | 42.57 | 3.24 | 10.7 | 99.78% |  |  | 100% |  |  | 76.17% |  | 14.25% | 229066.5 | 228426.298 | 146.681 | 228279.617 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 11.6667 | 6.29 |  | 5.78 |  | 32.82 | 40.29 | 3.89 | 8.5 | 99.58% |  |  | 100% |  |  | 78.46% |  | 18.89% | 303505.1 | 302835.605 | 143.681 | 302691.924 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 10.8833 | 4.44 |  | 3.98 |  | 33.67 | 42.05 | 2.77 | 8.9 | 100% |  |  | 100% |  |  | 79.43% |  | 13.17% | 212042.5 | 211172.845 | 143.681 | 211029.164 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 13.4667 | 5.32 |  | 4.96 |  | 31.72 | 42.78 | 1.64 | 5.1 | 99.56% |  |  | 100% |  |  | 78.39% |  | 16.2% | 261299.05 | 259670.743 | 135.681 | 259535.062 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 12.4333 | 4.53 |  | 4.17 |  | 30.22 | 39.34 | 3.06 | 9.5 | 99.98% |  |  | 100% |  |  | 81.17% |  | 14.1% | 227578.3 | 226079.287 | 135.681 | 225943.606 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 13.25 | 2.53 |  | 2.4 |  | 28.91 | 32.29 | 0.946 | 5.7 | 96.01% |  |  | 100% |  |  | 79.62% |  | 7.962% | 128207.03 | 127693.287 | 135.681 | 127557.606 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 13.5 | 5.62 |  | 5.19 |  | 31.15 | 42.22 | 1.35 | 6.1 | 98.93% |  |  | 100% |  |  | 76.07% |  | 16.45% | 264314.4 | 263653.358 | 133.681 | 263519.677 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 13.2167 | 5.81 |  | 5.3 |  | 33.23 | 41.42 | 1.87 | 4.9 | 99.87% |  |  | 100% |  |  | 79.53% |  | 17.56% | 282611.15 | 281490.64 | 133.681 | 281356.959 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 13.3 | 4.95 |  | 4.58 |  | 30.76 | 41.42 | 1.21 | 6.5 | 99.31% |  |  | 100% |  |  | 78.06% |  | 14.9% | 239843.7 | 238787.797 | 133.681 | 238654.116 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 13.3333 | 6.96 |  | 6.44 |  | 33.08 | 45.26 | 1.88 | 5.5 | 99.71% |  |  | 100% |  |  | 75.97% |  | 20.38% | 329656.49 | 326685.442 | 133.681 | 326551.761 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 13.65 | 6.57 |  | 6.18 |  | 33.46 | 42.64 | 3.12 | 7.5 | 99.86% |  |  | 100% |  |  | 78.29% |  | 20.16% | 324493.01 | 323091.37 | 120.681 | 322970.689 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 13.4333 | 6.68 |  | 6.3 |  | 34.28 | 42.05 | 4.04 | 8.1 | 99.96% |  |  | 100% |  |  | 76.9% |  | 20.19% | 325151.3 | 323519.832 | 116.681 | 323403.151 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 12.8833 | 6.01 |  | 5.64 |  | 31.5 | 41.46 | 2.01 | 6.7 | 99.37% |  |  | 100% |  |  | 76.06% |  | 17.87% | 287351.88 | 286457.904 | 105.681 | 286352.223 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 13.05 | 5.07 |  | 4.65 |  | 30.91 | 41.13 | 1.51 | 9.7 | 99.06% |  |  | 100% |  |  | 76.14% |  | 14.75% | 238197.7 | 236444.405 | 105.681 | 236338.724 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 13.1833 | 4.19 |  | 3.89 |  | 30.09 | 37.22 | 2.43 | 9.3 | 99.29% |  |  | 100% |  |  | 80.51% |  | 13.05% | 210024.2 | 209152.788 | 105.681 | 209047.107 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 13.05 | 3.23 |  | 3.03 |  | 29.64 | 35.33 | 1.69 | 4.3 | 99.32% |  |  | 100% |  |  | 81.73% |  | 10.32% | 166212.4 | 165401.16 | 95.681 | 165305.479 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | 13.15 | 2.61 |  | 2.41 |  | 27.91 | 32.27 | 0.185 | 4.7 | 98.74% |  |  | 100% |  |  | 81.56% |  | 8.19% | 132771 | 131303.317 | 95.681 | 131207.636 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | 13.4 | 4.34 |  | 4.07 |  | 30.38 | 37.35 | 1.48 | 7.1 | 99.5% |  |  | 100% |  |  | 78.27% |  | 13.27% | 213894.3 | 212734.465 | 95.681 | 212638.784 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | 13.3667 | 4.77 |  | 4.56 |  | 31.07 | 39.16 | 2.32 | 5.7 | 99.78% |  |  | 100% |  |  | 77.65% |  | 14.75% | 237266.1 | 236444.781 | 95.681 | 236349.1 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | 13.35 | 4.55 |  | 4.15 |  | 30.97 | 40.04 | 1.49 | 7.5 | 99.93% |  |  | 100% |  |  | 77.57% |  | 13.41% | 216167.6 | 214965.633 | 95.681 | 214869.952 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | 13.2167 | 5.37 |  | 5.13 |  | 31.55 | 42.78 | 1.29 | 4.3 | 98.88% |  |  | 100% |  |  | 77.69% |  | 16.61% | 267586.7 | 266122.048 | 95.681 | 266026.367 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | 13.2 | 4.52 |  | 4.5 |  | 32.64 | 41.48 | 1.41 | 3.9 | 99.97% |  |  | 100% |  |  | 77.29% |  | 14.49% | 233878.073 | 232266.206 | 95.681 | 232170.525 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | [8 empty] | 0% | 0 | 0 | 0 | 0 | 66.75 | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Raw_Data
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273 | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302
Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Plant DC Capcity (MW) | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | BLK1_INV1 | BLK1_INV2 | BLK1_INV3 | BLK1_INV4 | BLK1_INV5 | BLK1_INV6 | BLK1_INV7 | BLK1_INV8 | BLK1_INV9 | BLK1_INV10 | BLK1_INV11 | BLK1_INV12 | BLK1_INV13 | BLK1_INV14 | BLK1_INV15 | BLK1_INV16 | BLK1_INV17 | BLK1_INV18 | BLK1_INV19 | BLK1_INV20 | BLK1_INV21 | BLK1_INV22 | BLK1_INV23 | BLK1_INV24 | BLK1_INV25 | BLK1_INV26 | BLK1_INV27 | BLK1_INV28 | BLK1_INV29 | BLK1_INV30 | BLK1_INV31 | BLK1_INV32 | BLK2_INV1 | BLK2_INV2 | BLK2_INV3 | BLK2_INV4 | BLK2_INV5 | BLK2_INV6 | BLK2_INV7 | BLK2_INV8 | BLK2_INV9 | BLK2_INV10 | BLK2_INV11 | BLK2_INV12 | BLK2_INV13 | BLK2_INV14 | BLK2_INV15 | BLK2_INV16 | BLK2_INV17 | BLK2_INV18 | BLK2_INV19 | BLK2_INV20 | BLK2_INV21 | BLK2_INV22 | BLK2_INV23 | BLK2_INV24 | BLK2_INV25 | BLK2_INV26 | BLK2_INV27 | BLK2_INV28 | BLK2_INV29 | BLK2_INV30 | BLK2_INV31 | BLK2_INV32 | BLK3_INV1 | BLK3_INV2 | BLK3_INV3 | BLK3_INV4 | BLK3_INV5 | BLK3_INV6 | BLK3_INV7 | BLK3_INV8 | BLK3_INV9 | BLK3_INV10 | BLK3_INV11 | BLK3_INV12 | BLK3_INV13 | BLK3_INV14 | BLK3_INV15 | BLK3_INV16 | BLK3_INV17 | BLK3_INV18 | BLK3_INV19 | BLK3_INV20 | BLK3_INV21 | BLK3_INV22 | BLK3_INV23 | BLK3_INV24 | BLK3_INV25 | BLK3_INV26 | BLK3_INV27 | BLK3_INV28 | BLK3_INV29 | BLK3_INV30 | BLK3_INV31 | BLK4_INV1 | BLK4_INV2 | BLK4_INV3 | BLK4_INV4 | BLK4_INV5 | BLK4_INV6 | BLK4_INV7 | BLK4_INV8 | BLK4_INV9 | BLK4_INV10 | BLK4_INV11 | BLK4_INV12 | BLK4_INV13 | BLK4_INV14 | BLK4_INV15 | BLK4_INV16 | BLK4_INV17 | BLK4_INV18 | BLK4_INV19 | BLK4_INV20 | BLK4_INV21 | BLK4_INV22 | BLK4_INV23 | BLK4_INV24 | BLK4_INV25 | BLK4_INV26 | BLK4_INV27 | BLK4_INV28 | BLK4_INV29 | BLK4_INV30 | BLK4_INV31 | BLK5_INV1 | BLK5_INV2 | BLK5_INV3 | BLK5_INV4 | BLK5_INV5 | BLK5_INV6 | BLK5_INV7 | BLK5_INV8 | BLK5_INV9 | BLK5_INV10 | BLK5_INV11 | BLK5_INV12 | BLK5_INV13 | BLK5_INV14 | BLK5_INV15 | BLK5_INV16 | BLK5_INV17 | BLK5_INV18 | BLK5_INV19 | BLK5_INV20 | BLK5_INV21 | BLK5_INV22 | BLK5_INV23 | BLK5_INV24 | BLK5_INV25 | BLK5_INV26 | BLK5_INV27 | BLK5_INV28 | BLK5_INV29 | BLK5_INV30 | BLK5_INV31 | BLK5_INV32 | BLK6_INV1 | BLK6_INV2 | BLK6_INV3 | BLK6_INV4 | BLK6_INV5 | BLK6_INV6 | BLK6_INV7 | BLK6_INV8 | BLK6_INV9 | BLK6_INV10 | BLK6_INV11 | BLK6_INV12 | BLK6_INV13 | BLK6_INV14 | BLK6_INV15 | BLK6_INV16 | BLK6_INV17 | BLK6_INV18 | BLK6_INV19 | BLK6_INV20 | BLK6_INV21 | BLK6_INV22 | BLK6_INV23 | BLK6_INV24 | BLK6_INV25 | BLK6_INV26 | BLK6_INV27 | BLK6_INV28 | BLK6_INV29 | BLK6_INV30 | BLK6_INV31 | BLK6_INV32 | BLK7_INV1 | BLK7_INV2 | BLK7_INV3 | BLK7_INV4 | BLK7_INV5 | BLK7_INV6 | BLK7_INV7 | BLK7_INV8 | BLK7_INV9 | BLK7_INV10 | BLK7_INV11 | BLK7_INV12 | BLK7_INV13 | BLK7_INV14 | BLK7_INV15 | BLK7_INV16 | BLK7_INV17 | BLK7_INV18 | BLK7_INV19 | BLK7_INV20 | BLK7_INV21 | BLK7_INV22 | BLK7_INV23 | BLK7_INV24 | BLK7_INV25 | BLK7_INV26 | BLK7_INV27 | BLK7_INV28 | BLK7_INV29 | BLK7_INV30 | BLK7_INV31 | BLK7_INV32 | BLK8_INV1 | BLK8_INV2 | BLK8_INV3 | BLK8_INV4 | BLK8_INV5 | BLK8_INV6 | BLK8_INV7 | BLK8_INV8 | BLK8_INV9 | BLK8_INV10 | BLK8_INV11 | BLK8_INV12 | BLK8_INV13 | BLK8_INV14 | BLK8_INV15 | BLK8_INV16 | BLK8_INV17 | BLK8_INV18 | BLK8_INV19 | BLK8_INV20 | BLK8_INV21 | BLK8_INV22 | BLK8_INV23 | BLK8_INV24 | BLK8_INV25 | BLK8_INV26 | BLK8_INV27 | BLK8_INV28 | AT (°C) 14 Hours | MT (°C) Gen. Hours | WS_Avg (m/s) (24 Hours) | WS_Max (m/s) | Rain (mm) | GHI | POA | GHI_Lost | POA_Lost | 33kV_IC1_ExPort | 33kV_IC1_Import | 33kV_IC2_ExPort | 33kV_IC2_Import | 33kV_IC3_ExPort | 33kV_IC3_Import | 33kV_IC4_ExPort | 33kV_IC4_Import |  | I31kV_PQM_Im | 33kV_IC1_ExPort(KWh) | 33kV_IC1_Import(KWh) | 33kV_IC2_ExPort(KWh) | 33kV_IC2_Import(KWh) | 33kV_IC3_ExPort(KWh) | 33kV_IC3_Import(KWh) | 33kV_IC4_ExPort(kWh) | 33kV_IC4_Import(KWh) | 132kV_PQM_Ex(KWh) | 132kV_PQM_Im(KWh) | 33kV_Net_Ex (kWh) | 132kV_Net_Ex (kWh) | Operating Hours | GHI (KWh/m2)2 | POA(KWh/m2)2 | Amm_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | Inv_Exp(KWh) | WPR_Eac | WPR_Edc | WPR
2025-03-29 | 2025 | 2025 |  |  | Mar-25 | 31 | 66750 | 7:00 | 19:00 | [266 empty] | 54996.705 | 306246841.6003 | 81683.2331 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-03-30 | 2025 | 2025 |  |  | Mar-25 | 31 | 66750 | 7:00 | 19:00 | [266 empty] | 55011.744 | 306590465.4889 | 81745.1624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.039 | 343623.8886 | 61.9293 | -15.039 | 343561.9593 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-03-31 | 2025 | 2025 |  |  | Mar-25 | 31 | 66750 | 7:00 | 19:00 | 1590.1 | 1625.2 | 1522.4 | 1520.1 | 1598.4 | 1485.5 | 1544.3 | 1555.5 | 1580.5 | 1513.2 | 1550.6 | 1573 | 1569.8 | 1408.7 | 1504.6 | 1484.1 | 1452.9 | 1468 | 1589.1 | 1590.5 | 1596.5 | 1494.7 | 1541.1 | 1529.8 | 1509.6 | 1605.5 | 1593.4 | 1625.1 | 1594.9 | 1646.2 | 1616.2 | 1543.3 | 1387.5 | 1817.1 | 1398.5 | 1593.3 | 1512.2 | 1457.7 | 1508.8 | 1471.4 | 1478.6 | 1456.7 | 1512.4 | 1529.3 | 1535.4 | 1547.8 | 1567.5 | 1472.3 | 1542.2 | 1494.4 | 1431.4 | 1453.4 | 1610.5 | 1732.5 | 1563.5 | 1613.1 | 1633.3 | 1544.4 | 1634.4 | 1601.2 | 1478.6 | 1625 | 1455 | 1300.5 | 1644.7 | 1649.7 | 1648.2 | 1654.1 | 1502.1 | 1508.6 | 1506.5 | 1492.4 | 1471.1 | 1522.5 | 1602.1 | 1694.3 | 1724.1 | 1445.1 | 1482.4 | 1604.5 | 1541.1 | 1529.1 | 1512.1 | 1523.2 | 1542.2 | 1492.5 | 1529.5 | 1451.4 | 1470.1 | 1472.5 | 1548.5 | 1574.5 | 1540.3 | 1462.6 | 1631.5 | 1470.1 | 1492 | 1511.1 | 1515.1 | 1505.1 | 1538.2 | 1498.1 | 1522.1 | 1474.1 | 1679.1 | 1565.1 | 1740.2 | 1676.5 | 1471.4 | 1613.2 | 1559.1 | 1572.4 | 1620.1 | 1710.4 | 1510.4 | 1484.3 | 1660.1 | 1624.2 | 1628.1 | 1543.3 | 1506.1 | 1645.2 | 1616.2 | 1546.4 | 1456.7 | 1621.1 | 0 | 1403.4 | 1717.1 | 1629 | 1560.1 | 1589.2 | 1582.2 | 1356.6 | 1602 | 1575.4 | 1561.2 | 1548.5 | 1623.5 | 1304.5 | 1635.6 | 1562.3 | 1544.4 | 1524 | 1317 | 1563.3 | 1427.7 | 1449.8 | 1605.7 | 1550.5 | 1650.6 | 1502.2 | 1561.5 | 1507.5 | 1489.4 | 1448.5 | 1461.4 | 1440.4 | 1320 | 1285 | 1540 | 1371 | 1305 | 1408 | 1512 | 1406 | 1360 | 1421 | 1462 | 1375 | 1422 | 1430 | 1597 | 1512 | 1626 | 1413 | 1433 | 1280 | 1732 | 1526 | 1495 | 1584 | 1525 | 1568 | 1524 | 1576 | 1508 | 1524 | 1510 | 1437 | 1419 | 1450 | 1436 | 1429 | 1549 | 1397 | 1292 | 1565 |  |  | 1262 | 1064 | 1532 |  | 1659 | 1454 | 1514 | 1472 | 1495 | 1511 | 1521 | 1531 | 1533 | 1537 | 1550 | 1546 | 1521 | 1729 | 1306 | 1295 | 1033 | 908 | 1084 | 1279 | 1486 | 1676 | 1472 | 1533 | 1555 | 1551 | 1593 | 1618 | 1178 | 1422 | 1293 | 1409 | 1141 |  | 1843 | 1480 | 564 | 1371 | 1421 |  |  | 1266 | 1268 | 1417 | 1250 | 1154 | 30.32 | 40.28 | 1.71 | 6.3 |  | 0 | 7.31 |  |  | 80931088.744 | 281250.305 | 54078351.551 | 61052.203 | 81718077.5 | 185254.507 | 59077703.113 | 55026.783 | 306934089.3774 | 81807.0917 | 80931088.744 | 281250.305 | 54078351.551 | 61052.203 | 81718077.5 | 185254.507 | 59077703.113 | 15.039 | 343623.8886 | 61.9293 | 275277648.854 | 343561.9593 | 12 | 0 | 7.31 | 30.32 | 40.28 | 1.71 | 6.3 | 364093.2
2025-04-01 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1577 | 1616 | 1507 | 1509 | 1568 | 1462 | 1505 | 1498 | 1469 | 1476 | 1539 | 1533 | 1529 | 1371 | 1508 | 1488 | 1398 | 1410 | 1535 | 1600 | 1519 | 1458 | 1565 | 1487 | 1592 | 1580 | 1565 | 1592 | 1557 | 1609 | 1590 | 1504 | 1400 | 1797 | 1399 | 1602 | 1507 | 1442 | 1467 | 1420 | 1465 | 1435 | 1473 | 1487 | 1492 | 1503 | 1621 | 1432 | 1510 | 1470 | 1398 | 1420 | 1560 | 1698 | 1488 | 1598 | 1560 | 1490 | 1590 | 1590 | 1348 | 1610 | 1390 | 1290 | 1350 | 1611 | 1616 | 1423 | 1484 | 1489 | 1263 | 1353 | 1448 | 1511 | 1467 | 1657 | 1680 | 1402 | 1439 | 1565 | 1498 | 1485 | 1468 | 1478 | 1498 | 1457 | 1487 | 1411 | 1410 | 1434 | 1510 | 1510 | 1502 | 1390 | 1610 | 1425 | 1446 | 1469 | 1470 | 1363 | 1496 | 1451 | 1474 | 1427 | 1641 | 1321 | 1692 | 1630 | 1427 | 1631 | 1516 | 1594 | 1637 | 1672 | 1453 | 1495 | 1626 | 1546 | 1594 | 1476 | 1503 | 1591 | 1536 | 1414 | 1496 | 1590 | 0 | 1377 | 1680 | 1678 | 1531 | 1554 | 1533 | 1190 | 1591 | 1481 | 1564 | 1514 | 1580 | 1367 | 1406 | 1483 | 1488 | 1506 | 1285 | 1676 | 1474 | 1340 | 1556 | 1563 | 1603 | 1461 | 1611 | 1509 | 1427 | 1410 | 1410 | 1403 | 1291 | 1257 | 1498 | 1334 | 1271 | 1370 | 1490 | 1390 | 1337 | 1580 | 1430 | 1336 | 1386 | 1391 | 1556 | 1471 | 1591 | 1470 | 1453 | 1311 | 1720 | 1521 | 1502 | 1547 | 1481 | 1526 | 1548 | 1544 | 1544 | 1548 | 1469 | 1396 | 1372 | 1404 | 1390 | 1381 | 1505 | 1354 | 1255 | 1525 |  |  | 1299 | 1048 | 1492 |  | 1618 | 1390 | 1468 | 1417 | 1461 | 1462 | 1476 | 1488 | 1488 | 1496 | 1506 | 1501 | 1478 | 1691 | 1338 | 1257 | 1080 | 930 | 998 | 1181 | 1368 | 1550 | 1350 | 1406 | 1490 | 1520 | 1480 | 1491 | 1111 | 1313 | 1188 | 1298 | 1052 |  | 1760 | 1470 | 590 | 1380 | 1298 |  |  | 1385 | 1184 | 1410 | 1230 | 1150 | 25.08 | 40.95 | 1.76 | 5.3 |  | 0 | 7.18 |  |  | 81024220.217 | 281265.893 | 54170029.175 | 61064.408 | 81809917.614 | 185282.999 | 59149543.494 | 55041.822 | 307277713.266 | 81869.021 | 93131.473 | 15.588 | 91677.624 | 12.205 | 91840.114 | 28.492 | 71840.381 | 15.039 | 343623.8886 | 61.9293 | 348418.268 | 343561.9593 | 12 | 0 | 7.18 | 25.08 | 40.95 | 1.76 | 5.3 | 354559
2025-04-02 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1496 | 1535 | 1432 | 1434 | 1510 | 1388 | 1470 | 1398 | 1390 | 1404 | 1498 | 1454 | 1451 | 1304 | 1370 | 1415 | 1352 | 1360 | 1511 | 1547 | 1439 | 1384 | 1583 | 1480 | 1562 | 1558 | 1551 | 1580 | 1546 | 1599 | 1526 | 1490 | 1330 | 1703 | 1370 | 1522 | 1467 | 1380 | 1409 | 1449 | 1402 | 1381 | 1414 | 1427 | 1418 | 1439 | 1538 | 1358 | 1480 | 1410 | 1370 | 1378 | 1507 | 1561 | 1480 | 1490 | 1510 | 1404 | 1568 | 1520 | 1413 | 1563 | 1340 | 1300 | 1410 | 1573 | 1581 | 1410 | 1436 | 1444 | 1278 | 1319 | 1390 | 1464 | 1498 | 1571 | 1594 | 1333 | 1364 | 1499 | 1418 | 1406 | 1390 | 1402 | 1423 | 1389 | 1438 | 1361 | 1420 | 1394 | 1490 | 1490 | 1456 | 1300 | 1582 | 1351 | 1371 | 1399 | 1393 | 1340 | 1417 | 1374 | 1397 | 1355 | 1583 | 1290 | 1623 | 1547 | 1351 | 1581 | 1472 | 1511 | 1562 | 1586 | 1381 | 1416 | 1544 | 1519 | 1543 | 1432 | 1468 | 1549 | 1507 | 1387 | 1456 | 1577 | 0 | 1341 | 1646 | 1631 | 1498 | 1510 | 1488 | 1178 | 1507 | 1490 | 1482 | 1387 | 1495 | 1292 | 1398 | 1411 | 1413 | 1426 | 1278 | 1586 | 1396 | 1274 | 1492 | 1487 | 1529 | 1414 | 1531 | 1422 | 1391 | 1369 | 1387 | 1333 | 1290 | 1292 | 1445 | 1282 | 1360 | 1378 | 1478 | 1398 | 1335 | 1501 | 1398 | 1378 | 1390 | 1321 | 1477 | 1397 | 1508 | 1392 | 1373 | 1242 | 1630 | 1441 | 1419 | 1464 | 1505 | 1445 | 1467 | 1510 | 1460 | 1467 | 1393 | 1410 | 1296 | 1320 | 1313 | 1305 | 1425 | 1282 | 1188 | 1446 |  |  | 1265 | 990 | 1410 |  | 1534 | 1310 | 1390 | 1339 | 1387 | 1387 | 1401 | 1412 | 1411 | 1422 | 1470 | 1490 | 1460 | 1710 | 1272 | 1186 | `1031 | 910 | 992 | 1173 | 1363 | 1546 | 1344 | 1400 | 1510 | 1498 | 1472 | 1489 | 1123 | 1303 | 1177 | 1289 | 1043 |  | 1175 | 1450 | 690 | 1310 | 1290 |  |  | 1368 | 1012 | 1390 | 1190 | 1158 | 26.5 | 39.7 | 1.9 | 5.9 |  | 0 | 6.87 |  |  | 81114928.986 | 281280.784 | 54257592.783 | 61077.806 | 81897649.596 | 185319.828 | 59218660.672 | 55054.694 | 307612421.636 | 81927.037 | 90708.769 | 14.891 | 87563.608 | 13.398 | 87731.982 | 36.829 | 69117.178 | 12.872 | 334708.37 | 58.016 | 335043.547 | 334650.354 | 12 | 0 | 6.87 | 26.5 | 39.7 | 1.9 | 5.9 | 341179
2025-04-03 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1342 | 1375 | 1283 | 1281 | 1292 | 1245 | 1134 | 1189 | 1199 | 1258 | 1313 | 1304 | 1299 | 1163 | 1230 | 1265 | 1211 | 1229 | 1379 | 1401 | 1308 | 1283 | 1422 | 1304 | 1409 | 1404 | 1397 | 1423 | 1405 | 1447 | 1387 | 1391 | 1197 | 1534 | 1194 | 1444 | 1226 | 1243 | 1283 | 1315 | 1263 | 1248 | 1296 | 1302 | 1295 | 1321 | 1398 | 1221 | 1203 | 1218 | 1166 | 1155 | 1331 | 1406 | 1187 | 1362 | 1231 | 1264 | 1411 | 1355 | 1272 | 1406 | 1300 | 1280 | 1156 | 1405 | 1439 | 1253 | 1289 | 1294 | 1078 | 1191 | 1257 | 1315 | 1285 | 1450 | 1467 | 1202 | 1249 | 1382 | 1301 | 1305 | 1298 | 1309 | 1303 | 1268 | 1315 | 1247 | 1154 | 1274 | 1324 | 690 | 1331 | 1125 | 1393 | 1248 | 1258 | 1284 | 1251 | 1184 | 1318 | 1285 | 1306 | 1273 | 1448 | 1152 | 1497 | 1365 | 1244 | 1448 | 1363 | 1358 | 1409 | 1422 | 1262 | 1272 | 1388 | 1373 | 1420 | 1286 | 1321 | 1395 | 1356 | 1254 | 1327 | 1431 | 521 | 775 | 1490 | 1460 | 1322 | 1326 | 1306 | 975 | 1346 | 1178 | 1325 | 1240 | 1338 | 1175 | 1196 | 1296 | 1265 | 1274 | 1108 | 1449 | 1293 | 1181 | 1372 | 1384 | 1412 | 1291 | 1375 | 1291 | 1265 | 1251 | 1261 | 1202 | 1151 | 1157 | 1293 | 1145 | 1076 | 1165 | 1144 | 966 | 1197 | 1343 | 1215 | 1137 | 1184 | 1185 | 1323 | 1248 | 1345 | 1242 | 1228 | 1109 | 1456 | 1286 | 1267 | 1313 | 1249 | 1290 | 1310 | 1308 | 1303 | 1308 | 1246 | 1184 | 1164 | 1194 | 1178 | 1173 | 1284 | 1153 | 1070 | 1302 |  |  | 1146 | 895 | 1273 |  | 1389 | 1124 | 1250 | 1203 | 1252 | 1249 | 1259 | 1269 | 1269 | 1278 | 1279 | 1277 | 1271 | 1444 | 1143 | 1062 | 919 | 762 | 894 | 1057 | 1225 | 1391 | 1207 | 1256 | 1400 | 1385 | 1338 | 1346 | 1041 | 1174 | 1058 | 1162 | 939 |  | 1265 | 1180 | 700 | 1087 | 1186 |  |  | 1012 | 815 | 1049 | 1180 | 1110 | 25.78 | 32 | 2.63 | 5.3 |  | 0 |  |  |  | 81196825.693 | 281293.339 | 54337502.169 | 61098.808 | 81976932.974 | 185359.42 | 59281082.425 | 55074.059 | 307915539.166 | 81986.655 | 81896.707 | 12.555 | 79909.386 | 21.002 | 79283.378 | 39.592 | 62421.753 | 19.365 | 303117.53 | 59.618 | 161772.536 | 303057.912 | 12 | 0 | 0 | 25.78 | 32 | 2.63 | 5.3 | 305040
2025-04-04 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1401 | 1428 | 1331 | 1332 | 1354 | 1301 | 1170 | 1235 | 1243 | 1311 | 1368 | 1770 | 1355 | 1216 | 1282 | 1320 | 1250 | 1273 | 1420 | 1445 | 1349 | 1296 | 1476 | 1345 | 1450 | 1445 | 1435 | 1472 | 1440 | 1489 | 1460 | 1389 | 1241 | 1624 | 1226 | 1393 | 1267 | 1272 | 1302 | 1378 | 1289 | 1273 | 1311 | 1318 | 1424 | 1349 | 1441 | 1256 | 1264 | 1286 | 1232 | 1195 | 1373 | 1478 | 1241 | 1438 | 1263 | 1306 | 1442 | 1384 | 1290 | 1449 | 1350 | 1380 | 1192 | 1446 | 1474 | 1311 | 1322 | 1329 | 1123 | 1222 | 1314 | 1351 | 1357 | 1517 | 1532 | 1277 | 1314 |  | 1348 | 1353 | 1336 | 1345 | 1327 | 1321 | 1348 | 1276 | 1214 | 1303 | 1376 | 1303 | 1367 | 1152 | 1410 | 1304 | 1314 | 1359 | 1290 | 1264 | 1379 | 1331 | 1348 | 1303 | 1504 | 1209 | 1528 | 1443 | 1307 | 1488 | 1413 | 1465 | 1518 | 1533 | 1337 | 1379 | 1505 | 1405 | 1472 | 1329 | 1363 | 1439 | 1405 | 1291 | 1366 | 1478 | 1237 | 1243 | 1525 | 1503 | 1363 | 1400 | 1374 | 1017 | 1402 | 1212 | 1365 | 1236 | 1406 | 1207 | 1253 | 1337 | 1318 | 1335 | 1140 | 1489 | 1301 | 1217 | 1408 | 1424 | 1449 | 1322 | 1432 | 1363 | 1294 | 1280 | 1278 | 1287 | 1183 | 1196 | 1340 | 1202 | 1134 | 1218 | 1205 | 1017 | 1227 | 1419 | 1273 | 1190 | 1237 | 1242 | 1393 | 1319 | 1405 | 1273 | 1255 | 1132 | 1493 | 1317 | 1299 | 1373 | 1298 | 1352 | 1340 | 1359 | 1337 | 1346 | 1311 | 1239 | 1231 | 1271 | 1226 | 1226 | 1327 | 1199 | 1117 | 1353 |  |  | 1032 | 923 | 1323 |  | 1458 | 1164 | 1316 | 1270 | 1310 | 1312 | 1326 | 1335 | 1336 | 1342 | 1350 | 1370 | 1359 | 1543 | 1231 | 1148 | 1020 | 798 | 979 | 1148 | 1337 | 1483 | 1310 | 1374 | 1510 | 1470 | 1447 | 1446 | 1095 | 1240 | 1114 | 1230 | 1000 |  | 1175 | 1250 | 677 | 990 | 1243 |  |  | 1143 | 910 | 1120 | 1272 | 1090 | 35.1 | 50.1 | 1.5 | 4.3 |  | 0 | 6.1 |  |  | 81281718.732 | 281316.668 | 54421147.914 | 61118.521 | 82060118.024 | 185405.861 | 59347306.787 | 55089.676 | 308233092.831 | 82048.512 | 84893.039 | 23.329 | 83645.745 | 19.713 | 83185.05 | 46.441 | 66224.362 | 15.617 | 317553.665 | 61.857 | 168495.742 | 317491.808 | 12 | 0 | 6.1 | 35.1 | 50.1 | 1.5 | 4.3 | 318035
2025-04-05 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1504.6 | 1533.2 | 1434.3 | 1430 | 1445 | 1391.2 | 1356.7 | 1317.3 | 1381.6 | 1387.3 | 1455.5 | 1454.2 | 1440.4 | 1292.1 | 1355.1 | 1394 | 1331.7 | 1348.9 | 1501.1 | 1530.4 | 1546.5 | 1371.2 | 1560.1 | 1454.4 | 1534.3 | 1532.5 | 1531.3 | 1556.2 | 1527.9 | 1570.5 | 1505.5 | 1470.6 | 1313.6 | 1720.1 | 1297.8 | 1377.2 | 1345.7 | 1374.3 | 1377.6 | 1415.6 | 1362.5 | 1347.5 | 1385 | 1394.4 | 1407.1 | 1428.5 | 1531 | 1333.2 | 1335.4 | 1362.9 | 1293.4 | 1251.3 | 1435.5 | 1343.4 | 1343.5 | 1484.5 | 1393 | 1358.5 | 1493.6 | 1333.7 | 1336.2 | 1499.5 | 1330 | 1395 | 1228.2 | 1532.6 | 1556.8 | 1350.6 | 1398.8 | 1407.9 | 1155.1 | 1292.6 | 1352.3 | 1432.4 | 1406.4 | 1606.7 | 1626.1 | 1350.6 | 1390.2 | 1511.4 | 1330 | 1433.2 | 1416.4 | 1424.6 | 1408.1 | 1373.2 | 1428.1 | 1353.6 | 1261.8 | 1373.2 | 1445.8 | 1376.7 | 1448.3 | 1178.7 | 1335.9 | 1379.4 | 1391.1 | 1416.3 | 1364.5 | 1307.3 | 1407.6 | 1412.5 | 1353.5 | 1383.5 | 1585.5 | 1249.3 | 1625.4 | 1526.1 | 1387.9 | 1584.4 | 1465.9 | 1561.4 | 1594.4 | 1626 | 1388.8 | 1473.8 | 1592.9 | 1492.1 | 1537.2 | 1431.1 | 1447.2 | 1531.9 | 1473.6 | 1370.8 | 1451.2 | 1552.8 | 1306.1 | 1312.9 | 1614.4 | 1593.2 | 1447.4 | 1484.4 | 1451.1 | 1099.1 | 1502.4 | 1283.3 | 1499.9 | 1288.7 | 1498.1 | 1287.1 | 1328.6 | 1418.7 | 1403.1 | 1421.5 | 1217 | 1590.5 | 1425.6 | 1295.5 | 1495.1 | 1511.4 | 1542.1 | 1403.5 | 1418.5 | 1401 | 1470.4 | 1351.9 | 1352.2 | 1358.2 | 1260.1 | 1267.4 | 1420.8 | 1278.4 | 1204.2 | 1290.1 | 1275.9 | 1071.1 | 1297 | 1495.6 | 1347.2 | 1256.5 | 1304.3 | 1310.9 | 1471.5 | 1394.5 | 1532.6 | 1363.3 | 1339.4 | 1214.8 | 1587.4 | 1414.3 | 1383.9 | 1456.3 | 1382.3 | 1489.4 | 1433.9 | 1459 | 1438.5 | 1348.5 | 1388.4 | 1313.8 | 1306.3 | 1356.6 | 1317.1 | 1306.6 | 1420.1 | 1307.2 | 1211.5 | 1468.8 |  |  | 1255 | 961.6 | 1405.3 |  | 1536.5 | 1228.2 | 1427.6 | 1380.2 | 1379.5 | 1421.6 | 1440.7 | 1446.3 | 1448.2 | 1447.2 | 1467.8 | 1470.2 | 1421.8 | 1651.1 | 1307.4 | 1216.5 | 1054.2 | 886.9 | 976.1 | 1125.9 | 1296.6 | 1452.6 | 1280.3 | 1343.2 | 1345.4 | 1350.3 | 1382 | 1407 | 1368.9 | 1237.2 | 1020.7 | 1222.8 | 1112 |  | 1357.6 | 1431.1 | 664.3 | 1326.3 | 1213.4 |  |  | 1352.3 | 1156.6 | 1200 | 1239.6 | 1315.3 | 37.8 | 58.63 | 1.48 | 7.5 |  | 0 | 5.9 |  |  | 81371402.865 | 281330.577 | 54509149.521 | 61128.592 | 82148517.468 | 185452.895 | 59414773.455 | 55101.734 | 308566273.151 | 82104.15 | 89684.133 | 13.909 | 88001.607 | 10.071 | 88399.444 | 47.034 | 67466.668 | 12.058 | 333180.32 | 55.638 | 177661.76 | 333124.682 | 12 | 0 | 5.9 | 37.8 | 58.63 | 1.48 | 7.5 | 336772.2
2025-04-06 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1483.7 | 1507.4 | 1390.6 | 1398.6 | 1408.1 | 1355.9 | 1384.8 | 1284.1 | 1385.7 | 1350.6 | 1418.7 | 1416.1 | 1404.9 | 1259.1 | 1321.8 | 1359.1 | 1288 | 1315.5 | 1451.8 | 1491 | 1390.3 | 1335.5 | 1520.9 | 1442 | 1495.9 | 1491.9 | 1482.8 | 1512.8 | 1484.6 | 1525.3 | 1420.3 | 1423.9 | 1281.8 | 1680.4 | 1266 | 1439.6 | 1311.6 | 1314.3 | 1342.3 | 1379.1 | 1330.4 | 1315.1 | 1351.1 | 1360.9 | 1367.2 | 1392.8 | 1401.6 | 1297.1 | 1335.7 | 1369.1 | 1287.3 | 1247.5 | 1430.7 | 1539 | 1396 | 1484 | 1406.3 | 1355.5 | 1490.3 | 1428 | 1401 | 1494.7 | 1330 | 1240 | 1290 | 1492.7 | 1521 | 1380.5 | 1361.5 | 1371.4 | 1186 | 1254.6 | 1292 | 1384.8 | 1390.5 | 1568.8 | 1584.7 | 1318.2 | 1354.2 | 1466.8 | 1392.7 | 1396.5 | 1379.4 | 1386.8 | 1371.7 | 1320 | 1391.2 | 1320.6 | 1190 | 1336.6 | 1400 | 1327.1 | 1411.7 | 1132 | 1311.5 | 1343.4 | 1354.1 | 1356.8 | 1329.4 | 1291.2 | 1422.7 | 1375.3 | 1392.6 | 1344.3 | 1547.1 | 1184.1 | 1579.4 | 1489.2 | 1350.9 | 1536 | 1419.3 | 1522.7 | 1545.1 | 1587.3 | 1335.4 | 1343.4 | 1555.8 | 1448.9 | 1404.1 | 1378.2 | 1408.2 | 1480.4 | 1421 | 1334 | 1402 | 1474 | 1280.9 | 1285.1 | 1631.8 | 1558.2 | 1414.7 | 1491.6 | 1419.5 | 1075 | 1459.2 | 1255.6 | 1412.5 | 1258.4 | 1461.4 | 1256.3 | 1298.5 | 1388.3 | 1368.9 | 1388.3 | 1187 | 1553.6 | 1393.8 | 1263.7 | 1460.7 | 1476.7 | 1505.2 | 1371.8 | 1481.4 | 1357.2 | 1339.9 | 1323.9 | 1325.2 | 1330.4 | 1231 | 1240.3 | 1425 | 1281 | 1226.7 | 1352 | 1257.6 | 1044.9 | 1265.9 | 1460.2 | 1317 | 1229.5 | 1274.1 | 1297.8 | 1433.1 | 1365.5 | 1544.3 | 1365.1 | 1357.1 | 1225.7 | 1500 | 1416.6 | 1394.3 | 1448.1 | 1403 | 1471.9 | 1439.5 | 1455 | 1444.6 | 1444.5 | 1393.3 | 1327.1 | 1359.2 | 1359.1 | 1314.7 | 1345.6 | 1408.7 | 1267.8 | 1163.3 | 1428 |  |  | 1244.9 | 955.3 | 1397 |  | 1559.7 | 1228 | 1408.2 | 1357.1 | 1340.5 | 1405.4 | 1413.7 | 1419.4 | 1422.7 | 1443.7 | 1435 | 1430.4 | 1382.3 | 1613.2 | 1272.7 | 1185.7 | 1040 | 855 | 988.1 | 1154 | 1354.8 | 1534.6 | 1334.7 | 1407 | 1405 | 1402 | 1416.5 | 1470.3 | 1098.5 | 1277.1 | 1167.1 | 1276.3 | 1026.3 |  | 1176.1 | 1407.9 | 758.9 | 1223.4 | 1213.7 |  |  | 1391.4 | 1280.4 | 1195 | 1190.5 | 1310 | 39.3 | 47.4 | 1.2 | 5.33 |  | 0 | 6.92 |  |  | 81459682.41 | 281344.869 | 54594618.216 | 61137.77 | 82235619.976 | 185501.963 | 59483445.32 | 55113.894 | 308895385.727 | 82159.511 | 88279.545 | 14.292 | 85468.695 | 9.178 | 87102.508 | 49.068 | 68671.865 | 12.16 | 329112.576 | 55.361 | 173724.77 | 329057.215 | 12 | 0 | 6.92 | 39.3 | 47.4 | 1.2 | 5.33 | 331522.2
2025-04-07 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1422 | 1445 | 1333 | 1339 | 1390 | 1300 | 1328 | 1280 | 1328 | 1340 | 1358 | 1356 | 1344 | 1204 | 1262 | 1299 | 1290 | 1256 | 1400 | 1422 | 1328 | 1276 | 1452 | 1420 | 1427 | 1421 | 1414 | 1440 | 1411 | 1444 | 1478 | 1390 | 1226 | 1612 | 1280 | 1410 | 1296 | 1259 | 1286 | 1322 | 1276 | 1262 | 1294 | 1303 | 1310 | 1334 | 1429 | 1297 | 1310 | 1314 | 1260 | 1230 | 1398 | 1476 | 1388 | 1426 | 1424 | 1301 | 1427 | 1394 | 1301 | 1435 | 1340 | 1310 | 1440 | 1430 | 1456 | 1299 | 1302 | 1315 | 1328 | 1210 | 1250 | 1332 | 1350 | 1502 | 1519 | 1320 | 1300 | 1406 | 1334 | 1338 | 1322 | 1330 | 1315 | 1297 | 1333 | 1317 | 1296 | 1281 | 1342 | 1376 | 1353 | 1191 | 1410 | 1289 | 1300 | 1299 | 1276 | 1260 | 1364 | 1319 | 1336 | 1293 | 1487 | 1200 | 1514 | 1425 | 1295 | 1473 | 1390 | 1460 | 1472 | 1519 | 1269 | 1374 | 1488 | 1420 | 1406 | 1331 | 1353 | 1420 | 1390 | 1282 | 1354 | 1478 | 1260 | 1280 | 1513 | 1491 | 1396 | 1392 | 1398 | 1100 | 1404 | 1299 | 1391 | 1260 | 1394 | 1280 | 1290 | 1388 | 1307 | 1399 | 1189 | 1484 | 1331 | 1211 | 1400 | 1415 | 1439 | 1316 | 1421 | 1312 | 1286 | 1271 | 1310 | 1274 | 1287 | 1303 | 1433 | 1269 | 1280 | 1372 | 1311 | 1099 | 1242 | 1430 | 1307 | 1299 | 1298 | 1296 | 1427 | 1341 | 1528 | 1337 | 1314 | 1230 | 1543 | 1364 | 1355 | 1403 | 1395 | 1430 | 1409 | 1475 | 1393 | 1402 | 1369 | 1306 | 1304 | 1304 | 1258 | 1291 | 1353 | 1211 | 1116 | 1354 |  |  | 1220 | 939 | 1360 |  | 1488 | 1230 | 1350 | 1301 | 1275 | 1339 | 1357 | 1357 | 1365 | 1378 | 1384 | 1372 | 1320 | 1552 | 1224 | 1135 | 1020 | 910 | 972 | 1145 | 1336 | 1510 | 1314 | 1386 | 1410 | 1378 | 1387 | 1459 | 1200 | 1256 | 1155 | 1268 | 1150 |  | 1700 | 1410 | 600 | 1210 | 1245 |  |  | 1178 | 1300 | 1300 | 1130 | 1098 | 41.9 | 51.1 | 1.1 | 3.13 |  | 0 | 6.5257 |  |  | 81544202.804 | 281359.701 | 54676516.993 | 61149.622 | 82320465.624 | 185544.891 | 59549914.342 | 55125.834 | 309212772.728 | 82213.909 | 84520.394 | 14.832 | 81898.777 | 11.852 | 84845.648 | 42.928 | 66469.022 | 11.94 | 317387.001 | 54.398 | 166392.487 | 317332.603 | 12 | 0 | 6.5257 | 41.9 | 51.1 | 1.1 | 3.13 | 324271
2025-04-08 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1318.6 | 1341.3 | 1243.2 | 1247 | 1320.2 | 1214.4 | 1280.2 | 1243.7 | 1300.1 | 1272.5 | 1269.5 | 1258.1 | 1280 | 1177.2 | 1212.7 | 1230 | 1240 | 1245 | 1380 | 1324 | 1335.1 | 1240.1 | 1340.2 | 1430 | 1324.4 | 1313.7 | 1380 | 1388 | 1382.3 | 1395.6 | 1390.6 | 1325.8 | 1190 | 1600.1 | 1248.6 | 1391.3 | 1275.2 | 1230.4 | 1280.2 | 1237.1 | 1290 | 1250 | 1240 | 1219.6 | 1228.8 | 1245.6 | 1341.3 | 1287.8 | 1301.9 | 1300.9 | 1278.2 | 1272.1 | 1390.9 | 1396.9 | 1345.9 | 1420.1 | 1420.7 | 1290.3 | 1448.3 | 1377.7 | 1249.4 | 1420 | 1308 | 1215.9 | 1333.8 | 1331.1 | 1352.3 | 1270.2 | 1280.4 | 1312.7 | 1239.3 | 1219.4 | 1243.7 | 1246.1 | 1333.5 | 1408.1 | 1423.7 | 1235.4 | 1292.2 | 1401.8 | 1250.3 | 1254.3 | 1238.3 | 1245.2 | 1239.6 | 1277.3 | 1243.8 | 1280.5 | 1290.2 | 1280.5 | 1336.9 | 1350.1 | 1265.5 | 1232.5 | 1360.4 | 1280.9 | 1290.7 | 1288.9 | 1240.4 | 1255.4 | 1253.8 | 1232 | 1248.8 | 1280.1 | 1395.2 | 1230.9 | 1413.9 | 1420.8 | 1289.4 | 1430.5 | 1370.5 | 1369 | 1396.3 | 1427.1 | 1250.6 | 1301.5 | 1405.5 | 1401.3 | 1399.4 | 1254.3 | 1268.5 | 1390.1 | 1368.2 | 1290.5 | 1268.5 | 1463.7 | 1247.1 | 1252.4 | 1419 | 1399.3 | 1372.1 | 1390.7 | 1376 | 1090 | 1398.1 | 1290.3 | 1366 | 1300.5 | 1310.7 | 1227.4 | 1265.5 | 1352 | 1324.9 | 1388.5 | 1190 | 1395.2 | 1299.5 | 1190.8 | 1390.3 | 1428.4 | 1399 | 1331 | 1426.6 | 1264 | 1299.3 | 1289.5 | 1295.9 | 1292.9 | 1276 | 1244.6 | 1477.1 | 1266.3 | 1328.3 | 1397 | 1423.5 | 1230.5 | 1277.5 | 1380.6 | 1249.5 | 1300.4 | 1299.9 | 1290.3 | 1410.4 | 1364.3 | 1454 | 1278.8 | 1281.5 | 1250.5 | 1475.3 | 1305.3 | 1366.5 | 1400.8 | 1388.2 | 1420 | 1388 | 1405.5 | 1339.6 | 1329.6 | 1310.6 | 1343.2 | 1288.1 | 1322.6 | 1250 | 1280 | 1270.9 | 1235.8 | 1052.1 | 1272.5 |  |  | 1204.6 | 930.1 | 1270.3 |  | 1452.5 | 1212.5 | 1261.4 | 1287.9 | 1272.6 | 1280.9 | 1287.5 | 1295.7 | 1297 | 1317.5 | 1290.5 | 1282.4 | 1324.1 | 1454.9 | 1144.9 | 1120.5 | 916.4 | 760.2 | 970.5 | 1177.5 | 1352.4 | 1415.5 | 1300 | 1296 | 1295.8 | 1280.2 | 1380.8 | 1471.4 | 1190.3 | 1250.5 | 1187 | 1250.8 | 1092.1 |  | 1708.5 | 1400.2 | 550.8 | 1210.9 | 1212.7 |  |  | 1162.8 | 1288.5 | 1315.2 | 1140.2 | 1115.2 | 43.9 | 51.1 | 1.1 | 3.13 |  | 0 | 6.0578 |  |  | 81623456.674 | 281374.677 | 54753444.461 | 61162.416 | 82400731.86 | 185586.944 | 59612531.256 | 55139.475 | 309511535.47 | 82271.483 | 79253.87 | 14.976 | 76927.468 | 12.794 | 80266.236 | 42.053 | 62616.914 | 13.641 | 298762.742 | 57.574 | 156153.568 | 298705.168 | 12 | 0 | 6.0578 | 43.9 | 51.1 | 1.1 | 3.13 | 315636
2025-04-09 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1233 | 1254 | 1180 | 1165 | 1222 | 1133 | 1158 | 1172 | 1199 | 1188 | 1189 | 1184 | 1173 | 1040 | 1098 | 1130 | 1120 | 1130 | 1219 | 1232 | 1150 | 1130 | 1248 | 1250 | 1231 | 1222 | 1290 | 1250 | 1255 | 1250 | 1300 | 1242 | 1073 | 351 | 1114 | 1208 | 1150 | 1102 | 1124 | 1155 | 1160 | 1160 | 1132 | 1141 | 1146 | 1164 | 1252 | 1136 | 1188 | 1178 | 1150 | 1171 | 1336 | 1329 | 1250 | 1278 | 1280 | 1171 | 1281 | 1270 | 1149 | 1291 | 1220 | 1080 | 1246 | 1244 | 1264 | 1190 | 1148 | 1143 | 1158 | 1132 | 1140 | 1166 | 1277 | 1316 | 1330 | 1154 | 1138 | 1250 | 1168 | 1172 | 1156 | 1164 | 1148 | 1155 | 1162 | 1143 | 1129 | 1140 | 1180 | 1310 | 1182 | 1160 | 1398 | 1125 | 1135 | 1162 | 1160 | 1150 | 1195 | 1153 | 1170 | 1131 | 1304 | 1140 | 1325 | 1302 | 1180 | 1290 | 1222 | 1281 | 1325 | 1334 | 1140 | 1205 | 1310 | 1319 | 1262 | 1178 | 1187 | 1298 | 1240 | 1123 | 1186 | 1498 | 1167 | 1140 | 1321 | 1303 | 1240 | 1218 | 1230 | 1000 | 1225 | 1245 | 1199 | 1200 | 1215 | 1150 | 1199 | 1240 | 1138 | 1230 | 1100 | 1298 | 1134 | 1057 | 1260 | 1239 | 1253 | 1147 | 1290 | 1141 | 1120 | 1108 | 1198 | 1140 | 1098 | 1162 | 1293 | 1146 | 1230 | 1280 | 1270 | 1160 | 1129 | 1297 | 1179 | 1200 | 1162 | 1166 | 1280 | 1207 | 1359 | 1195 | 1200 | 1176 | 1386 | 1218 | 1226 | 1259 | 1290 | 1300 | 1256 | 1327 | 1252 | 1243 | 1232 | 1240 | 1153 | 1156 | 1130 | 1139 | 1220 | 1150 | 1009 | 1233 |  |  | 1198 | 898 | 1280 |  | 1250 | 1278 | 1182 | 1172 | 1149 | 1209 | 1214 | 1233 | 1230 | 1244 | 1213 | 1201 | 1230 | 1365 | 1072 | 1110 | 860 | 810 | 910 | 1011 | 1213 | 1372 | 1198 | 1244 | 1298 | 1278 | 1287 | 1300 | 1099 | 1219 | 1099 | 1124 | 1010 |  | 1498 | 1398 | 450 | 1198 | 1123 |  |  | 1098 | 1298 | 1199 | 1110 | 1110 | 39.9 | 50.1 | 1.1 | 3.4 |  | 0 | 5.6268 |  |  | 81698640.225 | 281383.068 | 54825971.097 | 61171.181 | 82476110.299 | 185620.066 | 59671741.712 | 55149.599 | 309793554.329 | 82309.564 | 75183.551 | 8.391 | 72526.636 | 8.765 | 75378.439 | 33.122 | 59210.456 | 10.124 | 282018.859 | 38.081 | 147693.031 | 281980.778 | 12 | 0 | 5.6268 | 39.9 | 50.1 | 1.1 | 3.4 | 289705
2025-04-10 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 971 | 984 | 912 | 911 | 965 | 892 | 901 | 932 | 990 | 940 | 926 | 922 | 910 | 818 | 854 | 882 | 940 | 940 | 952 | 963 | 896 | 920 | 981 | 960 | 963 | 954 | 999 | 950 | 935 | 954 | 990 | 1000 | 835 | 1105 | 888 | 940 | 898 | 857 | 874 | 890 | 899 | 899 | 888 | 883 | 893 | 908 | 978 | 884 | 898 | 976 | 925 | 864 | 990 | 980 | 950 | 997 | 988 | 860 | 999 | 990 | 943 | 1010 | 910 | 898 | 968 | 964 | 980 | 950 | 884 | 885 | 898 | 881 | 862 | 902 | 1010 | 1020 | 1030 | 893 | 899 | 968 | 904 | 906 |  | 900 | 889 | 899 | 907 | 895 | 883 | 898 | 917 | 992 | 918 | 892 | 978 | 868 | 876 | 897 | 896 | 949 | 926 | 895 | 908 | 950 | 1008 | 909 | 1021 | 1005 | 914 | 1000 | 947 | 989 | 1032 | 1031 | 883 | 933 | 1012 | 961 | 972 | 938 | 960 | 978 | 943 | 894 | 919 | 1010 | 826 | 833 | 1022 | 1010 | 920 | 949 | 927 | 805 | 958 | 913 | 916 | 809 | 949 | 929 | 946 | 915 | 850 | 960 | 931 | 928 | 840 | 784 | 904 | 921 | 928 | 847 | 1010 | 845 | 831 | 822 | 910 | 922 | 862 | 916 | 1009 | 893 | 933 | 968 | 1002 | 945 | 883 | 1007 | 932 | 961 | 919 | 913 | 1015 | 954 | 1053 | 924 | 928 | 931 | 1068 | 942 | 945 | 970 | 952 | 1009 | 971 | 1031 | 969 | 965 | 957 | 920 | 899 | 994 | 851 | 886 | 946 | 853 | 796 | 964 |  |  | 840 | 646 | 940 |  | 1012 | 929 | 912 | 897 | 890 | 932 | 945 | 947 | 948 | 958 | 970 | 950 | 954 | 1101 | 834 | 767 | 620 | 610 | 653 | 760 | 895 | 1014 | 943 | 929 | 978 | 998 | 967 | 949 | 913 | 932 | 846 | 934 | 773 |  | 1175 | 950 | 426 | 862 | 815 |  |  | 898 | 978 | 1010 | 898 | 810 | 34.9 | 49 | 3 | 5 |  | 0 | 4.36 |  |  | 81756527.707 | 281390.022 | 54882722.441 | 61177.887 | 82534835.19 | 185649.094 | 59717471.191 | 55158.877 | 310012420.729 | 82339.924 | 57887.482 | 6.954 | 56751.344 | 6.706 | 58724.891 | 29.028 | 45729.479 | 9.278 | 218866.4 | 30.36 | 114625.166 | 218836.04 | 12 | 0 | 4.36 | 34.9 | 49 | 3 | 5 | 223694
2025-04-11 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1107 | 1131 | 1048 | 1046 | 1110 | 1025 | 1029 | 1010 | 1041 | 1024 | 1059 | 1057 | 1043 | 938 | 1012 | 1049 | 963 | 996 | 1092 | 1126 | 1059 | 1022 | 1171 | 1093 | 1113 | 1110 | 1097 | 1120 | 1091 | 1121 | 1200 | 1098 | 961 | 1283 | 908 | 1079 | 986 | 987 | 1033 | 1057 | 989 | 989 | 1029 | 1044 | 1025 | 1049 | 1122 | 1040 | 1035 | 1060 | 1004 | 1050 | 1201 | 1188 | 1087 | 1154 | 1143 | 1040 | 1149 | 1106 | 1034 | 1163 | 1210 | 1098 | 1128 | 1120 | 1150 | 1099 | 1027 | 1031 | 1069 | 1059 | 1046 | 1049 | 1170 | 1170 | 1184 | 1017 | 1007 | 1122 | 1040 | 1040 | 1038 | 1039 | 1026 | 1036 | 1084 | 1074 | 1044 | 1041 | 1067 | 1078 | 1082 | 1024 | 1200 | 1002 | 1032 | 1063 | 1038 | 1041 | 1079 | 1035 | 1066 | 1036 | 1198 | 1044 | 1186 | 1175 | 1068 | 1187 | 1146 | 1140 | 1201 | 1189 | 1048 | 1074 | 1172 | 1114 | 1175 | 1064 | 1094 | 1133 | 1114 | 1030 | 1081 | 1478 | 950 | 968 | 1165 | 1154 | 1059 | 1083 | 1051 | 898 | 1104 | 1098 | 1051 | 978 | 1059 | 1004 | 988 | 1046 | 1024 | 1094 | 999 | 1168 | 1006 | 942 | 1093 | 1113 | 1126 | 1026 | 1119 | 1024 | 1001 | 988 | 1050 | 1178 | 966 | 1025 | 1130 | 1001 | 1039 | 1088 | 1125 | 1055 | 983 | 1137 | 1040 | 999 | 1025 | 1019 | 1140 | 1068 | 1201 | 1044 | 1043 | 931 | 1199 | 1059 | 1068 | 1096 | 1076 | 1159 | 1100 | 1172 | 1089 | 1104 | 1069 | 1034 | 1021 | 1016 | 977 | 1005 | 1064 | 962 | 900 | 1086 |  |  | 944 | 738 | 1059 |  | 1165 | 1132 | 1051 | 1020 | 1045 | 1058 | 1065 | 1072 | 1069 | 1083 | 1086 | 1080 | 1149 | 1235 | 975 | 894 | 790 | 640 | 781 | 913 | 999 | 1200 | 1018 | 1100 | 1098 | 1097 | 1186 | 1141 | 975 | 994 | 900 | 997 | 960 |  | 1250 | 1068 | 398 | 985 | 918 |  |  | 1000 | 1000 | 1088 | 945 | 913 | 36.6 | 55.86 | 2.52 | 13.1 |  | 0 | 4.88 |  |  | 81824612.484 | 281411.612 | 54949789.39 | 61214.424 | 82601901.2 | 185683.778 | 59770602.626 | 55201.359 | 310267495.625 | 82401.977 | 68084.777 | 21.59 | 67066.949 | 36.537 | 67066.01 | 34.684 | 53131.435 | 42.482 | 255074.896 | 62.053 | 135093.599 | 255012.843 | 12 | 0 | 4.88 | 36.6 | 55.86 | 2.52 | 13.1 | 257651
2025-04-12 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1392 | 1415 | 1315 | 1313 | 1396 | 1287 | 1302 | 1199 | 1310 | 1288 | 1332 | 1330 | 1311 | 1180 | 1282 | 1324 | 1249 | 1276 | 1409 | 1442 | 1345 | 1293 | 1481 | 1303 | 1448 | 1440 | 1433 | 1457 | 1386 | 1425 | 1350 | 1378 | 1215 | 1600 | 1148 | 1364 | 1263 | 1294 | 1315 | 1346 | 1296 | 1283 | 1310 | 1327 | 1323 | 1325 | 1442 | 1332 | 1230 | 1260 | 1210 | 1198 | 1388 | 1330 | 1202 | 1275 | 1255 | 1133 | 1286 | 1232 | 1178 | 1283 | 1226 | 1110 | 1455 | 1446 | 1484 | 1318 | 1327 | 1334 | 1358 | 1333 | 1268 | 1357 | 1396 | 1480 | 1496 | 1286 | 1271 | 1422 | 1315 | 1316 | 1314 | 1316 | 1325 | 1284 | 1365 | 1352 | 1326 | 1320 | 1378 | 1240 | 1377 | 1313 | 1330 | 1310 | 1319 | 1357 | 1349 | 1265 | 1394 | 1348 | 1370 | 1321 | 1518 | 1220 | 1501 | 1505 | 1370 | 1506 | 1425 | 1441 | 1505 | 1517 | 1327 | 1360 | 1494 | 1404 | 1455 | 1341 | 1375 | 1432 | 1394 | 1297 | 1365 | 1498 | 1229 | 1261 | 1478 | 1470 | 1398 | 1378 | 1335 | 1131 | 1432 | 1299 | 1365 | 1270 | 1341 | 1331 | 1271 | 1318 | 1310 | 1440 | 1254 | 1486 | 1282 | 1202 | 1390 | 1411 | 1432 | 1306 | 1424 | 1344 | 1272 | 1254 | 1190 | 1245 | 1213 | 1288 | 1419 | 1257 | 1285 | 1373 | 1340 | 1267 | 1242 | 1429 | 1307 | 1203 | 1285 | 1277 | 1426 | 1341 | 1520 | 1330 | 1339 | 1206 | 1531 | 1361 | 1374 | 1404 | 1367 | 1452 | 1399 | 1481 | 1401 | 1403 | 1344 | 1318 | 1287 | 1283 | 1200 | 1262 | 1333 | 1206 | 1129 | 1357 |  |  | 1197 | 926 | 1327 |  | 1466 | 1210 | 1324 | 1289 | 1303 | 1331 | 1339 | 1346 | 1342 | 1362 | 1365 | 1361 | 1361 | 1553 | 1225 | 1138 | 910 | 810 | 977 | 1143 | 1327 | 1510 | 1282 | 1386 | 1298 | 1310 | 1445 | 1432 | 1178 | 1248 | 1136 | 1251 | 1178 |  | 1478 | 1263 | 578 | 1163 | 1153 |  |  | 1078 | 1178 | 1299 | 1270 | 1078 | 29.88 | 43.21 | 1.3 | 6.1 |  | 0 | 6.15 |  |  | 81907526.273 | 281425.064 | 55034099.627 | 61224.371 | 82686891.459 | 185720.486 | 59836769.598 | 55214.015 | 310585448.108 | 82457.052 | 82913.789 | 13.452 | 84310.237 | 9.947 | 84990.259 | 36.708 | 66166.972 | 12.656 | 317952.483 | 55.075 | 167200.627 | 317897.408 | 12 | 0 | 6.15 | 29.88 | 43.21 | 1.3 | 6.1 | 321089
2025-04-13 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1443 | 1470 | 1366 | 1365 | 1450 | 1339 | 1367 | 1257 | 1372 | 1348 | 1426 | 1416 | 1391 | 1259 | 1335 | 1374 | 1312 | 1329 | 1487 | 1496 | 1394 | 1339 | 1532 | 1445 | 1504 | 1493 | 1486 | 1516 | 1473 | 1510 | 1310 | 1334 | 1276 | 1687 | 1200 | 1433 | 1316 | 1339 | 1358 | 1394 | 1342 | 1331 | 1354 | 1369 | 1383 | 1405 | 1508 | 1384 | 1308 | 1340 | 1266 | 1331 | 1518 | 1502 | 1388 | 1478 | 1445 | 1305 | 1491 | 1433 | 1332 | 1477 | 1278 | 1080 | 1515 | 1506 | 1525 | 1340 | 1380 | 1387 | 1396 | 1345 | 1277 | 1408 | 1417 | 1548 | 1570 | 1370 | 1363 | 1486 | 1403 | 1402 | 1397 | 1399 | 1385 | 1326 | 1407 | 1391 | 1365 | 1358 | 1418 | 1278 | 1427 | 1363 | 1310 | 1365 | 1361 | 1386 | 1393 | 1278 | 1445 | 1391 | 1413 | 1364 | 1564 | 1198 | 1568 | 1563 | 1425 | 1551 | 1444 | 1512 | 1558 | 1582 | 1357 | 1423 | 1550 | 1449 | 1479 | 1390 | 1419 | 1491 | 1416 | 1340 | 1412 | 1464 | 1290 | 1319 | 1546 | 1539 | 1463 | 1446 | 1402 | 1195 | 1532 | 1480 | 1477 | 1454 | 1407 | 1399 | 1332 | 1390 | 1379 | 1550 | 1321 | 1573 | 1393 | 1262 | 1453 | 1478 | 1495 | 1364 | 1485 | 1357 | 1326 | 1312 | 1178 | 1326 | 1265 | 1341 | 1518 | 1317 | 1378 | 1452 | 1354 | 1231 | 1307 | 1512 | 1386 | 1284 | 1372 | 1364 | 1508 | 1431 | 1578 | 1382 | 1399 | 1254 | 1604 | 1418 | 1437 | 1471 | 1442 | 1505 | 1453 | 1544 | 1454 | 1458 | 1432 | 1389 | 1327 | 1322 | 1165 | 1301 | 1384 | 1241 | 1164 | 1401 |  |  | 1203 | 955 | 1364 |  | 1503 | 1210 | 1370 | 1348 | 1335 | 1390 | 1401 | 1411 | 1406 | 1426 | 1408 | 1417 | 1365 | 1601 | 1273 | 1182 | 898 | 878 | 1007 | 1184 | 1373 | 1578 | 1365 | 1452 | 1278 | 1363 | 1482 | 1486 | 1117 | 1295 | 1179 | 1299 | 1198 |  | 1520 | 1365 | 644 | 1183 | 1195 |  |  | 1163 | 1191 | 1298 | 1263 | 1191 | 31.82 | 40.8 | 3.02 | 7.1 |  | 0 | 6.14 |  |  | 81995608.799 | 281439.981 | 55121205.499 | 61234.011 | 82776560.366 | 185766.511 | 59905210.194 | 55227.06 | 310918312.508 | 82518.014 | 88082.526 | 14.917 | 87105.872 | 9.64 | 89668.907 | 46.025 | 68440.596 | 13.045 | 332864.4 | 60.962 | 175163.841 | 332803.438 | 12 | 0 | 6.14 | 31.82 | 40.8 | 3.02 | 7.1 | 335292
2025-04-14 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1457 | 1485 | 1383 | 1384 | 1471 | 1363 | 1382 | 1266 | 1395 | 1362 | 1427 | 1413 | 1392 | 1266 | 1323 | 1363 | 1295 | 1314 | 1471 | 1480 | 1380 | 1326 | 1521 | 1432 | 1489 | 1477 | 1472 | 1503 | 1460 | 1495 | 1363 | 1322 | 1300 | 1681 | 1208 | 1455 | 1304 | 1321 | 1347 | 1379 | 1324 | 1311 | 1336 | 1351 | 1355 | 1388 | 1491 | 1378 | 1306 | 1336 | 1263 | 1328 | 1503 | 1483 | 1374 | 1465 | 1450 | 1285 | 1471 | 1413 | 1314 | 1477 | 1263 | 1098 | 1499 | 1488 | 1509 | 1330 | 1365 | 1371 | 1381 | 1331 | 1270 | 1392 | 1398 | 1557 | 1588 | 1371 | 1355 | 1468 | 1406 | 1401 | 1383 | 1383 | 1369 | 1307 | 1391 | 1377 | 1350 | 1345 | 1399 | 1298 | 1412 | 1349 | 1298 | 1348 | 1344 | 1373 | 1376 | 1266 | 1424 | 1373 | 1396 | 1348 | 1541 | 1182 | 1572 | 1545 | 1406 | 1534 | 1402 | 1496 | 1547 | 1563 | 1342 | 1406 | 1533 | 1433 | 1456 | 1377 | 1403 | 1478 | 1398 | 1324 | 1394 | 1478 | 1276 | 1297 | 1521 | 1514 | 1438 | 1450 | 1423 | 1207 | 1544 | 1486 | 1480 | 1439 | 1398 | 1402 | 1353 | 1398 | 1391 | 1546 | 1328 | 1565 | 1356 | 1251 | 1446 | 1470 | 1480 | 1353 | 1495 | 1345 | 1319 | 1307 | 1190 | 1325 | 1281 | 1356 | 1534 | 1330 | 1307 | 1453 | 1357 | 1191 | 1312 | 1512 | 1376 | 1269 | 1361 | 1349 | 1379 | 1417 | 1548 | 1357 | 1378 | 1233 | 1578 | 1394 | 1415 | 1446 | 1424 | 1480 | 1428 | 1531 | 1433 | 1433 | 1412 | 1273 | 1324 | 1306 | 1166 | 1330 | 1395 | 1255 | 1168 | 1419 |  |  | 1188 | 943 | 1357 |  | 1484 | 1173 | 1353 | 1339 | 1334 | 1382 | 1399 | 1406 | 1403 | 1420 | 1404 | 1399 | 1358 | 1587 | 1257 | 1164 | 963 | 810 | 993 | 1174 | 1379 | 1562 | 1386 | 1448 | 1298 | 1378 | 1490 | 1469 | 1109 | 1291 | 1169 | 1300 | 1178 |  | 1498 | 1382 | 633 | 1197 | 1176 |  |  | 1110 | 1263 | 1278 | 1210 | 1163 | 32.37 | 45.01 | 1.79 | 6.1 |  | 0 | 6.51 |  |  | 82083194.141 | 281455.645 | 55207413.543 | 61246.338 | 82865707.869 | 185809.522 | 59973320.461 | 55239.414 | 311248951.343 | 82573.423 | 87585.342 | 15.664 | 86208.044 | 12.327 | 89147.503 | 43.011 | 68110.267 | 12.354 | 330638.835 | 55.409 | 173765.395 | 330583.426 | 12 | 0 | 6.51 | 32.37 | 45.01 | 1.79 | 6.1 | 333086
2025-04-15 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1424 | 1452 | 1351 | 1355 | 1432 | 1328 | 1333 | 1228 | 1351 | 1319 | 1378 | 1365 | 1343 | 1222 | 1274 | 1315 | 1276 | 1273 | 1433 | 1422 | 1325 | 1272 | 1460 | 1364 | 1435 | 1419 | 1415 | 1447 | 1410 | 1444 | 1378 | 1307 | 1269 | 1631 | 1194 | 1425 | 1295 | 1301 | 1312 | 1349 | 1308 | 1290 | 1301 | 1315 | 1322 | 1345 | 1444 | 1333 | 1288 | 1318 | 1246 | 1311 | 1484 | 1465 | 1357 | 1449 | 1431 | 1267 | 1471 | 1414 | 1312 | 1467 | 1278 | 1461 | 1451 | 1457 | 1289 | 1318 | 1326 | 1335 | 1290 | 1229 | 1346 | 1377 | 1525 | 1545 | 1323 | 1424 | 1360 | 1356 | 1337 | 1337 | 1325 | 1272 | 1345 | 1333 | 1304 | 1301 | 1351 | 1412 | 1365 | 1303 | 1410 | 1363 | 1278 | 1302 | 1311 | 1332 | 1337 | 1234 | 1379 | 1333 | 1356 | 1334 | 1495 | 1151 | 1520 | 1496 | 1360 | 1484 | 1364 | 1465 | 1512 | 1514 | 1304 | 1359 | 1485 | 1340 | 1413 | 1345 | 1376 | 1437 | 1362 | 1281 | 1348 | 1463 | 1259 | 1279 | 1502 | 1497 | 1429 | 1435 | 1394 | 1190 | 1519 | 1470 | 1471 | 1445 | 1351 | 1358 | 1330 | 1361 | 1349 | 1499 | 1286 | 1510 | 1315 | 1214 | 1401 | 1428 | 1435 | 1316 | 1458 | 1314 | 1292 | 1278 | 1163 | 1280 | 1242 | 1316 | 1496 | 1299 | 1421 | 1434 | 1317 | 1289 | 1269 | 1462 | 1328 | 1218 | 1314 | 1299 | 1292 | 1364 | 1499 | 1313 | 1332 | 1194 | 1524 | 1348 | 1368 | 1394 | 1394 | 1432 | 1380 | 1487 | 1386 | 1386 | 1356 | 1250 | 1306 | 1259 | 1150 | 1292 | 1349 | 1224 | 1144 | 1376 |  |  | 1157 | 926 | 1317 |  | 1436 | 1214 | 1307 | 1292 | 1294 | 1336 | 1353 | 1359 | 1356 | 1371 | 1380 | 1384 | 1333 | 1568 | 1217 | 1125 | 925 | 863 | 881 | 1178 | 1363 | 1510 | 1310 | 1410 | 1263 | 1298 | 1445 | 1478 | 1111 | 1270 | 1163 | 1278 | 1110 |  | 1478 | 1351 | 614 | 1180 | 1168 |  |  | 1135 | 1256 | 1270 | 1225 | 1135 | 32.7 | 43.6 | 1.6 | 6.5 |  | 0 | 6.23 |  |  | 82168621 | 281469 | 55291405 | 61256 | 82952664 | 185854 | 60036190 | 55251 | 311567840.3 | 82626.6 | 85426.859 | 13.355 | 83991.457 | 9.662 | 86956.131 | 44.478 | 62869.539 | 11.586 | 318888.957 | 53.177 | 169395.299 | 318835.78 | 12 | 0 | 6.23 | 32.7 | 43.6 | 1.6 | 6.5 | 326506
2025-04-16 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1403 | 1428 | 1328 | 1330 | 1407 | 1310 | 1313 | 1209 | 1330 | 1298 | 1360 | 1346 | 1322 | 1202 | 1275 | 1314 | 1266 | 1274 | 1431 | 1434 | 1331 | 1280 | 1465 | 1380 | 1432 | 1413 | 1413 | 1430 | 1380 | 1409 | 1363 | 1253 | 1250 | 1608 | 1211 | 1402 | 1307 | 1288 | 1309 | 1342 | 1294 | 1279 | 1290 | 1304 | 1308 | 1355 | 1444 | 1315 | 1283 | 1313 | 1247 | 1312 | 1495 | 1480 | 1355 | 1437 | 1411 | 1252 | 1480 | 1415 | 1301 | 1450 | 1263 | 1425 | 1462 | 1453 | 1476 | 1268 | 1323 | 1333 | 1342 | 1277 | 1196 | 1331 | 1355 | 1512 | 1525 | 1301 | 1288 | 1396 | 1338 | 1335 | 1314 | 1316 | 1309 | 1255 | 1341 | 1330 | 1314 | 1307 | 1369 | 1290 | 1351 | 1298 | 1263 | 1282 | 1290 | 1302 | 1315 | 1202 | 1360 | 1314 | 1337 | 1315 | 1478 | 1124 | 1497 | 1472 | 1340 | 1496 | 1353 | 1444 | 1474 | 1490 | 1272 | 1339 | 1464 | 1338 | 1411 | 1341 | 1380 | 1427 | 1352 | 1303 | 1371 | 1425 | 1255 | 1295 | 1510 | 1509 | 1428 | 1425 | 1371 | 1168 | 1491 | 1442 | 1440 | 1415 | 1309 | 1332 | 1308 | 1362 | 1323 | 1471 | 1262 | 1481 | 1331 | 1238 | 1429 | 1470 | 1466 | 1335 | 1443 | 1327 | 1304 | 1296 | 1098 | 1259 | 1225 | 1298 | 1478 | 1284 | 1400 | 1431 | 1299 | 1269 | 1252 | 1439 | 1306 | 1199 | 1291 | 1277 | 1270 | 1338 | 1476 | 1294 | 1311 | 1176 | 1500 | 1328 | 1348 | 1376 | 1411 | 1411 | 1361 | 1466 | 1362 | 1364 | 1334 | 1188 | 1287 | 1244 | 1111 | 1272 | 1327 | 1203 | 1124 | 1350 |  |  | 1180 | 919 | 1296 |  | 1494 | 1220 | 1287 | 1275 | 1261 | 1317 | 1332 | 1337 | 1334 | 1350 | 1360 | 1363 | 1300 | 1546 | 1199 | 1105 | 910 | 825 | 943 | 1117 | 1316 | 1531 | 1339 | 1399 | 1278 | 1300 | 1418 | 1366 | 1094 | 1241 | 1113 | 1237 | 996 |  | 1175 | 1345 | 604 | 1261 | 1214 |  |  | 1098 | 1234 | 1301 | 1270 | 1117 | 34.09 | 46.02 | 1.33 | 6.1 |  | 0 | 6.27 |  |  | 82253458.237 | 281482.329 | 55374252.019 | 61264.956 | 83038923.775 | 185897.441 | 60101967.276 | 55263.176 | 311887179.23 | 82681.229 | 84837.237 | 13.329 | 82847.019 | 8.956 | 86259.775 | 43.441 | 65777.276 | 12.176 | 319338.93 | 54.629 | 167661.971 | 319284.301 | 12 | 0 | 6.27 | 34.09 | 46.02 | 1.33 | 6.1 | 323020
2025-04-17 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1355 | 1375 | 1281 | 1281 | 1360 | 1265 | 1275 | 1248 | 1295 | 1286 | 1306 | 1318 | 1296 | 1152 | 1240 | 1272 | 1217 | 1235 | 1379 | 1389 | 1297 | 1252 | 1423 | 1341 | 1381 | 1389 | 1379 | 1411 | 1370 | 1395 | 1310 | 1253 | 1203 | 1546 | 1189 | 1350 | 1285 | 1244 | 1275 | 1300 | 1246 | 1233 | 1257 | 1277 | 1267 | 1310 | 1389 | 1288 | 1219 | 1300 | 1208 | 1369 | 1450 | 1400 | 1314 | 1309 | 1400 | 1334 | 1400 | 1400 | 1324 | 1400 | 1461 | 1406 | 1398 | 1422 | 1400 | 1269 | 1295 | 1305 | 1211 | 1200 | 1300 | 1270 | 1460 | 1468 | 1500 | 1266 | 1360 | 1301 | 1308 | 1299 | 1303 | 1260 | 1180 | 1318 | 1303 | 1284 | 1248 | 1248 | 1331 | 1226 | 1334 | 1272 | 1298 | 1261 | 1264 | 1225 | 1266 | 1119 | 1307 | 1266 | 1294 | 1290 | 1452 | 1045 | 1499 | 1413 | 1289 | 1461 | 1306 | 1387 | 1391 | 1431 | 1192 | 1288 | 1409 | 1300 | 1359 | 1292 | 1326 | 1373 | 1280 | 1258 | 1331 | 1426 | 1213 | 1245 | 1451 | 1450 | 1376 | 1375 | 1318 | 1122 | 1436 | 1383 | 1387 | 1364 | 1293 | 1321 | 1262 | 1338 | 1288 | 1442 | 1240 | 1457 | 1306 | 1201 | 1394 | 1427 | 1427 | 1307 | 1451 | 1309 | 1286 | 1269 | 1026 | 1232 | 1178 | 1243 | 1423 | 1228 | 1337 | 1374 | 1239 | 1216 | 1201 | 1378 | 1254 | 1153 | 1240 | 1216 | 1284 | 1424 | 1245 | 1264 | 1132 | 1439 | 1500 | 1297 | 1323 | 1361 | 1400 | 1408 | 1316 | 1400 | 1284 | 1300 | 1284 | 1149 | 1236 | 1205 | 1079 | 1225 | 1274 | 1152 | 1069 | 1297 |  |  | 1132 | 882 | 1246 |  | 1363 | 1173 | 1241 | 1232 | 1183 | 1267 | 1281 | 1283 | 1281 | 1299 | 1308 | 1311 | 1215 | 1483 | 1152 | 1062 | 926 | 855 | 906 | 1082 | 1296 | 1480 | 1312 | 1364 | 1226 | 1280 | 1327 | 1331 | 1066 | 1228 | 1082 | 1218 | 984 |  | 1175 | 1318 | 585 | 1285 | 1178 |  |  | 1185 | 1251 | 1299 | 1251 | 1074 | 35.7 | 46 | 0.6 | 6.78 |  | 0 | 6.11 |  |  | 82335200 | 281497 | 55454144 | 61275 | 83122389 | 185944 | 60165461 | 55276 | 312195388.5 | 82741.8 | 81741.763 | 14.671 | 79891.981 | 10.044 | 83465.225 | 46.559 | 63493.724 | 12.824 | 308209.27 | 60.571 | 161609.029 | 308148.699 | 12 | 0 | 6.11 | 35.7 | 46 | 0.6 | 6.78 | 314197
2025-04-18 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1328 | 1353 | 1259 | 1355 | 1356 | 1247 | 1235 | 1251 | 1266 | 1254 | 1260 | 1276 | 1256 | 1105 | 1190 | 1224 | 1175 | 1184 | 1319 | 1330 | 1349 | 1204 | 1370 | 1379 | 1325 | 1333 | 1325 | 1359 | 1317 | 1347 | 1326 | 1225 | 1176 | 1505 | 1154 | 1324 | 1240 | 1202 | 1236 | 1262 | 1202 | 1201 | 1223 | 1243 | 1220 | 1261 | 1340 | 1242 | 1241 | 1271 | 1195 | 1257 | 1430 | 1417 | 1335 | 1384 | 1390 | 1273 | 1405 | 1363 | 1247 | 1402 | 1363 | 1463 | 1364 | 1357 | 1378 | 1195 | 1237 | 1244 | 1255 | 1204 | 1124 | 1259 | 1294 | 1436 | 1445 | 1242 | 1230 | 1347 | 1261 | 1271 | 1270 | 1263 | 1212 | 1179 | 1264 | 1251 | 1229 | 1222 | 1295 | 1210 | 1284 | 1223 | 1226 | 1224 | 1235 | 1235 | 1254 | 1148 | 1297 | 1260 | 1284 | 1266 | 1430 | 1062 | 1477 | 1393 | 1271 | 1402 | 1284 | 1331 | 1365 | 1403 | 1203 | 1248 | 1380 | 1280 | 1337 | 1237 | 1274 | 1368 | 1297 | 1261 | 1279 | 1468 | 1167 | 1198 | 1397 | 1399 | 1329 | 1343 | 1297 | 1113 | 1421 | 1357 | 1373 | 1327 | 1284 | 1281 | 1240 | 1284 | 1266 | 1405 | 1206 | 1368 | 1256 | 1156 | 1343 | 1374 | 1375 | 1258 | 1400 | 1260 | 1239 | 1224 | 1068 | 1204 | 1198 | 1199 | 1369 | 1187 | 1292 | 1323 | 1263 | 1210 | 1155 | 1326 | 1207 | 1107 | 1190 | 1179 | 1170 | 1234 | 1371 | 1199 | 1216 | 1090 | 1385 | 1228 | 1247 | 1276 | 1315 | 1312 | 1258 | 1360 | 1267 | 1269 | 1235 | 1102 | 1180 | 1146 | 1021 | 1168 | 1218 | 1107 | 1033 | 1241 |  |  | 1233 | 875 | 1184 |  | 1297 | 1118 | 1186 | 1176 | 1170 | 1212 | 1227 | 1234 | 1229 | 1244 | 1253 | 1258 | 1217 | 1424 | 1103 | 1014 | 963 | 896 | 998 | 1056 | 1240 | 1417 | 1249 | 1302 | 1263 | 1298 | 1319 | 1270 | 1012 | 1176 | 1032 | 1178 | 948 |  | 1175 | 1263 | 551 | 1173 | 1127 |  |  | 1098 | 1235 | 1264 | 1200 | 1063 | 35.61 | 47.4 | 1.3 | 5.1 |  | 0 | 5.95 |  |  | 82415821.321 | 281510.713 | 55532508.045 | 61284.336 | 83203137.502 | 185982.206 | 60226428.183 | 55288.399 | 312495765.901 | 82799.368 | 80621.321 | 13.713 | 78364.045 | 9.336 | 80748.502 | 38.206 | 60967.183 | 12.399 | 300377.401 | 57.568 | 158962.317 | 300319.833 | 12 | 0 | 5.95 | 35.61 | 47.4 | 1.3 | 5.1 | 305558
2025-04-19 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1318 | 1344 | 1246 | 1236 | 1328 | 1232 | 1209 | 1219 | 1244 | 1234 | 1237 | 1246 | 1226 | 1079 | 1188 | 1224 | 1175 | 1190 | 1128 | 1322 | 1250 | 1197 | 1375 | 1280 | 1303 | 1307 | 1298 | 1331 | 1283 | 1315 | 1363 | 1193 | 1162 | 1476 | 1131 | 1313 | 1212 | 1173 | 1205 | 1230 | 1170 | 1168 | 1190 | 1210 | 1185 | 1259 | 1325 | 1212 | 1189 | 1217 | 1160 | 1220 | 1392 | 1379 | 1316 | 1314 | 1363 | 1221 | 1367 | 1328 | 1188 | 1349 | 1400 | 1461 | 13143 | 1337 | 1356 | 1163 | 1227 | 1234 | 1245 | 1202 | 1082 | 1218 | 1256 | 1398 | 1407 | 1208 | 1192 | 1331 | 1228 | 1237 | 1209 | 1211 | 1178 | 1182 | 1264 | 1252 | 1225 | 1220 | 1271 | 1256 | 1277 | 1247 | 1268 | 1201 | 1200 | 1225 | 1222 | 1135 | 1271 | 1228 | 1252 | 1231 | 1398 | 1054 | 1446 | 1373 | 1254 | 1371 | 1278 | 1330 | 1382 | 1379 | 1201 | 1252 | 1367 | 1312 | 1319 | 1225 | 1246 | 1338 | 1280 | 1232 | 1293 | 1498 | 1167 | 1197 | 1400 | 1388 | 1325 | 1331 | 1284 | 1103 | 1399 | 1324 | 1338 | 1267 | 1283 | 1272 | 1230 | 1270 | 1255 | 1397 | 1197 | 1353 | 1229 | 1133 | 1310 | 1344 | 1341 | 1230 | 1368 | 1226 | 1206 | 1193 | 1100 | 1169 | 1106 | 1172 | 1338 | 1160 | 1257 | 1292 | 1166 | 1143 | 1126 | 1294 | 1179 | 1080 | 1162 | 1161 | 1142 | 1203 | 1413 | 1227 | 1221 | 1101 | 1369 | 1242 | 1204 | 1237 | 1282 | 1357 | 1287 | 1377 | 1283 | 1301 | 1202 | 1076 | 1156 | 1126 | 1011 | 1142 | 1195 | 1083 | 1014 | 1214 |  |  | 1098 | 858 | 1162 |  | 1297 | 1091 | 1186 | 1184 | 1162 | 1230 | 1227 | 1246 | 1233 | 1263 | 1221 | 1232 | 1207 | 1389 | 1080 | 1063 | 998 | 898 | 889 | 1040 | 1238 | 1390 | 1228 | 1277 | 1268 | 1310 | 1309 | 1251 | 1001 | 1156 | 1014 | 1157 | 929 |  | 1175 | 1241 | 604 | 1156 | 1108 |  |  | 1110 | 1278 | 1263 | 1210 | 1063 | 35.4 | 46.4 | 1.2 | 5.3 |  | 0 | 5.87 |  |  | 82494845 | 281530 | 55609764 | 61302 | 83282860 | 186033 | 60286490 | 55303 | 312791511.1 | 82871.8 | 79023.679 | 19.287 | 77255.955 | 17.664 | 79722.498 | 50.794 | 60061.817 | 14.601 | 295745.199 | 72.432 | 156242.683 | 295672.767 | 12 | 0 | 5.87 | 35.4 | 46.4 | 1.2 | 5.3 | 312642
2025-04-20 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1466 | 1477 | 1357 | 1354 | 1446 | 1337 | 1345 | 1357 | 1374 | 1381 | 1364 | 1378 | 1363 | 1213 | 1306 | 1342 | 1280 | 1309 | 1474 | 1466 | 1374 | 1303 | 1488 | 1404 | 1468 | 1447 | 1441 | 1457 | 1390 | 1423 | 1402 | 1294 | 1261 | 1602 | 1230 | 1426 | 1317 | 1277 | 1310 | 1336 | 1271 | 1273 | 1294 | 1316 | 1286 | 1374 | 1440 | 1315 | 1319 | 1352 | 1273 | 1339 | 1519 | 1506 | 1435 | 1467 | 1503 | 1334 | 1488 | 1443 | 1288 | 1460 | 1463 | 1498 | 1459 | 1454 | 1069 | 1194 | 1318 | 1334 | 1355 | 1250 | 1385 | 1356 | 1556 | 1537 | 1553 | 1338 | 1329 | 1412 | 1354 | 1373 | 1365 | 1370 | 1280 | 1213 | 1385 | 1371 | 1333 | 1295 | 1365 | 1298 | 1398 | 1388 | 1302 | 1299 | 1320 | 1282 | 1322 | 1168 | 1371 | 1329 | 1358 | 1336 | 1508 | 1071 | 1568 | 1480 | 1363 | 1486 | 1329 | 1435 | 1450 | 1515 | 1253 | 1357 | 1486 | 1483 | 1391 | 1334 | 1351 | 1436 | 1334 | 1335 | 1354 | 1563 | 1275 | 1299 | 1515 | 1512 | 1443 | 1445 | 1390 | 1194 | 1522 | 1436 | 1455 | 1374 | 1405 | 1391 | 1335 | 1389 | 1376 | 1523 | 1317 | 1486 | 1376 | 1270 | 1450 | 1475 | 1485 | 1358 | 1485 | 1336 | 1314 | 1313 | 1278 | 1296 | 1213 | 1279 | 1451 | 1260 | 1366 | 1402 | 1266 | 1256 | 1255 | 1437 | 1319 | 1221 | 1300 | 1295 | 1277 | 1358 | 1545 | 1348 | 1355 | 1218 | 1503 | 1370 | 1307 | 1370 | 1396 | 1477 | 1412 | 1500 | 1417 | 1429 | 1362 | 1222 | 1266 | 1224 | 1139 | 1307 | 1354 | 1233 | 1117 | 1368 |  |  | 1197 | 932 | 1280 |  | 1388 | 1189 | 1327 | 1304 | 1267 | 1350 | 1361 | 1350 | 1362 | 1383 | 1263 | 1210 | 1244 | 1534 | 1171 | 1077 | 1010 | 963 | 965 | 1134 | 1355 | 1509 | 1330 | 1383 | 1310 | 1398 | 1362 | 1349 | 1086 | 1256 | 1101 | 1256 | 1007 |  | 1175 | 1348 | 660 | 1249 | 1199 |  |  | 1202 | 1212 | 1280 | 1298 | 1096 | 35.9 | 47.6 | 1.6 | 5.1 |  | 0 | 6.7 |  |  | 82581398.495 | 281543.717 | 55693455.236 | 61311.454 | 83370328.118 | 186091.183 | 60351293.025 | 55314.633 | 313113666.068 | 82927.647 | 86553.495 | 13.717 | 83691.236 | 9.454 | 87468.118 | 58.183 | 64803.025 | 11.633 | 322154.968 | 55.847 | 170221.56 | 322099.121 | 12 | 0 | 6.7 | 35.9 | 47.6 | 1.6 | 5.1 | 327345
2025-04-21 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1450 | 1498 | 1344 | 1338 | 1447 | 1326 | 1369 | 1367 | 1393 | 1398 | 1360 | 1376 | 1359 | 1219 | 1302 | 1337 | 1266 | 1297 | 1464 | 1458 | 1361 | 1295 | 1475 | 1400 | 1460 | 1438 | 1431 | 1461 | 1431 | 1460 | 1450 | 1450 | 1400 | 1650 | 1400 | 1441 | 1302 | 1263 | 1292 | 1320 | 1300 | 1405 | 1276 | 1297 | 1287 | 1376 | 1445 | 1400 | 1409 | 1410 | 1300 | 1289 | 1466 | 1452 | 1450 | 1391 | 1452 | 1271 | 1413 | 1374 | 1224 | 1388 | 1490 | 1510 | 1454 | 1448 | 1467 | 1205 | 1327 | 1351 | 1361 | 1259 | 1390 | 1362 | 1557 | 1535 | 1549 | 1329 | 1318 | 1404 | 1344 | 1363 | 1349 | 1355 | 1282 | 1214 | 1395 | 1391 | 1344 | 1301 | 1368 | 1397 | 1385 | 1384 | 1310 | 1291 | 1302 | 1278 | 1304 | 1150 | 1355 | 1312 | 1342 | 1320 | 1490 | 1098 | 1555 | 1470 | 1346 | 1475 | 1324 | 1426 | 1448 | 1500 | 1250 | 1342 | 1468 | 1463 | 1384 | 1317 | 1334 | 1422 | 1329 | 1318 | 1337 | 1426 | 1257 | 1280 | 1495 | 1489 | 1422 | 1428 | 1384 | 1200 | 1529 | 1436 | 1468 | 1386 | 1378 | 1373 | 1332 | 1379 | 1350 | 1502 | 1295 | 1516 | 1355 | 1252 | 1449 | 1456 | 1477 | 1362 | 1465 | 1360 | 1337 | 1320 | 1325 | 1282 | 1246 | 1314 | 1503 | 1303 | 1443 | 1445 | 1317 | 1270 | 1263 | 1447 | 1322 | 1218 | 1302 | 1292 | 1281 | 1356 | 1528 | 1333 | 1341 | 1203 | 1486 | 1355 | 1292 | 1358 | 1428 | 1462 | 1396 | 1502 | 1401 | 1412 | 1354 | 1218 | 1250 | 1213 | 1132 | 1300 | 1339 | 1203 | 1121 | 1357 |  |  | 1181 | 921 | 1272 |  | 1394 | 1242 | 1311 | 1290 | 1259 | 1334 | 1343 | 1339 | 1343 | 1368 | 1369 | 1356 | 1235 | 1542 | 1156 | 1061 | 1062 | 998 | 952 | 1116 | 1337 | 1489 | 1317 | 1369 | 1362 | 1400 | 1398 | 1380 | 1090 | 1300 | 1150 | 1303 | 1100 |  | 1250 | 1360 | 668 | 1298 | 1283 |  |  | 1210 | 1412 | 1300 | 1310 | 1117 | 37.4 | 47.37 | 2.08 | 5.4 |  | 0 | 6.75 |  |  | 82666836.801 | 281560.312 | 55776650.679 | 61327.538 | 83457790.293 | 186135.647 | 60416203.414 | 55328.08 | 313434297.117 | 82986.708 | 85438.306 | 16.595 | 83195.443 | 16.084 | 87462.175 | 44.464 | 64910.389 | 13.447 | 320631.049 | 59.061 | 168601.07 | 320571.988 | 12 | 0 | 6.75 | 37.4 | 47.37 | 2.08 | 5.4 | 328589
2025-04-22 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1563 | 1564 | 1437 | 1432 | 1551 | 1422 | 1464 | 1462 | 1483 | 1494 | 1492 | 1488 | 1466 | 1316 | 1397 | 1423 | 1308 | 1339 | 1506 | 1502 | 1405 | 1357 | 1539 | 1455 | 1507 | 1484 | 1478 | 1509 | 1504 | 1528 | 1498 | 1398 | 1324 | 1681 | 1347 | 1551 | 1387 | 1352 | 1403 | 1433 | 1340 | 1347 | 1387 | 1409 | 1412 | 1470 | 1577 | 1427 | 1382 | 1421 | 1335 | 1409 | 1603 | 1586 | 1479 | 1525 | 1575 | 1376 | 1529 | 1484 | 1325 | 1428 | 1510 | 1580 | 1580 | 1571 | 1590 | 1261 | 1413 | 1422 | 1464 | 1326 | 1479 | 1434 | 1638 | 1611 | 1635 | 1406 | 1398 | 1467 | 1427 | 1448 | 1424 | 1414 | 1423 | 1339 | 1488 | 1475 | 1448 | 1379 | 1478 | 1400 | 1483 | 1475 | 1378 | 1353 | 1386 | 1339 | 1379 | 1419 | 1431 | 1398 | 1429 | 1406 | 1565 | 1424 | 1638 | 1566 | 1436 | 1561 | 1384 | 1506 | 1522 | 1594 | 1310 | 1423 | 1552 | 1593 | 1446 | 1443 | 1476 | 1520 | 1408 | 1447 | 1438 | 1463 | 1354 | 1390 | 1614 | 1622 | 1549 | 1561 | 1510 | 1296 | 1652 | 1548 | 1486 | 1492 | 1470 | 1462 | 1448 | 1479 | 1399 | 1605 | 1391 | 1625 | 1600 | 1341 | 1543 | 1556 | 1576 | 1451 | 1557 | 1447 | 1426 | 1407 | 1363 | 1304 | 1343 | 1408 | 1618 | 1401 | 1554 | 1559 | 1412 | 1346 | 1347 | 1538 | 1405 | 1297 | 1386 | 1373 | 1357 | 1444 | 1628 | 1429 | 1428 | 1281 | 1585 | 1442 | 1378 | 1442 | 1547 | 1556 | 1479 | 1606 | 1493 | 1505 | 1441 | 1296 | 1332 | 1286 | 1198 | 1385 | 1428 | 1262 | 1181 | 1452 |  |  | 1266 | 982 | 1354 |  | 1561 | 1363 | 1396 | 1370 | 1323 | 1418 | 1431 | 1410 | 1432 | 1451 | 1461 | 1450 | 1572 | 1627 | 1232 | 1133 | 1100 | 1010 | 1019 | 1189 | 1427 | 1582 | 1399 | 1452 | 1410 | 1462 | 1421 | 1414 | 1141 | 1319 | 1156 | 1318 | 1052 |  | 1175 | 1414 | 700 | 1313 | 1257 |  |  | 1278 | 1400 | 1335 | 1320 | 1149 | 37.9 | 46.08 | 1.93 | 5.1 |  | 0 | 7.08 |  |  | 82757675.466 | 281573.49 | 55865708.265 | 61336.975 | 83551224.232 | 186178.147 | 60485503.243 | 55339.845 | 313776481.848 | 83040.583 | 90838.665 | 13.178 | 89057.586 | 9.437 | 93433.939 | 42.5 | 69299.829 | 11.765 | 342184.731 | 53.875 | 179873.636 | 342130.856 | 12 | 0 | 7.08 | 37.9 | 46.08 | 1.93 | 5.1 | 347261
2025-04-23 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1634 | 1639 | 1516 | 1505 | 1633 | 1507 | 1518 | 1519 | 1486 | 1560 | 1548 | 1539 | 1517 | 1362 | 1440 | 1467 | 1357 | 1368 | 1535 | 1529 | 1433 | 1385 | 1574 | 1482 | 1534 | 1512 | 1507 | 1504 | 1529 | 1557 | 1560 | 1425 | 1383 | 1730 | 1424 | 1614 | 1481 | 1434 | 1460 | 1494 | 1424 | 1423 | 1443 | 1463 | 1458 | 1524 | 1623 | 1483 | 1435 | 1476 | 1387 | 1461 | 1664 | 1646 | 1574 | 1612 | 1652 | 1426 | 1601 | 1540 | 1431 | 808 | 1570 | 1560 | 1623 | 1616 | 1634 | 1278 | 1448 | 1440 | 1524 | 1354 | 1526 | 1468 | 1662 | 1637 | 1668 | 1434 | 1434 | 1498 | 1474 | 1484 | 1476 | 1482 | 1462 | 1518 | 1548 | 1536 | 1506 | 1420 | 1518 | 852 | 1526 | 1522 | 1392 | 1380 | 1445 | 1374 | 1467 | 1475 | 1474 | 1478 | 1511 | 1491 | 1614 | 1520 | 1670 | 1602 | 1478 | 1644 | 1440 | 1540 | 1554 | 1631 | 1336 | 1451 | 1586 | 1656 | 1488 | 1495 | 1533 | 1558 | 1441 | 1517 | 1528 | 1489 | 1402 | 1439 | 1671 | 1678 | 1600 | 1605 | 1543 | 1329 | 1682 | 1585 | 1621 | 1524 | 1501 | 1501 | 1483 | 1526 | 1424 | 1651 | 1393 | 1673 | 1561 | 1408 | 1614 | 1641 | 1640 | 1516 | 1615 | 1508 | 1487 | 1467 | 1430 | 1400 | 1395 | 1455 | 1671 | 1438 | 1592 | 1600 | 1445 | 1376 | 1415 | 1571 | 1486 | 1358 | 1457 | 1440 | 1388 | 1511 | 1673 | 1459 | 1467 | 1314 | 1627 | 1461 | 1416 | 1477 | 1643 | 1682 | 1526 | 1668 | 1536 | 1547 | 1509 | 1340 | 1424 | 1389 | 1234 | 1445 | 1481 | 1301 | 1210 | 1489 |  |  | 1303 | 1009 | 1400 |  | 1606 | 1405 | 1308 | 1339 | 1506 | 1502 | 1405 | 1358 | 1540 | 1416 | 1432 | 1461 | 1461 | 1450 | 1627 | 1233 | 1134 | 1111 | 1011 | 1189 | 1337 | 1478 | 1378 | 1410 | 1428 | 1463 | 1232 | 1310 | 1067 | 1232 | 1081 | 1234 | 998 |  | 1175 | 1445 | 699 | 1343 | 1284 |  |  | 1210 | 1310 | 1380 | 1298 | 1175 | 38 | 46.1 | 2 | 5.3 |  | 0 | 7.22 |  |  | 82851348.837 | 281586.673 | 55957678.329 | 61345.996 | 83647713.106 | 186202.292 | 60554920.387 | 55352.806 | 314127642.011 | 83095.409 | 93673.371 | 13.183 | 91970.064 | 9.021 | 96488.874 | 24.145 | 69417.144 | 12.961 | 351160.163 | 54.826 | 185621.231 | 351105.337 | 12 | 0 | 7.22 | 38 | 46.1 | 2 | 5.3 | 355743
2025-04-24 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1619 | 1624 | 1501 | 1492 | 1608 | 1487 | 1482 | 1482 | 1453 | 1527 | 1514 | 1502 | 1484 | 1328 | 1433 | 1477 | 1432 | 1435 | 1605 | 1575 | 1490 | 1438 | 1641 | 1538 | 1575 | 1545 | 1533 | 1506 | 1552 | 1579 | 1580 | 1445 | 1374 | 1712 | 1418 | 1616 | 1470 | 1408 | 1427 | 1459 | 1399 | 1394 | 1415 | 1429 | 1448 | 1515 | 1604 | 1455 | 1224 | 1256 | 1187 | 1252 | 1426 | 1414 | 1346 | 1381 | 1402 | 1220 | 1411 | 1370 | 1226 | 1112 | 1595 | 1563 | 1594 | 1587 | 1603 | 1251 | 1418 | 1419 | 1491 | 1311 | 1512 | 1436 | 1648 | 1622 | 1653 | 1414 | 1421 | 1452 | 1470 | 1476 | 1471 | 1487 | 1452 | 1509 | 1518 | 1505 | 1476 | 1377 | 1474 | 755 | 1508 | 1515 | 1395 | 1325 | 1422 | 1321 | 1461 | 1486 | 1463 | 1475 | 1505 | 1482 | 1589 | 1493 | 1638 | 1611 | 1498 | 1578 | 1394 | 1501 | 1509 | 1623 | 1306 | 1430 | 1580 | 1613 | 1440 | 1456 | 1497 | 1515 | 1390 | 1478 | 1492 | 1492 | 1377 | 1406 | 1631 | 1639 | 1567 | 1571 | 1525 | 1322 | 1680 | 1568 | 1612 | 1515 | 1513 | 1500 | 1465 | 1501 | 1436 | 1658 | 1386 | 1671 | 1483 | 1376 | 1587 | 1654 | 1608 | 1491 | 1631 | 1486 | 1447 | 1472 | 1389 | 1404 | 1366 | 1424 | 1636 | 1408 | 1557 | 1567 | 1413 | 1343 | 1388 | 1534 | 1452 | 1334 | 1432 | 1418 | 1354 | 1480 | 1671 | 1462 | 1482 | 1324 | 1671 | 1488 | 1449 | 1491 | 1606 | 1650 | 1527 | 1644 | 1543 | 1551 | 1489 | 1342 | 1413 | 1379 | 1229 | 1423 | 1472 | 1274 | 1184 | 1479 |  |  | 1279 | 992 | 1369 |  | 1573 | 1371 | 1448 | 1342 | 1334 | 1416 | 1459 | 1401 | 1453 | 1452 | 1468 | 1453 | 1574 | 1625 | 1430 | 1139 | 1139 | 1114 | 1008 | 1175 | 1405 | 1564 | 1377 | 1435 | 1434 | 1467 | 1538 | 1392 | 1127 | 1302 | 1141 | 1304 | 1441 |  | 1175 | 1449 | 621 | 1315 | 1263 |  |  | 1278 | 1353 | 1260 | 1152 | 1182 | 36.5 | 45.1 | 2.47 | 8.3 |  | 0 | 7.18 |  |  | 82942719.164 | 281600.438 | 56048174.186 | 61355.935 | 83743255.547 | 186244.522 | 60624877.611 | 55365.967 | 314474585.976 | 83153.541 | 91370.327 | 13.765 | 90495.857 | 9.939 | 95542.441 | 42.23 | 69957.224 | 13.161 | 346943.965 | 58.132 | 181842.48 | 346885.833 | 12 | 0 | 7.18 | 36.5 | 45.1 | 2.47 | 8.3 | 351420
2025-04-25 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1522 | 1531 | 1418 | 1410 | 1520 | 1408 | 1398 | 1398 | 1371 | 1443 | 1433 | 1420 | 1399 | 1254 | 1354 | 1398 | 1178 | 1179 | 1330 | 1312 | 1226 | 1191 | 1354 | 1282 | 1325 | 1308 | 1302 | 1282 | 1293 | 1319 | 1584 | 1208 | 1287 | 1621 | 1343 | 1420 | 1391 | 1331 | 1352 | 1379 | 1343 | 1333 | 1361 | 1371 | 1395 | 1438 | 1534 | 1398 | 1347 | 1397 | 1321 | 1390 | 1578 | 1563 | 1475 | 1519 | 1535 | 1333 | 1553 | 1508 | 1340 | 1115 | 1592 | 1573 | 1508 | 1500 | 1517 | 1183 | 1348 | 1342 | 1413 | 1260 | 1443 | 1364 | 1573 | 1549 | 1579 | 1356 | 1361 | 1391 | 1402 | 1404 | 1401 | 1415 | 1400 | 1433 | 1451 | 1438 | 1409 | 1292 | 1312 | 1000 | 1533 | 1443 | 1396 | 1355 | 1365 | 1408 | 1377 | 1401 | 1437 | 1390 | 1417 | 1394 | 1540 | 1404 | 1541 | 1520 | 1417 | 1504 | 1508 | 1453 | 1469 | 1559 | 1408 | 1383 | 1517 | 1539 | 1512 | 1392 | 1422 | 1428 | 1513 | 1401 | 1405 | 1489 | 1319 | 1347 | 1563 | 1570 | 1508 | 1517 | 1472 | 1262 | 1597 | 1490 | 1531 | 1437 | 1439 | 1420 | 1408 | 1415 | 1358 | 1561 | 1306 | 1574 | 1435 | 1296 | 1494 | 1510 | 1512 | 1403 | 1535 | 1400 | 1382 | 1374 | 1392 | 1335 | 1280 | 1339 | 1533 | 1324 | 1459 | 1468 | 1408 | 1267 | 1307 | 1446 | 1370 | 1258 | 1353 | 1339 | 1280 | 1393 | 1610 | 1402 | 1410 | 1266 | 1595 | 1424 | 1380 | 1420 | 1506 | 1568 | 1466 | 1570 | 1476 | 1482 | 1408 | 1310 | 1335 | 1303 | 1203 | 1343 | 1429 | 1257 | 1170 | 1410 |  |  | 1231 | 934 | 1290 |  | 1488 | 1296 | 1379 | 1327 | 1382 | 1378 | 1390 | 1395 | 1398 | 1394 | 1389 | 1440 | 1493 | 1550 | 1364 | 1163 | 1132 | 1107 | 929 | 1084 | 1297 | 1441 | 1270 | 1319 | 1421 | 1455 | 1416 | 1285 | 1035 | 1199 | 1049 | 1202 | 956 |  | 1175 | 1433 | 581 | 1237 | 1188 |  |  | 1271 | 1347 | 1188 | 1152 | 1039 | 37.08 | 47.02 | 1.4 | 6.5 |  | 0 | 7.1 |  |  | 83028954.272 | 281612.677 | 56135133.047 | 61364.572 | 83833891.496 | 186312.499 | 60691066.882 | 55377.348 | 314804205.234 | 83205.261 | 86235.108 | 12.239 | 86958.861 | 8.637 | 90635.949 | 67.977 | 66189.271 | 11.381 | 329619.258 | 51.72 | 173173.093 | 329567.538 | 12 | 0 | 7.1 | 37.08 | 47.02 | 1.4 | 6.5 | 335649
2025-04-26 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1168 | 1144 | 1091 | 1079 | 1169 | 1088 | 1086 | 1088 | 1071 | 1133 | 1116 | 1104 | 1086 | 1060 | 1039 | 1071 | 1038 | 1036 | 1174 | 1155 | 1079 | 1053 | 1195 | 1133 | 1166 | 1155 | 1151 | 1162 | 1158 | 1180 | 1076 | 1089 | 1081 | 1243 | 1037 | 1091 | 1087 | 1044 | 1057 | 1077 | 1044 | 1029 | 1049 | 1056 | 1070 | 1092 | 1173 | 1071 | 1071 | 1099 | 1047 | 1088 | 1240 | 1226 | 1168 | 1203 | 1228 | 1095 | 1227 | 1191 | 1080 | 1206 | 1083 | 1204 | 1175 | 1170 | 1184 | 974 | 1055 | 1030 | 1084 | 1042 | 1102 | 1062 | 1211 | 1198 | 1214 | 1048 | 1056 | 1104 | 1074 | 1077 | 1077 | 1085 | 1068 | 1083 | 1103 | 1090 | 1088 | 1082 | 1116 | 1131 | 1103 | 1097 | 1134 | 1052 | 1053 | 1069 | 1046 | 1064 | 1092 | 1058 | 1078 | 1068 | 1196 | 1100 | 1189 | 1170 | 1077 | 1197 | 1187 | 1136 | 1160 | 1200 | 1068 | 1074 | 1169 | 1216 | 1209 | 1082 | 1101 | 1127 | 1183 | 1090 | 1105 | 1196 | 1017 | 1037 | 1199 | 1199 | 1153 | 1156 | 1131 | 966 | 1223 | 1142 | 1170 | 1101 | 1102 | 1093 | 1077 | 1088 | 1033 | 1193 | 1002 | 1198 | 1073 | 998 | 1161 | 1174 | 1177 | 1084 | 1174 | 1084 | 1067 | 1055 | 1054 | 1022 | 1083 | 1039 | 1195 | 1027 | 1125 | 1141 | 1110 | 985 | 1016 | 1122 | 1060 | 977 | 1053 | 1034 | 1001 | 1078 | 1241 | 1079 | 1088 | 1089 | 1233 | 1102 | 1067 | 1106 | 1163 | 1208 | 1133 | 1216 | 1139 | 1140 | 1097 | 1101 | 1019 | 1011 | 1113 | 1025 | 1082 | 1130 | 1060 | 1083 |  |  | 1050 | 768 | 1013 |  | 1137 | 1011 | 1054 | 1020 | 1053 | 1065 | 1056 | 1073 | 1084 | 1105 | 1086 | 1114 | 1166 | 1219 | 1035 | 1113 | 1050 | 1060 | 914 | 1008 | 1029 | 1153 | 1026 | 1055 | 1021 | 1089 | 1130 | 1038 | 835 | 957 | 842 | 959 | 758 |  | 1175 | 1163 | 588 | 1200 | 1050 |  |  | 1011 | 1100 | 1080 | 1157 | 981 | 36.9 | 43.37 | 1.8 | 9.9 |  | 0 | 5.34 |  |  | 83099811.757 | 281622.638 | 56203507.306 | 61372.195 | 83904016.468 | 186328.13 | 60742671.538 | 55387.237 | 315064821.334 | 83247.126 | 70857.485 | 9.961 | 68374.259 | 7.623 | 70124.972 | 15.631 | 51604.656 | 9.889 | 260616.1 | 41.865 | 139214.16 | 260574.235 | 12 | 0 | 5.34 | 36.9 | 43.37 | 1.8 | 9.9 | 266123
2025-04-27 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1233 | 1194 | 1147 | 1136 | 1228 | 1137 | 1142 | 1133 | 1126 | 1192 | 1170 | 1150 | 1136 | 1125 | 1192 | 1170 | 1082 | 1094 | 1226 | 1150 | 1146 | 1262 | 1187 | 1232 | 1225 | 1232 | 1214 | 1262 | 1234 | 1206 | 1235 | 1213 | 975 | 1048 | 930 | 1069 | 1069 | 1027 | 1054 | 1074 | 1022 | 1011 | 1045 | 1050 | 1053 | 1078 | 1172 | 1071 | 1068 | 1068 | 1093 | 1041 | 1080 | 1236 | 1225 | 1162 | 1180 | 1228 | 1094 | 1213 | 1178 | 1070 | 1192 | 1213 | 1205 | 1199 | 1219 | 1088 | 1096 | 1055 | 1127 | 1129 | 1143 | 1100 | 1273 | 1254 | 1276 | 1102 | 1099 | 1158 | 1128 | 1134 | 1119 | 1086 | 1112 | 1134 | 1151 | 1139 | 1136 | 1130 | 1159 | 1241 | 1145 | 1160 | 1206 | 1086 | 1091 | 1121 | 1111 | 1111 | 1141 | 1122 | 1137 | 1113 | 1273 | 1133 | 1276 | 1220 | 1127 | 1221 | 1205 | 1170 | 1227 | 1248 | 1131 | 1111 | 1209 | 1225 | 1224 | 1106 | 1124 | 1149 | 1196 | 1115 | 1133 | 1187 | 1056 | 1073 | 1249 | 1246 | 1196 | 1201 | 1169 | 1005 | 1257 | 1192 | 1218 | 1160 | 1162 | 1151 | 1115 | 1153 | 1086 | 1258 | 1052 | 1262 | 1125 | 1043 | 1204 | 1224 | 1226 | 1123 | 1214 | 1121 | 1104 | 1092 | 1057 | 1081 | 1026 | 1078 | 1237 | 1065 | 1170 | 1182 | 1160 | 1021 | 1060 | 1165 | 1125 | 1026 | 1113 | 1086 | 1032 | 1125 | 1177 | 1277 | 1113 | 1008 | 1275 | 1139 | 1100 | 1140 | 1208 | 1252 | 1167 | 1255 | 1175 | 1170 | 1138 | 1028 | 1031 | 1011 | 1103 | 1133 | 1095 | 982 | 956 | 1106 |  |  | 997 | 765 | 1027 |  | 1171 | 1018 | 1076 | 1042 | 1078 | 1091 | 1086 | 1100 | 1112 | 1126 | 1136 | 1134 | 1183 | 1206 | 1255 | 1069 | 903 | 1052 | 760 | 912 | 1050 | 1151 | 1050 | 1061 | 1133 | 1092 | 1140 | 1083 | 950 | 1103 | 930 | 1010 | 965 |  | 1172 | 1170 | 931 | 1204 | 1032 |  |  | 1056 | 1032 | 1078 | 1153 | 1103 | 38 | 45.8 | 1.9 | 6.1 |  | 0 | 5.5 |  |  | 83171848.185 | 281686.886 | 56274614.128 | 61382.252 | 83976924.049 | 186398.997 | 60795693.149 | 55399.988 | 315333493.718 | 83305.997 | 72036.428 | 64.248 | 71106.822 | 10.057 | 72907.581 | 70.867 | 53021.611 | 12.751 | 268672.384 | 58.871 | 143068.945 | 268613.513 | 12 | 0 | 5.5 | 38 | 45.8 | 1.9 | 6.1 | 274076
2025-04-28 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1375.6 | 1331.9 |  | 1267.5 | 1366.8 | 1266.4 | 1274 | 1261.9 | 1255.4 | 1325.2 | 1314 | 1280.1 | 1260.3 | 1179.1 | 1207.8 | 1246.7 | 1208.7 | 1222.7 | 1364 | 1373.6 | 1286.6 | 1292.1 | 1403.3 | 1340.3 | 1382.2 | 1364.7 | 1361.8 | 1400.7 | 1344.6 | 1378.4 | 1239.3 | 1259.8 | 1154.4 | 1456.1 | 1099.5 | 1263.6 | 1258.1 | 1200.2 | 1264.1 | 1277.8 | 1210.7 | 1222.4 | 1262.5 | 1254.9 | 1249.1 | 1273.8 | 1386.9 | 1270.6 | 1258.1 | 1287.1 | 1222.1 | 1269.6 | 1401.5 | 1440.5 | 1367.4 | 1385.9 | 1442.9 | 1295.4 | 1421.2 | 1377.5 | 1261.4 | 1398 | 1265.7 | 1132.1 | 1370.1 | 1363.1 | 1386.9 | 1216.6 | 1251 | 1201.1 | 1267.4 | 1266.5 | 1284.2 | 1267.1 | 1471.6 | 1450.4 | 1459.5 | 1253.7 | 1242.1 | 1337.1 | 1270.1 | 1279.5 | 1265.2 | 1225.3 | 1252.5 | 1270.1 | 1289.3 | 1275.4 | 1272.8 | 1268 | 1323.4 | 1375 | 1296 | 1291.7 | 1328.4 | 1217.8 | 1235.5 | 1266.1 | 1255.9 | 1258.6 | 1291.2 | 1267.7 | 1287.9 | 1260.9 | 1405.5 | 1282.3 | 1385.6 | 1409.7 | 1286.1 | 1403.7 | 1373.7 | 1374.1 | 1421.3 | 1443.1 | 1284.1 | 1293.4 | 1405.1 | 1406.2 | 1401.9 | 1248.1 | 1281.5 | 1326.1 | 1364.2 | 1264.9 | 1282.2 | 1386.5 | 1179.3 | 1202.7 | 1400 | 1399.8 | 1343.1 | 1350.2 | 1306.9 | 1138 | 1440 | 1371.1 | 1387.3 | 1311.5 | 1306.5 | 1288.3 | 1247.4 | 1292.3 | 1223.2 | 1411.5 | 1183.6 | 1417.6 | 1264.1 | 1171.9 | 1353.6 | 1372.9 | 1378.7 | 1267 | 1369.3 | 1307 | 1246.5 | 1230.7 | 1235.5 | 1213.2 | 1147.1 | 1203.1 | 1378.6 | 1189.4 | 1309.9 | 1317.6 | 1279 | 1135.2 | 1187.9 | 1295.1 | 1251.3 | 1141.7 | 1242.5 | 1210.6 | 1149.4 | 1252.3 | 1430.2 | 1248.4 | 1255.6 | 1129.8 | 1427.7 | 1274.2 | 1230.7 | 1271.1 | 1351.6 | 1397.8 | 1309.4 | 1405.5 | 1317 | 1319.4 | 1268.8 | 1145.4 | 1160.7 | 1133.9 | 817 | 1180.2 | 1273.8 | 1122.8 | 1086.4 | 1302.2 |  |  | 1085.6 | 848.4 | 1175.3 |  | 1327.6 | 1157.3 | 1219.3 | 1188.2 | 1224.8 | 1233.6 | 1232.3 | 1244.3 | 1258.9 | 1291.9 | 1291.5 | 1297.9 | 1374.4 | 1438.4 | 1214.6 | 1021.2 | 930.5 | 574.8 | 862.5 | 1005.9 | 1163 | 1308.6 | 1171.9 | 1214.6 | 1224.5 | 1276 | 1307.2 | 1192.9 | 969.7 | 1106.5 | 977.5 | 1112.9 | 1065 |  | 1670.5 | 1313 | 512.6 | 1245 | 1200 |  |  | 1202.9 | 1173.9 | 738.9 | 1112 | 1012 | 38.9724 | 45.8338 | 2.2649 | 5.9 |  | 0 | 6.2 |  |  | 83254910.28 | 281723.886 | 56355236.306 | 61393.252 | 84058696.005 | 186454.997 | 60856040.738 | 55412 | 315638896.479 | 83366.997 | 83062.095 | 37 | 80622.178 | 11 | 81771.956 | 56 | 60347.589 | 12.012 | 305402.761 | 61 | 163636.273 | 305341.761 | 12 | 0 | 6.2 | 38.9724 | 45.8338 | 2.2649 | 5.9 | 306127.9
2025-04-29 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1407 | 1364 | 1308 | 1299 | 1396 | 1295 | 1302 | 1289 | 1283 | 1353 | 1343 | 1311 | 1290 | 1208 | 1234 | 1278 | 1238 | 1306 | 1394 | 1408 | 1318 | 1321 | 1439 | 1369 | 1414 | 1398 | 1394 | 1432 | 1371 | 1411 | 1264 | 1289 | 1177 | 1560 | 1117 | 1288 | 1290 | 1258 | 1293 | 1308 | 1254 | 1251 | 1291 | 1282 | 1301 | 1320 | 1437 | 1300 | 1289 | 1318 | 1255 | 1302 | 1445 | 1490 | 1397 | 1418 | 1475 | 1325 | 1458 | 1409 | 1294 | 1428 | 1299 | 1154 | 1404 | 1396 | 1421 | 1325 | 1281 | 1283 | 1299 | 1298 | 1311 | 1302 | 1504 | 1483 | 1495 | 1299 | 1279 | 1390 | 1331 | 1327 | 1298 | 1307 | 1302 | 1313 | 1322 | 1307 | 1302 | 1299 | 1354 | 1363 | 1329 | 1325 | 1399 | 1239 | 1270 | 1298 | 1290 | 1293 | 1324 | 1301 | 1326 | 1300 | 1447 | 1320 | 1601 | 1444 | 1320 | 1448 | 1410 | 1411 | 1485 | 1479 | 1314 | 1328 | 1440 | 1441 | 1437 | 1284 | 1319 | 1356 | 1401 | 1298 | 1316 | 1425 | 1210 | 1223 | 1428 | 1429 | 1373 | 1379 | 1327 | 1163 | 1471 | 1399 | 1477 | 1337 | 1338 | 1314 | 1267 | 1316 | 1149 | 1447 | 1214 | 1454 | 1290 | 1200 | 1386 | 1406 | 1414 | 1301 | 1486 | 1304 | 1280 | 1262 | 1280 | 1251 | 1173 | 1228 | 1410 | 1215 | 1339 | 1344 | 1293 | 1163 | 1208 | 1319 | 1277 | 1161 | 1262 | 1230 | 1168 | 1277 | 1465 | 1276 | 1286 | 1153 | 1462 | 1304 | 1259 | 1291 | 1383 | 1431 | 1339 | 1439 | 1347 | 1351 | 1292 | 1164 | 1191 | 1154 | 940 | 1209 | 1309 | 1169 | 1113 | 1336 |  |  | 1254 | 872 | 1182 |  | 1330 | 1255 | 1249 | 1214 | 1255 | 1264 | 1266 | 1278 | 1296 | 1326 | 1321 | 1331 | 1405 | 1472 | 1246 | 1040 | 951 | 688 | 894 | 1057 | 1334 | 1368 | 1323 | 1335 | 1230 | 1450 | 1381 | 1264 | 1022 | 1224 | 1031 | 1194 | 1031 |  | 1665 | 1195 | 520 | 1110 | 1142 |  |  | 1097 | 1225 | 798 | 1178 | 1099 | 40 | 46 | 2.1 | 5.1 |  | 0 | 6.38 |  |  | 83340164.309 | 281785 | 56438227.545 | 61405 | 84142145.623 | 186495 | 60919090.96 | 55425 | 315953204.4097 | 83421 | 85254.029 | 61.114 | 82991.239 | 11.748 | 83449.618 | 40.003 | 63050.222 | 13 | 314307.9307 | 54.003 | 168172.406 | 314253.9277 | 12 | 0 | 6.38 | 40 | 46 | 2.1 | 5.1 | 316090
2025-04-30 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1370.1 | 1329.7 | 1272 | 1262.9 | 1358.6 | 1260.8 | 1269.7 | 1256.5 | 1248.5 | 1318.5 | 1307.4 | 1276 | 1257.2 | 1174.6 | 1202 | 1245.6 | 1206.7 | 1273.1 | 1358.5 | 1372.7 | 1285.1 | 1286.5 | 1401 | 1437.3 | 1377.9 | 1359.5 | 1356.9 | 1396 | 1373.5 | 1376.2 | 1236.2 | 1321.7 | 1147.6 | 1524.4 | 1195.9 | 1253.7 | 1258.2 | 1233 | 1259.4 | 1275.4 | 1240.3 | 1227 | 1258.2 | 1248.8 | 1277.8 | 1306.8 | 1409.5 | 1266.1 | 1255.5 | 1283.7 | 1223.3 | 1276.8 | 1430.6 | 1472.1 | 1362.2 | 1168.5 | 1438.9 | 1289.9 | 1420.2 | 1430.4 | 1263.4 | 1393.4 | 1262.7 | 1126.5 | 1367.2 | 1359.2 | 1383.6 | 1270.4 | 1247.3 | 1249.6 | 1265.3 | 1263.7 | 1275.4 | 1266.9 | 1462.6 | 1441.3 | 1454.4 | 1267.1 | 1246.1 | 1350.9 | 1300.6 | 1295.4 | 1261.9 | 1271.6 | 1276.6 | 1302.5 | 1233.8 | 1278 | 1268.7 | 1263 | 1317.4 | 1342.6 | 1294 | 1289.4 | 1377.2 | 1205.9 | 1235.9 | 1264.7 | 1254 | 1257.2 | 1287.4 | 1264.1 | 1289.1 | 1262.8 | 1406.4 | 1281.9 | 1557.6 | 1405.2 | 1282.3 | 1407.4 | 1371.8 | 1371.3 | 1441.7 | 1438.3 | 1279.3 | 1290.8 | 1401.1 | 1403.5 | 1398 | 1249.3 | 1282.8 | 1322.6 | 1365 | 1262.9 | 1280.2 | 1385.9 | 1183.5 | 1195.2 | 1391.4 | 1394.1 | 1341.2 | 1346.8 | 1293.7 | 1133.4 | 1434.5 | 1363.4 | 1382 | 1301.8 | 1305.5 | 1283 | 1236.9 | 1285.4 | 1121.4 | 1411.4 | 1184.3 | 1372.9 | 1262.1 | 1170.8 | 1351.4 | 1372.4 | 1378.7 | 1269.9 | 1449.2 | 1270.6 | 1250.9 | 1230.9 | 1239.5 | 1221.7 | 1144 | 1197.3 | 1374.1 | 1186.7 | 1306.7 | 1310.3 | 1243.5 | 997.1 | 1200.4 | 1334.4 | 1252.2 | 1129.5 | 1237.7 | 1194.8 | 1173.4 | 1243.2 | 1427.4 | 1245.6 | 1256.1 | 1126.4 | 1445.2 | 1274.1 | 1244 | 1261.1 | 1350.8 | 1396.6 | 1307.9 | 1404.2 | 1313.1 | 1317 | 1256.5 | 1131.1 | 1157.1 | 1122.2 | 1101.1 | 1175.6 | 1272.5 | 1233.1 | 1082.5 | 1298.2 |  |  | 1087.1 | 847.8 | 1208.7 |  | 1321.5 | 1149.9 | 1215 | 1181.6 | 1220.6 | 1231.8 | 1232.5 | 1244.2 | 1261.8 | 1292.3 | 1285 | 1295 | 1365.3 | 1431.5 | 1213.7 | 1014.9 | 926 | 717.9 | 850.9 | 1006.8 | 1277.5 | 1392.3 | 1296.6 | 1308.2 | 1315.5 | 1365.5 | 1390.3 | 1312.7 | 976.6 | 1203 | 980.5 | 1152.8 | 1005.7 |  | 1645 | 1282.1 | 521.5 | 1192.2 | 1128 |  |  | 1190.8 | 1166.4 | 794.5 | 1121.6 | 1055.5 | 35.51 | 43.47 | 2.54 | 6.7 |  | 0 | 6.29 |  |  | 83423432.755 | 281823.456 | 56518786.828 | 61413.795 | 84223652.282 | 186538.509 | 60981207.812 | 55435.396 | 316260211.859 | 83464.615 | 83268.446 | 38.456 | 80559.283 | 8.795 | 81506.659 | 43.509 | 62116.852 | 10.396 | 307007.4493 | 43.615 | 163780.478 | 306963.8343 | 12 | 0 | 6.29 | 35.51 | 43.47 | 2.54 | 6.7 | 308834.9
2025-05-01 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 7:00 | 19:00 | 1312.3 | 1273.4 | 1219.5 | 1212.5 | 1304.8 | 1208.9 | 1214.3 | 1201.7 | 1215.7 | 1263 | 1251.2 | 1221.8 | 1201.9 | 1124.6 | 1183.3 | 1231.8 | 1181.6 | 1238.4 | 1305.5 | 1314.2 | 1241.1 | 1251.2 | 1375.2 | 1381.6 | 1319.7 | 1301.1 | 1300.8 | 1340.8 | 1326.2 | 1317.6 | 1312.2 | 1288.2 | 1119.2 | 1462.8 | 1145.2 | 1201 | 1203.7 | 1178.1 | 1205.3 | 1219.7 | 1184.7 | 1172.4 | 1204.6 | 1195.6 | 1223.5 | 1255.4 | 1349.6 | 1211.8 | 1213.2 | 1233.5 | 1176.1 | 1231.4 | 1380.8 | 1413.8 | 1307.8 | 1324.4 | 1375.3 | 1233.9 | 1386.7 | 1379.8 | 1206.9 | 1333.7 | 1201.6 | 1071.2 | 1364.9 | 1304.8 | 1323 | 1225.9 | 1193.3 | 1194.8 | 1210.8 | 1208.6 | 1220.3 | 1211.2 | 1398.2 | 1378 | 1389.4 | 1210 | 1190 | 1289.5 | 1243.2 | 1238.4 | 1206.8 | 1215.9 | 1221.6 | 1250.9 | 1184.8 | 1226.2 | 1211.6 | 1210.1 | 1262 | 1292.3 | 1236.7 | 1233 | 1313.5 | 1171.5 | 1180.2 | 1209.1 | 1198.3 | 1202.5 | 1231.2 | 1208.8 | 1233.6 | 1208.2 | 1344.6 | 1220.9 | 1490.8 | 1343 | 1226.5 | 1345.8 | 1312.3 | 1320.5 | 1388.2 | 1380.2 | 1222.8 | 1239.8 | 1345 | 1341.3 | 1334.2 | 1215.9 | 1249.2 | 1334.7 | 1316.7 | 1207.8 | 1224.5 | 1312.5 | 1159.3 | 1161.3 | 1330.4 | 1333.3 | 1275 | 1319.5 | 1268.4 | 1085.1 | 1375.1 | 1306.1 | 1326.1 | 1247 | 1251.9 | 1243.2 | 1185.4 | 1258.8 | 1077.4 | 1345.4 | 1136.4 | 1342.8 | 1223.8 | 1124.1 | 1292.6 | 1316 | 1319.7 | 1213.6 | 1386.9 | 1215.3 | 1195.7 | 1178.3 | 1181.3 | 1189.6 | 1119.4 | 1145.7 | 1317.8 | 1136.5 | 1249.2 | 1255 | 1282.6 | 1100.7 | 1173.7 | 1311.6 | 1221 | 1081.8 | 1193.7 | 1144.2 | 1233.4 | 1208.4 | 1367.2 | 1194.3 | 1249.5 | 1111.5 | 1415.5 | 1251.3 | 1230.2 | 1212 | 1294.6 | 1339.3 | 1251.8 | 1344.3 | 1264.4 | 1260.6 | 1201.5 | 1118.6 | 1151.3 | 1114.2 | 1063.2 | 1149.3 | 1227.5 | 1209.9 | 1036.9 | 1265.6 |  |  | 1042 | 813.4 | 1158.6 |  | 1268.2 | 1120.2 | 1167.2 | 1138.7 | 1175.2 | 1179 | 1181.3 | 1190.6 | 1209.3 | 1237.2 | 1228.2 | 1245.6 | 1306.2 | 1369.4 | 1163.3 | 971 | 886.5 | 707.1 | 899.1 | 1017.6 | 1254.2 | 1357.1 | 1263 | 1273.4 | 1277.6 | 1323.1 | 1356.2 | 1273.2 | 958.4 | 1180 | 960.6 | 1128.9 | 984.4 |  | 1578.1 | 1229.2 | 501.1 | 1143.4 | 1100.8 |  |  | 1139.3 | 1117.4 | 797.8 | 1080 | 1000.1 | 34.64 | 42.7 | 3.78 | 7.5 |  | 0 | 6.3 |  |  | 83503615.233 | 281835.466 | 56596133.071 | 61424 | 84302475.451 | 186580 | 61041530.906 | 55471.573 | 316556555.744 | 83487.6 | 80182.478 | 12.01 | 77346.243 | 10.205 | 78823.169 | 41.491 | 60323.094 | 36.177 | 296343.885 | 22.985 | 157506.506 | 296320.9 | 12 | 0 | 6.3 | 34.64 | 42.7 | 3.78 | 7.5 | 298175.2
2025-05-02 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 7:00 | 19:00 | 931.2 | 903.1 | 871.3 | 863.9 | 932.6 | 866.2 | 858.4 | 859.9 | 858.4 | 904.8 | 880.7 | 873 | 859.6 | 810.1 | 830.1 | 864.1 | 823.6 | 859 | 932.3 | 928.7 | 866.7 | 873.6 | 957.6 | 979.4 | 931.5 | 922.8 | 917.2 | 950.4 | 958 | 942.1 | 938.6 | 941.3 | 796.7 | 1105.3 | 832.4 | 859.7 | 857.5 | 837.6 | 845.6 | 850.7 | 840.1 | 822.2 | 843.6 | 836.8 | 854.1 | 887.4 | 934.1 | 846.8 | 856.7 | 877.3 | 833.9 | 854.3 | 952.1 | 975.8 | 926.8 | 942.8 | 971.1 | 859.2 | 969.6 | 985.1 | 858.5 | 970.4 | 853.5 | 879.4 | 932.7 | 917.8 | 933.3 | 899.7 | 845.2 | 842.2 | 854.9 | 853.4 | 863.3 | 855.4 | 970.7 | 556.1 | 988.2 | 836.9 | 827.3 | 915.9 | 857.9 | 855.8 | 849.7 | 857.1 | 850.1 | 861.4 | 873 | 861.5 | 854.8 | 850.3 | 887.9 | 924 | 874.2 | 871.9 | 930.6 | 836.2 | 825.7 | 868 | 839.1 | 848.4 | 871.1 | 843.6 | 869.9 | 853.6 | 955 | 863.4 | 1054.7 | 942.8 | 860.7 | 953.2 | 933.3 | 918.2 | 971.2 | 962.9 | 853 | 861 | 940.8 | 960.6 | 953.4 | 853.4 | 875.7 | 948 | 937.3 | 854.4 | 868 | 931.4 | 828.7 | 823.2 | 940.7 | 941.5 | 892.2 | 907.4 | 894.6 | 764.3 | 963.3 | 916.8 | 923.9 | 877.8 | 880.2 | 875.1 | 837.6 | 915.7 | 764.7 | 958 | 800.6 | 932.5 | 855 | 793.3 | 915.7 | 933.3 | 936.2 | 859.4 | 986.2 | 858.2 | 840.7 | 829.9 | 830.3 | 828.6 | 850.2 | 819.2 | 947 | 812.5 | 913.3 | 918.4 | 926.2 | 792.1 | 809.4 | 922.6 | 843.6 | 805.8 | 852.8 | 818.9 | 915.2 | 855.7 | 962 | 842 | 852.2 | 810.2 | 973.1 | 871.4 | 905.9 | 910.2 | 955.4 | 943.6 | 885.1 | 950.1 | 887.4 | 892.2 | 854.9 | 842.1 | 813.4 | 822.2 | 814.9 | 811.9 | 854.6 | 835.9 | 723 | 873.3 |  |  | 756.4 | 592.7 | 855 |  | 918.5 | 798.1 | 849.3 | 822.4 | 843.1 | 840.1 | 844.5 | 850.2 | 850.6 | 869.3 | 853.6 | 870.7 | 923.3 | 977.9 | 826.8 | 720.5 | 650.1 | 578.8 | 652.7 | 739.2 | 853.6 | 929.2 | 899.4 | 903.6 | 900.1 | 896.6 | 922 | 903.3 | 697.9 | 833 | 697 | 813.6 | 709.8 |  | 1101 | 870.2 | 347.6 | 802.5 | 775.1 |  |  | 822.7 | 853.1 | 565.1 | 767.8 | 725.4 | 26.59 | 33.02 | 3.03 | 7.7 |  | 0 | 4.16 |  |  | 83560630.704 | 281851.284 | 56650810.423 | 61437 | 84358523.571 | 186623 | 61084340.104 | 55483 | 316766786.327 | 83569.12 | 57015.471 | 15.818 | 54677.352 | 13 | 56048.12 | 43 | 42809.198 | 11.427 | 210230.583 | 81.52 | 111664.005 | 210149.063 | 12 | 0 | 4.16 | 26.59 | 33.02 | 3.03 | 7.7 | 211112
2025-05-03 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 7:00 | 19:00 | 1289.3 | 1249.1 | 1206.8 | 1201.5 | 1293.8 | 1199.4 | 1192.9 | 1196.8 | 1192 | 1253.4 | 1220.5 | 1214.9 | 1198.1 | 1129.2 | 1169 | 1198.8 | 1146.1 | 1194.5 | 1293.9 | 1289.1 | 1205.7 | 1209.7 | 1328.7 | 1356.4 | 1300.9 | 1283.5 | 1278.5 | 1325.8 | 1332.1 | 1319 | 1329.5 | 1320.7 | 1118.1 | 1541.2 | 1143.8 | 1212.9 | 1189.9 | 1167.9 | 1184.2 | 1197.9 | 1178 | 1158.2 | 1182 | 1175 | 1189.5 | 1202.2 | 1295.5 | 1184.4 | 1194.1 | 1191.6 | 1153.2 | 1196.7 | 1345.9 | 1351 | 1289.6 | 1309.6 | 1347.4 | 1206.4 | 1344.4 | 1361.1 | 1196.4 | 1350.5 | 1198.2 | 1193.1 | 1296.1 | 1276.2 | 1299.1 | 1230 | 1186.8 | 1177.7 | 1189.8 | 1189 | 1214.3 | 1194.2 | 1355.2 | 1345.4 | 1348.4 | 1170.3 | 1157.7 | 1269.3 | 1196.5 | 1195.7 | 1186.8 | 1196.7 | 1189.1 | 1197.4 | 1211.9 | 1196.7 | 1170.1 | 1183.2 | 1237.3 | 1286 | 1218.2 | 1214.1 | 1293.8 | 1142.4 | 1156.7 | 1199.4 | 1177.7 | 1188 | 1219.6 | 1182.4 | 1210.1 | 1189.9 | 1349.5 | 1199 | 1439 | 1322.9 | 1201.3 | 1320.5 | 1292.2 | 1279.3 | 1348.1 | 1341.1 | 1191.3 | 1200.8 | 1313.5 | 1329.2 | 1321.1 | 1186.1 | 1213.3 | 1313.3 | 1294.3 | 1189 | 1205.2 | 1332.5 | 1120.1 | 1138.5 | 1322 | 1319.3 | 1220 | 1266 | 1225.6 | 1069.4 | 1342.2 | 1283.7 | 1294.9 | 1228.1 | 1218.7 | 1208.8 | 1270.4 | 1266.2 | 1144.8 | 1324.4 | 1101.6 | 1337.3 | 1187 | 1101.5 | 1272.2 | 1297 | 1299.8 | 1192.7 | 1365.3 | 1229.3 | 1173.1 | 1159 | 1149.1 | 1155.4 | 1184 | 1146.8 | 1313.8 | 1142.7 | 1292.4 | 1273.5 | 1309.5 | 1114.1 | 1128.1 | 1290.4 | 1171 | 1125.9 | 1230 | 1147.2 | 1280.9 | 1199.6 | 1335.9 | 1173.5 | 1176.2 | 1112.6 | 1349.6 | 1177.8 | 1261.8 | 1278.6 | 1307.8 | 1303.5 | 1230.9 | 1325.6 | 1233.6 | 1214 | 1194.6 | 1174.7 | 1130 | 1123.8 | 1070.4 | 1127.1 | 1186.5 | 1159.8 | 1003.5 | 1207.9 |  |  | 1043.7 | 816.6 | 1173 |  | 1277.9 | 1096.1 | 1180.7 | 1151.8 | 1175.6 | 1182.4 | 1183.7 | 1192.1 | 1201.5 | 1216.8 | 1142.5 | 1211 | 1290.5 | 1361.9 | 1140.9 | 1007.7 | 905.2 | 800.1 | 873 | 1035.9 | 1200.2 | 1334.2 | 1251.6 | 1252.2 | 1204.6 | 1301.6 | 1330.7 | 1188 | 1012] | 1169.2 | 1018.8 | 1113 | 991 |  | 1356 | 1167.5 | 508 | 1089.3 | 1059.2 |  |  | 1206.8 | 1243.5 | 784.2 | 1015.6 | 931 | 27 | 31 | 3.1 | 5.9 |  | 0 | 5.85 |  |  | 83639719.132 | 281866.63 | 56726946.982 | 61457.096 | 84436429.55 | 186658.586 | 61144398.403 | 55497.082 | 317059642.463 | 83628.29 | 79088.428 | 15.346 | 76136.559 | 20.096 | 77905.979 | 35.586 | 60058.299 | 14.082 | 292856.136 | 59.17 | 155189.545 | 292796.966 | 12 | 0 | 5.85 | 27 | 31 | 3.1 | 5.9 | 293330
2025-05-04 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:29 | 6:20 | 1414 | 1371 | 1323 | 1318 | 1423 | 1316 | 1307 | 1328 | 1372 | 1383 | 1338 | 1345 | 1325 | 1244 | 1318 | 1312 | 1255 | 1310 | 1417 | 1417 | 1322 | 1326 | 1451 | 1484 | 1428 | 1409 | 1403 | 1453 | 1462 | 1442 | 1410 | 1444 | 1222 | 1617 | 1251 | 1328 | 1306 | 1292 | 1305 | 1321 | 1297 | 1282 | 1301 | 1294 | 1313 | 1332 | 1430 | 1303 | 1353 | 1331 | 1274 | 1328 | 1513 | 1498 | 1412 | 1436 | 1479 | 1321 | 1473 | 1494 | 1324 | 1483 | 1307 | 1304 | 1414 | 1395 | 1418 | 1310 | 1292 | 1286 | 1302 | 1299 | 1339 | 1308 | 1475 | 1398 | 1468 | 1276 | 1273 | 1376 | 1310 | 1313 | 1309 | 1320 | 1312 | 1326 | 1342 | 1325 | 1244 | 1290 | 1345 | 1378 | 1293 | 1341 | 1412 | 1269 | 1278 | 1328 | 1300 | 1317 | 1355 | 1312 | 1341 | 1316 | 1488 | 1328 | 1564 | 1444 | 1322 | 1455 | 1432 | 1387 | 1452 | 1463 | 1303 | 1298 | 1432 | 1453 | 1469 | 1306 | 1328 | 1423 | 1418 | 1300 | 1337 | 1433 | 1221 | 1245 | 1443 | 1443 | 1284 | 1389 | 1341 | 1168 | 1471 | 1404 | 1417 | 1382 | 1333 | 1322 | 1326 | 1378 | 1198 | 1450 | 1213 | 1464 | 1299 | 1207 | 1390 | 1414 | 1426 | 1306 | 1493 | 1308 | 1286 | 1267 | 1414 | 1234 | 1300 | 1253 | 1445 | 1247 | 1422 | 1408 | 1433 | 1217 | 1235 | 1409 | 1484 | 1233 | 1310 | 1251 | 1396 | 1312 | 1476 | 1291 | 1301 | 1222 | 1483 | 1322 | 1387 | 1407 | 1477 | 1446 | 1352 | 1459 | 1397 | 1364 | 1311 | 1294 | 1237 | 1237 | 1244 | 1317 | 1267 | 1278 | 1100 | 1276 |  |  | 1100 | 998 | 1396 |  | 1259 | 1313 | 1279 | 1312 | 1309 | 1316 | 1318 | 1328 | 1339 | 1252 | 1328 | 1411 | 1485 | 1378 | 1106 | 999 | 876 | 798 | 929 | 1114 | 1323 | 1434 | 1342 | 1342 | 1219 | 1310 | 1403 | 1393 | 1109 | 1285 | 1113 | 1207 | 1074 |  | 1410 | 1333 | 598 | 1246 | 1195 |  |  | 1339 | 1383 | 860 | 1126 | 1010 | 33.65 | 43.22 | 1.9 | 7.5 |  | 0 | 6.49 |  |  | 83726824.722 | 281882.851 | 56809802.29 | 61467.68 | 84521862.024 | 186707.953 | 61210236.424 | 55510.862 | 317380486.88 | 83692.452 | 87105.59 | 16.221 | 82855.308 | 10.584 | 85432.474 | 49.367 | 65838.021 | 13.78 | 320844.417 | 64.162 | 169934.093 | 320780.255 | 12 | 0 | 6.49 | 33.65 | 43.22 | 1.9 | 7.5 | 322757
2025-05-05 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:32 | 18:17 | 927.5 | 900.4 | 867.5 | 865.8 | 933.3 | 861.3 | 868.1 | 864.7 | 893.3 | 901.5 | 877.5 | 875.4 | 862.5 | 811.6 | 856.7 | 854.1 | 822.7 | 856.2 | 925 | 925.5 | 861.6 | 857.7 | 944.4 | 962.7 | 929.6 | 912.4 | 907.1 | 942.3 | 942.5 | 935.4 | 929.5 | 934.9 | 805.9 | 1065.4 | 841.4 | 938.1 | 861.6 | 853.1 | 864.9 | 874.9 | 859.6 | 846.8 | 863.1 | 855.8 | 871.8 | 878.3 | 946.8 | 865.7 | 899.4 | 884.6 | 842 | 871.8 | 994.1 | 984.5 | 931.7 | 942.5 | 984 | 868.7 | 968.1 | 978.7 | 873.6 | 976.5 | 870 | 847 | 931.4 | 918.7 | 934.7 | 905 | 855.6 | 779 | 861.2 | 860 | 877.9 | 861.5 | 965.7 | 1001.5 | 960 | 834.2 | 832.7 | 922.6 | 867.9 | 865.1 | 861.8 | 864.7 | 864.7 | 871.3 | 880.1 | 868.5 | 874.1 | 855.7 | 888.1 | 934.6 | 870.2 | 879 | 932.5 | 821.7 | 835.9 | 866.3 | 857.2 | 853.5 | 885.5 | 860.4 | 880 | 862.8 | 979.2 | 867.2 | 1019 | 954.6 | 872 | 962.1 | 938.8 | 892.7 | 955.7 | 962.7 | 858.7 | 863.7 | 946.7 | 956.3 | 960.4 | 859.3 | 875.6 | 938.8 | 934.6 | 856.3 | 872 | 940.1 | 834.3 | 835.1 | 941.9 | 945.2 | 901.7 | 908.1 | 905.2 | 768.3 | 962.4 | 926.3 | 931.2 | 879.7 | 876 | 858.2 | 832.5 | 903.3 | 769.1 | 947.7 | 783.9 | 924.6 | 846.4 | 785.7 | 906.4 | 923.7 | 930.3 | 853.5 | 945.6 | 861.8 | 850.5 | 831.1 | 827.7 | 810.9 | 850.9 | 817.6 | 959.3 | 830.1 | 951.6 | 922.6 | 953.3 | 791.8 | 806 | 919.7 | 839.3 | 804.3 | 826.6 | 816.5 | 909.2 | 853.8 | 977.1 | 845.9 | 949.1 | 796.3 | 974 | 864.5 | 905.7 | 917.4 | 975.6 | 952.9 | 890.1 | 972.6 | 884 | 892 | 858.8 | 792.6 | 797.5 | 780.6 | 773.3 | 807.5 | 852.7 | 818.4 | 710.3 | 859.8 |  |  | 782.6 | 541.4 | 827 |  | 917.1 | 765.1 | 854.3 | 827.3 | 854.2 | 860.3 | 862.9 | 866 | 868.7 | 876.1 | 809.1 | 865 | 926 | 940.2 | 807 | 718.3 | 644.6 | 568.5 | 623.4 | 749.5 | 893 | 957.9 | 881.2 | 888.7 | 810.5 | 931.4 | 913.5 | 913.6 | 727.1 | 857.6 | 736 | 814.6 | 719.9 |  | 1139.9 | 868.9 | 397.2 | 813.4 | 780.9 |  |  | 870.2 | 900.7 | 568 | 748.4 | 741.8 | 27.91 | 34.01 | 2.69 | 9.1 |  | 0 | 4.14 |  |  | 83784058.891 | 281898.851 | 56864716.575 | 61479.68 | 84577882.491 | 186757.953 | 61253729.251 | 55528.862 | 317591883.672 | 83756.214 | 57234.169 | 16 | 54914.285 | 12 | 56020.467 | 50 | 43492.827 | 18 | 211396.792 | 63.762 | 112120.454 | 211333.03 | 12 | 0 | 4.14 | 27.91 | 34.01 | 2.69 | 9.1 | 212087.7
2025-05-06 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:09 | 18:24 | 1403.8 | 1413.5 | 1314.9 | 1308.9 | 1410.1 | 1303.3 | 1310.6 | 1311.6 | 1353.5 | 1366.1 | 1332.4 | 1325.1 | 1304.5 | 1228.6 | 1307.5 | 1301.2 | 1245.2 | 1296.6 | 1404.3 | 1402.9 | 1308.5 | 1313.6 | 1436.6 | 1472.5 | 1414.1 | 1396.7 | 1389 | 1443.5 | 1454.8 | 1436.5 | 1441.5 | 1444.8 | 1194.9 | 1567 | 1227 | 1395.6 | 1263.4 | 1244 | 1259.7 | 1274.3 | 1252.8 | 1234.1 | 1255.7 | 1249.6 | 1265.9 | 1281.6 | 1375.4 | 1255.4 | 1315.2 | 1293.1 | 1271.4 | 1271.1 | 1450.2 | 1438.1 | 1367.7 | 1386.7 | 1441.3 | 1281.4 | 1425.5 | 1444.7 | 1272.1 | 1440.2 | 1267.6 | 1257.9 | 1413.7 | 1402.1 | 1417.7 | 1425.8 | 1296.2 | 1301.1 | 1302.6 | 1300.7 | 1325.2 | 1301.2 | 1466.2 | 1471.5 | 1466.8 | 1273 | 1266.2 | 1372.6 | 1308.7 | 1310.1 | 1303.2 | 1314.7 | 1304.8 | 1314.8 | 1326.9 | 1306.7 | 1303.7 | 1293.1 | 1353.9 | 1361.2 | 1338.1 | 1328.8 | 1440.5 | 1302.3 | 1300.4 | 1311.9 | 1293.1 | 1300 | 1336.8 | 1298.7 | 1325.5 | 1300.7 | 1471.5 | 1312.1 | 1549.1 | 1447 | 1316.4 | 1449 | 1413.9 | 1390.2 | 1451.9 | 1462.6 | 1304.1 | 1279.5 | 1434.5 | 1450.8 | 1447.2 | 1297.4 | 1322.4 | 1418.2 | 1413.1 | 1301.5 | 1315.9 | 1430.4 | 1293.6 | 1304.5 | 1439 | 1438.6 | 1378.9 | 1382.6 | 1371.2 | 1162.9 | 1467.7 | 1403.3 | 1416.6 | 1389.7 | 1382.2 | 1308.4 | 1273.9 | 1380.2 | 1251.2 | 1440.9 | 1203 | 1455.7 | 1289.4 | 1201.9 | 1385.2 | 1409.6 | 1418.3 | 1302.6 | 1487.8 | 1302.6 | 1283.3 | 1264.8 | 1265.8 | 1278.5 | 1297.5 | 1245.9 | 1447.9 | 1248.1 | 1430.6 | 1407 | 1446.5 | 1221.8 | 1240.3 | 1407.2 | 1286.3 | 1236 | 1275.7 | 1250.8 | 1410.3 | 1312.7 | 1474 | 1289.1 | 1300 | 1240 | 1482.5 | 1347.2 | 1158.1 | 1417.2 | 1455.7 | 1425 | 1373.1 | 1458.3 | 1355.8 | 1364.2 | 1315.5 | 1208 | 1247.6 | 1245.6 | 1187.9 | 1242.6 | 1240.2 | 1201.3 | 1096.7 | 1308.8 |  |  | 1003.4 | 873 | 1292.1 |  | 1388.3 | 1193.3 | 1262.9 | 1265.2 | 1289.4 | 1296.9 | 1297.1 | 1304.3 | 1307.7 | 1322.8 | 1256.6 | 1324.7 | 1469.7 | 1490.2 | 1224.9 | 1125.6 | 1010.6 | 863 | 956 | 1142.8 | 1360.1 | 1464.9 | 1381.8 | 1375 | 1345.5 | 1379.2 | 1398.4 | 1436 | 1153.8 | 1297.7 | 1165.3 | 1243.2 | 1020.2 |  | 1693.2 | 1313.9 | 541.4 | 1226.2 | 1187.7 |  |  | 1308.4 | 1371.1 | 878 | 1167.9 | 980.5 | 30.59 | 43.32 | 1.89 | 5.1 |  | 0 | 6.31 |  |  | 83869638.121 | 281921.136 | 56947478.718 | 61523.885 | 84663181.628 | 186809.826 | 61320152.131 | 55583.377 | 317911517.35 | 83859.522 | 85579.23 | 22.285 | 82762.143 | 44.205 | 85299.137 | 51.873 | 66422.88 | 54.515 | 319633.678 | 103.308 | 168274.883 | 319530.37 | 12.25 | 0 | 6.31 | 30.59 | 43.32 | 1.89 | 5.1 | 321279.5
2025-05-07 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:56 | 18:30 | 885.8 | 892.1 | 827.8 | 823.8 | 893.8 | 825.8 | 830.3 | 830.1 | 853.1 | 859.5 | 841.9 | 838.3 | 826 | 774.2 | 826.5 | 820 | 789.5 | 823.8 | 887.6 | 889.3 | 831.4 | 828.9 | 903.4 | 926.9 | 898.9 | 887 | 878.9 | 910.3 | 917 | 906.8 | 915.2 | 911.1 | 783.6 | 1023.8 | 803.4 | 911.6 | 824.3 | 811.5 | 823.4 | 831.1 | 821.8 | 815.1 | 821.1 | 818.2 | 828.3 | 837.8 | 894.5 | 821 | 855.9 | 841 | 827.1 | 829.8 | 945 | 939.6 | 893.5 | 904.3 | 8938.5 | 834.2 | 928.3 | 938 | 829.6 | 935.9 | 823.9 | 802 | 899.7 | 893.5 | 902.7 | 907.1 | 822.4 | 826.2 | 828.1 | 825.1 | 846.8 | 831.8 | 936.3 | 906.7 | 935.2 | 814.4 | 810.6 | 873.7 | 832.3 | 833.7 | 828.4 | 836.8 | 828.3 | 834.5 | 840.6 | 829.4 | 826 | 819.5 | 859 | 886.2 | 848.2 | 846 | 927.8 | 808.3 | 813 | 841 | 830.9 | 834.7 | 855.8 | 830.4 | 847 | 832.2 | 944.2 | 834.5 | 976.5 | 926.8 | 841.1 | 923.6 | 898.6 | 892.3 | 922.1 | 936.1 | 833.4 | 769.8 | 921.9 | 920.6 | 922.6 | 825.2 | 842.6 | 905.4 | 897.4 | 828.5 | 838.9 | 908.3 | 790.9 | 794.6 | 921.3 | 921 | 887.2 | 881.1 | 850.2 | 739.3 | 934.2 | 900.2 | 906.4 | 892.9 | 877.6 | 833.8 | 809.8 | 870.8 | 806.8 | 916.2 | 761.5 | 927 | 822 | 764.7 | 880.6 | 894.9 | 905.1 | 829.3 | 944.3 | 831.7 | 819.2 | 807.9 | 811.5 | 798.2 | 827 | 794.8 | 921 | 800.1 | 917.5 | 895.3 | 927.4 | 778.1 | 796.7 | 905.9 | 825.9 | 799.9 | 822.3 | 801.1 | 842.2 | 842.2 | 938.5 | 822.5 | 828.4 | 814 | 947.5 | 838.5 | 888.2 | 899 | 935.7 | 907 | 898.4 | 933.3 | 863.8 | 866.7 | 838 | 781 | 801.2 | 790.5 | 672.9 | 820.1 | 791.5 | 818.9 | 704.5 | 841.5 |  |  | 655.5 | 564.5 | 823.2 |  | 888.2 | 772.5 | 810.3 | 802.6 | 825.6 | 821.9 | 825.6 | 824.1 | 836.2 | 841 | 823.7 | 847.3 | 938.8 | 954.2 | 776.4 | 741.3 | 600.2 | 500 | 607.2 | 725.5 | 870.8 | 931.8 | 866.6 | 869.3 | 881.5 | 869.5 | 891 | 900 | 722 | 827.9 | 735.5 | 788.2 | 670.9 |  | 1075.5 | 835.5 | 376.2 | 779.5 | 750 |  |  | 832.7 | 873.8 | 562.1 | 744.1 | 610.1 | 26.11 | 40.91 | 2.1 | 4.9 |  | 0 | 5.46 |  |  | 83924495.221 | 281921.743 | 56999990.355 | 61559.483 | 84717738.397 | 186820.499 | 61362560.511 | 55627.81 | 318115576.327 | 83861.638 | 54857.1 | 0.607 | 52511.637 | 35.598 | 54556.769 | 10.673 | 42408.38 | 44.433 | 204058.977 | 2.116 | 107332.532 | 204056.861 | 12.5667 | 0 | 5.46 | 26.11 | 40.91 | 2.1 | 4.9 | 213164.2
2025-05-08 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:13 | 18:40 | 1281 | 1291 | 1205 | 1195 | 1300 | 1200 | 1210 | 1210 | 1254 | 1264 | 1226 | 1219 | 1202 | 1133 | 1205 | 1201 | 1148 | 1195 | 1302 | 1294 | 1207 | 1215 | 1329 | 1366 | 1307 | 1291 | 1288 | 1340 | 1349 | 1334 | 1310 | 1342 | 1147 | 934 | 1180 | 1340 | 1213 | 1190 | 1202 | 1208 | 1202 |  | 1205 | 1201 | 1215 | 1217 | 1310 | 1201 | 1240 | 1217 | 1200 | 1200 | 1370 | 1360 | 1299 | 1306 | 1367 | 1212 | 1351 | 1375 | 1212 | 1361 | 1276 | 1098 | 1382 | 1374 | 1383 | 1230 | 1280 | 1283 | 1291 | 1248 | 1335 | 1275 | 1433 | 1402 | 1436 | 1258 | 1259 | 1340 | 1304 | 1302 | 1288 | 1303 | 1296 | 1294 | 1300 | 1275 | 1266 | 1265 | 1301 | 1210 | 1312 | 1321 | 1398 | 1266 | 1263 | 1312 | 1285 | 1298 | 1330 | 1288 | 1315 | 1297 | 1447 | 1303 | 1513 | 1432 | 1308 | 1413 | 1404 | 1380 | 1422 | 1306 | 1188 | 1404 | 1420 | 1424 | 1286 | 1304 | 1377 | 1389 | 1296 | 1317 | 1298 | 1410 | 1062 | 1099 | 1270 | 1273 | 1135 | 1225 | 1175 | 1039 | 1316 | 1270 | 1271 | 1254 | 1237 | 1173 | 1123 | 1227 | 1120 | 1289 | 1078 | 1255 | 1155 | 1074 | 1225 | 1254 | 1255 | 1155 | 1322 | 1160 | 1145 | 1123 | 1110 | 1131 | 1096 | 1198 | 1152 | 1341 | 1155 | 1318 | 1301 | 1228 | 1025 | 1150 | 1062 | 1150 | 1062 | 1192 | 1301 | 1217 | 1360 | 1189 | 1199 | 1173 | 1369 | 1215 | 1284 | 1310 | 1343 | 1316 | 1299 | 1347 | 1251 | 1258 | 1215 | 1224 | 1269 | 1261 | 1248 | 1276 | 1234 | 1277 | 1098 | 1304 |  |  | 1140 | 879 | 1284 |  | 1373 | 1206 | 1282 | 1249 | 1280 | 1286 | 1284 | 1292 | 1297 | 1299 | 1308 | 1440 | 1463 | 1193 | 1143 | 1198 | 1010 | 810 | 944 | 1128 | 1348 | 1440 | 1374 | 1368 | 1310 | 1346 | 1385 | 1423 | 1151 | 1294 | 1159 | 1230 | 1048 |  | 1175 | 1310 | 587 | 810 | 1164 |  |  | 1278 | 1337 | 864 | 1161 | 990 | 31.23 | 40.22 | 2.05 | 7.9 |  | 0 | 6.54 |  |  | 84038086.452 | 281938.345 | 57081493.737 | 61571.092 | 84794945.871 | 186840 | 61428667.418 | 55643.599 | 318419804.813 | 83928.17 | 113591.231 | 16.602 | 81503.382 | 11.609 | 77207.474 | 19.501 | 66106.907 | 15.789 | 304228.486 | 66.532 | 195066.402 | 304161.954 | 12.45 | 0 | 6.54 | 31.23 | 40.22 | 2.05 | 7.9 | 302578
2025-05-09 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:15 | 18:24 | 1446 | 1459 | 1359 | 1353 | 1466 | 1363 | 1364 | 1366 | 1414 | 1430 | 1380 | 1376 | 1358 | 1282 | 1358 | 1354 | 1278 | 1310 | 1396 | 1408 | 1309 | 1316 | 1478 | 1478 | 1415 | 1410 | 1393 | 1452 | 1457 | 1439 | 1498 | 1468 | 1272 | 1637 | 1315 | 1482 | 1336 | 1315 | 1340 | 1354 | 1329 | 1314 | 1336 | 1332 | 1347 | 1355 | 1431 | 1343 | 1399 | 1373 | 1349 | 1343 | 1532 | 1520 | 1460 | 1473 | 1541 | 1363 | 1512 | 1533 | 1346 | 1523 | 1378 | 1363 | 1447 | 1432 | 1455 | 1219 | 1326 | 1328 | 1346 | 1349 | 1361 | 1308 | 1495 | 1455 | 1500 | 1308 | 1302 | 1367 | 1355 | 1352 | 1339 | 1347 | 1350 | 1351 | 1365 | 1344 | 1352 | 1340 | 1388 | 1310 | 1373 | 1365 | 1410 | 1290 | 1296 | 1344 | 1318 | 1331 | 1362 | 1320 | 1347 | 1329 | 1498 | 1233 | 1557 | 1478 | 1350 | 1446 | 1446 | 1405 | 1461 | 1492 | 1343 | 1203 | 1457 | 1478 | 1475 | 1319 | 1350 | 1395 | 1447 | 1336 | 1349 | 1463 | 1239 | 1271 | 1464 | 1469 | 1307 | 1419 | 1370 | 1201 | 1503 | 1450 | 1449 | 1431 | 1406 | 1334 | 1307 | 1400 | 1278 | 1463 | 1224 | 1427 | 1316 | 1225 | 1401 | 1426 | 1433 | 1321 | 1515 | 1322 | 1305 | 1288 | 1278 | 1255 | 1353 | 1301 | 1510 | 1305 | 1491 | 1467 | 1393 | 1163 | 1303 | 1206 | 1344 | 1314 | 1346 | 1317 | 1480 | 1387 | 1528 | 1339 | 1342 | 1321 | 1542 | 1368 | 1445 | 1472 | 1516 | 1482 | 1465 | 1520 | 1401 | 1409 | 1370 | 1377 | 1298 | 1286 | 1268 | 1307 | 1268 | 1312 | 1134 | 1364 |  |  | 1121 | 914 | 1338 |  | 1436 | 1271 | 1312 | 1286 | 1309 | 1315 | 1320 | 1322 | 1358 | 1363 | 1346 | 1349 | 1493 | 1519 | 1243 | 1199 | 1095 | 870 | 921 | 1096 | 1308 | 1397 | 1328 | 1320 | 1390 | 1410 | 1341 | 1375 | 1106 | 1251 | 1115 | 1188 | 1014 |  | 1175 | 1378 | 518 | 1228 | 1193 |  |  | 1310 | 1318 | 1382 | 898 | 1184 | 32.39 | 43.99 | 1.81 | 7.1 |  | 0 | 6.68 |  |  | 84093096.913 | 281952.252 | 57165631.997 | 61582.723 | 84882994.442 | 186889.538 | 61495600.917 | 55657.622 | 318747693.799 | 83981.736 | 55010.461 | 13.907 | 84138.26 | 11.631 | 88048.571 | 49.538 | 66933.499 | 14.023 | 327888.986 | 53.566 | 139123.183 | 327835.42 | 12.15 | 0 | 6.68 | 32.39 | 43.99 | 1.81 | 7.1 | 328786
2025-05-10 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:05 | 18:10 | 1244 | 1254.3 | 1165.3 | 1160.2 | 1256.7 | 1160.3 | 1168 | 1168.3 | 1205.5 | 1214.9 | 1188.9 | 1182.5 | 1164.5 | 1096.4 | 1132.6 | 1156.7 | 1106.2 | 1147.7 | 1238.9 | 1238.4 | 1159.3 | 1159.3 | 1271.1 | 1298.5 | 1254.6 | 1234.5 | 1126.4 | 1274 | 1282.3 | 1265.1 | 1165.3 | 1268.6 | 1087.3 | 1415.9 | 1124.9 | 1263 | 1151.4 | 1137.4 | 1155.6 | 1167.69 | 1147.9 | 1136.2 | 1105.1 | 1147 | 1160.3 | 1166.2 | 1257.8 | 1152.9 | 1203.5 | 1181.8 | 1161.3 | 1159.6 | 1322.3 | 1312.3 | 1251.7 | 1267.5 | 1320.6 | 1175.8 | 1298.7 | 1306.9 | 1167.8 | 1306.9 | 1162.3 | 1135.6 | 1256.3 | 1247.3 | 1260.1 | 1098.3 | 1142.6 | 1151.7 | 1161.1 | 1157.4 | 1177.9 | 1141.5 | 1300.3 | 1270.6 | 1302.9 | 1125.8 | 1123.6 | 1200 | 1165.9 | 1163.9 | 1152.3 | 1162.6 | 1161.6 | 1172.7 | 1155.6 | 1158.3 | 1148 | 1192.9 | 824.9 | 1182.1 | 1177.4125 | 1251 | 1321 | 1115.3 | 1124.7 | 1169.6 | 1150.2 | 1158.2 | 1186.3 | 1153.6 | 1174.7 | 1157.7 | 1314.9 | 1158.2 | 1376.2 | 1288.7 | 1171.4 | 1269.2 | 1257.1 | 1225.4 | 1278.2 | 1296.8 | 1165.9 | 1104.5 | 1269.3 | 1288.6 | 1285.6 | 1154.6 | 1177 | 1228.7 | 1259.4 | 1161.8 | 1171.6 | 1270.3 | 1069.6 | 1097 | 1268.2 | 1218.6 | 1123.9 | 1216.7 | 1168 | 1026.6 | 1289.9 | 1238.2 | 1244.4 | 1113.4 | 1209.9 | 1147.6 | 1117 | 1209.3 | 1103.1 | 1263.5 | 1055.1 | 1233.9 | 1136.2 | 1058.9 | 1223.96 | 1247 | 1251.2 | 1148 | 1319.4 | 1174 | 1147.8 | 1133.2 | 1118.9 | 1080.6 | 1138.5 | 1091.3 | 1268.4 | 1097.6 | 1252.7 | 1226.8 | 1168.3 | 968.2 | 1095.5 | 1000.2 | 1135.5 | 1109.6 | 1132.3 | 1110.7 | 1247.3 | 1165.4 | 1237.6 | 1124.6 | 1135.9 | 1113.6 | 1303 | 1152.4 | 1219.3 | 1248.1 | 1270.3 | 1241.8 | 1231.6 | 1275 | 1168.1. | 1189.5 | 1160.8 | 1166 | 1143.9 | 1122.8 | 1110.4 | 1167.4 | 1107.1 | 1165.4 | 981.4 | 1187.6 |  |  | 1005.6 | 799.5 | 1161.9 |  | 1251.2 | 1109.4 | 1165.2 | 1124.7 | 1159.6 | 1162.3 | 1180.1 | 1170 | 1181.4 | 1184.2 | 1166.9 | 1176.4 | 1298.7 | 1317 | 1079.4 | 1041.1 | 998 | 962 | 821 | 975.7 | 1168.2 | 1246.7 | 1180.3 | 1177.9 | 1306 | 1256.3 | 1200.1 | 1220.7 | 974.6 | 1112 | 988.4 | 1059.3 | 901 |  | 1175.1 | 1290 | 520 | 1198 | 1075.2 |  |  | 1280 | 1150.9 | 1204 | 766 | 1020.1 | 29.02 | 40.1 | 1.6 | 5.4 |  | 0 | 5.78 |  |  | 84170081.762 | 281964.316 | 57238934.706 | 61593.285 | 84958087.189 | 186920.646 | 61554663.804 | 55671.488 | 319031987.79 | 84029.622 | 76984.849 | 12.064 | 73302.709 | 10.562 | 75092.747 | 31.108 | 59062.887 | 13.866 | 284293.991 | 47.886 | 150264.932 | 284246.105 | 12.0833 | 0 | 5.78 | 29.02 | 40.1 | 1.6 | 5.4 | 283650.6625
2025-05-11 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:48 | 18:15 | 1468 | 1482 | 1375 | 1367 | 1475 | 1366 | 1372 | 1375 | 1420 | 1431 | 1398 | 1394 | 1373 | 1294 | 1376 | 1370 | 1312 | 1367 | 1475 | 1477 | 1380 | 1382 | 1513 | 1545 | 1489 | 1468 | 1461 | 1514 | 1525 | 1510 | 1440 | 1517 | 1272 | 1668 | 1313 | 1482 | 1363 | 1341 | 1356 | 1370 | 1352 | 1336 | 1292 | 1344 | 1362 | 1374 | 1481 | 1352 | 1416 | 1392 | 1368 | 1366 | 1555 | 1543 | 1468 | 1490 | 1550 | 1383 | 1539 | 1557 | 1373 | 1546 | 1310 | 1310 | 1482 | 1472 | 1491 | 1328 | 1360 | 1355 | 1366 | 1361 | 1384 | 1370 | 1545 | 1495 | 1538 | 1319 | 1313 | 1439 | 1365 | 1366 | 1356 | 1395 | 1363 | 1369 | 1384 | 1364 | 1364 | 1351 | 1417 | 1310 | 1391 | 1384 | 1478 | 1308 | 1319 | 1376 | 1355 | 1364 | 1399 | 1363 | 1384 | 1363 | 1560 | 1374 | 1638 | 1525 | 1386 | 1560 | 1491 | 1471 | 1537 | 1538 | 1371 | 1387 | 1514 | 1547 | 1534 | 1376 | 1396 | 1482 | 1497 | 1377 | 1385 | 1460 | 1264 | 1310 | 1503 | 1452 | 1333 | 1442 | 1375 | 1217 | 1533 | 1465 | 1478 | 1458 | 1439 | 1371 | 1319 | 1420 | 1313 | 1502 | 1266 | 1520 | 1351 | 1258 | 1474 | 1482 | 1496 | 1370 | 1576 | 1375 | 1357 | 1341 | 1310 | 1276 | 1358 | 1304 | 1512 | 1254 | 1487 | 1464 | 1504 | 1329 | 1298 | 1311 | 1350 | 1313 | 1340 | 1308 | 1478 | 1383 | 1476 | 1341 | 1357 | 1325 | 1512 | 1357 | 1471 | 1473 | 1515 | 1482 | 1469 | 1518 | 1410 | 1418 | 1374 | 1374 | 1356 | 1344 | 1227 | 1379 | 1307 | 1378 | 1156 | 1405 |  |  | 1177 | 926 | 1377 |  | 1488 | 1314 | 1378 | 1342 | 1373 | 1372 | 1392 | 1381 | 1393 | 1414 | 1382 | 1388 | 1546 | 1576 | 1281 | 1236 | 1278 | 1263 | 1105 | 1196 | 1429 | 1541 | 1465 | 1453 | 1410 | 1478 | 1475 | 1517 | 1220 | 1360 | 1234 | 1305 | 1107 |  | 1350 | 1398 | 587 | 1280 | 1281 |  |  | 1230 | 1319 | 1369 | 1436 | 1226 | 31.8 | 43.4 | 1.5 | 4.8 |  | 0 | 6.7 |  |  | 84260905.719 | 281980.514 | 57325630.313 | 61632.383 | 85046238.548 | 186946.059 | 61625296.528 | 55720.302 | 319368171.542 | 84092.853 | 90823.957 | 16.198 | 86695.607 | 39.098 | 88151.359 | 25.413 | 70632.724 | 48.814 | 336183.752 | 63.231 | 177464.268 | 336120.521 | 12.45 | 0 | 6.7 | 31.8 | 43.4 | 1.5 | 4.8 | 338732
2025-05-12 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:13 | 18:32 | 1500 | 1512 | 1401 | 1395 | 1502 | 1392 | 1401 | 1403 | 1446 | 1460 | 1427 | 1422 | 1401 | 1319 | 1392 | 1394 | 1336 | 1393 | 1508 | 1511 | 1401 | 1409 | 1539 | 1579 | 1522 | 1502 | 1496 | 1550 | 1565 | 1542 | 1425 | 1552 | 1305 | 1702 | 1347 | 1517 | 1391 | 1371 | 1388 | 1401 | 1380 | 1354 | 1323 | 1377 | 1391 | 1404 | 1511 | 1381 | 1444 | 1421 | 1394 | 1393 | 1585 | 1576 | 1500 | 1516 | 1579 | 1412 | 1568 | 1590 | 1401 | 1577 | 1391 | 1370 | 1518 | 1508 | 1526 | 1350 | 1385 | 1388 | 1397 | 1393 | 1415 | 1396 | 1590 | 1545 | 1583 | 1350 | 1342 | 1452 | 1397 | 1397 | 1387 | 1397 | 1386 | 1399 | 1413 | 1394 | 1393 | 1379 | 1447 | 1356 | 1423 | 1416 | 1543 | 1342 | 1351 | 1408 | 1388 | 1396 | 1436 | 1395 | 1424 | 1396 | 1599 | 1413 | 1674 | 1560 | 1417 | 1556 | 1528 | 1499 | 1541 | 1576 | 1404 | 1301 | 1548 | 1585 | 1574 | 1413 | 1430 | 1512 | 1534 | 1409 | 1419 | 1548 | 1346 | 1367 | 1563 | 1495 | 1364 | 1474 | 1408 | 1244 | 1570 | 1501 | 1512 | 1481 | 1474 | 1406 | 1350 | 1455 | 1345 | 1539 | 1367 | 1555 | 1387 | 1291 | 1511 | 1520 | 1533 | 1405 | 1615 | 1410 | 1389 | 1375 | 1328 | 1307 | 1393 | 1341 | 1552 | 1283 | 1525 | 1498 | 1539 | 1297 | 1323 | 1518 | 1375 | 1339 | 1352 | 1334 | 1504 | 1410 | 1517 | 1377 | 1389 | 1355 | 1524 | 1405 | 1486 | 1504 | 1551 | 1517 | 1507 | 1497 | 1447 | 1455 | 1400 | 1404 | 1392 | 1386 | 1362 | 1413 | 1340 | 1411 | 1185 | 1437 |  |  | 1205 | 980 | 1409 |  | 1520 | 1343 | 1414 | 1378 | 1406 | 1405 | 1423 | 1414 | 1424 | 1444 | 1415 | 1422 | 1582 | 1611 | 1305 | 1266 | 1095 | 919 | 1130 | 1185 | 1420 | 1519 | 1458 | 1460 | 1450 | 1478 | 1463 | 1511 | 1212 | 1357 | 1226 | 1290 | 1097 |  | 1520 | 1368 | 534 | 1280 | 1400 |  |  | 1470 | 1312 | 1335 | 1415 | 1422 | 35.13 | 43.88 | 1.88 | 7.3 |  | 0 | 6.85 |  |  | 84353521.617 | 281995.734 | 57414124.155 | 61641.407 | 85137234.455 | 186972.569 | 61697142.631 | 55734.393 | 319711873.326 | 84154.281 | 92615.898 | 15.22 | 88493.842 | 9.024 | 90995.907 | 26.51 | 71846.103 | 14.091 | 343701.784 | 61.428 | 181085.496 | 343640.356 | 12.3167 | 0 | 6.85 | 35.13 | 43.88 | 1.88 | 7.3 | 345699
2025-05-13 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:03 | 18:30 | 1250 | 1272 | 1181 | 1176 | 1270 | 1173 | 1178 | 1182 | 1221 | 1232 | 1168 | 1182 | 1156 | 1076 | 1132 | 1175 | 1088 | 1071 | 1161 | 1161 | 1075 | 1084 | 1188.9 | 1218 | 1171 | 1156 | 1153 | 1198 | 1209 | 1192 | 1198 | 1202 | 1126.7 | 1430 | 1131 | 1267 | 1166 | 1151 | 1168 | 1180 | 1163 | 1105 | 1135 | 1158 | 1168 | 1178 | 1267 | 1159 | 1213 | 1195 | 1171 | 1168 | 1331 | 1320 | 1260 | 1281 | 1330 | 1192 | 1317 | 1333 | 1180 | 1297 | 1158 | 1110 | 1273 | 1262 | 1277 | 1128.8 | 1159 | 1160 | 1169 | 1166 | 1186 | 1159 | 1322 | 1298 | 1325 | 1139 | 1131 | 1210 | 1171 | 1178 | 1161 | 1169 | 1165 | 1170 | 1183 | 1167 | 1167 | 1158 | 1212 | 1212 | 1175 | 1154 | 1303 | 1117 | 1127 | 1167 | 1148 | 1157 | 1188 | 1156 | 1175 | 1153 | 1310 | 1167 | 1371 | 1289 | 1172 | 1267 | 1258 | 1233 | 1273 | 1304 | 1163 | 1106 | 1276 | 1301 | 1291 | 1165 | 1185 | 1263 | 1267 | 1166 | 1174 | 1398 | 1130 | 1134 | 1302 | 1238 | 1159 | 1246 | 1164 | 1025 | 1298 | 1244 | 1254 | 1238 | 1214 | 1155 | 1117 | 1212 | 1124 | 1270 | 1080 | 1241 | 1147 | 1069 | 1249 | 1264 | 1265 | 1158 | 1327 | 1159 | 1144 | 1135 | 1198 | 1088 | 1170 | 1131 | 1308 | 1112 | 1291 | 1263 | 1301 | 1089 | 1110 | 1276 | 1157 | 1125 | 1131 | 1123 | 1273 | 1186 | 1272 | 1157 | 1166 | 1141 | 1282 | 1182 | 1250 | 1264 | 1308 | 1278 | 1268 | 1260 | 1214 | 1221 | 1173 | 1169 | 1144 | 1137 | 1119 | 1162 | 1131 | 1160 | 975 | 1183 |  |  | 1004 | 842 | 1155 |  | 1252 | 1114 | 1163 | 1126 | 1158 | 1159 | 1171 | 1164 | 1175 | 1187 | 1165 | 1173 | 1301 | 1332 | 1075 | 1037 | 908 | 750 | 894 | 1003 | 1205 | 1282 | 1234 | 1223 | 1208 | 1228 | 1243 | 1278 | 1032 | 1145 | 1037 | 1091 | 925 |  | 1375 | 1170 | 425.9 | 1070.4 | 1076 |  |  | 1098 | 1142 | 1103 | 1103 | 1032 | 34.36 | 42.16 | 1.65 | 11.7 |  | 0 | 5.73 |  |  | 84429612.061 | 282011.535 | 57488191.804 | 61677.352 | 85214024.795 | 187000.005 | 61757442.493 | 55778.947 | 319998971.929 | 84220.239 | 76090.444 | 15.801 | 74067.649 | 35.945 | 76790.34 | 27.436 | 60299.862 | 44.554 | 287098.603 | 65.958 | 150106.347 | 287032.645 | 12.45 | 0 | 5.73 | 34.36 | 42.16 | 1.65 | 11.7 | 286967.7
2025-05-14 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:30 | 18:25 | 1516 | 1529 | 1418 | 1410 | 1463 | 1406 | 1420 | 1424 | 1466 | 1477 | 1451 | 1444 | 1424 | 1339 | 1358 | 1408 | 1351 | 1408 | 1522 | 1529 | 1362 | 1423 | 1558 | 1598 | 1542 | 1522 | 1516 | 1471 | 1588 | 1563 | 1542 | 1577 | 1311 | 1719 | 1351 | 1521 | 1404 | 1384 | 1406 | 1421 | 1396 | 1331 | 1341 | 1395 | 1406 | 1418 | 1526 | 1399 | 1466 | 1441 | 1410 | 1408 | 1602 | 1591 | 1511 | 1535 | 1602 | 1433 | 1585 | 1605 | 1419 | 1591 | 1425 | 1309 | 1537 | 1527 | 1547 | 1313 | 1408 | 1403 | 1419 | 1414 | 1426 | 1407 | 1628 | 1572 | 1604 | 1365 | 1348 | 1453 | 1415 | 1410 | 1398 | 1406 | 1407 | 1412 | 1427 | 1408 | 1415 | 1400 | 1468 | 1422 | 1437 | 1429 | 1415 | [63 empty] | 1404 | 1352 | 1565 | 1351 | 1544 | 1510 | 1556 | 1300 | 1332 | 1532 | 1390 | 1354 | 1381 | 1347 | 1525 | 1426 | 1528 | 1386 | 1400 | 1362 | 1542 | 1416 | 1502 | 1515 | 1567 | 1533 | 1519 | 1508 | 1456 | 1468 | 1416 | 1416 | [32 empty] | 844 | 1003 | 1205 | 1282 | 1234 | 1223 | 1363 | 1310 | 1243 | 1278 | 1032 | 1145 | 1037 | 1091 | 925 | [13 empty] | 38.2 | 45.38 | 2.6 | 7.1 |  | 0 | 6.95 |  |  | 84523132.602 | 282028.228 | 57577637.485 | 61704.247 | 85306571.244 | 187045.615 | 61830305.101 | 55807.783 | 320347094.315 | 84286.91 | 93520.541 | 16.693 | 89445.681 | 26.895 | 92546.449 | 45.61 | 72862.608 | 28.836 | 348122.386 | 66.671 | 182922.634 | 348055.715 | 12.9167 | 0 | 6.95 | 38.2 | 45.38 | 2.6 | 7.1 | 201945
2025-05-15 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:40 | 18:34 | 1470 | 1483 | 1376 | 1367 | 1442.4 | 1368 | 1382 | 1385 | 1428 | 1438 | 1407 | 1400 | 1382 | 1301 | 1318 | 1366 | 1378 | 1364 | 1476 | 1480 | 1321 | 1381 | 1511 | 1551 | 1495 | 1510 | 1471 | 1525 | 1543 | 1518 | 1563 | 1530 | 1268 | 1669 | 1311 | 1494 | 1364 | 1343 | 1364 | 1379 | 1354 | 1289 | 1301 | 1352 | 1377 | 1374 | 1489 | 1364 | 1424 | 1398 | 1378 | 1374 | 1555 | 1543 | 1471 | 1488 | 1559 | 1389 | 1536 | 1556 | 1376 | 1545 | 1463 | 1298 | 1488 | 1478 | 1498 | 1273 | 1359 | 1367 | 1375 | 1372 | 1389 | 1363 | 1558 | 1523 | 1552 | 1346 | 1318 | 1401 | 1379 | 1380 | 1356 | 1362 | 1375 | 1369 | 1393 | 1374 | 1373 | 1359 | 1421 | 1298 | 1400 | 1390 | 1410 | 1343 | 1354 | 1357 | 1329 | 1291 | 1421 | 1375 | 1393 | 1344 | 1547 | 1184 | 1379 | 1489 | 1391 | 1536 | 1419 | 1523 | 1545 | 1587 | 1331 | 1343 | 1556 | 1449 | 1404 | 1378 | 1408 | 1480 | 1421 | 1334 | 1402 | 1474 | 1259 | 1285 | 1510 | 1498 | 1426 | 1428 | 1384 | 1263 | 1529 | 1436 | 1478 | 1400 | 1398 | 1383 | 1342 | 1389 | 1350 | 1510 | 1300 | 1516 | 1400 | 1268 | 1449 | 1456 | 1477 | 1362 | 1465 | 1360 | 1337 | 1320 | 1325 | 1282 | 1361 | 1311 | 1522 | 1312 | 1496 | 1464 | 1508 | 1260 | 1289 | 1485 | 1349 | 1312 | 1339 | 1306 | 1478 | 1379 | 1480 | 1343 | 1357 | 1320 | 1495 | 1372 | 1455 | 1470 | 1523 | 1489 | 1471 | 1462 | 1411 | 1422 | 1377 | 1371 | 1268 | 1213 | 1210 | 1310 | 1339 | 1210 | 1121 | 1357 |  |  | 1181 | 921 | 1272 |  | 1394 | 1242 | 1311 | 1290 | 1259 | 1334 | 1343 | 1339 | 1343 | 1368 | 1369 | 1356 | 1398 | 1542 | 1156 | 1061 | 1069 | 998 | 952 | 1116 | 1337 | 1489 | 1317 | 1369 | 1362 | 1400 | 1398 | 1380 | 1090 | 1300 | 1150 | 1303 | 1100 |  | 1250 | 1360 | 610 | 1298 | 1283 |  |  | 1210 | 1412 | 1300 | 1310 | 1117 | 38.52 | 46.82 | 2.05 | 5.8 |  | 0 | 6.81 |  |  | 84614020.421 | 282042.855 | 57664448.69 | 61713.367 | 85396598.142 | 187073.753 | 61901422.817 | 55823.055 | 320685759.859 | 84346.922 | 90887.819 | 14.627 | 86811.205 | 9.12 | 90026.898 | 28.138 | 71117.716 | 15.272 | 338665.544 | 60.012 | 177675.277 | 338605.532 | 12.9 | 0 | 6.81 | 38.52 | 46.82 | 2.05 | 5.8 | 334705.4
2025-05-16 | 2026 |  |  |  | May-25 | 31 | 66750 | 5:15 | 18:24 | 1262 | 1272 | 1181 | 1176 | 1250 | 1173 | 1179 | 1181 | 1221 | 1233 | 1208 | 1202 | 1186 | 1116 | 1167 | 1175 | 1167 | 1153 | 1249 | 1253 | 1209 | 1283 | 1318 | 1303 | 1312 | 1253 | 1253 | 1339 | 1313 | 1298 | 1292 | 1332 | 1130 | 1430 | 1203 | 1293 | 1167 | 1151 | 1168 | 1181 | 1163 | 1170 | 1158 | 1208 | 1168 | 1178 | 1267 | 1159 | 1213 | 1196 | 1171 | 1168 | 1331 | 1321 | 1260 | 1281 | 1330 | 1192 | 1303 | 1317 | 1334 | 1292 | 1227 | 1109 | 1273 | 1262 | 1277 | 1088 | 1193 | 1197 | 1192 | 1166 | 1186 | 1159 | 1322 | 1293 | 1325 | 1139 | 1181 | 1299 | 1201 | 1172 | 1161 | 1169 | 1165 | 1170 | 1183 | 1167 | 1167 | 1158 | 1212 | 1270 | 1190 | 1184 | 1200 | 1125 | 1135 | 1162 | 1160 | 1150 | 1195 | 1153 | 1170 | 1193 | 1304 | 1140 | 1325 | 1302 | 1180 | 1290 | 1282 | 1281 | 1325 | 1334 | 1140 | 1205 | 1310 | 1319 | 1262 | 1178 | 1187 | 1298 | 1240 | 1123 | 1186 | 1498 | 1167 | 1140 | 1321 | 1303 | 1240 | 1258 | 1230 | 1102 | 1225 | 1245 | 1240 | 1234 | 1215 | 1150 | 1199 | 1240 | 1138 | 1230 | 1100 | 1298 | 1134 | 1057 | 1260 | 1239 | 1253 | 1147 | 1290 | 1141 | 1180 | 1160 | 1198 | 1140 | 1171 | 1131 | 1308 | 1180 | 1291 | 1320 | 1301 | 1089 | 1160 | 1276 | 1157 | 1125 | 1132 | 1123 | 1273 | 1186 | 1272 | 1157 | 1166 | 1141 | 1282 | 1182 | 1250 | 1264 | 1308 | 1278 | 1268 | 1260 | 1214 | 1221 | 1173 | 1169 | 1153 | 1156 | 1130 | 1139 | 1220 | 1150 | 1009 | 1233 |  |  | 1198 | 898 | 1280 |  | 1250 | 1278 | 1182 | 1172 | 1149 | 1209 | 1214 | 1233 | 1230 | 1244 | 1213 | 1201 | 1230 | 1365 | 1072 | 1110 | 860 | 810 | 910 | 1011 | 1213 | 1372 | 1198 | 1244 | 1298 | 1278 | 1287 | 1300 | 1099 | 1219 | 1099 | 1100 | 970 |  | 1230 | 1200 | 450 | 1210 | 1123 |  |  | 1098 | 1298 | 1050 | 1100 | 930 | 37.78 | 42.3 | 2.3 | 11.3 |  | 0 | 5.56 |  |  | 84689361.033 | 282058.64 | 57735686.702 | 61735.503 | 85470963.71 | 187105.571 | 61960225.142 | 55851.671 | 320965372.624 | 84407.417 | 75340.612 | 15.785 | 71238.012 | 22.136 | 74365.568 | 31.818 | 58802.325 | 28.616 | 279612.765 | 60.495 | 146540.703 | 279552.27 | 13.15 | 0 | 5.56 | 37.78 | 42.3 | 2.3 | 11.3 | 292468
2025-05-17 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:27 | 18:25 | 1094 | 1105 | 1030 | 1026 | 1080 | 1024 | 1018 | 1021 | 1053 | 1060 | 1038 | 1036 | 1019 | 958 | 998 | 1009 | 993 | 1000 | 1076 | 1083 | 998 | 1016 | 1113 | 1142 | 1098 | 1082 | 1082 | 1123 | 1126 | 1115 | 1123 | 1121 | 998 | 1271 | 993 | 1123 | 994 | 1013 | 994 | 1004 | 1023 | 993 | 1001 | 1023 | 999 | 1016 | 1088 | 992 | 1039 | 1098 | 1008 | 1066 | 1150 | 1140 | 1093 | 1116 | 1144 | 1020 | 1122 | 1153 | 1005 | 1126 | 1030 | 998 | 1085 | 1076 | 1090 | 998 | 1098 | 1088 | 1098 | 1023 | 1008 | 998 | 1154 | 1190 | 1145 | 1034 | 1023 | 1098 | 1006 | 1013 | 1003 | 1006 | 1003 | 1014 | 1011 | 999 | 1023 | 1013 | 1089 | 1100 | 1019 | 1078 | 1100 | 1002 | 1032 | 1063 | 1038 | 1041 | 1079 | 1035 | 1066 | 1036 | 1198 | 1044 | 1186 | 1175 | 1068 | 1187 | 1146 | 1140 | 1201 | 1189 | 1048 | 1074 | 1172 | 1114 | 1175 | 1064 | 1094 | 1133 | 1114 | 1030 | 1081 | 1478 | 950 | 968 | 1165 | 1154 | 1059 | 1083 | 1051 | 898 | 1104 | 1098 | 1051 | 1083 | 1059 | 1004 | 988 | 1046 | 1024 | 1094 | 999 | 1168 | 1006 | 942 | 1093 | 1113 | 1126 | 1026 | 1119 | 1024 | 1001 | 988 | 1050 | 1178 | 994 | 958 | 1108 | 959 | 1103 | 1073 | 1112 | 928 | 950 | 1086 | 985 | 959 | 980 | 959 | 1081 | 1009 | 1085 | 985 | 990 | 967 | 1093 | 1003 | 1061 | 1074 | 1125 | 1096 | 1078 | 1070 | 1030 | 1040 | 1008 | 1003 | 1021 | 1016 | 977 | 1005 | 1064 | 961 | 900 | 1086 |  |  | 944 | 738 | 1059 |  | 1165 | 1132 | 1051 | 1020 | 1045 | 1058 | 1065 | 1072 | 1069 | 1083 | 1086 | 1080 | 1149 | 1235 | 975 | 894 | 790 | 640 | 783 | 913 | 999 | 1200 | 1018 | 1100 | 1098 | 1097 | 1186 | 1141 | 975 | 994 | 900 | 997 | 960 |  | 1250 | 1068 | 498 | 985 | 918 |  |  | 1000 | 1000 | 970 | 920 | 860 | 34.4 | 42 | 2.7 | 19.29 |  | 0 | 4.84 |  |  | 84756017.786 | 282077.977 | 57798684.403 | 61771.515 | 85536883.57 | 187144.417 | 62011259.85 | 55889.816 | 321211838.837 | 84479.581 | 66656.753 | 19.337 | 62997.701 | 36.012 | 65919.86 | 38.846 | 51034.708 | 38.145 | 246466.213 | 72.164 | 129599.105 | 246394.049 | 12.9667 | 0 | 4.84 | 34.4 | 42 | 2.7 | 19.29 | 254893
2025-05-18 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:14 | 18:23 | 1439 | 1449 | 1344 | 1339 | 1402 | 1340 | 1343 | 1346 | 1387 | 1395 | 1368 | 1363 | 1343 | 1262 | 1310 | 1328 | 1298 | 1327 | 1440 | 1441 | 1310 | 1341 | 1470 | 1507 | 1455 | 1435 | 1430 | 1485 | 1500 | 1480 | 1498 | 1490 | 1247 | 1630 | 1293 | 1455 | 1304 | 1307 | 1324 | 1336 | 1317 | 1298 | 1298 | 1330 | 1276 | 1388 | 1441 | 1317 | 1378 | 1355 | 1398 | 1330 | 1513 | 1502 | 1435 | 1462 | 1516 | 1351 | 1496 | 1458 | 1337 | 1507 | 1337 | 1298 | 1445 | 1435 | 1455 | 1227 | 1316 | 1321 | 1331 | 1326 | 1346 | 1295 | 1518 | 1483 | 1509 | 1300 | 1298 | 1403 | 1336 | 1337 | 1323 | 1329 | 1330 | 1334 | 1347 | 1328 | 1328 | 1314 | 1382 | 1398 | 1358 | 1348 | 1463 | 1328 | 1344 | 1373 | 1376 | 1310 | 1424 | 1373 | 1396 | 1348 | 1541 | 1310 | 1572 | 1545 | 1406 | 1534 | 1402 | 1496 | 1547 | 1563 | 1342 | 1406 | 1533 | 1433 | 1456 | 1377 | 1403 | 1478 | 1417 | 1324 | 1394 | 1482 | 1276 | 1297 | 1521 | 1514 | 1438 | 1450 | 1423 | 1207 | 1544 | 1486 | 1480 | 1439 | 1398 | 1402 | 1353 | 1398 | 1391 | 1546 | 1328 | 1565 | 1356 | 1251 | 1446 | 1470 | 1480 | 1353 | 1496 | 1345 | 1318 | 1307 | 1310 | 1325 | 1328 | 1278 | 1482 | 1282 | 1465 | 1412 | 1477 | 1244 | 1263 | 1455 | 1317 | 1285 | 1309 | 1278 | 1443 | 1360 | 1444 | 1315 | 1315 | 1287 | 1457 | 1338 | 1414 | 1442 | 1482 | 1442 | 1439 | 1426 | 1375 | 1389 | 1351 | 1350 | 1324 | 1306 | 1266 | 1330 | 1395 | 1232 | 1168 | 1419 |  |  | 1210 | 943 | 1357 |  | 1484 | 1378 | 1353 | 1339 | 1334 | 1382 | 1399 | 1406 | 1403 | 1420 | 1404 | 1399 | 1478 | 1587 | 1257 | 1164 | 963 | 810 | 998 | 1174 | 1379 | 1562 | 1386 | 1448 | 1363 | 1378 | 1490 | 1468 | 1264 | 1291 | 1169 | 1300 | 1198 |  | 1478 | 1383 | 633 | 1263 | 1278 |  |  | 1160 | 1263 | 1234 | 1198 | 1110 | 32.3 | 41.68 | 1.14 | 4.7 |  | 0 | 6.4 |  |  | 84844195.864 | 282091.684 | 57882888.841 | 61778.917 | 85624746.958 | 187158.05 | 62078515.979 | 55902.753 | 321539137.169 | 84534.381 | 88178.078 | 13.707 | 84204.438 | 7.402 | 87863.388 | 13.633 | 67256.129 | 12.937 | 327298.332 | 54.8 | 172361.407 | 327243.532 | 13.15 | 0 | 6.4 | 32.3 | 41.68 | 1.14 | 4.7 | 332920
2025-05-19 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:14 | 18:27 | 1413 | 1425 | 1321 | 1315 | 1373 | 1317 | 1317 | 1320 | 1360 | 1372 | 1346 | 1341 | 1321 | 1242 | 1308 | 1317 | 1261 | 1311 | 1417 | 1418 | 1310 | 1326 | 1454 | 1490 | 1428 | 1410 | 1406 | 1459 | 1471 | 1452 | 1425 | 1464 | 1221 | 1597 | 1269 | 1447 | 1304 | 1280 | 1296 | 1309 | 1290 | 1259 | 1276 | 1246 | 1284 | 1311 | 1411 | 1290 | 1348 | 1326 | 1305 | 1302 | 1483 | 1472 | 1402 | 1432 | 1483 | 1328 | 1475 | 1437 | 1309 | 1476 | 1359 | 1258 | 1415 | 1403 | 1427 | 1285 | 1301 | 1292 | 1308 | 1306 | 1333 | 1288 | 1488 | 1456 | 1479 | 1271 | 1249 | 1391 | 1308 | 1307 | 1295 | 1302 | 1303 | 1306 | 1332 | 1301 | 1305 | 1288 | 1356 | 1400 | 1340 | 1331 | 1398 | 1273 | 1264 | 1326 | 1302 | 1316 | 1351 | 1309 | 1336 | 1276 | 1499 | 1329 | 1557 | 1465 | 1328 | 1469 | 1433 | 1406 | 1474 | 1474 | 1317 | 1322 | 1450 | 1481 | 1478 | 1316 | 1335 | 1417 | 1372 | 1321 | 1369 | 1432 | 1264 | 1264 | 1463 | 1458 | 1408 | 1418 | 1412 | 1195 | 1484 | 1380 | 1434 | 1420 | 1397 | 1324 | 1338 | 1371 | 1327 | 1437 | 1284 | 1399 | 1304 | 1211 | 1358 | 1424 | 1431 | 1311 | 1505 | 1318 | 1298 | 1286 | 1254 | 1232 | 1310 | 1270 | 1458 | 1264 | 1437 | 1411 | 1449 | 1220 | 1243 | 1428 | 1303 | 1259 | 1288 | 1253 | 1418 | 1328 | 1416 | 1292 | 1306 | 1273 | 1439 | 1325 | 1398 | 1412 | 1475 | 1414 | 1415 | 1398 | 1365 | 1365 | 1319 | 1312 | 1293 | 1224 | 1218 | 1313 | 1245 | 1311 | 1102 | 1336 |  |  | 1168 | 912 | 1309 |  | 1424 | 1258 | 1315 | 1280 | 1308 | 1310 | 1324 | 1278 | 1323 | 1283 | 1317 | 1325 | 1475 | 1504 | 1216 | 1177 | 910 | 798 | 936 | 1111 | 1314 | 1404 | 1343 | 1332 | 1378 | 1398 | 1358 | 1392 | 1136 | 1266 | 1136 | 1278 | 1210 |  | 1401 | 1402 | 610 | 1298 | 1237 |  |  | 1198 | 1278 | 1210 | 1178 | 1121 | 36.2 | 40 | 1.1 | 4.2 |  | 0 | 6.27 |  |  | 84931095.141 | 282106.839 | 57965993.75 | 61788.116 | 85711093.859 | 187189.533 | 62145633.467 | 55919.967 | 321862485.793 | 84589.752 | 86899.277 | 15.155 | 83104.909 | 9.199 | 86346.901 | 31.483 | 67117.488 | 17.214 | 323348.624 | 55.371 | 169979.832 | 323293.253 | 13.2167 | 0 | 6.27 | 36.2 | 40 | 1.1 | 4.2 | 324288
2025-05-20 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:14 | 18:26 | 1397 | 1409 | 1306 | 1301 | 1370 | 1301 | 1302 | 1305 | 1345 | 1356 | 1330 | 1325 | 1305 | 1228 | 1304 | 1298 | 1268 | 1303 | 1414 | 1416 | 1316 | 1317 | 1438 | 1482 | 1430 | 1411 | 1405 | 1460 | 1472 | 1452 | 1415 | 1461 | 1207 | 1583 | 1243 | 1455 | 1298 | 1267 | 1278 | 1293 | 1272 | 1270 | 1282 | 1268 | 1308 | 1308 | 1404 | 1275 | 1338 | 1314 | 1293 | 1309 | 1467 | 1463 | 1392 | 1415 | 1467 | 1313 | 1455 | 1433 | 1295 | 1465 | 1398 | 1260 | 1413 | 1391 | 1423 | 1263 | 1282 | 1278 | 1295 | 1292 | 1318 | 1285 | 1494 | 1457 | 1481 | 1263 | 1232 | 1351 | 1300 | 1298 | 1281 | 1288 | 1290 | 1292 | 1317 | 1310 | 1291 | 1281 | 1342 | 1363 | 1325 | 1318 | 1398 | 1262 | 1260 | 1316 | 1298 | 1306 | 1344 | 1301 | 1333 | 1311 | 1497 | 1321 | 1564 | 1450 | 1314 | 1436 | 1423 | 1385 | 1426 | 1456 | 1302 | 1310 | 1434 | 1468 | 1471 | 1303 | 1321 | 1401 | 1360 | 1308 | 1327 | 1470 | 1255 | 1263 | 1450 | 1446 | 1395 | 1404 | 1400 | 1197 | 1476 | 1365 | 1424 | 1405 | 1389 | 1316 | 1327 | 1359 | 1320 | 1427 | 1276 | 1353 | 1295 | 1203 | 1353 | 1411 | 1421 | 1302 | 1493 | 1315 | 1292 | 1275 | 1298 | 1227 | 1296 | 1254 | 1441 | 1246 | 1423 | 1393 | 1431 | 1202 | 1259 | 1447 | 1302 | 1245 | 1288 | 1233 | 1416 | 1312 | 1411 | 1280 | 1302 | 1266 | 1429 | 1311 | 1393 | 1395 | 1467 | 1405 | 1398 | 1383 | 1353 | 1353 | 1301 | 1294 | 1283 | 1236 | 1201 | 1307 | 1230 | 1313 | 1089 | 1329 |  |  | 1134 | 904 | 1292 |  | 1410 | 1249 | 1302 | 1272 | 1295 | 1297 | 1310 | 1300 | 1308 | 1329 | 1302 | 1311 | 1459 | 1476 | 1201 | 1167 | 910 | 810 | 957 | 1136 | 1378 | 1439 | 1377 | 1363 | 1398 | 1363 | 1386 | 1427 | 1202 | 1296 | 1161 | 1263 | 1223 |  | 1855 | 1361 | 598 | 1278 | 1223 |  |  | 1210 | 1356 | 1226 | 1164 | 1132 | 36.2 | 38.23 | 1.3 | 6.3 |  | 0 | 6.27 |  |  | 85017444.06 | 282131.806 | 58048179.351 | 61814.197 | 85796789.223 | 187222.612 | 62212722.54 | 55950.155 | 322183673.474 | 84680.598 | 86348.919 | 24.967 | 82185.601 | 26.081 | 85695.364 | 33.079 | 67089.073 | 30.188 | 321187.681 | 90.846 | 168483.472 | 321096.835 | 13.2 | 0 | 6.27 | 36.2 | 38.23 | 1.3 | 6.3 | 323147
2025-05-21 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:16 | 18:27 | 1279 | 1291 | 1197 | 1194 | 1252 | 1192 | 1220.3 | 1193 | 1232 | 1242 | 1217 | 1211 | 1196 | 1124 | 1193 | 1189 | 1174 | 1193 | 1293 | 1295 | 1205 | 1205 | 1319 | 1360 | 1310 | 1291 | 1288 | 1340 | 1355 | 1339 | 1325 | 1352 | 1128 | 1458 | 1176 | 1346 | 1208 | 1188 | 1203 | 1202 | 1201 | 1185 | 1212 | 1185 | 1214 | 1210 | 1310 | 1189 | 1223 | 1205 | 1196 | 1197 | 1372 | 1343 | 1275 | 1308 | 1341 | 1201 | 1340 | 1308 | 1209 | 1363 | 1325 | 1208 | 1290 | 1269 | 1300 | 1167 | 1171 | 1165 | 1183 | 1180 | 1216 | 1186 | 1374 | 1343 | 1364 | 1171 | 1169.4 | 1254 | 1208 | 1208 | 1196 | 1201 | 1205 | 1202 | 1203 | 1196 | 1179 | 1170 | 1226 | 1298 | 1226 | 1217 | 1310 | 1155 | 1163 | 1199 | 1184 | 1192 | 1225 | 1186 | 1215 | 1195 | 1361 | 1205 | 1428 | 1323 | 1198 | 1305 | 1296 | 1270 | 1315 | 1330 | 1188 | 1263 | 1311 | 1335 | 1337 | 1188 | 1207 | 1294.1 | 1309.1 | 1195 | 1210 | 1326 | 1192 | 1165 | 1323 | 1319 | 1273 | 1281 | 1277 | 1093 | 1344 | 1249 | 1300 | 1286 | 1266 | 1195 | 1210 | 1246 | 1206 | 1300 | 1209 | 1263 | 1179 | 1095 | 1258 | 1287 | 1295 | 1184 | 1355 | 1198 | 1181 | 1163 | 1165 | 1145 | 1181 | 1144 | 1311 | 1165 | 1298 | 1276 | 1308 | 1163 | 1170 | 1328 | 1192 | 1144 | 1184 | 1150 | 1309 | 1204 | 1330 | 1169 | 1186 | 1162 | 1304 | 1199 | 1268 | 1287 | 1284 | 1278 | 1275 | 1281 | 1236 | 1233 | 1203 | 1245 | 1188 | 1165 | 1119 | 1220 | 1152 | 1211 | 1000 | 1238 |  |  | 1046 | 824 | 1179 |  | 1291 | 1144 | 1205 | 1175 | 1211 | 1181 | 1219 | 1186 | 1208 | 1214 | 1203 | 1198 | 1378 | 1364 | 1098 | 1066 | 868 | 726 | 889.7 | 1047 | 1260 | 1328 | 1270 | 1263 | 1264 | 1298 | 1323 | 1298 | 1126 | 1180 | 1054 | 1163 | 1126 |  | 1698 | 1298 | 550 | 1210 | 1169 |  |  | 1110 | 1266 | 1240 | 1110 | 1051 | 35.5 | 28 | 1.1 | 4.3 |  | 0 | 5.79 |  |  | 85097003.114 | 282158.202 | 58123585.217 | 61835.796 | 85875128.954 | 187246.759 | 62274322.813 | 55975.842 | 322478484.407 | 84768.572 | 79559.054 | 26.396 | 75405.866 | 21.599 | 78339.731 | 24.147 | 61600.273 | 25.687 | 294810.933 | 87.974 | 154916.925 | 294722.959 | 13.1833 | 0 | 5.79 | 35.5 | 28 | 1.1 | 4.3 | 297837.6
2025-05-22 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:16 | 18:29 | 1401 | 1396 | 1300 | 1275 | 1384 | 1319 | 1294 | 1316 | 1362 | 1372 | 1334 | 1338 | 1321 | 1243 | 1311 | 1321 | 1260 | 1314 | 1423 | 1411 | 1292 | 1332 | 1461 | 1475 | 1443 | 1392 | 1420 | 1476 | 1479 | 1458 | 1443.5 | 1486 | 1208 | 1610 | 1297 | 1478 | 1239 | 1300 | 1319 | 1275 | 1316 | 1284 | 1300 | 1268 | 1300 | 1327 | 1433 | 1304 | 1366 | 1344 | 1276 | 1333 | 1514 | 1492 | 1409 | 1434 | 1480 | 1325 | 1479 | 1438 | 1325 | 1495 | 1412 | 1305 | 1421 | 1395 | 1433 | 1311 | 1311 | 1298 | 1318 | 1316 | 1338 | 1309 | 1500 | 1465 | 1493 | 1279 | 1293 | 1398 | 1319 | 1314 | 1304 | 1308 | 1313 | 1301 | 1328 | 1319 | 1315 | 1308 | 1359 | 1375 | 1348 | 1341 | 1423.6 | 1271 | 1264 | 1312 | 1292 | 1303 | 1342 | 1300 | 1330 | 1305 | 1432 | 1322 | 1559 | 1446 | 1312 | 1456 | 1423 | 1394 | 1472 | 1485 | 1302 | 1271 | 1432 | 1463 | 1462 | 1316 | 1329 | 1429 | 1427 | 1312 | 1328 | 1438 | 1241 | 1275 | 1462 | 1450 | 1405 | 1421 | 1368 | 1228 | 1513 | 1402 | 1450 | 1443 | 1425 | 1334 | 1342 | 1396 | 1346 | 1462 | 1302 | 1390 | 1313 | 1139 | 1395 | 1419 | 1422 | 1296 | 1492 | 1312 | 1290 | 1275 | 1325 | 1277 | 1311 | 1271 | 1455 | 1263 | 1443 | 1409 | 1454 | 1280 | 1295 | 1468 | 1320 | 1316 | 1332 | 1318 | 1450 | 1357 | 1474 | 1296 | 1308 | 1284 | 1446 | 1328 | 1399 | 1420 | 1431 | 1425 | 1417 | 1400 | 1368 | 1316 | 1319 | 1391 | 1294 | 1265 | 1217 | 1321 | 1256 | 1314 | 1105 | 1344 |  |  | 1190 | 849 | 1255 |  | 1418 | 1251 | 1321 | 1290 | 1317 | 1325 | 1333 | 1333 | 1336 | 1364 | 1322 | 1316 | 1473 | 1500 | 1212 | 1166 | 962 | 835 | 964 | 1053 | 1368 | 1461 | 1387 | 1369 | 1378 | 1450.2 | 1455 | 1441 | 1226 | 1271 | 1163 | 1322 | 1192 |  | 1721 | 1371.1 | 519 | 1275 | 1227 |  |  | 1127.6 | 1362.5 | 1348.6 | 1207.7 | 1097 | 33.8 | 43.42 | 3.64 | 8.3 |  | 6.88 | 6.41 |  |  | 85184158.709 | 282186.32 | 58207030.719 | 61858.545 | 85961987.153 | 187281.33 | 62341902.179 | 56009.599 | 322803070.42 | 84859.421 | 87155.595 | 28.118 | 83445.502 | 22.749 | 86858.199 | 34.571 | 67579.366 | 33.757 | 324586.013 | 90.849 | 170550.23 | 324495.164 | 13.2167 | 6.88 | 6.41 | 33.8 | 43.42 | 3.64 | 8.3 | 327534.8
2025-05-23 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:13 | 18:29 | 1402.2 | 1418.1 | 1319.9 | 1316.7 | 1391.6 | 1310.8 | 1294.8 | 1301 | 1352.3 | 1367.5 | 1324.6 | 1320.9 | 1308.7 | 1241.4 | 1309.5 | 1312.2 | 1261.1 | 1300.1 | 1411.7 | 1413.8 | 1318.2 | 1322.8 | 1456.9 | 1495 | 1430.4 | 1412.6 | 1410.5 | 1470.4 | 1476.87 | 1462.2 | 1449.6 | 1473.7 | 1240 | 1599.3 | 1283.4 | 1471.4 | 1314.7 | 1283.6 | 1303.6 | 1344.4 | 1302 | 1263.6 | 1309.8 | 1287.4 | 1311.7 | 1318.6 | 1428.6 | 1300.1 | 1368.5 | 1346.8 | 1274.9 | 1329.8 | 1522.8 | 1482.3 | 1394.7 | 1421.1 | 1459.9 | 1315.6 | 1468.5 | 1432.7 | 1332.1 | 1496.5 | 1328.3 | 1274.6 | 1441 | 1421.4 | 1450.4 | 1301.6 | 1316.1 | 1303.2 | 1259.7 | 1318.8 | 1323.5 | 1293.7 | 1482.8 | 1446.9 | 1477.9 | 1292.9 | 1278 | 1375.7 | 1311.9 | 1311 | 1299.1 | 1309.7 | 1304 | 1301.5 | 1317.9 | 1280.7 | 1320.3 | 1312.2 | 1377.4 | 1385.8 | 1336.5 | 1327.4 | 1485.5 | 1279.2 | 1269.5 | 1297.9 | 1276.1 | 1289.6 | 1330.2 | 1284.5 | 1318.1 | 1289.2 | 1422.4 | 1314.2 | 1542 | 1433.1 | 1302.8 | 1430.7 | 1417.7 | 1391.4 | 1456 | 1445.7 | 1288.8 | 1282.6 | 1420.2 | 1459.6 | 1458.3 | 1325 | 1331.8 | 1432.8 | 1443.1 | 1306.5 | 1321.4 | 1432.5 | 1265.4 | 1264.9 | 1458.2 | 1459.5 | 1432.3 | 1439.7 | 1432.5 | 1227.2 | 1508.6 | 1393.1 | 1435 | 1429.4 | 1410.1 | 1324.4 | 1382 | 1398.4 | 1330.5 | 1455.6 | 1286.4 | 1394.4 | 1318.7 | 1222.8 | 1409.9 | 1430 | 1414.9 | 1285.6 | 1479 | 1298.2 | 1272.9 | 1267.4 | 1268.5 | 1271.4 | 1298.8 | 1259.7 | 1445.3 | 1250.3 | 1429.4 | 1406.5 | 1438.3 | 1279.1 | 1285 | 1458.3 | 1306.8 | 1321 | 1322.1 | 1306.8 | 1439.8 | 1346.9 | 1465.8 | 1285.5 | 1294 | 1272.6 | 1432.3 | 1317.5 | 1385.8 | 1407.1 | 1417.5 | 1415.1 | 1405.7 | 1408.7 | 1354.9 | 1307.7 | 1317.1 | 1379.6 | 1286 | 1260.3 | 1217.7 | 1313.6 | 1254.9 | 1304.9 | 1094.5 | 1333 |  |  | 1174.4 | 902.9 | 1282.1 |  | 1393.3 | 1228 | 1322.9 | 1304.9 | 1310.1 | 1342.1 | 1332.4 | 1348.8 | 1340.7 | 1378.5 | 1320.8 | 1333.3 | 1488.7 | 1517.4 | 1198.7 | 1151.6 | 999.8 | 851.6 | 967 | 1100 | 1356.5 | 1440.2 | 1374.7 | 1369.8 | 1390.2 | 1450.1 | 1437.8 | 1465.6 | 1239 | 1273.7 | 1166.8 | 1257 | 1176.8 |  | 1751 | 1381.2 | 520.8 | 1293.9 | 1238.7 |  |  | 1301.9 | 1331.6 | 1351.4 | 1212.7 | 1095 | 34.93 | 46.23 | 3.32 | 7.1 |  | 6.9 | 6.38 |  |  | 85271343.807 | 282224.438 | 58289730.442 | 61891.294 | 86048437.603 | 187325.901 | 62409065.75 | 56053.356 | 323126301.235 | 84960.27 | 87185.098 | 38.118 | 82699.723 | 32.749 | 86450.45 | 44.571 | 67163.571 | 43.757 | 323230.815 | 100.849 | 169813.954 | 323129.966 | 13.2667 | 6.9 | 6.38 | 34.93 | 46.23 | 3.32 | 7.1 | 326090.97
2025-05-24 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:15 | 18:29 | 1259.4 | 1269.5 | 1180 | 1169.7 | 1227.7 | 1172.6 | 1146.2 | 1148.8 | 1187 | 1197.9 | 1177.5 | 1170.4 | 1151.3 | 1089 | 1155 | 1153.4 | 1128.5 | 1148.6 | 1250.8 | 1247.9 | 1158.2 | 1163.4 | 1278.3 | 1311.4 | 1280 | 1274.3 | 1261.4 | 1293.7 | 1311.1 | 1290.1 | 1295.5 | 1300.7 | 1104.5 | 1430.4 | 1141.9 | 1315.1 | 1145.2 | 1142.7 | 1160.8 | 1188.3 | 1158.3 | 1137.5 | 1163.7 | 1143.1 | 1164.4 | 1170.3 | 1267.4 | 1155.7 | 1213.9 | 1191.7 | 1129.4 | 1177.7 | 1347.1 | 1315.2 | 1254.5 | 1287.6 | 1307.7 | 1172.6 | 1304.5 | 1273.9 | 1183.5 | 1332.5 | 1174.2 | 1141.5 | 1281.8 | 1261.4 | 1290.2 | 1159.5 | 1162.5 | 1152.8 | 1168.6 | 1172.6 | 1183 | 1144.9 | 1333.9 | 1303.8 | 1325.4 | 1149.9 | 1135.3 | 1235.4 | 1163 | 1164.9 | 1158.2 | 1172.4 | 1155.3 | 1159 | 1168.8 | 1115.4 | 1171.9 | 1161.1 | 1217.6 | 1241.5 | 1144.1 | 1180.5 | 1330.5 | 1136.6 | 1127.8 | 1149.3 | 1136.3 | 1141.6 | 1176.5 | 1143.4 | 1172.6 | 1146.6 | 1266.5 | 1161.4 | 1383.1 | 1260.9 | 1148.1 | 1268.7 | 1252.1 | 1251.4 | 1318.6 | 1301.6 | 1135.7 | 1129.9 | 1276.1 | 1312.9 | 1296.1 | 1189 | 1203.7 | 1279.2 | 1217.4 | 1167.3 | 1165.1 | 1271.5 | 1194.5 | 1180.3 | 1339.4 | 1330 | 1283.2 | 1291.3 | 1281.7 | 1100.5 | 1357.5 | 1251.6 | 1293.2 | 1286.8 | 1274.4 | 1198.1 | 1269.9 | 1263.3 | 1196.5 | 1311.1 | 1159.2 | 1228.8 | 1188.7 | 1107.3 | 1238.1 | 1306.3 | 1307.4 | 1183.5 | 1334.7 | 1169.2 | 1144.5 | 1150.3 | 1157.2 | 1155.5 | 1158.3 | 1124.4 | 1295.4 | 1116.6 | 1272.5 | 1255.4 | 1273 | 1176.4 | 1135.8 | 1290.8 | 1164.7 | 1160.5 | 1171.9 | 1167.4 | 1274.4 | 1190.1 | 1268.6 | 1154.3 | 1167.1 | 1142.4 | 1279.2 | 1178.1 | 1241.5 | 1255.6 | 1127.9 | 762.5 | 1257.9 | 1264.9 | 1222.6 | 1176.1 | 1171.5 | 1232.9 | 1138.1 | 1078.4 | 1114.9 | 1158.4 | 1101.5 | 1150 | 962 | 1174.4 |  |  | 1039.3 | 812.6 | 1152.1 |  | 1236 | 1099.9 | 1171.6 | 1155.3 | 1156 | 1186 | 1171.3 | 1186.1 | 1175.8 | 1206.8 | 1164.5 | 1193.2 | 1318.8 | 1344.8 | 1061.7 | 1020.2 | 895.5 | 770 | 869.4 | 1005.8 | 1196.3 | 1281.7 | 1227.8 | 1224.6 | 1212.5 | 1311.5 | 1276.7 | 1272.8 | 1120.3 | 1151.8 | 1061.8 | 1127.5 | 1093.2 |  | 1550.5 | 1227.4 | 472 | 1141 | 1098.2 |  |  | 1161.4 | 1197.3 | 1187.1 | 1078.7 | 992.2 | 35.89 | 44.51 | 4.63 | 7.7 |  | 6.17 | 5.67 |  |  | 85348803.993 | 282272.556 | 58363669.317 | 61938.043 | 86125519.623 | 187381.472 | 62469113.062 | 56111.113 | 323414575.721 | 85081.119 | 77460.186 | 48.118 | 73938.875 | 46.749 | 77082.02 | 55.571 | 60047.312 | 57.757 | 288274.486 | 120.849 | 151304.194 | 288153.637 | 13.2333 | 6.17 | 5.67 | 35.89 | 44.51 | 4.63 | 7.7 | 290997.7
2025-05-25 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:45 | 18:31 | 1448 | 1462.1 | 1353.7 | 1350 | 1443.4 | 1344.4 | 1343.4 | 1345.2 | 1391.6 | 1399.1 | 1368.1 | 1359.4 | 1341.6 | 1264.3 | 1339 | 1336.9 | 1337.2 | 1329.1 | 1438.8 | 1442.6 | 1345 | 1344 | 1475.9 | 1516.9 | 1462.5 | 1450.6 | 1439.4 | 1491.2 | 1503.2 | 1485.5 | 1501.1 | 1496.2 | 1260.7 | 1637.4 | 1313 | 1501.1 | 1345.8 | 1310.8 | 1332.6 | 1356.7 | 1329.9 | 1314.7 | 1338.9 | 1312.8 | 1336.9 | 1346.9 | 1451.4 | 1325.3 | 1383.7 | 1360.6 | 1301.2 | 1254.1 | 1537.8 | 1510.4 | 1438.7 | 1522.1 | 1516.3 | 1349.5 | 1498.8 | 1458.4 | 1350 | 1520.1 | 1336.8 | 1302.3 | 1458.7 | 1446.5 | 1465.8 | 1359.8 | 1338.5 | 1329.6 | 1339.2 | 1337.5 | 1357.8 | 1342.6 | 1526.9 | 1492.4 | 1527.8 | 1342.9 | 1325.1 | 1461.2 | 1348.5 | 1351.3 | 1337.1 | 1354.9 | 1336.7 | 1339.1 | 1355.4 | 1342.9 | 1334.4 | 1324.7 | 1387.2 | 1474.3 | 1369.3 | 1359.9 | 1507.6 | 1323 | 1334.2 | 1326 | 1302 | 1316 | 1351 | 1309 | 1336 | 1326 | 1499 | 1329 | 1557 | 1465 | 1328 | 1469 | 1433 | 1406 | 1474 | 1474 | 1317 | 1322 | 1450 | 1481 | 1428 | 1316 | 1335 | 1477 | 1372 | 1321 | 1338 | 1525 | 1324 | 1331.9 | 1463 | 1458 | 1408 | 1418 | 1412 | 1195 | 1484 | 1400 | 1434 | 1350 | 1397 | 1324 | 1418 | 1421 | 1327 | 1437 | 1334 | 1409 | 1304 | 1211 | 1408 | 1424 | 1431 | 1311 | 1505 | 1318 | 1328 | 1332.9 | 1329.1 | 1332 | 1326.7 | 1289.9 | 1470.7 | 1298.2 | 1458.3 | 1489.1 | 1467.5 | 1379.1 | 1308.2 | 1485.5 | 1336.2 | 1333.6 | 1354.5 | 1350.9 | 1471.7 | 1374.9 | 1443 | 1315.8 | 1325.6 | 1304 | 1461.8 | 1344.6 | 1416.6 | 1448.1 | 1445 | 1444.1 | 1438.7 | 1451.4 | 1383.4 | 1335.4 | 1351.9 | 1405.4 | 1293 | 1324 | 1258 | 1313 | 1345 | 1271 | 1102 | 1336 |  |  | 1188 | 932 | 1319 |  | 1424 | 1278 | 1315 | 1280 | 1308 | 1310 | 1324 | 1333 | 1323 | 1335.3 | 1317 | 1325 | 1475 | 1504 | 1216 | 1177 | 1026 | 897.1 | 1016 | 1131 | 1354 | 1474 | 1423 | 1432.1 | 1353.5 | 1465.9 | 1478 | 1462 | 1296 | 1366 | 1256 | 1350 | 1273 |  | 1875 | 1421.8 | 537 | 1320 | 1287 |  |  | 1278 | 1401 | 1370 | 1266 | 1181 | 36.28 | 44.75 | 2.4 | 6.5 |  | 6.76 | 6.25 |  |  | 85437787.569 | 282335.674 | 58448978.722 | 61998.792 | 86213949.856 | 187445.043 | 62538374.165 | 56181.87 | 323746300.695 | 85241.968 | 88983.576 | 63.118 | 85309.405 | 60.749 | 88430.233 | 63.571 | 69261.103 | 70.757 | 331724.974 | 160.849 | 174169.114 | 331564.125 | 12.7667 | 6.76 | 6.25 | 36.28 | 44.75 | 2.4 | 6.5 | 333824.3
2025-05-26 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:14 | 18:31 | 1120.8 | 1087.1 | 1051.2 | 1046.4 | 1081.8 | 1042.9 | 1041.2 | 1043.8 | 1081.4 | 1088 | 1061.3 | 1056 | 1041.4 | 979.4 | 1037.6 | 1037.9 | 990.2 | 1030.2 | 1119.5 | 1121 | 1040.7 | 1043.8 | 1144.9 | 1176.4 | 1134.3 | 1125.7 | 1116.1 | 1155 | 1172.6 | 1151.8 | 1152.5 | 1162.8 | 968.8 | 1271.8 | 1009.5 | 1155.4 | 1041.7 | 1014.3 | 1030.4 | 1049.9 | 1025.7 | 1010.7 | 1033.9 | 1013.7 | 1032.2 | 1041.2 | 1122.8 | 1028.5 | 1066.6 | 1049.6 | 1014.1 | 1035.1 | 1186.5 | 1166.9 | 1112.7 | 1176.4 | 1176.3 | 1049.6 | 1163.8 | 1135 | 1044.8 | 1181.2 | 1035.9 | 1018 | 1121 | 1111 | 1126.6 | 1085.3 | 1028.8 | 1021.6 | 1030.8 | 1028.1 | 1051.2 | 1034.6 | 1170.7 | 1150.9 | 1173.5 | 1029.7 | 1017.4 | 1125 | 1036.6 | 1039.3 | 1028.3 | 1041.2 | 1026.8 | 1032.3 | 1044.9 | 1034.4 | 1027.8 | 1017 | 1066.2 | 1091.2 | 1055.4 | 1045.7 | 1156.2 | 1018 | 1013.7 | 1040.9 | 1025.4 | 1031.3 | 1058.1 | 1025.9 | 1044.6 | 1023.4 | 1170.1 | 1039.5 | 1226.2 | 1149.7 | 1041.9 | 1154.5 | 1120.3 | 1107.8 | 1170 | 1160.1 | 1033.7 | 1019.7 | 1145.9 | 1161.3 | 1154 | 1038.3 | 1054.7 | 1121.6 | 1090.7 | 1039.2 | 1045.4 | 1183 | 1009 | 1011.6 | 1166.8 | 1152.3 | 1110.8 | 1116.4 | 1113 | 952.5 | 1170.1 | 1088.4 | 1124.6 | 1118.5 | 1100.8 | 1039.3 | 1098.8 | 1101.5 | 1032.7 | 1133.36 | 1008.1 | 1097.9 | 1027.7 | 958.6 | 1066.5 | 1126.6 | 1130.3 | 1036 | 1184.9 | 1038.5 | 1022.8 | 1015.3 | 1025.5 | 1019.4 | 1018.1 | 988.5 | 1142.9 | 1011.9 | 1112.8 | 1121.2 | 1122.5 | 1034.7 | 1004.2 | 1151.6 | 1030.7 | 1031.1 | 1043.9 | 1028.6 | 1145.5 | 1064.7 | 1123.1 | 1004.6 | 1012.1 | 997.2 | 1121.2 | 1031.5 | 1080.6 | 1128.2 | 1110.3 | 1106.6 | 1101 | 1118.1 | 1059.8 | 1042.6 | 1037.6 | 1087.8 | 1014.2 | 1005.1 | 1012.1 | 1030 | 1026.4 | 1031.8 | 866.9 | 1054.4 |  |  | 935.5 | 729.4 | 1030.4 |  | 1113.5 | 999.4 | 1034.4 | 869.6 | 1027.7 | 1033.3 | 1039.6 | 1038.3 | 1041.5 | 1060.6 | 1035.1 | 1044.8 | 1164 | 1187.1 | 960.6 | 924.7 | 800.2 | 677 | 769.6 | 883.5 | 1025.9 | 1104.2 | 1050.4 | 1041.3 | 1019.4 | 1055.5 | 1098.2 | 1086.8 | 927.1 | 998.7 | 931.8 | 962.9 | 897 |  | 1450.1 | 1098.4 | 411.5 | 1007.7 | 975.9 |  |  | 1030.1 | 1075.5 | 1063.4 | 993.6 | 920.1 | 32.47 | 39.01 | 3.18 | 8.3 |  | 5.25 | 4.81 |  |  | 85506921.012 | 282398.792 | 58515310.988 | 62059.541 | 86282183.959 | 187508.614 | 62591209.703 | 56252.627 | 324002684.181 | 85402.817 | 69133.443 | 63.118 | 66332.266 | 60.749 | 68234.103 | 63.571 | 52835.538 | 70.757 | 256383.486 | 160.849 | 135341.842 | 256222.637 | 13.2833 | 5.25 | 4.81 | 32.47 | 39.01 | 3.18 | 8.3 | 258237.06
2025-05-27 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:10 | 18:31 | 1358.8 | 1320.4 | 1274 | 1270.6 | 1315.6 | 1266.5 | 1263 | 1270 | 1311.4 | 1321.7 | 1286.2 | 1280.9 | 1266.5 | 1190.4 | 1264 | 1261.4 | 1179.8 | 1154.3 | 1250.9 | 1253.7 | 1168.7 | 1171.8 | 1255.9 | 1316.7 | 1260.4 | 1276.1 | 1267.6 | 1311.2 | 1302 | 1318.8 | 1300.9 | 1310 | 1167.4 | 1529.4 | 1211.3 | 1398.5 | 1251.7 | 1217.1 | 1235.5 | 1261 | 1243 | 1216.3 | 1237.3 | 1211.8 | 1229.6 | 1234.6 | 1341.7 | 1228.3 | 1264.7 | 1265.5 | 1209.6 | 1228.5 | 1415.9 | 1389.8 | 1341.4 | 1427.3 | 1421.7 | 1267.1 | 1407.2 | 1372.4 | 1258.5 | 1422.6 | 1235.6 | 1201.5 | 1340.5 | 1331.7 | 1339.8 | 1314.6 | 1233.2 | 1227.9 | 1224 | 1217.1 | 1261.1 | 1236.4 | 1406.2 | 1384.1 | 1404 | 1233 | 1219.4 | 1330.1 | 1240.4 | 1244.7 | 1225.5 | 1247 | 1226.2 | 1225.1 | 1236.8 | 1228.1 | 1215.1 | 1207.1 | 1265.5 | 1332.5 | 1251.3 | 1248.6 | 1378.3 | 1228.3 | 1225.7 | 1254.7 | 1246.5 | 1246.5 | 1281.7 | 1250.8 | 1276.4 | 1249.4 | 1419.8 | 1257.8 | 1485.2 | 1385.5 | 1255.4 | 1363.7 | 1341.7 | 1323.3 | 1391.4 | 1393.4 | 1247.2 | 1212.6 | 1375.3 | 1375.5 | 1373.8 | 1242.1 | 1265.7 | 1357.5 | 1361.5 | 1254.7 | 1259.6 | 1408.6 | 1145.4 | 1139.9 | 1406 | 1390.7 | 1355.6 | 1359.1 | 1352.8 | 1159.1 | 1437.4 | 1329.7 | 1389.7 | 1377.5 | 1374.5 | 1293.2 | 1339.2 | 1340.7 | 1297.4 | 1405.1 | 1257.1 | 1322.1 | 1264.2 | 1178.9 | 1367.3 | 1380 | 1394.4 | 1273.5 | 1443 | 1272.9 | 1245.9 | 1237.1 | 1239.3 | 1169.5 | 1264.5 | 1255.1 | 1414.3 | 1222.4 | 1398.7 | 1355.7 | 1400.2 | 1260.1 | 1245.5 | 1422.2 | 1277.9 | 1270.7 | 1290 | 1265.7 | 1406.8 | 1311.2 | 1370.2 | 1247.3 | 1245.6 | 1234.4 | 1395.3 | 1277.6 | 1332.5 | 1359.1 | 1392.7 | 1380.3 | 1365.8 | 1352.6 | 1308.5 | 1267.8 | 1244.5 | 1332 | 1216.1 | 1205.1 | 1237.4 | 1240.5 | 1242.1 | 1250.7 | 1049.4 | 1277.7 |  |  | 1121 | 870.3 | 1238.7 |  | 1353 | 1218.1 | 1232.5 | 1223.5 | 1230 | 1232.2 | 1261 | 1247.1 | 1264.2 | 1274.7 | 1254.8 | 1262.6 | 1404.3 | 1429 | 1146 | 1116.8 | 960.4 | 811.1 | 955.1 | 1101.1 | 1293.1 | 1380.9 | 1324.4 | 1321.1 | 1313.5 | 1366 | 1376.1 | 1364.1 | 1190.1 | 1268.1 | 1212.1 | 1223.1 | 1141.1 |  | 1717.8 | 1301.4 | 501.4 | 1212 | 1178.3 |  |  | 1199.1 | 1313.1 | 1275.1 | 1194.1 | 1091.7 | 34.17 | 39.27 | 1.95 | 5.7 |  | 6.45 | 5.98 |  |  | 85588649.621 | 282458.91 | 58594183.415 | 62116.29 | 86365956.86 | 187568.185 | 62655291.274 | 56322.384 | 324310907.99 | 85561.666 | 81728.609 | 60.118 | 78872.427 | 56.749 | 83772.901 | 59.571 | 64081.571 | 69.757 | 308223.809 | 158.849 | 160484.169 | 308064.96 | 13.35 | 6.45 | 5.98 | 34.17 | 39.27 | 1.95 | 5.7 | 311840.2
2025-05-28 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:06 | 18:31 | 1052.8 | 1019.8 | 983.2 | 980.7 | 1016.2 | 978.1 | 981.6 | 981.9 | 1014 | 1017.8 | 1000.4 | 993.2 | 978.5 | 921.5 | 974.5 | 971.2 | 932 | 968.1 | 1046.9 | 1049.2 | 980.2 | 989.5 | 1073.5 | 1104.4 | 1066.9 | 1060.1 | 1052.3 | 1090 | 1103.5 | 1087.6 | 1006.1 | 1097.5 | 851.4 | 1055.6 | 954.8 | 1081.6 | 984.7 | 960.5 | 955.8 | 989.5 | 971.7 | 963.5 | 977.8 | 960.2 | 977.1 | 985.4 | 1060.4 | 979.2 | 1009.9 | 991.7 | 938.5 | 981.3 | 1122.7 | 1103.8 | 1050.5 | 1107.6 | 1109.3 | 986.7 | 1093.8 | 1061.7 | 989.5 | 1113.8 | 977.2 | 951.1 | 1054.4 | 1046.8 | 1061.5 | 1036.8 | 935.1 | 962.1 | 970.2 | 967.6 | 987 | 969 | 1104.8 | 1085.7 | 1105.1 | 971.2 | 955.9 | 1046.1 | 972.8 | 977.2 | 965.3 | 979.6 | 962.9 | 967.3 | 978.9 | 969 | 962.6 | 953.3 | 1001.8 | 1049.9 | 990.9 | 982.8 | 1089.7 | 958.1 | 961.9 | 978.7 | 974.7 | 971.2 | 998.2 | 974.8 | 995.7 | 978.7 | 1116.4 | 986.4 | 1163.4 | 1085.6 | 982.6 | 1083.7 | 1055.8 | 1044.8 | 1096.7 | 1094.9 | 975.8 | 928.8 | 1082.5 | 1091.8 | 1087.4 | 975.4 | 992.6 | 1044.5 | 1013.6 | 977.7 | 984.7 | 1111.6 | 551.7 | 586.4 | 703.7 | 692.8 | 615.2 | 666.6 | 655.8 | 559.8 | 684.9 | 639.8 | 662 | 656.2 | 646.2 | 614.2 | 647.2 | 643.8 | 622.3 | 674 | 603.3 | 639.8 | 617.5 | 580.7 | 678 | 682.9 | 687.2 | 630.5 | 715.8 | 631.8 | 622 | 618.3 | 624.5 | 620.4 | 451.5 | 436.9 | 503 | 436.9 | 508.9 | 482.7 | 516.2 | 444.5 | 445.7 | 506.2 | 457.3 | 452.7 | 462.9 | 455.9 | 501.6 | 471.9 | 472 | 447.8 | 450 | 443.5 | 502.8 | 457.3 | 478.5 | 487.4 | 506.7 | 492.9 | 486 | 483.6 | 468.6 | 454.7 | 437.6 | 477.2 | 935.2 | 915.3 | 881.2 | 956 | 952.9 | 956.1 | 802.2 | 974.6 |  |  | 852 | 643.4 | 946 |  | 1030.7 | 904.1 | 959 | 934.8 | 953.8 | 959.8 | 973.1 | 968.2 | 973.4 | 991.6 | 968.6 | 980 | 1092.7 | 1116.1 | 897 | 868.4 | 750.7 | 631.8 | 692.5 | 813.5 | 985.8 | 1047.1 | 993.9 | 976.5 | 985.5 | 1041.5 | 1044.4 | 1026.3 | 836.2 | 927.7 | 835.8 | 885.5 | 783.4 |  | 1180.5 | 942.8 | 391.3 | 873 | 845.7 |  |  | 962.9 | 978 | 875.9 | 841.5 | 741.5 | 36.79 | 48.09 | 1.97 | 4.9 |  | 6.79 | 6.28 |  |  | 85653541.874 | 282521.028 | 58656363.174 | 62174.039 | 86401496.786 | 187607.756 | 62704410.555 | 56393.141 | 324522533.773 | 85721.515 | 64892.253 | 62.118 | 62179.759 | 57.749 | 35539.926 | 39.571 | 49119.281 | 70.757 | 211625.783 | 159.849 | 126952.145 | 211465.934 | 13.4167 | 6.79 | 6.28 | 36.79 | 48.09 | 1.97 | 4.9 | 212537.6
2025-05-29 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:09 | 18:19 | 1087.9 | 1075.2 | 1015.7 | 1014.6 | 1048.6 | 1009.8 | 1010.7 | 1012.3 | 1045.3 | 1051.3 | 1029.8 | 1022.9 | 1007.6 | 944.7 | 1003.8 | 1000.8 | 1001.3 | 1000.2 | 1077.8 | 1082.1 | 1010.7 | 1007.8 | 1104.6 | 1134.4 | 1100.4 | 1089.8 | 1081 | 1124.3 | 1138.1 | 1135.2 | 1129.1 | 1131.8 | 940 | 1245.8 | 992.9 | 1126.6 | 1017.7 | 998.8 | 1002.5 | 1031.3 | 1012.4 | 1007.9 | 1021.4 | 1004.5 | 1010.5 | 1018 | 1095.4 | 1003.5 | 1045.1 | 1027.6 | 968.6 | 1012.4 | 1158.7 | 1139.9 | 1081.8 | 1126 | 1143.2 | 1017.4 | 1128.8 | 1094.4 | 1026.3 | 1152.5 | 1010.6 | 974.9 | 1097.1 | 1090.1 | 1105.1 | 1080.8 | 1004.7 | 1003.3 | 1010 | 1007.8 | 1027.5 | 1010 | 1166.5 | 1143.3 | 1163.1 | 1023.7 | 999.6 | 1090.9 | 1022.8 | 1022.7 | 1007.8 | 1019.9 | 1005.4 | 1010.7 | 1021.4 | 1012.3 | 1006.4 | 997.4 | 1047.7 | 1088.5 | 1031.4 | 1022.2 | 1137.6 | 998.2 | 1006.5 | 1019.1 | 1018.2 | 1012.5 | 1037.2 | 1016.2 | 1034 | 1017.7 | 1164.3 | 1018.4 | 1199.2 | 1131.3 | 1020.5 | 1126.5 | 1094.6 | 1091.1 | 1147 | 1140.3 | 1015.4 | 962.5 | 1128.3 | 1134.7 | 1130.2 | 1015.4 | 1029 | 1090.5 | 1055.1 | 1014.7 | 1021.2 | 1153.7 | 925.1 | 945.2 | 1059.4 | 1044.4 | 927.8 | 1009.3 | 999.1 | 854.7 | 1048.3 | 977.3 | 1014.2 | 1002.3 | 983.5 | 931.7 | 984.8 | 980.7 | 940.5 | 1017.8 | 901 | 959.1 | 926.4 | 862.6 | 1004.8 | 1011.4 | 1016.5 | 935.7 | 1069.4 | 942 | 931.7 | 922.9 | 935.5 | 931.4 | 110.4 | 108.1 | 123.3 | 106.7 | 123.7 | 121.8 | 123.5 | 115.7 | 107.8 | 121.9 | 105.8 | 113.9 | 111.2 | 114.9 | 122.6 | 115.8 | 120.9 | 108.2 | 105.8 | 107.4 | 124.9 | 106.4 | 117.8 | 123.8 | 110.4 | 119.5 | 116.7 | 118.1 | 113.6 | 112.1 | 113 | 116.9 | 994 | 967 | 921.8 | 1012.2 | 1004.6 | 1011.8 | 847.6 | 1030.6 |  |  | 916.6 | 686.4 | 1001 |  | 976 | 1009.8 | 1009.8 | 980.6 | 1007.3 | 1009.3 | 1027.7 | 1021.5 | 1025.4 | 1042.3 | 1017.6 | 1029.3 | 1148.3 | 1171.9 | 936.8 | 912.2 | 786.1 | 663.4 | 670.5 | 791.7 | 953.2 | 1022.7 | 961.3 | 943.1 | 964.5 | 991.5 | 1019.2 | 955.6 | 855.4 | 907 | 807.7 | 865.3 | 768.4 |  | 1300.2 | 1014.2 | 385.1 | 938.4 | 910.4 |  |  | 1033 | 1052.4 | 885 | 910.9 | 788 | 35.73 | 41.95 | 2.07 | 9.69 |  | 5.38 | 4.87 |  |  | 85720663.674 | 282584.146 | 58721000.481 | 62233.788 | 86435802.361 | 187649.327 | 62755226.617 | 56462.898 | 324739366.519 | 85883.364 | 67121.8 | 63.118 | 64637.307 | 59.749 | 34305.575 | 41.571 | 50816.062 | 69.757 | 216832.746 | 161.849 | 131636.24 | 216670.897 | 13.1667 | 5.38 | 4.87 | 35.73 | 41.95 | 2.07 | 9.69 | 218430.9
2025-05-30 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:12 | 18:13 | 1194.2 | 1189.9 | 1157.9 | 1113.5 | 1171.6 | 1111 | 1108.3 | 1111.7 | 1149 | 1159.6 | 1130.2 | 1124.7 | 1109.3 | 1041.8 | 1106.8 | 1101.8 | 1085.4 | 1100.2 | 1168.3 | 1190.8 | 1111.3 | 1110.7 | 1213.8 | 1246 | 1208.8 | 1199.1 | 1199.1 | 1230.5 | 1231.9 | 1253 | 1259.5 | 1238.1 | 1030.5 | 1360.7 | 1085.3 | 1231.9 | 1123.4 | 1095.4 | 1112.1 | 1129.8 | 1108.5 | 1096.9 | 1114.9 | 1094.4 | 1113 | 1111.4 | 1209.7 | 1140.6 | 1140.6 | 1121.2 | 1089.7 | 1104.7 | 1269.7 | 1249.8 | 1188.7 | 1255.2 | 1252.4 | 1118.3 | 1240.6 | 1208.6 | 1126.1 | 1268.8 | 1104.5 | 1075.2 | 1196.8 | 1189.7 | 1205.4 | 1176.6 | 1096.5 | 1094.1 | 1101.6 | 1098.1 | 1120 | 1101.1 | 1267.2 | 1241.2 | 1265.7 | 1114.2 | 1092.6 | 1182.6 | 1113.4 | 1114.5 | 1096.1 | 1111.4 | 1110.2 | 1104.8 | 1113.2 | 1102.5 | 1096.6 | 1085.7 | 1142.7 | 1185.5 | 1124.1 | 1115.5 | 1241.1 | 1087 | 1092.1 | 1112.3 | 1103.7 | 1104.4 | 1136.2 | 1107.4 | 1131 | 1110.5 | 1271.3 | 1118 | 1314.2 | 1232 | 1117.5 | 1229.7 | 1202.8 | 1188.5 | 1250.8 | 1243.9 | 1107.1 | 1081.6 | 1227.8 | 1246.4 | 1239.2 | 1116 | 1128.6 | 1243.5 | 1289.5 | 1113.2 | 1121.2 | 1266.7 | 1081.1 | 1078.4 | 1258.8 | 1243.6 | 1175.8 | 1203.8 | 1192.5 | 1022.5 | 1254.9 | 1164.1 | 1210.3 | 1173.3 | 1177.5 | 1116.6 | 1176.7 | 1172.2 | 1116.9 | 1213.6 | 1079.9 | 1167.9 | 1105.6 | 1030.3 | 1195.4 | 1208.8 | 1216.7 | 1118.5 | 1283.5 | 1127.6 | 1110.7 | 1097.2 | 1101.5 | 1087.9 | 1071.2 | 1079.6 | 1211.1 | 1064.5 | 1215.8 | 1201.2 | 1195.8 | 1121.5 | 1071.7 | 1203.4 | 1064.5 | 1111.5 | 1108.2 | 1121.5 | 1207.9 | 1169.1 | 1216.5 | 1063.8 | 1069.1 | 1075.5 | 1213.5 | 1078.8 | 1179.5 | 1201.2 | 1197.5 | 1121.7 | 1154.5 | 1220.5 | 1111.8 | 1119.7 | 1108.5 | 1159.4 | 1095.8 | 1079 | 1080.5 | 1111.9 | 1105.5 | 1114 | 931.4 | 1134 |  |  | 1008.2 | 792.1 | 1104.8 |  | 1203.1 | 1069.2 | 1112.5 | 1081.1 | 1107 | 1108.6 | 1127 | 1121.4 | 1124.1 | 1143.6 | 1117 | 1128.8 | 1256.4 | 1279.8 | 1025 | 996.6 | 860 | 724.1 | 845.3 | 981.7 | 1149 | 1243.1 | 1173.1 | 1247 | 1151.4 | 1174.9 | 1234.5 | 1251.5 | 1091.4 | 1134.6 | 1082.7 | 1087.8 | 1027.8 |  | 1475.5 | 1190.6 | 437.5 | 1078.3 | 1050.8 |  |  | 1081 | 1121.7 | 1101.3 | 1043.6 | 997 | 36.45 | 45.55 | 2.33 | 7.9 |  | 5.85 | 5.34 |  |  | 85794428.611 | 282650.264 | 58791589.399 | 62295.537 | 86508783.115 | 187691.898 | 62812737.713 | 56533.655 | 325014163.677 | 86045.213 | 73764.937 | 66.118 | 70588.918 | 61.749 | 72980.754 | 42.571 | 57511.096 | 70.757 | 274797.158 | 161.849 | 144225.988 | 274635.309 | 13.0167 | 5.85 | 5.34 | 36.45 | 45.55 | 2.33 | 7.9 | 277904.9
2025-05-31 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:13 | 18:24 | 1073.4 | 1003 | 1002 | 1000.6 | 1001 | 995.6 | 997.5 | 998.1 | 1031.4 | 1039.6 | 1014.1 | 1009.4 | 995.1 | 937 | 994.4 | 991.1 | 997 | 989.2 | 1068 | 1071.4 | 1008 | 1023.09 | 1098.8 | 1141 | 1099 | 1081.4 | 1071 | 1109.5 | 1129.5 | 1107.8 | 1121.8 | 1117.4 | 944.8 | 1234.4 | 988.6 | 1107.8 | 1006.4 | 980.7 | 995.9 | 1014.1 | 990.1 | 985.8 | 989.8 | 975.5 | 1010.2 | 989.2 | 1096.6 | 993.7 | 1039.9 | 1032.6 | 908.9 | 1010.6 | 1161.2 | 1144.4 | 1070.1 | 1128.3 | 1127.2 | 1003.1 | 1113 | 1009.4 | 1008.3 | 1135.5 | 1005.4 | 961.7 | 1084.1 | 1076.4 | 1092.9 | 1063.1 | 991.9 | 992.7 | 998.8 | 994.3 | 1017.1 | 995.9 | 1157.9 | 1134 | 1156.1 | 1015 | 994.1 | 1062.9 | 1010.3 | 1012.9 | 992.1 | 1008.1 | 1009.6 | 1014.7 | 1010.2 | 998.9 | 992.2 | 981.9 | 1033.4 | 1065.2 | 1018.3 | 1012 | 1123.7 | 985.8 | 992 | 1009.9 | 1001.8 | 1003.3 | 1032.2 | 1005 | 1028.2 | 1007.6 | 1158.2 | 1012.1 | 1119.5 | 1118.1 | 1013.2 | 1103.3 | 1087.1 | 1072.7 | 1114.9 | 1125.3 | 1004.2 | 997.5 | 1112.8 | 1123.3 | 1120.6 | 1006 | 1020.2 | 1113.2 | 1124.1 | 1006.2 | 1014.4 | 1144.9 | 998.9 | 987.1 | 1139.9 | 1120.6 | 1076 | 1084.2 | 1074.2 | 921.2 | 1059.4 | 1050.6 | 1090.4 | 1100.5 | 1060.5 | 1007.2 | 1059.6 | 1060.7 | 1007.3 | 1095.8 | 973.4 | 1035.3 | 1000.5 | 932.8 | 1081.3 | 1093.6 | 1102.5 | 1013 | 1164.3 | 1022.3 | 1006.1 | 994 | 1005.5 | 998 | 989.5 | 980.9 | 1121.2 | 972.6 | 1119.5 | 1125.5 | 1120.1 | 1035.5 | 981.5 | 1118.4 | 991.5 | 1031.5 | 1036.9 | 1034.8 | 1124.5 | 1031.8 | 1021.5 | 992.6 | 989.5 | 981.5 | 1129.6 | 987.5 | 1084.2 | 1116.2 | 1123.1 | 1029.5 | 1081.6 | 1013.8 | 1029.5 | 988.8 | 1026.4 | 1079.5 | 984.9 | 981.2 | 991.5 | 1002.4 | 998.6 | 1001.8 | 840.9 | 1021.7 |  |  | 906.5 | 710.5 | 991.9 |  | 1084.2 | 980.7 | 1011.3 | 980.2 | 1002.9 | 1007.3 | 1023.3 | 1018.9 | 1022.7 | 1033.6 | 1014 | 1024 | 1143 | 1163.8 | 924 | 899 | 774.3 | 656.1 | 769.2 | 879.3 | 1034.5 | 1109.7 | 1066.6 | 1122 | 1031.5 | 1061.4 | 1104.2 | 1112.6 | 950 | 1020.9 | 941.5 | 991 | 926 |  | 1330 | 1067.7 | 414.1 | 995.4 | 938.8 |  |  | 1024.6 | 1040.2 | 1053.7 | 946.8 | 901 | 33.5 | 42 | 3.1 | 8.3 |  | 5.3 | 4.85 |  |  | 85860885.701 | 282715.293 | 58855621.315 | 62358.83 | 86575069.974 | 187741 | 62864610.12 | 56612.761 | 325261923.023 | 86205.025 | 66457.09 | 65.029 | 64031.916 | 63.293 | 66286.859 | 49.102 | 51872.407 | 79.106 | 247759.346 | 159.812 | 130360.684 | 247599.534 | 13.1833 | 5.3 | 4.85 | 33.5 | 42 | 3.1 | 8.3 | 251303.79
2025-06-01 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:14 | 18:33 | 985.3 | 995.1 | 908.1 | 920.9 | 994.5 | 918.2 | 921.1 | 912.5 | 954.2 | 959.4 | 938.8 | 934.2 | 917.9 | 862.9 | 917.1 | 921.5 | 873.6 | 910 | 987.9 | 990.7 | 920.6 | 920.2 | 1007.6 | 1036 | 1006.9 | 997.3 | 988.7 | 1021.7 | 1040.6 | 1023.5 | 1031.7 | 1030.8 | 865.2 | 1139.4 | 902.2 | 1031.9 | 925.6 | 901 | 918.2 | 931.6 | 913.1 | 907.3 | 920.6 | 832.1 | 918 | 921.7 | 995.5 | 911.5 | 946.7 | 930.7 | 916.6 | 918.9 | 1050 | 1034.8 | 988.2 | 1040.1 | 1042.5 | 927.5 | 1028.5 | 1041.4 | 925.1 | 1046.4 | 918.8 | 892.2 | 987.9 | 980.6 | 996.5 | 971.1 | 905.9 | 901.1 | 909.8 | 905.8 | 927.6 | 911.9 | 1051 | 1030.4 | 1045.5 | 916.1 | 906 | 985.3 | 920 | 922.1 | 909.2 | 921.2 | 911.5 | 913.5 | 920 | 912.1 | 905.3 | 916.9 | 942.7 | 990.8 | 929.8 | 922.3 | 1023 | 900.1 | 903.5 | 915.8 | 909.4 | 908.5 | 933.4 | 908.6 | 927.8 | 910.6 | 1047.7 | 912.8 | 1090.1 | 1017.1 | 917.7 | 1014.6 | 981.8 | 983.2 | 1029 | 1024.6 | 911.3 | 915.5 | 1015 | 1017.6 | 1014.6 | 912.3 | 927 | 1019.1 | 1025.5 | 910.9 | 916.4 | 1021.5 | 901.4 | 909.9 | 1029.3 | 1018.7 | 907.2 | 989.5 | 985.7 | 843.6 | 1036 | 1041.4 | 1031.8 | 1038.5 | 973 | 926.5 | 1042 | 1036.6 | 921.2 | 1003.7 | 887.9 | 948.2 | 914 | 850.2 | 981.8 | 994.7 | 998.7 | 912.3 | 1040.7 | 915.7 | 921.6 | 911.6 | 909.6 | 917.5 | 887.5 | 891.2 | 1027.5 | 892.3 | 1031.3 | 1029.5 | 1025.6 | 919.5 | 889.5 | 1021.5 | 885.5 | 920.1 | 911.5 | 915.7 | 1030.6 | 915.4 | 1021.5 | 891.1 | 886.4 | 890.7 | 1024.4 | 888.1 | 957.6 | 1019.5 | 1028.3 | 916.4 | 966.3 | 1024.4 | 920.4 | 923.5 | 921.4 | 964.5 | 901.5 | 911.2 | 907.5 | 916.6 | 907.8 | 676.5 | 769.2 | 929 |  |  | 820.9 | 621.7 | 907.7 |  | 993.4 | 878 | 918 | 892.5 | 913.6 | 914.6 | 925.3 | 920.9 | 925.2 | 936.2 | 920.7 | 930.2 | 1037.4 | 1056.8 | 849.7 | 827.8 | 710.6 | 601.2 | 717.4 | 808.4 | 943.4 | 1017.8 | 983.7 | 962.4 | 935.5 | 989.7 | 1010.7 | 1116.3 | 860.9 | 929.5 | 869.2 | 926.7 | 868.5 |  | 1238.4 | 965.1 | 424.5 | 897.9 | 873.4 |  |  | 906.6 | 950.9 | 911.7 | 856.9 | 815.3 | 31.9 | 40.8 | 3.4 | 6.2 |  | 4.91 | 4.4 |  |  | 85922250.649 | 282756.322 | 58914133.54 | 62411.123 | 86636539.254 | 187780.102 | 62911708.9 | 56689.867 | 325491068.834 | 86361.837 | 61364.948 | 41.029 | 58512.225 | 52.293 | 61469.28 | 39.102 | 47098.78 | 77.106 | 229145.811 | 156.812 | 119783.851 | 228988.999 | 13.3167 | 4.91 | 4.4 | 31.9 | 40.8 | 3.4 | 6.2 | 229035.1
2025-06-02 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:15 | 17:56 | 1020.1 | 1026 | 984.9 | 1026 | 1098.5 | 1016.8 | 1014.6 | 932.7 | 1051.5 | 1057.3 | 1034.1 | 1030 | 1013.7 | 952.5 | 1012.5 | 1006.2 | 963.1 | 1004.7 | 1091.6 | 1092.3 | 1016.1 | 1016.4 | 1110.6 | 1144.6 | 1111.2 | 1100.8 | 1093.6 | 1130.8 | 1153.3 | 1130 | 1155.5 | 1145.5 | 1005.2 | 1154.5 | 1050.2 | 1182.9 | 1054 | 1024.5 | 1043 | 1056.2 | 1038.1 | 1030.5 | 1047.4 | 1041.2 | 1042.3 | 1049 | 1130.8 | 1035.8 | 1078.3 | 1058.6 | 1041.5 | 1044.4 | 1194.9 | 1177.3 | 1123.6 | 1199 | 1185 | 1054.3 | 1169.4 | 1185.9 | 1050.7 | 1193.2 | 1037.1 | 1021.1 | 1166.8 | 1161.2 | 1170 | 1141.6 | 1069.2 | 1067.6 | 1071.8 | 1066.7 | 1084 | 1066.3 | 1207.5 | 1187 | 1210.7 | 1066.2 | 1056.8 | 1141.7 | 1025.9 | 1076.3 | 1061.3 | 1077.6 | 1060.3 | 1062.6 | 1071.2 | 1060.6 | 1062.8 | 1052 | 1108 | 1168.09 | 1083.1 | 1075.4 | 1203 | 1055.7 | 1054.3 | 1078.3 | 1062.2 | 1070 | 1097.8 | 1065.4 | 1087.1 | 1064 | 1215.6 | 1077.7 | 1265 | 1188 | 1080.5 | 1183.4 | 1160.7 | 1140.5 | 1196.1 | 1196.7 | 1073.3 | 1027.4 | 1181.2 | 1199.9 | 1198.7 | 1077.6 | 1089.3 | 1148.2 | 1144.3 | 1073.1 | 1083.3 | 1217.5 | 903.2 | 917.7 | 1145.5 | 1132 | 1008.7 | 1097.7 | 1094.5 | 938.1 | 1155 | 1075.2 | 1114.9 | 1021.3 | 1093 | 1034.9 | 1081.6 | 1078.5 | 1028.1 | 1119.9 | 996.1 | 1061.3 | 1019.5 | 946.8 | 1092.3 | 1106.8 | 1114.3 | 1019.2 | 1167.1 | 1024.6 | 1006 | 1005 | 1010.5 | 1006.4 | 960.3 | 944.4 | 1090.2 | 951.1 | 1100.1 | 1109.1 | 1101.6 | 965.6 | 954.6 | 1111.8 | 960.6 | 969.3 | 965.6 | 967.1 | 1090.1 | 992.1 | 1109.1 | 948.8 | 957.2 | 953.3 | 1101.4 | 955.1 | 1070.7 | 1101.1 | 1111.9 | 971.2 | 1067.1 | 1107.8 | 1000.1 | 1001.1 | 1011.2 | 1069.1 | 1054.4 | 1050.3 | 1055.2 | 1068.9 | 1064.1 | 1059.9 | 900 | 1083.8 |  |  | 960.1 | 723.8 | 1060 |  | 1144.2 | 1019.3 | 1075.3 | 1071.1 | 1068.9 | 1070.8 | 1083.1 | 1079.7 | 1083.8 | 1095.4 | 1076.4 | 1086.7 | 1250.5 | 1221.7 | 980 | 955.8 | 823.3 | 694.4 | 841.2 | 961.5 | 1119.3 | 1191.7 | 1122 | 1121.1 | 1105.5 | 1134.5 | 1171.7 | 1182.8 | 1008.4 | 1100.7 | 996 | 1052.3 | 985.5 |  | 1400.5 | 1097.4 | 484.3 | 1021.1 | 991.1 |  |  | 1079.8 | 1091.7 | 1090.1 | 1018.9 | 912.1 | 32.2 | 41.3 | 3.2 | 4.8 |  | 5.82 | 5.25 |  |  | 85990477.919 | 282794.351 | 58982150.982 | 62461.416 | 86703331.58 | 187817.204 | 62966455.413 | 56765.973 | 325748697.178 | 86518.649 | 68227.27 | 38.029 | 68017.442 | 50.293 | 66792.326 | 37.102 | 54746.513 | 76.106 | 257628.344 | 156.812 | 136156.39 | 257471.532 | 12.6833 | 5.82 | 5.25 | 32.2 | 41.3 | 3.2 | 4.8 | 259288.99
2025-06-03 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:19 | 18:33 | 891.8 | 902.2 | 825.3 | 977.8 | 1052.6 | 976.4 | 976.5 | 924.2 | 1010.1 | 1016.3 | 992.7 | 988.2 | 971.4 | 912.8 | 971.3 | 966.6 | 922.9 | 961.3 | 1039.7 | 1043.5 | 972.5 | 973.6 | 1066.8 | 1095.1 | 1060.1 | 1051.7 | 1044.5 | 1082.6 | 1094.4 | 1081.4 | 1101.5 | 1105.5 | 726.3 | 831.2 | 853.5 | 959 | 857.9 | 837.3 | 853.8 | 866.4 | 846.6 | 840 | 857.6 | 860.5 | 855.5 | 860.8 | 928.3 | 834.5 | 885.5 | 870.1 | 857.7 | 867.8 | 980.4 | 966.6 | 922.2 | 975.7 | 972.3 | 866 | 956.7 | 967.3 | 859.7 | 971.7 | 852.2 | 835 | 1061.7 | 1056.6 | 1064.3 | 1040.5 | 980.5 | 980.3 | 991.2 | 986.2 | 1007.6 | 978.7 | 1105.3 | 1084.2 | 1115.9 | 986.6 | 980 | 1042.7 | 955.1 | 999.2 | 987.7 | 1002.3 | 990.2 | 993.4 | 999.2 | 991.7 | 984.96 | 975.3 | 1012 | 1045.5 | 1004.8 | 1001.3 | 1099.2 | 995.5 | 980.2 | 996.8 | 982.6 | 989.5 | 1013.3 | 987.1 | 1003.1 | 983.8 | 1110.4 | 994.9 | 1148.6 | 1087.8 | 996 | 1074.9 | 1065.3 | 982.9 | 1088.9 | 1098.9 | 993.4 | 934.5 | 1077.8 | 1094.1 | 1093.9 | 993.4 | 1000.1 | 1045.6 | 1030.3 | 990.8 | 1001.1 | 1112 | 812.2 | 817.2 | 918.6 | 905.9 | 839.4 | 875.6 | 870.9 | 749 | 917.6 | 857.1 | 887.7 | 810.5 | 863.1 | 820 | 862 | 762.7 | 816.9 | 889.6 | 784.4 | 872.9 | 810.1 | 673 | 871.6 | 881.4 | 887.9 | 814.6 | 930.1 | 818.4 | 836 | 814.6 | 820.5 | 821.4 | 935.5 | 929.5 | 1035.5 | 933.4 | 1031.5 | 1039.4 | 1021.5 | 975.8 | 940.5 | 1045.5 | 920.2 | 970.5 | 974.5 | 971.4 | 1034.4 | 969.1 | 1044.5 | 931.9 | 939.4 | 945.1 | 1047.5 | 933.5 | 999.5 | 1041.5 | 1037.1 | 1020.4 | 987.1 | 1045 | 965.5 | 983.7 | 971.5 | 999 | 953.3 | 940.2 | 820 | 965.4 | 962.9 | 841.5 | 816 | 979.2 |  |  | 856.3 | 662.3 | 960.4 |  | 1038.7 | 932.7 | 989.5 | 928.4 | 985.9 | 987.4 | 999 | 996.7 | 999.8 | 998.7 | 994.9 | 1000 | 1103.8 | 1122.4 | 882.4 | 866.4 | 744.8 | 625.1 | 724.2 | 849.5 | 1014.7 | 1082.8 | 1027.1 | 1005.2 | 1021.5 | 1045.5 | 1076.1 | 1021.1 | 869.4 | 977.9 | 867.1 | 931.6 | 838.4 |  | 1270.2 | 976.5 | 401.1 | 918.1 | 883 |  |  | 1002.9 | 994.3 | 980.6 | 881.8 | 831.2 | 32.1 | 40.8 | 2.8 | 7.1 |  | 5.12 | 4.62 |  |  | 86050319.559 | 282835.659 | 59044847.468 | 62500.709 | 86761490.088 | 187849.235 | 63016997.599 | 56840.709 | 325979691.535 | 86675.461 | 59841.64 | 41.308 | 62696.486 | 39.293 | 58158.508 | 32.031 | 50542.186 | 74.736 | 230994.357 | 156.812 | 122457.525 | 230837.545 | 13.2333 | 5.12 | 4.62 | 32.1 | 40.8 | 2.8 | 7.1 | 231929.06
2025-06-04 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:10 | 18:33 | 1193.4 | 1204.8 | 1072 | 1113.2 | 1198.9 | 1113.2 | 1115.2 | 1066.5 | 1157.3 | 1160.4 | 1138.8 | 1135.5 | 1116 | 1053.6 | 1116 | 1112.8 | 1067.3 | 1095.5 | 1198.3 | 1197.9 | 1113.6 | 1074.4 | 1226.6 | 1260.3 | 1210.6 | 1203.9 | 1194.6 | 1234.3 | 1256.6 | 1229.4 | 1245.5 | 1239.5 | 1031.4 | 1290.7 | 1061.2 | 1208.4 | 1084.5 | 1066.1 | 1076 | 1096.3 | 1064.4 | 1063.1 | 1079.5 | 1071.1 | 1077.5 | 1085.6 | 1172.5 | 1071.1 | 1114 | 1115.1 | 1082.2 | 1069.9 | 1240.8 | 1220.7 | 1166.7 | 1230.2 | 1233.4 | 1100 | 1219.7 | 1236.5 | 1087.7 | 1231.4 | 1069.1 | 993.2 | 1191.5 | 1183.1 | 1198.7 | 1168.5 | 1094.1 | 1086.1 | 1096 | 1092.4 | 1114.9 | 1098.5 | 1252.1 | 1230.4 | 1250.9 | 1099.5 | 1087.2 | 1197.9 | 1071.1 | 1107.7 | 1096.4 | 1110.6 | 1096 | 1098.2 | 1107.1 | 1098.3 | 1087.1 | 1075.5 | 1136.7 | 1214.5 | 1121.4 | 1109.2 | 1231.9 | 1078.5 | 1078.4 | 1108.4 | 1087.9 | 1096.2 | 1126.5 | 1091.4 | 1110.3 | 1079.5 | 1247.2 | 1107.8 | 1311.7 | 1224.1 | 1110.1 | 1230.8 | 1197.5 | 1178.4 | 1244.1 | 1238.1 | 1100.7 | 1100.5 | 1221 | 1246.9 | 1238 | 1106.3 | 1120.9 | 1244.2 | 1241.5 | 1104.9 | 1112.5 | 1261.6 | 1082.2 | 1088.8 | 1233.7 | 1215.1 | 1133.1 | 1177.1 | 1171.6 | 1003.8 | 1235.5 | 1147 | 1188.4 | 1109.1 | 1162.2 | 1099.4 | 1157.3 | 1153.7 | 1090.9 | 1193.1 | 1063.8 | 1211.5 | 1084.1 | 1008.7 | 1172.9 | 1184.6 | 1195.5 | 1094.9 | 1254.8 | 1099.7 | 1079.5 | 1069.7 | 1078.5 | 1037.5 | 1064.5 | 1069.5 | 1201.2 | 1071.5 | 1188.1 | 1181.5 | 1193.1 | 1109.2 | 1074.5 | 1189.3 | 1077.5 | 1111.8 | 1107.5 | 1109.4 | 1181.6 | 1109.5 | 1185.2 | 1079.5 | 1074.6 | 1081.6 | 1189.9 | 1069.5 | 1149.5 | 1188.2 | 1196.2 | 1104.5 | 1145.8 | 1191.2 | 1104.6 | 1109.4 | 1111.9 | 1141.4 | 1075.5 | 1083.2 | 1078.1 | 1090.3 | 1088.5 | 1094.4 | 920.9 | 1115 |  |  | 981.8 | 781.1 | 1094.5 |  | 1180.4 | 1071.2 | 1101.9 | 977.2 | 1089 | 1097.7 | 1105.4 | 1104.2 | 1107 | 1125.2 | 1104.8 | 1109.8 | 1240.7 | 1263.4 | 1020.7 | 989.4 | 850.9 | 717.9 | 852.1 | 981.2 | 1132.9 | 1216.6 | 1165.6 | 1169.2 | 1142.5 | 1174.5 | 1208.1 | 1201 | 1055.6 | 1123.2 | 1032.1 | 1071.2 | 1001.2 |  | 1455.5 | 1168 | 447.2 | 1079.2 | 1032.1 |  |  | 1123.2 | 1140.1 | 1140.1 | 1044.3 | 984.2 | 36.4 | 48 | 3.1 | 6.3 |  | 5.74 | 5.18 |  |  | 86122985.268 | 282856.967 | 59115455.755 | 62524.002 | 86834246.849 | 187871.266 | 63073854.344 | 56919.445 | 326252327.595 | 86832.273 | 72665.709 | 21.308 | 70608.287 | 23.293 | 72756.761 | 22.031 | 56856.745 | 78.736 | 272636.06 | 156.812 | 143229.395 | 272479.248 | 13.3833 | 5.74 | 5.18 | 36.4 | 48 | 3.1 | 6.3 | 273632.5
2025-06-05 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:06 | 18:36 | 1276 | 1349 | 1245 | 1245 | 1343 | 1247 | 1253 | 1228 | 1294 | 1299 | 1278 | 1272 | 1250 | 1176 | 1252 | 1244 | 1191 | 1236 | 1352 | 1351 | 1254 | 1205 | 1320 | 1416 | 1367 | 1355 | 1346 | 1391 | 1413 | 1382 | 1254 | 1289 | 1213 | 1449 | 1212 | 1422 | 1247 | 1240 | 1257 | 1278 | 1254 | 1244 | 1261 | 1138 | 1259 | 1271 | 1368 | 1197 | 1303 | 1281 | 1261 | 1213 | 1446 | 1427 | 1358 | 1432 | 1438 | 1280 | 1420 | 1440 | 1213 | 1367 | 1254 | 958 | 1421 | 1395 | 1433 | 1311 | 1311 | 1298 | 1318 | 1316 | 1338 | 1309 | 1500 | 1465 | 1493 | 1278 | 1253 | 1397 | 1319 | 1314 | 1304 | 1380 | 1313 | 1301 | 1328 | 1319 | 1315 | 1308 | 1359 | 1347 | 1348 | 1341 | 1325 | 1157 | 1286 | 1317 | 1298 | 1305 | 1340 | 1303 | 1325 | 1293 | 1474 | 1321 | 1538 | 1445 | 1318 | 1441 | 1422 | 1298 | 1457 | 1465 | 1310 | 1190 | 1438 | 1478 | 1469 | 1316 | 1328 | 1400 | 1376 | 1312 | 1324 | 1253 | 1105 | 1124 | 1401 | 1383 | 1285 | 1340 | 1334 | 1142 | 1402 | 1289 | 1337 | 1221 | 1307 | 1248 | 1319 | 1301 | 1241 | 1357 | 1207 | 1332 | 1238 | 1153 | 1337 | 1352 | 1362 | 1249 | 1430 | 1255 | 1232 | 1221 | 1254 | 1223 | 1310 | 1270 | 1458 | 1264 | 1437 | 1411 | 1449 | 1350 | 1243 | 1428 | 1303 | 1302 | 1325 | 1358 | 1418 | 1328 | 1416 | 1292 | 1306 | 1273 | 1439 | 1325 | 1398 | 1412 | 1475 | 1365 | 1415 | 1425 | 1365 | 1365 | 1319 | 1412 | 1266 | 1277 | 1248 | 1280 | 1270 | 1283 | 1066 | 1300 |  |  | 1131 | 898 | 1264 |  | 1353 | 1298 | 1320 | 1283 | 1310 | 1307 | 1326 | 1325 | 1326 | 1334 | 1318 | 1319 | 1468 | 1495 | 1190 | 1161 | 903 | 825 | 965 | 1132 | 1360 | 1457 | 1404 | 1362 | 1294 | 1377 | 1447 | 1392 | 1230 | 1297 | 1198 | 1298 | 1210 |  | 1698 | 1357 | 488 | 1298 | 1359 |  |  | 1341 | 1184 | 1310 | 1198 | 1122 | 36.8 | 52.03 | 3.2 | 8.3 |  | 6.7 | 6.3 |  |  | 86205731.344 | 282896.231 | 59198310.589 | 62568.023 | 86917129.675 | 187898.132 | 63141168.652 | 56991.445 | 326567840.292 | 86987.148 | 82746.076 | 39.264 | 82854.834 | 44.021 | 82882.826 | 26.866 | 67314.308 | 72 | 315512.697 | 154.875 | 165517.625 | 315357.822 | 13.5 | 6.7 | 6.3 | 36.8 | 52.03 | 3.2 | 8.3 | 317965
2025-06-06 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:09 | 18:36 | 1375 | 1406 | 1249 | 1299 | 1395 | 1296 | 1296 | 1191 | 1344 | 1351 | 1318 | 1312 | 1292 | 1216 | 1292 | 1287 | 1228 | 1277 | 1388 | 1388 | 1291 | 1242 | 1365 | 1458 | 1404 | 1391 | 1383 | 1433 | 1452 | 1428 | 1270 | 1332 | 1232 | 1578 | 1231 | 1446 | 1294 | 1263 | 1282 | 1301 | 1278 | 1269 | 1286 | 1154 | 1281 | 1293 | 1390 | 1220 | 1279 | 1262 | 1290 | 1236 | 1472 | 1450 | 1384 | 1465 | 1463 | 1300 | 1441 | 1457 | 1297 | 1461 | 1268 | 968 | 1398 | 1387 | 1389 | 1278 | 1287 | 1250 | 1265 | 1289 | 1290 | 1290 | 1423 | 1387 | 1403 | 1250 | 1207 | 1308 | 1209 | 1278 | 1289 | 1209 | 1267 | 1290 | 1265 | 1293 | 1245 | 1246 | 1301 | 1296 | 1291 | 1295 | 1308 | 1152 | 1250 | 1295 | 1280 | 1285 | 1320 | 1283 | 1309 | 1281 | 1471 | 1301 | 1538 | 1438 | 1300 | 1421 | 1407 | 1376 | 1440 | 1450 | 1285 | 1164 | 1433 | 1462 | 1456 | 1299 | 1312 | 1400 | 1359 | 1295 | 1305 | 1298 | 1149 | 1168 | 1456 | 1437 | 1336 | 1395 | 1389 | 1189 | 1465 | 1355 | 1406 | 1287 | 1376 | 1311 | 1374 | 1354 | 1304 | 1419 | 1269 | 1438 | 1291 | 1198 | 1392 | 1407 | 1416 | 1299 | 1489 | 1305 | 1282 | 1269 | 1300 | 1275 | 1298 | 1239 | 1443 | 1257 | 1429 | 1401 | 1412 | 1348 | 1221 | 1413 | 1278 | 1290 | 1302 | 1340 | 1398 | 1302 | 1421 | 1278 | 1301 | 1257 | 1401 | 1313 | 1378 | 1401 | 1460 | 1368 | 1402 | 1411 | 1378 | 1360 | 1311 | 1419 | 1285 | 1256 | 1241 | 1267 | 1269 | 1278 | 1082 | 1298 |  |  | 1151 | 912 | 1284 |  | 1395 | 1303 | 1301 | 1272 | 1289 | 1295 | 1303 | 1300 | 1303 | 1321 | 1301 | 1303 | 1456 | 1485 | 1192 | 1164 | 978 | 780 | 978 | 1152 | 1339 | 1444 | 1379 | 1389 | 1310 | 1391 | 1434 | 1398 | 1247 | 1310 | 1228 | 1289 | 1191 |  | 1678 | 1398 | 481 | 1287 | 1212 |  |  | 1173 | 1210 | 1270 | 1178 | 1108 | 30.8 | 50.3 | 31.1 | 8.5 |  | 6.6 | 6.32 |  |  | 86290534.396 | 282928.059 | 59280165.923 | 62601.116 | 87002384.052 | 187939.878 | 63207771.983 | 57066.456 | 326886109.748 | 87143.419 | 84803.052 | 31.828 | 81855.334 | 33.093 | 85254.377 | 41.746 | 66603.331 | 75.011 | 318269.456 | 156.271 | 166593.465 | 318113.185 | 13.45 | 6.6 | 6.32 | 30.8 | 50.3 | 31.1 | 8.5 | 319248
2025-06-07 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:07 | 18:36 | 1464 | 1500 | 1332 | 1388 | 1487 | 1381 | 1381 | 1275 | 1428 | 1435 | 1405 | 1396 | 1377 | 1296 | 1374 | 1370 | 1308 | 1361 | 1475 | 1480 | 1379 | 1323 | 1459 | 1556 | 1501 | 1484 | 1477 | 1532 | 1546 | 1526 | 1310 | 1424 | 1363 | 1678 | 1307 | 1533 | 1372 | 1343 | 1363 | 1388 | 1363 | 1348 | 1371 | 1243 | 1374 | 1382 | 1489 | 1306 | 1359 | 1343 | 1373 | 1316 | 1571 | 1548 | 1470 | 1562 | 1557 | 1383 | 1532 | 1549 | 1380 | 1552 | 1363 | 1100 | 1455 | 1435 | 1442 | 1369 | 1327 | 1324 | 1331 | 1325 | 1338 | 1328 | 1500 | 1475 | 1490 | 1328 | 1289 | 1397 | 1319 | 1378 | 1352 | 1308 | 1345 | 1342 | 1328 | 1344 | 1332 | 1329 | 1385 | 1463 | 1348 | 1341 | 1410 | 1240 | 1353 | 1381 | 1365 | 1371 | 1407 | 1369 | 1392 | 1360 | 1561 | 1382 | 1609 | 1531 | 1388 | 1502 | 1502 | 1445 | 1506 | 1544 | 1378 | 1250 | 1524 | 1549 | 1539 | 1384 | 1402 | 1502 | 1458 | 1381 | 1390 | 1385 | 1221 | 1240 | 1549 | 1527 | 1417 | 1479 | 1477 | 1267 | 1548 | 1444 | 1497 | 1369 | 1449 | 1374 | 1458 | 1423 | 1385 | 1501 | 1341 | 1467 | 1360 | 1266 | 1476 | 1489 | 1501 | 1376 | 1572 | 1383 | 1363 | 1350 | 1390 | 1357 | 1378 | 1322 | 1578 | 1363 | 1588 | 1563 | 1510 | 1498 | 1363 | 1563 | 1478 | 1410 | 1408 | 1478 | 1510 | 1398 | 1508 | 1398 | 1408 | 1363 | 1563 | 1410 | 1478 | 1498 | 1563 | 1463 | 1502 | 1503 | 1498 | 1478 | 1498 | 1510 | 1360 | 1350 | 1334 | 1368 | 1365 | 1371 | 1159 | 1399 |  |  | 1229 | 998 | 1365 |  | 1487 | 1385 | 1381 | 1342 | 1374 | 1387 | 1390 | 1388 | 1391 | 1406 | 1393 | 1400 | 1560 | 1591 | 1272 | 1245 | 998 | 1010 | 1068 | 1342 | 1420 | 1506 | 1445 | 1455 | 1391 | 1480 | 1520 | 1503 | 1300 | 1394 | 1319 | 1392 | 1298 |  | 1785 | 1487 | 520 | 1332 | 1297 |  |  | 1198 | 1305 | 1364 | 1261 | 1219 | 31.9 | 52.8 | 3.9 | 6.4 |  | 6.98 | 6.78 |  |  | 86380975.695 | 282973 | 59366988.104 | 62645 | 87093065.921 | 187994.148 | 63278498.708 | 57141 | 327224555.014 | 87299.1 | 90441.299 | 44.941 | 86822.181 | 43.884 | 90681.869 | 54.27 | 70726.725 | 74.544 | 338445.266 | 155.681 | 177174.655 | 338289.585 | 13.4833 | 6.98 | 6.78 | 31.9 | 52.8 | 3.9 | 6.4 | 340883
2025-06-08 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:08 | 18:36 | 1418.2 | 1451 | 1308.4 | 1342.1 | 1441.1 | 1338.1 | 1338.8 | 1342 | 1384.4 | 1392 | 1308.9 | 1357 | 1335.3 | 1257.1 | 1336.3 | 1330 | 1298.4 | 1323.7 | 1439.1 | 1439.6 | 1341 | 1311.1 | 1412.6 | 1508.9 | 1460 | 1442.4 | 1435.8 | 1486.6 | 1505.9 | 1481.3 | 1405.2 | 1441.5 | 1271.2 | 1634.2 | 1301.3 | 1493.2 | 1337.8 | 1305.9 | 1333.9 | 1349.1 | 1323.8 | 1312.2 | 1337.6 | 1325.8 | 1345.6 | 1348.7 | 1456 | 1329.6 | 1379.8 | 1356.8 | 1344 | 1344.6 | 1539.3 | 1516.9 | 1429.2 | 1513.5 | 1511.3 | 1345 | 1491.96 | 1509.9 | 1342.5 | 1513.8 | 1283.6 | 1293.7 | 1442.2 | 1433.2 | 1453.7 | 1412.2 | 1322.3 | 1331.2 | 1338.9 | 1333 | 1363.5 | 1319.8 | 1522.5 | 1490.1 | 1517 | 1337.1 | 1321.1 | 1424.8 | 1341.1 | 1346.6 | 1329.6 | 1348.2 | 1343.2 | 1346.2 | 1349.8 | 1257 | 1327.3 | 1311.6 | 1374.5 | 1412.4 | 1367.6 | 1368.6 | 1493.5 | 1261.2 | 1314.2 | 1341.4 | 1324.6 | 1330.4 | 1364.8 | 1328.4 | 1352.7 | 1321.5 | 1519.2 | 1342.7 | 1577.8 | 1480.4 | 1346.1 | 1465.4 | 1450.2 | 1403.8 | 1472.4 | 1499.6 | 1338.1 | 1269.9 | 1484.9 | 1506.4 | 1497.7 | 1343.9 | 1358.4 | 1491.5 | 1498.5 | 1338.7 | 1347.4 | 1501.5 | 1194.7 | 1215.4 | 1511.7 | 1489.6 | 1401 | 1441.2 | 1436.8 | 1232.9 | 1516 | 1411.4 | 1458.2 | 1343.1 | 1416.6 | 1344.2 | 1421.1 | 1401 | 1351.1 | 1463.4 | 1311.5 | 1431.3 | 1327.7 | 1234.4 | 1435.8 | 1448.3 | 1462.5 | 1341.8 | 1531.5 | 1345.4 | 1325.2 | 1312.9 | 1324.5 | 1335.4 | 1311.1 | 1315.4 | 1484.4 | 1312.5 | 1487.1 | 1467.5 | 1481.5 | 1501.1 | 1311.5 | 1477 | 1321.5 | 1345.5 | 1349.4 | 1389.4 | 1443.4 | 1341.5 | 1488.4 | 1321.5 | 1319.4 | 1315.9 | 1481.4 | 1324.5 | 1424.8 | 1488.4 | 1496.4 | 1405.5 | 1441.1 | 1496.4 | 1349.5 | 1339.2 | 1342.5 | 1398.4 | 1322.1 | 1318.9 | 1216.23 | 1311.4 | 1323.7 | 1225.4 | 1129.5 | 1356.4 |  |  | 1193.3 | 929.4 | 1328.5 |  | 1467.5 | 1296.5 | 1341.2 | 1314.4 | 1334.6 | 1338.4 | 1349.1 | 1346.6 | 1348.6 | 1365.3 | 1359 | 1363.6 | 1516.2 | 1551 | 1230.1 | 1173.4 | 1006 | 866.2 | 1009.1 | 1171.4 | 1382.1 | 1485.1 | 1413.1 | 1411.1 | 1401.1 | 1434.5 | 1478.1 | 1511.1 | 1298.4 | 1411.1 | 1321.4 | 1375.4 | 1255.4 |  | 1799.4 | 1401 | 495.1 | 1296.4 | 1265.4 |  |  | 1208.4 | 1294.4 | 1323.7 | 1241.1 | 1215.5 | 38.8 | 45.5 | 1.23 | 6.3 |  | 6.9 | 6.38 |  |  | 86469599.092 | 283017.941 | 59451373.583 | 62688.884 | 87181638.97 | 188048.418 | 63347683.734 | 57215.544 | 327555142.666 | 87454.781 | 88623.397 | 44.941 | 84385.479 | 43.884 | 88573.049 | 54.27 | 69185.026 | 74.544 | 330587.652 | 155.681 | 172920.051 | 330431.971 | 13.4667 | 6.9 | 6.38 | 38.8 | 45.5 | 1.23 | 6.3 | 332985.59
2025-06-09 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:08 | 18:36 | 1460.9 | 1473.2 | 1324.6 | 1379.1 | 1477.2 | 1376.3 | 1356.5 | 1364.9 | 1410.8 | 1421.6 | 1383.3 | 1376.6 | 1356 | 1231 | 1354.3 | 1349.2 | 1346.2 | 1344.2 | 1460.8 | 1463.5 | 1360.3 | 1363 | 1462.4 | 1531.8 | 1484 | 1464.9 | 1458.4 | 1511 | 1531.5 | 1504.2 | 1511.1 | 1501.5 | 1283.6 | 1650.7 | 1285.4 | 1511.6 | 1354.6 | 1322.4 | 1342.2 | 1363.8 | 1355.6 | 1325.7 | 1351.1 | 1339 | 1359.8 | 1362.2 | 1472.9 | 1344.5 | 1409.8 | 1388.3 | 1367.5 | 1365.4 | 1531.2 | 1538 | 1458.8 | 1521.1 | 1532.8 | 1363.6 | 1516.6 | 1530.8 | 1361.9 | 1534.9 | 1367.4 | 1307.9 | 1478.2 | 1469 | 1489.3 | 1438 | 1337.4 | 1352.2 | 1360.1 | 1354.5 | 1361 | 1331.6 | 1542.8 | 1512 | 1539.1 | 1352.4 | 1339.1 | 1442.1 | 1357.7 | 1363.8 | 1346.5 | 1363.7 | 1361.2 | 1365.6 | 1367.2 | 1302 | 1345.6 | 1331.6 | 1398.9 | 1431.1 | 1359 | 1374.4 | 1528.4 | 1277.5 | 1331.4 | 1360.6 | 1341.2 | 1350.4 | 1356 | 1347.7 | 1355 | 1340.9 | 1547.1 | 1365.9 | 1501 | 1511.9 | 1366.8 | 1483.3 | 1476.2 | 1431.1 | 1482.6 | 1519.3 | 1356.4 | 1276.5 | 1500.3 | 1531.4 | 1524.5 | 1367.9 | 1382.1 | 1489.3 | 1494.9 | 1361.1 | 1370.5 | 1550.3 | 1317.6 | 1337 | 1529.5 | 1510.7 | 1402.7 | 1461.3 | 1456.9 | 1223 | 1454 | 1425.7 | 1483.6 | 1386.3 | 1421 | 1351 | 1442.4 | 1422.6 | 1373.4 | 1504.2 | 1352.5 | 1472.3 | 1363.7 | 1257.2 | 1460.9 | 1471.4 | 1487.5 | 1362.8 | 1527 | 1367.3 | 1345.6 | 1331.1 | 1344.7 | 1337.9 | 1333.5 | 1332.2 | 1525.5 | 1331.5 | 1531.5 | 1511.1 | 1516.1 | 1384.2 | 1328.1 | 1539.1 | 1334.5 | 1379.4 | 1391.5 | 1386.7 | 1521.8 | 1393.4 | 1501 | 1340.5 | 1323.4 | 1333.6 | 1502 | 1328.4 | 1429.4 | 1497 | 1525.8 | 1389.4 | 1437.8 | 1499 | 1389.4 | 1396.1 | 1384.7 | 1434.8 | 1346.8 | 1342 | 1313.1 | 1337 | 1346.7 | 1356.7 | 1147.1 | 1377.9 |  |  | 1218.1 | 941.5 | 1340.1 |  | 1487.1 | 1325.3 | 1366.7 | 1322.6 | 1357.3 | 1358.4 | 1370.7 | 1368.2 | 1368.5 | 1379.4 | 1379.3 | 1387 | 1543.7 | 1569.4 | 1201.1 | 1198 | 1022.5 | 843.3 | 1036.5 | 1201.1 | 1405.7 | 1508.5 | 1437.7 | 1437.4 | 1425.5 | 1455.5 | 1502.8 | 1501 | 1312.4 | 1392.2 | 1278.3 | 1345.4 | 1255 |  | 1785.5 | 1434.2 | 501 | 1323 | 1284.6 |  |  | 1250 | 1332.2 | 1355 | 1265.2 | 1189 | 40.38 | 45.99 | 2.41 | 7.7 |  | 7.2 | 6.66 |  |  | 86559923.409 | 283057.882 | 59536817.374 | 62724.768 | 87271938.549 | 188098.688 | 63418184.82 | 57284.088 | 327891536.652 | 87601.462 | 90324.317 | 39.941 | 85443.791 | 35.884 | 90299.579 | 50.27 | 70501.086 | 68.544 | 336393.986 | 146.681 | 175692.283 | 336247.305 | 13.4667 | 7.2 | 6.66 | 40.38 | 45.99 | 2.41 | 7.7 | 338140.4
2025-06-10 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:09 | 18:38 | 1556.6 | 1591.8 | 1474.2 | 1469.9 | 1582.7 | 1472.9 | 1465.7 | 1471.4 | 1519.2 | 1528.1 | 1423.1 | 1444.1 | 1466.4 | 1332.1 | 1464.9 | 1458.6 | 1455.1 | 1448.9 | 1554.9 | 1560.1 | 1462.6 | 1467.5 | 1574.1 | 1587.9 | 1578.2 | 1558.9 | 1551.1 | 1607.3 | 1626.1 | 1600.1 | 1601.1 | 1596.4 | 1366.4 | 1763.6 | 1427 | 1625.6 | 1446.7 | 1409.6 | 1435.5 | 1455.3 | 1425.7 | 1464.5 | 1459.5 | 1425 | 1454.1 | 1456.6 | 1572.7 | 1430.5 | 1498.4 | 1476.6 | 1454.9 | 1451.9 | 1663.6 | 1636.7 | 1566 | 1634.4 | 1585 | 1431.1 | 1633.3 | 1628.1 | 1449.9 | 1633.1 | 1453.4 | 1301.1 | 1576.2 | 1565.2 | 1563.2 | 1525.3 | 1418.5 | 1442 | 1449.8 | 1443.6 | 1455.2 | 1456.1 | 1630.2 | 1602 | 1633.2 | 1428.2 | 1424.7 | 1555 | 1445.6 | 1451.2 | 1433.8 | 1452 | 1448.8 | 1453.5 | 1456.9 | 1446 | 1435.1 | 1420.7 | 1477.9 | 1554.1 | 1443 | 1432.2 | 1631.3 | 1419.5 | 1415.4 | 1450.5 | 1423.3 | 1441.1 | 1401.1 | 1438.2 | 1464.1 | 1433.4 | 1596.1 | 1458.7 | 1621.2 | 1615.2 | 1465 | 1591.1 | 1580.7 | 1531.1 | 1599.1 | 1623.6 | 1454.5 | 1481.6 | 1586.3 | 1633.4 | 1617.8 | 1452.5 | 1459.2 | 1587.1 | 1591.1 | 1468.4 | 1467.9 | 1650.8 | 1417.7 | 1446.8 | 1653.5 | 1634.2 | 1577 | 1584.5 | 1551.1 | 1311.1 | 1558.1 | 1544.9 | 1557.1 | 1541.2 | 1511.1 | 1440.1 | 1563.3 | 1531.1 | 1439 | 1555.1 | 1453.1 | 1575.5 | 1438 | 1338.9 | 1558.1 | 1569.6 | 1583.9 | 1453.2 | 1616.2 | 1434.6 | 1454.2 | 1424.8 | 1425.5 | 1430.5 | 1401.1 | 1398.2 | 1621.1 | 1411.1 | 1619.1 | 1601 | 1597.4 | 1462.1 | 1415.1 | 1596.1 | 1407.6 | 1459.8 | 1462.4 | 1455.8 | 1611.2 | 1447 | 1591.2 | 1409.1 | 1415.5 | 1405.1 | 1596.5 | 1412.6 | 1534.2 | 1604 | 1594.4 | 1459.1 | 1527.1 | 1651.1 | 1455.1 | 1449.5 | 1457.4 | 1529.8 | 1436.1 | 1427.2 | 1393.2 | 1399 | 1437.2 | 1447.7 | 1176.3 | 1411.1 |  |  | 1302.6 | 1011.1 | 1434.1 |  | 1581.6 | 1411.1 | 1454.4 | 1434.1 | 1448.3 | 1451.9 | 1461.7 | 1429.1 | 1459.2 | 1450.7 | 1409.2 | 1444.5 | 1634.4 | 1623.2 | 1254.1 | 1254.1 | 1087.5 | 861.1 | 1101.1 | 1272.2 | 1526.2 | 1627 | 1557.7 | 1530.1 | 1496.1 | 1564.5 | 1623.5 | 1601.1 | 1371.8 | 1465.1 | 1378.1 | 1434.1 | 1331.1 |  | 1879.2 | 1515.1 | 541.1 | 1434.1 | 1367.8 |  |  | 1312.7 | 1403 | 1153.4 | 1376.5 | 1277.7 | 41.33 | 46.5 | 3.21 | 8.7 |  | 7.54 | 7.03 |  |  | 86656408.961 | 283097.823 | 59628020.794 | 62760.652 | 87368567.069 | 188148.958 | 63492214.783 | 57352.632 | 328249588.859 | 87748.143 | 96485.552 | 39.941 | 91203.42 | 35.884 | 96628.52 | 50.27 | 74029.963 | 68.544 | 358052.207 | 146.681 | 187613.147 | 357905.526 | 13.4833 | 7.54 | 7.03 | 41.33 | 46.5 | 3.21 | 8.7 | 359956.5
2025-06-11 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:10 | 18:37 | 1454.2 | 1488.4 | 1322.3 | 1374 | 1478.6 | 1359.1 | 1370.5 | 1361.1 | 1420.2 | 1428.9 | 1371.1 | 1351.1 | 1372 | 1288.1 | 1373 | 1367.7 | 1366.2 | 1363.5 | 1484.4 | 1487.3 | 1379.6 | 1380.6 | 1450.1 | 1531.1 | 1467.1 | 1485 | 1478.7 | 1531.7 | 1542.5 | 1536.2 | 1545.6 | 1524.2 | 1279.7 | 1678.6 | 1334.9 | 1516.1 | 1350.7 | 1326.1 | 1340.7 | 1357.8 | 1332.6 | 1317.9 | 1342 | 1330.1 | 1353.6 | 1358.6 | 1467.7 | 1337.8 | 1402.3 | 1380.2 | 1359.7 | 1357.6 | 1555.6 | 1528.1 | 1459.5 | 1519.1 | 1548 | 1361.1 | 1535 | 1521.1 | 1354.9 | 1527.8 | 1358 | 1223.1 | 1476.9 | 1468.8 | 1487.9 | 1445.8 | 1342.4 | 1345.5 | 1354.2 | 1348.7 | 1377 | 1330.1 | 1521.1 | 1520.6 | 1523.1 | 1352.7 | 1332 | 1434.1 | 1353.3 | 1358.4 | 1340.1 | 1355.7 | 1352.6 | 1357.4 | 1361.7 | 1338 | 1339.4 | 1327.7 | 1401.4 | 1431.2 | 1361.2 | 1368.8 | 1533.47 | 1330.6 | 1319.7 | 1359.3 | 1340.4 | 1368.7 | 1361.9 | 1351.9 | 1372 | 1326.8 | 1485.4 | 1375.3 | 1496.1 | 1511.1 | 1351.2 | 1497.2 | 1451.1 | 1442.2 | 1486.1 | 1543.5 | 1345.2 | 1386.5 | 1517.2 | 1551.6 | 1501 | 1355.2 | 1356.2 | 1501 | 1496.3 | 1361.2 | 1356.7 | 1541.1 | 1321 | 1352.7 | 1547.6 | 1527 | 1473 | 1477.6 | 1475.5 | 1265.7 | 1456 | 1443.9 | 1466.7 | 1458.9 | 1444.4 | 1378.8 | 1460.2 | 1438.5 | 1357.5 | 1459.1 | 1348.7 | 1469.6 | 1360.7 | 1237.2 | 1479.7 | 1453.3 | 1475.2 | 1351.2 | 1547.2 | 1353.1 | 1349.6 | 1351.2 | 1355.5 | 1339.6 | 1310.2 | 1320.5 | 1482.2 | 1311.5 | 1465.5 | 1481.1 | 1467.6 | 1367.2 | 1321.5 | 1471.5 | 1312.5 | 1387.1 | 1369.2 | 1371.2 | 1469.5 | 1366.9 | 1471.5 | 1311.5 | 1315.5 | 1309.5 | 1471.2 | 1311.5 | 1461.2 | 1485.2 | 1486.8 | 1369.1 | 1471.5 | 1481.5 | 1371.2 | 1401.2 | 1378.2 | 1471.9 | 1340.6 | 1331.5 | 1313.2 | 1332.8 | 1342.2 | 1351 | 1101.1 | 1323.2 |  |  | 1215.9 | 950.1 | 1341.8 |  | 1483.2 | 1341.2 | 1359.9 | 1335.6 | 1352.5 | 1356 | 1365.7 | 1362.9 | 1363.2 | 1378.8 | 1336.6 | 1387 | 1538.5 | 1541.2 | 1181.1 | 1131.1 | 971.2 | 823.2 | 1050.2 | 1212.1 | 1425.6 | 1533 | 1455.5 | 1429.1 | 1435.5 | 1461.5 | 1488.2 | 1487.6 | 1275.2 | 1377.5 | 1287 | 1343.1 | 1241.2 |  | 1955.1 | 1434.2 | 521.1 | 1323 | 1277.6 |  |  | 1276 | 1365.1 | 1401.2 | 1272.2 | 1234.2 | 40.35 | 47.76 | 2.22 | 5.5 |  | 7.17 | 6.59 |  |  | 86747016.976 | 283137.764 | 59713989.758 | 62796.536 | 87459071.419 | 188199.228 | 63561866.987 | 57421.176 | 328586168.023 | 87894.824 | 90608.015 | 39.941 | 85968.964 | 35.884 | 90504.35 | 50.27 | 69652.204 | 68.544 | 336579.164 | 146.681 | 176501.154 | 336432.483 | 13.45 | 7.17 | 6.59 | 40.35 | 47.76 | 2.22 | 5.5 | 338030.77
2025-06-12 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:09 | 18:35 | 1321.1 | 1352.8 | 1233.2 | 1249.8 | 1344.5 | 1252.1 | 1250.1 | 1251.1 | 1291.9 | 1298.8 | 1232 | 1231 | 1246.7 | 1134 | 1246.6 | 1242.9 | 1240.3 | 1236.6 | 1352 | 1349.9 | 1251.3 | 1212 | 1351 | 1392 | 1348 | 1352.9 | 1345.8 | 1400 | 1412 | 1392.7 | 1389.1 | 1396.4 | 1195.6 | 1515.5 | 1251.2 | 1356.8 | 1258.6 | 1222.3 | 1220.1 | 1239.3 | 1236.5 | 1214.3 | 1222.4 | 1211.5 | 1230.9 | 1235.4 | 1336 | 1220 | 1275.3 | 1257.3 | 1236.2 | 1235.6 | 1418 | 1389.1 | 1334.3 | 1408.3 | 1411.8 | 1256.2 | 1395.1 | 1391 | 1259.87 | 1376 | 1236.3 | 1106 | 1340 | 1329.9 | 1349.6 | 1314.3 | 1223.3 | 1222 | 1230.8 | 1225.2 | 1251 | 1229.2 | 1388 | 1400.3 | 1424 | 1255.5 | 1240.3 | 1324.4 | 1244 | 1235 | 1248.8 | 1243 | 1226.3 | 1230.3 | 1259.5 | 1250 | 1220.4 | 1211.1 | 1276.4 | 1355.2 | 1234 | 1229 | 1392.1 | 1247.5 | 1230.5 | 1233 | 1246.6 | 1245.5 | 1234 | 1246.3 | 1244 | 1212.3 | 1370.5 | 1256.6 | 1387 | 1380.1 | 1255.4 | 1381.1 | 1348.9 | 1323.2 | 1369.3 | 1398.2 | 1247.1 | 1251.7 | 1378.2 | 1400 | 1395.8 | 1240.1 | 1262.8 | 1378.5 | 1381.3 | 1246.6 | 1257 | 1409 | 1223 | 1229.1 | 1408.8 | 1387 | 1336.7 | 1341.9 | 1338.7 | 1149.4 | 1334 | 1316.6 | 1332 | 1332 | 1301 | 1248.7 | 1319.9 | 1323 | 1243 | 1351 | 1216.5 | 1333 | 1236.3 | 1157.8 | 1350.9 | 1367.9 | 1349 | 1254.7 | 1421.8 | 1253 | 1236.6 | 1230.1 | 1235.5 | 1239.9 | 1230.5 | 1235.5 | 1356.5 | 1231.5 | 1355.5 | 1364.5 | 1359.1 | 1275.5 | 1245.5 | 1374.5 | 1239.4 | 1279.4 | 1271.5 | 1269.5 | 1366.5 | 1281.4 | 1375.5 | 1231.5 | 1249 | 1234.4 | 1369.4 | 1236.5 | 1313.2 | 1361.5 | 1369.4 | 1279.4 | 1321.2 | 1371.5 | 1269.6 | 1268.7 | 1288.5 | 1326 | 1239.9 | 1227 | 1212 | 1244.4 | 1238.6 | 1250 | 1033 | 1223 |  |  | 1095.5 | 869.4 | 1232.2 |  | 1342.8 | 1211 | 1249.2 | 1212 | 1246.5 | 1229.1 | 1227.8 | 1238.3 | 1255.4 | 1252.7 | 1222.7 | 1252.3 | 1389.4 | 1417.1 | 1055 | 1095.7 | 901 | 755 | 945 | 1089 | 1289.8 | 1387.8 | 1315.7 | 1323 | 1301.2 | 1321.2 | 1382 | 1371 | 1212 | 1261 | 1201 | 1212 | 1121 |  | 1755 | 1342 | 476 | 1212 | 1232 |  |  | 1176 | 1256 | 1275.5 | 1165 | 1100 | 39.97 | 49.84 | 2.3 | 5.5 |  | 6.58 | 6.05 |  |  | 86829808.384 | 283177.705 | 59792684.301 | 62832.42 | 87541481.108 | 188249.498 | 63625249.37 | 57489.72 | 328893320.931 | 88041.505 | 82791.408 | 39.941 | 78694.543 | 35.884 | 82409.689 | 50.27 | 63382.383 | 68.544 | 307152.908 | 146.681 | 161410.126 | 307006.227 | 13.4333 | 6.58 | 6.05 | 39.97 | 49.84 | 2.3 | 5.5 | 309854.97
2025-06-13 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:11 | 16:34 | 1178.3 | 1208.4 | 1099.7 | 1113.8 | 1200.4 | 1117.2 | 1115.4 | 1116.3 | 1151.9 | 1154.4 | 1137.1 | 1127.3 | 1110.6 | 1046.1 | 1112.6 | 1109.9 | 1107.8 | 1105.5 | 1207.2 | 1206.5 | 1119.6 | 1122.3 | 1231.1 | 1271.5 | 1227.5 | 1212.8 | 1209.1 | 1258.1 | 1269.2 | 1249.8 | 1255.5 | 1261.1 | 1069.5 | 1369.2 | 1119.5 | 1221.1 | 1126.9 | 1099.6 | 1123 | 1139.8 | 1116.4 | 1104.3 | 1128.5 | 1117.2 | 1130.9 | 1130.4 | 1222.3 | 1119.2 | 1145.5 | 1139.3 | 1110.4 | 1115 | 1287.4 | 1266.4 | 1190.5 | 1260.5 | 1260.3 | 1122.1 | 1245.9 | 1262.9 | 1133.2 | 1275.3 | 1106.3 | 1011 | 1233.2 | 1209.5 | 1222.9 | 1185.9 | 1092.6 | 1124.4 | 1131.6 | 1126.1 | 1148.1 | 1091.1 | 1267.2 | 1249.2 | 1262.6 | 1114 | 1114.1 | 1186.1 | 1126.7 | 1128.7 | 1119.2 | 1135.1 | 1127.5 | 1125.2 | 1134 | 1124.1 | 1119.8 | 1112.5 | 1148.5 | 1180.5 | 1144.4 | 1142.4 | 1278.8 | 1119.3 | 1109 | 1130.9 | 1120.7 | 1121.7 | 1121 | 1122 | 1138.9 | 1100.3 | 1227.3 | 1129.9 | 1242 | 1220.3 | 1132.3 | 1242.9 | 1212.5 | 1181.1 | 1223 | 1246.3 | 1123.4 | 1132.8 | 1231.4 | 1239.7 | 1236.7 | 1121.8 | 1135.2 | 1226.6 | 1230 | 1126.6 | 1133.5 | 1223.9 | 1089.3 | 1096.6 | 1262 | 1241 | 1192.9 | 1196.1 | 1194.2 | 1027.6 | 1188 | 1179.6 | 1201 | 1205.8 | 1170.7 | 1109.1 | 1178.7 | 1178 | 1118.1 | 1210.9 | 1106 | 1186.9 | 1103.1 | 1034.4 | 1210.1 | 1222.3 | 1221 | 1122 | 1272.6 | 1123.8 | 1109.8 | 1101 | 1115.5 | 1120.5 | 1114 | 1111.1 | 1255.9 | 1090.8 | 1239 | 1255.5 | 1244 | 1165.8 | 1108.2 | 1263.5 | 1118 | 1121.5 | 1137.6 | 1121.1 | 1232.1 | 1148.4 | 1223 | 1117.1 | 1116 | 1103.4 | 1241 | 1111 | 1180.6 | 1236.2 | 1243.4 | 1131 | 1201 | 1251 | 1154 | 1159 | 1123 | 1174.7 | 1101 | 1105.1 | 1078 | 1115 | 1119 | 1111 | 910 | 1090 |  |  | 996.4 | 782 | 1109.1 |  | 1214 | 1091.1 | 1137.4 | 1091.1 | 1121 | 1119.2 | 1123 | 1123 | 1118.3 | 1127.2 | 1125 | 1115 | 1265.4 | 1271 | 954 | 986 | 821 | 667 | 861.1 | 981.1 | 1170.2 | 1251.5 | 1182.1 | 1212 | 1189.1 | 1255.5 | 1232.7 | 1233.1 | 1056 | 1156.1 | 1050 | 1099.1 | 1017.5 |  | 1459.5 | 1176.2 | 421 | 1111.2 | 1056.2 |  |  | 1065 | 1123 | 1149.8 | 1055.5 | 1001.5 | 39.42 | 48.96 | 3.4 | 12.9 |  | 5.96 | 5.45 |  |  | 86904181.726 | 283217.646 | 59863454.302 | 62868.304 | 87615930.416 | 188299.768 | 63682724.362 | 57558.264 | 329170266.65 | 88188.186 | 74373.342 | 39.941 | 70770.001 | 35.884 | 74449.308 | 50.27 | 57474.992 | 68.544 | 276945.719 | 146.681 | 145067.518 | 276799.038 | 11.3833 | 5.96 | 5.45 | 39.42 | 48.96 | 3.4 | 12.9 | 279024.1
2025-06-14 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:08 | 18:43 | 1326 | 1354 | 1203 | 1253 | 1338 | 1246 | 1237 | 1240 | 1280 | 1291 | 1260 | 1256 | 1236 | 1161 | 1237 | 1233 | 1225 | 1224 | 1328 | 1331 | 1240 | 1244 | 1361 | 1399 | 1349 | 1336 | 1328 | 1377 | 1399 | 1374 | 1381 | 1385 | 1173 | 1513 | 1224 | 1342 | 1233 | 1202 | 1221 | 1238 | 1217 | 1208 | 1224 | 1209 | 1224 | 1228 | 1323 | 1211 | 1280 | 1258 | 1235 | 1232 | 1400 | 1377 | 1324 | 1411 | 1393 | 1241 | 1377 | 1397 | 1235 | 1395 | 1220 | 1087 | 1327 | 1317 | 1336 | 1300 | 1215 | 1209 | 1218 | 1211 | 1239 | 1219 | 1393 | 1368 | 1390 | 1224 | 1211 | 1313 | 1228 | 1232 | 1216 | 1234 | 1217 | 1220 | 1228 | 1216 | 1203 | 1194 | 1263 | 1331 | 1242 | 1232 | 1370 | 1210 | 1204 | 1229 | 1215 | 1218 | 1252 | 1213 | 1238 | 1208 | 1378 | 1231 | 1411 | 1366 | 1234 | 1371 | 1331 | 1324 | 1385 | 1394 | 1226 | 1253 | 1378 | 1397 | 1378 | 1246 | 1262 | 1352 | 1349 | 1232 | 1238 | 1351 | 1200 | 1214 | 1386 | 1367 | 1316 | 1321 | 1318 | 1131 | 1321 | 1298 | 1341 | 1335 | 1289 | 1239 | 1307 | 1311 | 1240 | 1347 | 1203 | 1319 | 1219 | 1132 | 1321 | 1331 | 1340 | 1231 | 1409 | 1236 | 1212 | 1203 | 1199 | 1211 | 1223 | 1199 | 1370 | 1181 | 1365 | 1356 | 1385 | 1260 | 1215 | 1383 | 1223 | 1252 | 1278 | 1251 | 1386 | 1289 | 1331 | 1208 | 1221 | 1198 | 1411 | 1236 | 1316 | 1388 | 1348 | 1311 | 1324 | 1375 | 1275 | 1276 | 1250 | 1323 | 1217 | 1217 | 1189 | 1227 | 1216 | 1101 | 1028 | 1248 |  |  | 1095 | 881 | 1215 |  | 1333 | 1201 | 1231 | 1206 | 1224 | 1227 | 1241 | 1233 | 1239 | 1261 | 1234 | 1247 | 1383 | 1411 | 1067 | 1071 | 886.8 | 756.6 | 941 | 1099 | 1294 | 1375 | 1319 | 1292 | 1261 | 1331 | 1373 | 1351 | 1169 | 1256 | 1199 | 1223 | 1123 |  | 1655 | 1301 | 471 | 1199 | 1178 |  |  | 1151 | 1222 | 1255 | 1155 | 1087 | 37.79 | 49.04 | 1.63 | 4.9 |  | 6.54 | 6.01 |  |  | 86986303.472 | 283257.587 | 59941488.966 | 62904.188 | 87698030.148 | 188350.038 | 63745789.345 | 57626.808 | 329475498.732 | 88334.867 | 82121.746 | 39.941 | 78034.664 | 35.884 | 82099.732 | 50.27 | 63064.983 | 68.544 | 305232.082 | 146.681 | 160080.585 | 305085.401 | 13.5833 | 6.54 | 6.01 | 37.79 | 49.04 | 1.63 | 4.9 | 307007.4
2025-06-15 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:15 | 18:29 | 970.9 | 991.1 | 901 | 910.7 | 988.2 | 916.3 | 918.3 | 920.4 | 951.3 | 953.9 | 935.2 | 930.1 | 912.7 | 871 | 911.4 | 909 | 904.4 | 913 | 979 | 981 | 897.4 | 905.8 | 998.4 | 1015.8 | 974.2 | 981 | 971 | 1021 | 1014.3 | 1022 | 1022 | 1024 | 850.1 | 1101 | 901 | 1001 | 906 | 891 | 901 | 898.1 | 893.2 | 899.5 | 901 | 901 | 906 | 888.9 | 991 | 901 | 941 | 939.2 | 901 | 904.2 | 1011 | 1017 | 971 | 1011 | 1014.1 | 904 | 1001.1 | 1012 | 905 | 1009.1 | 904.1 | 801 | 1001.6 | 993.8 | 1007.2 | 982.1 | 918.3 | 912.4 | 921.3 | 915.3 | 938.9 | 919.3 | 1049.2 | 1030.4 | 1047.4 | 923.1 | 912.6 | 1001.1 | 926.1 | 928.8 | 917.9 | 931.8 | 917.3 | 921.5 | 928.5 | 919.1 | 910.6 | 902.7 | 953.6 | 1010 | 939.3 | 932.1 | 1035.6 | 912.7 | 907.4 | 945.2 | 926.1 | 937.2 | 941 | 929.3 | 941.1 | 911.1 | 1031.1 | 918.9 | 1021 | 1045.8 | 921 | 1031.1 | 1009 | 1002.1 | 1060.8 | 1055.9 | 943.6 | 950.8 | 1039.8 | 1073.2 | 1065.2 | 949.2 | 959.7 | 1025.1 | 1012 | 948.7 | 955.4 | 1191.1 | 891 | 893.4 | 1013.4 | 1006.4 | 969.5 | 973.2 | 974.3 | 838.5 | 971 | 961 | 994.4 | 986.6 | 955.1 | 901.3 | 965.9 | 971 | 891.6 | 980.4 | 891 | 981 | 891 | 823.1 | 962.3 | 970.3 | 973.3 | 896.1 | 1027.5 | 895.9 | 898 | 891 | 893 | 889 | 881.4 | 884 | 991.1 | 901 | 1001 | 996 | 994.2 | 941 | 901 | 999.8 | 911.1 | 932 | 925.8 | 921 | 1009.1 | 931 | 992 | 911 | 885.1 | 901 | 1027.3 | 898.2 | 969.3 | 1015.5 | 1022 | 961.7 | 955.1 | 991.6 | 929.7 | 924.7 | 949.7 | 964.9 | 922.5 | 930.3 | 982.5 | 927.6 | 921.5 | 929.9 | 789.6 | 948.7 |  |  | 822 | 650.3 | 927.8 |  | 1024.4 | 900.8 | 934.3 | 914.5 | 926.8 | 931.4 | 938.1 | 934.6 | 937.3 | 955.5 | 932.3 | 942.5 | 1043.8 | 1064.8 | 801 | 798 | 656 | 555 | 699.8 | 824.3 | 985.1 | 1065.1 | 1025.7 | 1010.7 | 985 | 1021 | 1056.1 | 1011.9 | 893 | 945.3 | 872 | 902.7 | 834.3 |  | 1242 | 1001 | 349 | 901 | 901 |  |  | 851 | 901 | 934 | 868 | 820 | 34.83 | 42.57 | 3.24 | 10.7 |  | 4.87 | 4.49 |  |  | 87046079.3 | 283297.528 | 60001329.281 | 62940.072 | 87758029.79 | 188400.308 | 63794673.512 | 57695.352 | 329703925.03 | 88481.548 | 59775.828 | 39.941 | 59840.315 | 35.884 | 59999.642 | 50.27 | 48884.167 | 68.544 | 228426.298 | 146.681 | 119540.318 | 228279.617 | 13.2333 | 4.87 | 4.49 | 34.83 | 42.57 | 3.24 | 10.7 | 229066.5
2025-06-16 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 6:13 | 17:53 | 1297 | 1322.9 | 1213.2 | 1214.1 | 1317.5 | 1224.1 | 1227.1 | 1227.8 | 1265.3 | 1269.7 | 1250.4 | 1241.9 | 1223.3 | 1153.3 | 1224.6 | 1222.8 | 1217.7 | 1211.2 | 1315.9 | 1316 | 1222.6 | 1227 | 1347.3 | 1377.2 | 1331.4 | 1314.4 | 1308.5 | 1359.7 | 1373.1 | 1354.3 | 1355.5 | 1349.5 | 1142 | 1484.1 | 1209.5 | 1335.3 | 1193.7 | 1184.3 | 1222.5 | 1215.9 | 1225.4 | 1201 | 1206.9 | 1192.7 | 1206.7 | 1210.7 | 1302.4 | 1211.5 | 1243.4 | 1236 | 1209.1 | 1204.2 | 1373.6 | 1353.7 | 1292.9 | 1365.4 | 1368.1 | 1219.8 | 1351.7 | 1369.6 | 1215.7 | 1370.6 | 1206.8 | 1100 | 1326.2 | 1316.7 | 1330.7 | 1298.2 | 1218.1 | 1213.3 | 1221 | 1214.8 | 1245 | 1222.3 | 1390.4 | 1365.5 | 1392 | 1225 | 1211.1 | 1323.3 | 1230.4 | 1234.7 | 1218.8 | 1235.8 | 1218.3 | 1220.5 | 1229.1 | 1218.1 | 1205 | 1197.9 | 1261.1 | 1325 | 1242.9 | 1236.5 | 1368.4 | 1212.9 | 1207.2 | 1239.7 | 1222.1 | 1226.9 | 1255.4 | 1224.5 | 1240.4 | 1213.4 | 1387.4 | 1238.2 | 1398.1 | 1365 | 1236.2 | 1375.2 | 1330 | 1310.6 | 1385.2 | 1376.2 | 1233.3 | 1240.5 | 1356.8 | 1375.3 | 1368.8 | 1232.6 | 1248.5 | 1344 | 1349.1 | 1231.7 | 1241.7 | 1394.9 | 1177.2 | 1170.2 | 1311 | 1321.6 | 1271.7 | 1279.6 | 1277.7 | 1080 | 1250 | 1261.4 | 1261 | 1259.9 | 1221 | 1156.3 | 1263.8 | 1257.5 | 1178 | 1276 | 1162.1 | 1279 | 1180.6 | 1078 | 1271 | 1269 | 1268 | 1172 | 1318 | 1172 | 1176.5 | 1168.7 | 1163.8 | 1172 | 1212.7 | 1190.1 | 1355.9 | 1175.4 | 1345.5 | 1337.9 | 1363.5 | 1248.2 | 1198.2 | 1361.5 | 1229.4 | 1226.6 | 1248.8 | 1224.5 | 1354.7 | 1261.5 | 1350.3 | 1201.3 | 1215.6 | 1191.2 | 1385.3 | 1228.4 | 1296.4 | 1366.4 | 1328.1 | 1276 | 1309.3 | 1360.2 | 1270.8 | 1270.8 | 1277.9 | 1301.2 | 1219.9 | 1209.1 | 1201 | 1221.7 | 1221.7 | 1225.5 | 1034.6 | 1249.4 |  |  | 1117.4 | 845.6 | 1230.3 |  | 1336.1 | 1183.1 | 1230.6 | 1196.3 | 1227.6 | 1227.5 | 1238 | 1236 | 1240.1 | 1252.2 | 1234.1 | 1242 | 1381.9 | 1409.7 | 1089 | 1070 | 901 | 754 | 932 | 1083.5 | 1283.4 | 1381.7 | 1318.4 | 1313.4 | 1295.5 | 1321.5 | 1374 | 1342 | 1143 | 1237 | 1151 | 1183.9 | 1123 |  | 1580.5 | 1278.2 | 461 | 1192.1 | 1141 |  |  | 1142 | 1204 | 1234 | 1156 | 1101 | 32.82 | 40.29 | 3.89 | 8.5 |  | 6.29 | 5.78 |  |  | 87126863.647 | 283334.469 | 60079561.358 | 62971.956 | 87838349.007 | 188447.578 | 63858367.094 | 57759.896 | 330006760.635 | 88625.229 | 80784.347 | 36.941 | 78232.077 | 31.884 | 80319.217 | 47.27 | 63693.582 | 64.544 | 302835.605 | 143.681 | 158947.599 | 302691.924 | 11.6667 | 6.29 | 5.78 | 32.82 | 40.29 | 3.89 | 8.5 | 303505.1
2025-06-17 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:12 | 16:05 | 911.4 | 933.7 | 865.2 | 867.9 | 924.3 | 859.1 | 857.6 | 860.3 | 888.8 | 894 | 872.4 | 867.2 | 855.7 | 807 | 852.9 | 842.3 | 846.7 | 843.5 | 910 | 915 | 855 | 854.2 | 943.3 | 963.9 | 929 | 915 | 910.5 | 949.3 | 952 | 942.5 | 951.5 | 948.8 | 805.4 | 1044.4 | 840.8 | 946.5 | 844.2 | 826.9 | 843 | 857.4 | 835.4 | 828.2 | 843.9 | 836.1 | 846.5 | 849.6 | 915.5 | 837.8 | 877.2 | 863.9 | 850.7 | 847.8 | 970 | 953 | 915 | 971.3 | 965.3 | 856.7 | 947.6 | 955.4 | 853 | 961 | 851.9 | 812.8 | 920.6 | 913.8 | 924 | 899.7 | 841.6 | 839.6 | 844.9 | 839.3 | 861 | 833.7 | 959.1 | 939.5 | 959.5 | 843.8 | 834 | 921 | 846.8 | 850.3 | 839.9 | 850.6 | 837.9 | 842.7 | 848.7 | 842.4 | 832.2 | 828.8 | 869.9 | 913.5 | 858.6 | 853.6 | 950.2 | 835.1 | 833.2 | 854.5 | 848.2 | 850.1 | 869.9 | 846.5 | 857.3 | 834.5 | 964.1 | 850.3 | 980.4 | 949 | 857.6 | 946.8 | 915.5 | 898.9 | 952 | 954.3 | 852 | 860.2 | 941.6 | 945.1 | 943.4 | 847.2 | 865.1 | 934 | 944 | 851.9 | 856.4 | 948.5 | 841.6 | 836.2 | 963.3 | 947.8 | 909.8 | 910.7 | 910.7 | 785.7 | 902 | 900.6 | 930.6 | 916.5 | 900.1 | 834 | 899 | 894.1 | 856.5 | 931.4 | 844 | 901 | 842.3 | 782.4 | 912.5 | 920.4 | 926.9 | 849.3 | 966.5 | 852.5 | 840.4 | 833.8 | 835.8 | 838.5 | 833.4 | 819 | 931.7 | 833 | 934.1 | 922.2 | 952.4 | 861.5 | 824.8 | 938.4 | 843.2 | 861 | 856.9 | 859 | 933 | 865.6 | 945.4 | 831.4 | 837.1 | 821.8 | 953.3 | 845.1 | 890.7 | 937.4 | 921.8 | 903.8 | 906.8 | 941.1 | 878.3 | 879.3 | 876.6 | 889.6 | 839 | 831 | 840.6 | 844.4 | 842 | 847.2 | 713.5 | 864.9 |  |  | 786.1 | 601 | 842.5 |  | 935.2 | 831.7 | 845.5 | 839 | 846.6 | 847.9 | 859 | 853.7 | 860.3 | 862.1 | 853.1 | 861.5 | 963.1 | 983.6 | 755 | 751 | 631 | 531 | 651 | 747.5 | 891.6 | 956.8 | 894 | 898.8 | 901.1 | 925.5 | 953.1 | 934 | 801 | 863 | 803 | 831 | 768 |  | 1151 | 901 | 335 | 831 | 801 |  |  | 799 | 855 | 868 | 801 | 755 | 33.67 | 42.05 | 2.77 | 8.9 | 0.8 | 4.44 | 3.98 |  |  | 87183482.456 | 283371.41 | 60133871.225 | 63003.84 | 87894643.099 | 188494.848 | 63902423.975 | 57824.44 | 330217933.48 | 88768.91 | 56618.809 | 36.941 | 54309.867 | 31.884 | 56294.092 | 47.27 | 44056.881 | 64.544 | 211172.845 | 143.681 | 110859.851 | 211029.164 | 10.8833 | 4.44 | 3.98 | 33.67 | 42.05 | 2.77 | 8.9 | 212042.5
2025-06-18 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:06 | 18:34 | 1115 | 1136.1 | 1053.4 | 1050.5 | 1142.4 | 1052.8 | 1065.8 | 1065.5 | 1095.4 | 1102.4 | 1085.5 | 1079.8 | 1057.3 | 995.3 | 1061.1 | 1013.1 | 1056.5 | 1057.5 | 1150.6 | 1152.4 | 1067 | 1066.2 | 1147.5 | 1201.8 | 1165.2 | 1149.4 | 1140.5 | 1186.3 | 1200.5 | 1215.5 | 1221.5 | 1205.4 | 944 | 1111.4 | 986.1 | 1115.9 | 986.1 | 988.3 | 1001.1 | 995.5 | 980.5 | 993.1 | 981 | 994.4 | 1004.2 | 991 | 1081.1 | 996.5 | 1034.1 | 1037.5 | 999.6 | 995.5 | 1124.2 | 1122.4 | 1081.2 | 1124.5 | 1139.8 | 1003.2 | 1123.5 | 1129.1 | 1002.9 | 1110.7 | 1001.1 | 941 | 1131.9 | 1123.2 | 1135 | 1105.4 | 1044.1 | 1044.1 | 1050.4 | 1044.9 | 1075.1 | 1032.2 | 1194 | 1177.3 | 1197.4 | 1057.6 | 1055.5 | 1148.5 | 1021 | 1041 | 1053 | 1070.6 | 1057.8 | 1057.5 | 1060.2 | 1051.3 | 1037.2 | 1029.4 | 1070 | 1125.7 | 1070.2 | 1067.6 | 1161.9 | 1049.9 | 1044.1 | 1065.7 | 1051.9 | 1057.6 | 1083.1 | 1055.1 | 1071.5 | 1046.6 | 1186.7 | 1056.2 | 1217.2 | 1169.3 | 1061.2 | 1177.7 | 1135.1 | 1111 | 1164.5 | 1172.8 | 1061.4 | 1063.4 | 1151.4 | 1174.1 | 1171.85 | 1053.7 | 1062.2 | 1146 | 1149.8 | 1052.3 | 1061.3 | 1187 | 1048 | 1051 | 1198.7 | 1183.3 | 1142.2 | 1144.7 | 1151.6 | 962.6 | 1101.8 | 1136.9 | 1169.2 | 1156.1 | 1129.4 | 1020.4 | 1135.3 | 1120.1 | 1064.7 | 1161.7 | 1028.6 | 1133.7 | 1058.2 | 980.4 | 1139.7 | 1149.7 | 1146.2 | 1053.3 | 1193.7 | 1056.3 | 1043.5 | 1039.7 | 1044.7 | 1043.4 | 1041 | 1051.5 | 1197.9 | 1039.2 | 1188 | 1180.4 | 1150 | 1096 | 1051.4 | 1175.1 | 1040 | 1071.2 | 1097.2 | 1069.4 | 1190.9 | 1101.6 | 1178 | 1071.1 | 1075 | 1058.9 | 1190.1 | 1048 | 1145.7 | 1176 | 1176.2 | 1101 | 1123 | 1179 | 1121.4 | 1126.3 | 1114 | 1142 | 1039.9 | 1022.4 | 1011 | 1038.2 | 1041.6 | 1023 | 882 | 1062.7 |  |  | 930.1 | 744 | 1038.7 |  | 1123.5 | 1022 | 1052 | 971.6 | 1048.9 | 1056.4 | 1059.1 | 1058.6 | 1059.4 | 1022 | 1053.4 | 1062.4 | 1175.8 | 1194.2 | 901 | 901 | 771 | 644 | 801 | 912.4 | 1094.8 | 1164.9 | 1114.7 | 1108.8 | 1099.5 | 1129.2 | 1159.2 | 1156 | 1011 | 1055 | 981 | 1044 | 945 |  | 1378 | 1101 | 412 | 1051 | 981 |  |  | 965 | 1039 | 1071 | 981 | 931 | 31.72 | 42.78 | 1.64 | 5.1 |  | 5.32 | 4.96 |  |  | 87251038.44 | 283395.351 | 60201269.853 | 63035.724 | 87965830.574 | 188542.118 | 63956006.601 | 57882.984 | 330477604.223 | 88904.591 | 67555.984 | 23.941 | 67398.628 | 31.884 | 71187.475 | 47.27 | 53582.626 | 58.544 | 259670.743 | 135.681 | 134898.787 | 259535.062 | 13.4667 | 5.32 | 4.96 | 31.72 | 42.78 | 1.64 | 5.1 | 261299.05
2025-06-19 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:24 | 17:50 | 989 | 984 | 912.2 | 911.6 | 978.4 | 907.6 | 911.3 | 911.3 | 940.2 | 946.8 | 919.3 | 923.1 | 908.3 | 854.3 | 910 | 885 | 906.2 | 902.5 | 978 | 980.7 | 912.9 | 912 | 963.2 | 1028 | 994.4 | 981.5 | 975.3 | 1015.7 | 1024.6 | 1024.5 | 1019.1 | 1028 | 878.6 | 1113.1 | 912.7 | 1033.5 | 910.7 | 885.6 | 895.5 | 914.5 | 901.5 | 893.3 | 903.3 | 913.5 | 905 | 909.4 | 977.6 | 901.2 | 931.4 | 945 | 903.8 | 901.1 | 1030.2 | 1017.7 | 968.8 | 1023.4 | 1027.4 | 914.5 | 1016.9 | 1030.1 | 911.7 | 1034.9 | 900.2 | 872 | 978.7 | 972.8 | 979.8 | 957.4 | 902.2 | 898.5 | 902.7 | 896.5 | 921.6 | 906.8 | 1044.4 | 1020 | 1042.3 | 914.1 | 900.8 | 990.6 | 910.2 | 913.9 | 900.8 | 913.3 | 897.1 | 902 | 906.4 | 899.8 | 887.9 | 902 | 927.8 | 968.8 | 918.3 | 914.2 | 1006.2 | 899.4 | 900.1 | 916.8 | 912.1 | 909.9 | 928.9 | 908.8 | 919.4 | 896.8 | 1028.2 | 908.7 | 1065.3 | 1011.2 | 911.9 | 1011.3 | 972.7 | 961 | 1020.2 | 1018.7 | 911.1 | 914.9 | 1006.2 | 1001.2 | 1005 | 897.7 | 915.4 | 1001 | 1011 | 903.1 | 911.1 | 1022.2 | 900.9 | 905.2 | 1039.3 | 1027.7 | 989 | 989.9 | 989.7 | 853.9 | 1009.8 | 979.9 | 1017.8 | 1002.8 | 988.6 | 891.5 | 978.8 | 976.8 | 934.9 | 1018.7 | 898.5 | 971 | 921.1 | 855.4 | 991.9 | 1000.7 | 1003.9 | 915.9 | 1039.1 | 917.6 | 906.3 | 902.4 | 912.2 | 905.4 | 913.4 | 896.6 | 1022.6 | 885.2 | 1020.7 | 1016.1 | 1030.3 | 936.7 | 898.6 | 1020.3 | 921.5 | 912.9 | 934.2 | 912.4 | 1016.1 | 939.9 | 1044.5 | 913.5 | 919.7 | 902.6 | 1045 | 927.8 | 978.4 | 1026.7 | 1014.4 | 950 | 994 | 1035.1 | 962.8 | 965.5 | 950.3 | 971.9 | 882.4 | 889.1 | 891.1 | 885.2 | 887.7 | 886.1 | 754.5 | 908.3 |  |  | 827 | 643.2 | 901 |  | 982.3 | 889.2 | 893.6 | 819.8 | 892.4 | 894.6 | 905.2 | 901.2 | 907.3 | 915.9 | 904 | 912 | 1018.1 | 1039.1 | 802.2 | 808.4 | 690.7 | 562.5 | 699.2 | 802.2 | 933.9 | 1003.4 | 961.6 | 978.1 | 941.2 | 978.7 | 1025.2 | 1012 | 890 | 925.5 | 890.1 | 888.7 | 853.5 |  | 1212.5 | 961.5 | 350.4 | 901.1 | 882 |  |  | 844.5 | 902.6 | 932.5 | 881.2 | 814.5 | 30.22 | 39.34 | 3.06 | 9.5 | 0.03 | 4.53 | 4.17 |  |  | 87311402.499 | 283419.292 | 60259321.38 | 63067.608 | 88027176.227 | 188589.388 | 64002405.579 | 57941.528 | 330703683.51 | 89040.272 | 60364.059 | 23.941 | 58051.527 | 31.884 | 61345.653 | 47.27 | 46398.978 | 58.544 | 226079.287 | 135.681 | 118359.761 | 225943.606 | 12.4333 | 4.53 | 4.17 | 30.22 | 39.34 | 3.06 | 9.5 | 227578.3
2025-06-20 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:27 | 18:42 | 570 | 581 | 539.1 | 536.5 | 562.3 | 536.6 | 536.8 | 537.3 | 341 | 558.7 | 547.4 | 543.9 | 534.4 | 502 | 535.3 | 511.63 | 532.4 | 529.9 | 582.7 | 580.7 | 536.2 | 537.9 | 566.9 | 608.4 | 586.6 | 581.9 | 578.5 | 602.1 | 613.1 | 580.7 | 588.5 | 434 | 518.8 | 432 | 538.4 | 610.3 | 540.6 | 525.3 | 533.3 | 541 | 533 | 522.6 | 536.6 | 531.3 | 536.1 | 536.8 | 444 | 528.8 | 552.6 | 391 | 534.5 | 535.1 | 611.2 | 602.7 | 573.8 | 608.1 | 607.1 | 539.3 | 600.4 | 612.4 | 538.6 | 615.2 | 533.7 | 521.2 | 574.6 | 571.2 | 589 | 586 | 526.2 | 525.2 | 528.5 | 523.7 | 541.1 | 532.1 | 608.9 | 599.7 | 607.9 | 533.3 | 527.3 | 584.6 | 534.1 | 474.1 | 528 | 534.4 | 524.6 | 527.9 | 522.3 | 527.4 | 518.3 | 508.7 | 543.6 | 569.1 | 530.4 | 531.3 | 607 | 0 | 0 | 536 | 532.8 | 522.5 | 546.8 | 520.1 | 539.1 | 525 | 610.2 | 0 | 0 | 601 | 536.3 | 602.9 | 581.4 | 589 | 601.4 | 596.8 | 530 | 537.3 | 570 | 599 | 601.7 | 530.8 | 541.2 | 532 | 519 | 535.2 | 540.3 | 599.3 | 544 | 529.1 | 568.4 | 444 | 579.6 | 578.4 | 578.8 | 501.2 | 592.9 | 575.9 | 595.5 | 584.1 | 577.5 | 549 | 589 | 577.5 | 538.1 | 588.3 | 520.7 | 560.3 | 539.1 | 499.9 | 581.5 | 582.4 | 582.3 | 464.1 | 613.3 | 541.8 | 531.2 | 527.3 | 539.5 | 533.5 | 538.9 | 530.8 | 606.7 | 522.9 | 470.6 | 524 | 609.5 | 556.9 | 452.9 | 451 | 356 | 529.4 | 553.6 | 527.2 | 434.6 | 385 | 598.1 | 524.1 | 538.6 | 529.1 | 615.4 | 545.9 | 424 | 444.7 | 596.3 | 585.5 | 585.1 | 608.2 | 558.3 | 555.5 | 448.5 | 330.9 | 522.4 | 515.4 | 523 | 513 | 522.2 | 391 | 442.4 | 538.4 |  |  | 469 | 371 | 534 |  | 579 | 510 | 521 | 519.1 | 527.3 | 533.4 | 535.2 | 512 | 534.8 | 542 | 529.6 | 401 | 599 | 612.6 | 493.1 | 478 | 407.5 | 345.3 | 397.6 | 470 | 537.3 | 597.3 | 569.9 | 565.4 | 544.5 | 577.5 | 594.2 | 587.5 | 523 | 534.9 | 524 | 534 | 473.4 |  | 711 | 565 | 201 | 507.2 | 489.6 |  |  | 488 | 503 | 534 | 491.8 | 475 | 28.91 | 32.29 | 0.946 | 5.7 | 0.4 | 2.53 | 2.4 |  |  | 87345961.541 | 283443.233 | 60291502.496 | 63099.492 | 88060847.752 | 188636.658 | 64029792.6 | 58000.072 | 330831376.797 | 89175.953 | 34559.042 | 23.941 | 32181.116 | 31.884 | 33671.525 | 47.27 | 27387.021 | 58.544 | 127693.287 | 135.681 | 66684.333 | 127557.606 | 13.25 | 2.53 | 2.4 | 28.91 | 32.29 | 0.946 | 5.7 | 128207.03
2025-06-21 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:10 | 18:40 | 1162.5 | 1155 | 1069 | 1064.6 | 1179.5 | 1069 | 1059 | 1072.2 | 1084 | 1130.5 | 1061 | 1081 | 1082.4 | 985 | 1082.3 | 1035.6 | 1074.7 | 1071.4 | 1167.2 | 1167.3 | 1067.2 | 1061 | 1144.4 | 1220.4 | 1151 | 1167.9 | 1159.8 | 1202.1 | 1218.7 | 1166 | 1161 | 1101 | 1024.1 | 1296.7 | 1065.5 | 1202 | 1059.6 | 1047.4 | 1072.4 | 1086.4 | 1059.8 | 1048.3 | 1073.8 | 1059.8 | 1078.9 | 1045 | 1119.2 | 1065.2 | 1120.3 | 1124.3 | 1051 | 1087.2 | 1240.7 | 1220.9 | 1144.9 | 1180 | 1218.8 | 1080.4 | 1193.4 | 1206.6 | 1074.2 | 1211.6 | 1061 | 1002 | 1161 | 1162.8 | 1156 | 1163.1 | 1058 | 1071 | 1068 | 1071.4 | 1084.5 | 1061 | 1219.8 | 1201 | 1224.6 | 1081.8 | 1083.7 | 1056 | 1067 | 1060.8 | 1084.6 | 1076 | 1079 | 1071 | 1074 | 1071 | 1063 | 1059.8 | 1101 | 1157.7 | 1064 | 1075.9 | 1212.9 | 1035.2 | 1033 | 1044.4 | 1031 | 1029.7 | 1048.9 | 1036 | 1033.6 | 1038 | 1171 | 928 | 1059 | 1154 | 1028.4 | 1169.6 | 1134 | 1139 | 1163.6 | 1160.4 | 1042.2 | 1042.1 | 1156 | 1159 | 1169 | 1037 | 1034.8 | 1081.2 | 1082 | 1037 | 1030.8 | 1181 | 1061 | 1055 | 1167 | 1161.1 | 1148.4 | 1123 | 1146.8 | 990.8 | 1139 | 1134.6 | 1154 | 1145.7 | 1124 | 1036 | 1139.3 | 1131.1 | 1077 | 1161.7 | 1044.9 | 1121 | 1063.1 | 985.6 | 1129.6 | 1152.6 | 1155.9 | 1050.2 | 1185.3 | 1042.9 | 1034 | 1034.1 | 1035.5 | 1047.4 | 1050 | 1064.2 | 1171 | 1040 | 1166.5 | 1191.8 | 1189.1 | 1109 | 1054.9 | 1184.7 | 1051.1 | 1103.6 | 1090 | 1104.3 | 1026 | 1068 | 1190 | 1051 | 1057 | 1061 | 1201 | 1055 | 1109 | 1188.9 | 1197.9 | 1071 | 1128 | 1184 | 1081 | 1103.2 | 1081 | 1110 | 1051 | 1053.4 | 1042 | 1063.5 | 1059 | 1051 | 867 | 1044 |  |  | 951 | 736.3 | 1058.9 |  | 1188.4 | 1057.2 | 1031 | 1044 | 1076.2 | 1067.3 | 1061 | 1054 | 1071 | 1043 | 1041 | 1035 | 1213.5 | 1201 | 901 | 901 | 789 | 671 | 808.7 | 956.4 | 1101 | 1211.2 | 1158.4 | 1154.9 | 1101 | 1169.5 | 1203.9 | 1193.6 | 1001 | 1081 | 1002 | 1033.4 | 968.5 |  | 1390 | 1112 | 401 | 1035 | 1001 |  |  | 990 | 1010 | 1080 | 992 | 933.5 | 31.15 | 42.22 | 1.35 | 6.1 |  | 5.62 | 5.19 |  |  | 87417389.103 | 283465.174 | 60358361.347 | 63129.376 | 88130710.583 | 188681.928 | 64085431.87 | 58056.616 | 331095030.155 | 89309.634 | 71427.562 | 21.941 | 66858.851 | 29.884 | 69862.831 | 45.27 | 55639.27 | 56.544 | 263653.358 | 133.681 | 138234.588 | 263519.677 | 13.5 | 5.62 | 5.19 | 31.15 | 42.22 | 1.35 | 6.1 | 264314.4
2025-06-22 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 4:59 | 18:12 | 1230.5 | 1228.1 | 1129.1 | 1134.2 | 1221 | 1141 | 1138 | 1145 | 1190 | 1190 | 1127 | 1147 | 1115.3 | 1046 | 1143 | 1100 | 1134 | 1152.5 | 1246 | 1231 | 1133 | 1135 | 1226.9 | 1280 | 1231 | 1239 | 1233.7 | 1285 | 1298 | 1239 | 1255.5 | 1198 | 1090 | 1379.4 | 1150.8 | 1280 | 1154.2 | 1135.8 | 1151.1 | 1147 | 1131 | 1135.6 | 1134 | 1121 | 1148 | 1129 | 1201 | 1141 | 1166.2 | 1103.4 | 1152 | 1150.5 | 1301 | 1290 | 1235.5 | 1278 | 1271 | 1132 | 1270 | 1290 | 1138 | 1290 | 1147.1 | 1050 | 1229 | 1231 | 1246.1 | 1215.3 | 1132 | 1136.1 | 1139 | 1134 | 1121 | 1145.1 | 1270 | 1282 | 1284.3 | 1145.4 | 1142.7 | 1251.7 | 1131 | 1129.1 | 1135.4 | 1149.6 | 1151 | 1146.1 | 1143.8 | 1143.7 | 1123.9 | 1115.2 | 1169.7 | 1199 | 1131 | 1127.3 | 1273.9 | 1139 | 1132.1 | 1127 | 1146.1 | 1143.2 | 1135 | 1143.4 | 1134 | 1121.7 | 1282.2 | 1135.5 | 1222 | 1267.1 | 1146.6 | 1269 | 1221.9 | 1150 | 1268.6 | 1277.2 | 1148.8 | 1141.3 | 1234 | 1248.3 | 1257.4 | 1122.2 | 1145.5 | 1186.4 | 1161.4 | 1133.2 | 1143 | 1275.1 | 1142.8 | 1139.9 | 1241 | 1265.2 | 1229.5 | 1201 | 1241.2 | 1051 | 1219 | 1231 | 1231 | 1224 | 1180 | 1101 | 1233.6 | 1213.6 | 1132 | 1234 | 1136 | 1148.7 | 1121 | 1041 | 1236.3 | 1232.2 | 1233 | 1147.3 | 1287.8 | 1134.1 | 1134.9 | 1128.8 | 1135.1 | 1142.5 | 1129.7 | 1132.8 | 1261 | 1112 | 1253.7 | 1262.5 | 1251 | 1186.3 | 1113.8 | 1253 | 1102 | 1152.8 | 1151.6 | 1155.4 | 1266 | 1152.1 | 1268 | 1101 | 1119.7 | 1127.2 | 1280 | 1137.6 | 1198.4 | 1249.2 | 1270.7 | 1180 | 1223.5 | 1271.5 | 1160 | 1170 | 1176.1 | 1142 | 1090 | 1111 | 1123 | 1101 | 1096.2 | 1117.3 | 935.4 | 1124.3 |  |  | 1021 | 801 | 1141 |  | 1212.3 | 1121 | 1109.6 | 1121.7 | 1112 | 1106.1 | 1122.6 | 1121.4 | 1129.1 | 1119.5 | 1128.5 | 1109.4 | 1269.7 | 1298.3 | 970 | 960 | 833 | 688 | 871.5 | 1001.1 | 1149.8 | 1249.8 | 1198.4 | 1209.7 | 1155.5 | 1212 | 1243.4 | 1249.55 | 1101.1 | 1155.4 | 1103.3 | 1131 | 1058 |  | 1500.1 | 1223 | 421 | 1109 | 1071 |  |  | 1040 | 1101 | 1143 | 1071 | 1031 | 33.23 | 41.42 | 1.87 | 4.9 |  | 5.81 | 5.3 |  |  | 87494165.934 | 283487.115 | 60430998.241 | 63159.26 | 88205890.186 | 188727.198 | 64142279.414 | 58113.16 | 331376520.795 | 89443.315 | 76776.831 | 21.941 | 72636.894 | 29.884 | 75179.603 | 45.27 | 56847.544 | 56.544 | 281490.64 | 133.681 | 149361.9 | 281356.959 | 13.2167 | 5.81 | 5.3 | 33.23 | 41.42 | 1.87 | 4.9 | 282611.15
2025-06-23 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:12 | 18:30 | 1067 | 1053.4 | 978 | 973.1 | 1049.2 | 973.9 | 972.6 | 973.1 | 931.6 | 1013.1 | 981 | 986.2 | 981.1 | 891 | 968.2 | 967.8 | 965.5 | 998.2 | 1045.4 | 1043.8 | 969.2 | 972 | 1046.1 | 1099.5 | 1057.6 | 1048.3 | 1059.1 | 1088.1 | 1097.8 | 1091.2 | 1109 | 1010 | 935.2 | 1232 | 970.4 | 1071 | 976.7 | 991 | 981.2 | 977.9 | 962.4 | 989.9 | 999.1 | 994.6 | 975.4 | 979.4 | 951 | 959.1 | 1010 | 911 | 969.6 | 973 | 1090 | 1091.4 | 1034.1 | 1100 | 1099.5 | 969.9 | 1087.4 | 1104.4 | 976.1 | 1080 | 973.4 | 890 | 1052.3 | 1057.4 | 1044 | 1038.1 | 976 | 974.1 | 975.4 | 967.1 | 961 | 961 | 1080 | 1098.5 | 1078 | 982.9 | 973 | 1071.9 | 980.6 | 965.9 | 974 | 989 | 970.6 | 973.1 | 974.9 | 968.8 | 956.1 | 945.7 | 999.9 | 1017 | 955 | 958 | 1071 | 958.1 | 745 | 985.2 | 956 | 960 | 970 | 958 | 951 | 946.6 | 1080 | 951 | 1080 | 1079.4 | 951 | 1059 | 1045.2 | 1052.8 | 1070 | 1061 | 951 | 964 | 967 | 1090 | 1059 | 975.5 | 956 | 1039.6 | 1016.1 | 951 | 967 | 1089 | 940.1 | 964.1 | 1080 | 1046 | 1029 | 1019.3 | 1044.5 | 860 | 1020 | 1030.7 | 869.7 | 1029 | 990 | 934 | 1039.6 | 1020.4 | 962.4 | 1042 | 946.6 | 1044 | 965 | 876 | 1063.4 | 1060.6 | 1048 | 971.2 | 1081 | 962.4 | 974 | 962.2 | 965.1 | 953 | 959.3 | 949.1 | 1079.5 | 920.9 | 989.4 | 988.2 | 1049 | 994 | 940 | 992.6 | 940 | 965.2 | 991.6 | 968.6 | 1060 | 980 | 1076.2 | 954.1 | 941 | 944.3 | 1061.6 | 951 | 1020 | 1041 | 1071 | 990 | 1024.5 | 1072.7 | 971 | 990.9 | 920 | 1010 | 950.1 | 935.8 | 941 | 941.7 | 956.6 | 931 | 780 | 931 |  |  | 860 | 615.9 | 953.6 |  | 1065.3 | 943.5 | 901.3 | 941.3 | 959.6 | 967.8 | 977 | 976.1 | 941 | 974.1 | 977.6 | 941 | 1080 | 1100 | 830 | 819 | 698 | 591 | 741 | 867.2 | 1032.5 | 1101.1 | 1051.5 | 1064.8 | 1032.7 | 1072.6 | 1110.7 | 1092.6 | 941.6 | 981 | 929.9 | 941.6 | 876.6 |  | 1301 | 1020 | 372 | 934 | 902 |  |  | 943 | 950 | 964 | 898 | 861.2 | 30.76 | 41.42 | 1.21 | 6.5 |  | 4.95 | 4.58 |  |  | 87558522.716 | 283500.056 | 60492999.11 | 63189.144 | 88268514.617 | 188772.468 | 64192397.921 | 58169.704 | 331615308.592 | 89576.996 | 64356.782 | 12.941 | 62000.869 | 29.884 | 62624.431 | 45.27 | 50118.507 | 56.544 | 238787.797 | 133.681 | 126314.826 | 238654.116 | 13.3 | 4.95 | 4.58 | 30.76 | 41.42 | 1.21 | 6.5 | 239843.7
2025-06-24 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:11 | 18:31 | 1415.2 | 1450.2 | 1345.8 | 1327 | 1436.1 | 1338.3 | 1337.7 | 1344.2 | 1391 | 1399.9 | 1361 | 1358 | 1287 | 1265.8 | 1341.4 | 1340.6 | 1329.7 | 1326.7 | 1440.1 | 1439.8 | 1342.7 | 1348.9 | 1421.6 | 1516.6 | 1463.2 | 1450.4 | 1409.1 | 1493.2 | 1509.5 | 1455 | 1455.5 | 1451.1 | 1258 | 1698.7 | 1311.1 | 1478.2 | 1283.4 | 1292.2 | 1317 | 1329.6 | 1307.1 | 1302.5 | 1326.1 | 1316.9 | 1335.1 | 1340.9 | 1408.9 | 1314.3 | 1373.3 | 1355 | 1331.9 | 1330.5 | 1519.3 | 1499.2 | 1421.4 | 1504 | 1501.7 | 1337.2 | 1483.1 | 1503.5 | 1333.2 | 1504.5 | 1329.7 | 1289.3 | 1453.1 | 1440.1 | 1452.1 | 1406.3 | 1328.1 | 1325.7 | 1327 | 1317.3 | 1351.3 | 1322.1 | 1491.7 | 1460.2 | 1499.9 | 1329 | 1318.5 | 1446.5 | 1342.5 | 1346.7 | 1327.7 | 1340.7 | 1329.6 | 1334.8 | 1331.7 | 1329.9 | 1301.8 | 1293.8 | 1352.5 | 1401.2 | 1348.2 | 1300.7 | 1483.4 | 1310.7 | 1288 | 1347.9 | 1315.6 | 1334.9 | 1362.4 | 1323.6 | 1332.7 | 1310.1 | 1501.5 | 1297.5 | 1536.6 | 746.5 | 1345.2 | 1495.1 | 1447.14 | 1435.1 | 1490.1 | 1501 | 1348.1 | 1343.4 | 1446.5 | 1486.2 | 1488 | 1334.5 | 1352.7 | 1427.6 | 1395.65 | 1337.9 | 1309.2 | 1478.9 | 1311.4 | 1292.4 | 1485.5 | 1472.2 | 1410.1 | 1390.7 | 1415.7 | 1201.1 | 1442.6 | 1376.8 | 1423 | 1435.6 | 1382.7 | 1319 | 1410.2 | 1402.2 | 1315.2 | 1441.2 | 1283.5 | 1416.5 | 1291.9 | 1209 | 1414 | 1409.8 | 1440.6 | 1313.5 | 1479 | 1312.4 | 1289 | 1291.1 | 1282.6 | 1303.4 | 1327.1 | 1303.1 | 1478.9 | 1282.1 | 1446 | 1447.2 | 1454 | 1365.4 | 1292.7 | 1457.3 | 1288 | 1326.7 | 1367.3 | 1337.5 | 1444 | 1370.5 | 1480.3 | 1309 | 1311.6 | 1287.6 | 1455.7 | 1335.2 | 1389.1 | 1453.1 | 1441 | 1420 | 1431 | 1474.8 | 1371.5 | 1350 | 1333.8 | 1410 | 1318.3 | 1309.1 | 1278 | 1302.1 | 1311.9 | 1281.1 | 1103.2 | 1290 |  |  | 1176 | 921 | 1312 |  | 1431.4 | 1297.1 | 1303.8 | 1303.6 | 1325.6 | 1327.7 | 1335.9 | 1336.1 | 1333.8 | 1289.1 | 1325.2 | 1335 | 1490.3 | 1497.6 | 1144 | 1101 | 944 | 801 | 1024.2 | 1165.3 | 1384 | 1497.3 | 1428.5 | 1423.7 | 1395.5 | 1435.5 | 1489.8 | 1476.3 | 1245 | 1339.1 | 1242.5 | 1323.2 | 1229.1 |  | 1801 | 1401.2 | 524.5 | 1301 | 1243.5 |  |  | 1301 | 1277.2 | 1301 | 1243.3 | 1178.5 | 33.08 | 45.26 | 1.88 | 5.5 |  | 6.96 | 6.44 |  |  | 87646933.478 | 283502.997 | 60576457.037 | 63219.028 | 88355329.828 | 188817.738 | 64260621.588 | 58226.248 | 331941994.034 | 89710.677 | 88410.762 | 2.941 | 83457.927 | 29.884 | 86815.211 | 45.27 | 68223.667 | 56.544 | 326685.442 | 133.681 | 171835.864 | 326551.761 | 13.3333 | 6.96 | 6.44 | 33.08 | 45.26 | 1.88 | 5.5 | 329656.49
2025-06-25 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:11 | 18:50 | 1398.7 | 1401.2 | 1326.1 | 1324.9 | 1421.9 | 1318.4 | 1322.7 | 1301.2 | 1365.9 | 1368.9 | 1312.1 | 1309.6 | 1264.1 | 1190.2 | 1316.9 | 1315.5 | 1310 | 1304.2 | 1409.8 | 1416.2 | 1321.2 | 1321.7 | 1398.6 | 1488.3 | 1436.1 | 1418.6 | 1371.1 | 1464.9 | 1472 | 1421.2 | 1425.5 | 1417.5 | 1255.2 | 1623.1 | 1297.7 | 1463.2 | 1309.5 | 1281.4 | 1303 | 1324.7 | 1293.7 | 1282 | 1306.5 | 1295.7 | 1316.6 | 1318 | 1411.5 | 1300.5 | 1356.2 | 1313.5 | 1313.2 | 1311 | 1469.7 | 1477.9 | 1387.7 | 1467.2 | 1464.1 | 1299.7 | 1469.5 | 1464.6 | 1320.3 | 1461.8 | 1313.7 | 1258.7 | 1429.3 | 1417.1 | 1434.3 | 1391.9 | 1312.5 | 1307.3 | 1312.5 | 1299.7 | 1319.1 | 1312.7 | 1488 | 1457.3 | 1490 | 1314.5 | 1300.7 | 1435 | 1321 | 1301 | 1305.8 | 1322.1 | 1303.6 | 1310 | 1308.2 | 1305.5 | 1277.8 | 1267.4 | 1336.9 | 1376.5 | 1330.1 | 1291.1 | 1467.3 | 1299.4 | 1303.3 | 1326.6 | 1310.4 | 1317.8 | 1321.1 | 1302.9 | 1315.1 | 1301.2 | 1485.2 | 1290.1 | 1490.3 | 1414.2 | 1309.1 | 1468.2 | 1421.4 | 1420.5 | 1456.1 | 1466.2 | 1324.2 | 1267.2 | 1418.6 | 1457.8 | 1466.8 | 1316.6 | 1319.1 | 1405.6 | 1368.1 | 1316.6 | 1290.2 | 1467.1 | 1290.2 | 1293.3 | 1413.8 | 1448.1 | 1402.1 | 1389.4 | 1395.1 | 1203.3 | 1401.1 | 1374.2 | 1390.1 | 1413.2 | 1354.3 | 1272.2 | 1381.8 | 1371.8 | 1303.3 | 1401.1 | 1264.5 | 1392.8 | 1280.8 | 1197.7 | 1402.8 | 1414.8 | 1401.1 | 1298.2 | 1486.5 | 1299.1 | 1275.2 | 1272.8 | 1272.8 | 1298.9 | 1275.7 | 1251.6 | 1414.9 | 1254.6 | 1408 | 1399 | 1442.2 | 1317.3 | 1251.2 | 1431.5 | 1264.5 | 1313.5 | 1317.6 | 1313.01 | 1414.4 | 1331.4 | 1418.2 | 1261.8 | 1273.8 | 1269.5 | 1411.6 | 1284.7 | 1359.2 | 1403.4 | 1442.5 | 1362.2 | 1376.7 | 1418.8 | 1333.7 | 1330.4 | 1324 | 1355.6 | 1279.3 | 1251.7 | 1264.5 | 1264 | 1294.3 | 1267.9 | 1071.2 | 1290 |  |  | 1174.4 | 902 | 1302.4 |  | 1417.7 | 1272.1 | 1287.8 | 1271.1 | 1303.2 | 1309.1 | 1321 | 1322.8 | 1290.1 | 1271.5 | 1317.5 | 1290 | 1482.4 | 1516.8 | 1154 | 1123 | 967 | 789 | 1000 | 1142.2 | 1366.4 | 1463 | 1386 | 1386.5 | 1374.5 | 1394.5 | 1460.8 | 1431.4 | 1224 | 1321.2 | 1221 | 1268 | 1204.5 |  | 1789 | 1367.7 | 503 | 1276.6 | 1230.6 |  |  | 1261.4 | 1255 | 1313 | 1232.5 | 1190.6 | 33.46 | 42.64 | 3.12 | 7.5 |  | 6.57 | 6.18 |  |  | 87734214.23 | 283515.938 | 60659715.158 | 63240.912 | 88440708.476 | 188855.008 | 64327958.783 | 58275.792 | 332265085.404 | 89831.358 | 87280.752 | 12.941 | 83258.121 | 21.884 | 85378.648 | 37.27 | 67337.195 | 49.544 | 323091.37 | 120.681 | 170504.048 | 322970.689 | 13.65 | 6.57 | 6.18 | 33.46 | 42.64 | 3.12 | 7.5 | 324493.01
2025-06-26 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:14 | 18:40 | 1414 | 1423.1 | 1339.2 | 1335.9 | 1427.5 | 1328.1 | 1320.3 | 1325.6 | 1369.2 | 1373.8 | 1336.6 | 1327.7 | 1289.7 | 1212 | 1308.2 | 1306.2 | 1297.9 | 1291.9 | 1397.6 | 1402 | 1310 | 1312.6 | 1387.4 | 1471.9 | 1417.9 | 1401.3 | 1369.6 | 1444.2 | 1453.8 | 1444.2 | 1423.4 | 1434.8 | 1247.4 | 1674.5 | 1290.8 | 1452.6 | 1300.1 | 1271.6 | 1291.6 | 1314.8 | 1285.3 | 1273.3 | 1293.8 | 1283.1 | 1308.1 | 1315.1 | 1414.9 | 1292.6 | 1366.7 | 1321.3 | 1320.4 | 1317.4 | 1471.8 | 1478.3 | 1378.7 | 1471.2 | 1459.4 | 1316.7 | 1458.5 | 1474 | 1310.1 | 1479.9 | 1307.5 | 1268.2 | 1425.3 | 1411.3 | 1429.7 | 1396 | 1310.8 | 1303.7 | 1313.6 | 1303.1 | 1302.3 | 1301.1 | 1456.7 | 1433.4 | 1470.4 | 1301.1 | 1290.6 | 1413.5 | 1309.8 | 1315.4 | 1301.2 | 1314.9 | 1297.4 | 1307.1 | 1309.2 | 1309.7 | 1280.4 | 1273 | 1342.5 | 1381.6 | 1326.3 | 1313.5 | 1459.6 | 1290.4 | 1287.7 | 1320.7 | 1295.5 | 1307.9 | 1311.2 | 1289.7 | 1302.8 | 1286.7 | 1454.3 | 1221.5 | 1493 | 1435.5 | 1313.9 | 1455.2 | 1403.3 | 1416.3 | 1461.3 | 1467.5 | 1318.1 | 1271.1 | 1435.3 | 1431.2 | 1444.4 | 1310.2 | 1326.4 | 1401 | 1353.4 | 1304.7 | 1309.1 | 1467.8 | 1289.6 | 1288.4 | 1431.1 | 1448.3 | 1391.5 | 1391.7 | 1396.4 | 1202.4 | 1389.1 | 1373.2 | 1398.2 | 1401.2 | 1351.2 | 1300.2 | 1387.4 | 1381.1 | 1308.4 | 1425.6 | 1271.8 | 1396.6 | 1280.7 | 1194.7 | 1384.5 | 1403.8 | 1410.5 | 1285.1 | 1475.6 | 1289.9 | 1268.6 | 1278.1 | 1266.9 | 1290.1 | 1289.6 | 1271.1 | 1431.1 | 1265.7 | 1421.1 | 1434.2 | 1439.1 | 1321.1 | 1265.5 | 1451.1 | 1280 | 1355 | 1343 | 1331.4 | 1421.6 | 1341.1 | 1421 | 1271.1 | 1271.8 | 1291 | 1431.1 | 1301 | 1384.5 | 1421.5 | 1410.5 | 1371.1 | 1398.1 | 1434.7 | 1344 | 1344.1 | 1339.4 | 1371.1 | 1291.8 | 1285.4 | 1286.1 | 1289.5 | 1290 | 1278 | 1070 | 1301.1 |  |  | 1181 | 915.7 | 1302.7 |  | 1442.7 | 1285.9 | 1291.4 | 1281.6 | 1301 | 1295.8 | 1331.1 | 1323.1 | 1301.1 | 1290 | 1312 | 1324.9 | 1483.3 | 1516.9 | 1151 | 1133.6 | 974.5 | 799 | 999.3 | 1176 | 1371.6 | 1476.7 | 1411 | 1409.5 | 1371.1 | 1421.7 | 1497.2 | 1479.8 | 1241.2 | 1347.7 | 1233.8 | 1289.8 | 1190.9 |  | 1801 | 1376.6 | 513.2 | 1275.8 | 1232.5 |  |  | 1261 | 1278.6 | 1321.1 | 1225.8 | 1206.1 | 34.28 | 42.05 | 4.04 | 8.1 |  | 6.68 | 6.3 |  |  | 87821123.068 | 283528.879 | 60742286.209 | 63259.796 | 88526223.941 | 188889.278 | 64396685.26 | 58321.336 | 332588605.236 | 89948.039 | 86908.838 | 12.941 | 82571.051 | 18.884 | 85515.465 | 34.27 | 68726.477 | 45.544 | 323519.832 | 116.681 | 169448.064 | 323403.151 | 13.4333 | 6.68 | 6.3 | 34.28 | 42.05 | 4.04 | 8.1 | 325151.3
2025-06-27 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:48 | 18:41 | 1288.4 | 1291.1 | 1190 | 1201 | 1300 | 1197.5 | 1181.6 | 1198.1 | 1202.1 | 1210 | 1190.1 | 1198.7 | 1144.7 | 1060 | 1186.6 | 1191.1 | 1181 | 1179.5 | 1251.6 | 1254.1 | 1167.6 | 1171.8 | 1257.9 | 1301.1 | 1267.8 | 1265.6 | 1221.5 | 1322.8 | 1317.6 | 1269.9 | 1265.5 | 1277.1 | 1102.4 | 1456.6 | 1142.8 | 1275.5 | 1151.6 | 1130 | 1148.9 | 1172.7 | 1140.6 | 1133.1 | 1150.5 | 1140.3 | 1166.3 | 1170.6 | 1212 | 1156.3 | 1220 | 1167.8 | 1171.1 | 1173 | 1301.1 | 1313.7 | 1212 | 1301.2 | 1312.2 | 1179 | 1298.8 | 1305.6 | 1167.4 | 1311.4 | 1159.6 | 1101.5 | 1259 | 1265.8 | 1271.8 | 1251.4 | 1152.5 | 1154.6 | 1161.9 | 1171.7 | 1165.7 | 1163 | 1304.7 | 1287.1 | 1299.8 | 1170.8 | 1167.9 | 1262.8 | 1163.5 | 1157.6 | 1169.8 | 1173.2 | 1169.3 | 1158.8 | 1158.8 | 1154 | 1154.8 | 1142.9 | 1196.4 | 1226 | 1167 | 1165.6 | 1316.6 | 1171 | 764.7 | 1172.6 | 1170.3 | 1167.8 | 1162.5 | 1173.1 | 1181.2 | 1127.7 | 1305.2 | 1178.8 | 1314.8 | 1257.8 | 1171.8 | 1316.5 | 1272.9 | 1258.8 | 1305.8 | 1320.8 | 1152.2 | 1123 | 1254.1 | 1275.6 | 1282 | 1175.6 | 1187.8 | 1236.2 | 1227.5 | 1154.4 | 1163.9 | 1278 | 1154 | 1141 | 1267.1 | 1269 | 1218.2 | 1230.9 | 1233.8 | 1061.6 | 1230.2 | 1212 | 1225.7 | 1220 | 1179.7 | 1127.78 | 1232.5 | 1221.1 | 1128.5 | 1230.6 | 1131.1 | 1231.1 | 1131.1 | 1034.6 | 1231.5 | 1220.6 | 1226.2 | 1123.1 | 1282.9 | 1124.8 | 1131.1 | 1125.1 | 1145.5 | 1140.5 | 1140.9 | 1119.4 | 1263 | 1131.4 | 1252.9 | 1254.8 | 1281.4 | 1176.1 | 1129.6 | 1247.4 | 1133.3 | 1172.4 | 1174.1 | 1156.2 | 1263.2 | 1182.6 | 1254.1 | 1122.5 | 1133.4 | 1121.1 | 1251.5 | 1140.2 | 1212 | 1254.1 | 1264.5 | 1215.8 | 1226.7 | 1267.4 | 1182.8 | 1183.4 | 1197.9 | 1210 | 1132.1 | 1135.8 | 1121.1 | 1138.3 | 1131.1 | 1113.1 | 956.1 | 1124.1 |  |  | 0.1 | 806.7 | 1148.9 |  | 1278.1 | 1158.9 | 1171.1 | 1128.3 | 1171.1 | 1160.3 | 1167.7 | 1174.8 | 1154.8 | 1131.8 | 1151.2 | 1156.4 | 1322.2 | 1350.6 | 1024.1 | 1020 | 871.2 | 701.2 | 886.7 | 1041.3 | 1248.5 | 1326.3 | 1262 | 1267.9 | 1255.5 | 1285 | 1320.3 | 1299 | 1091.1 | 1187.2 | 1101 | 1141.5 | 1051.7 |  | 1621.5 | 1221.1 | 435.8 | 1132.1 | 1091.6 |  |  | 1121.1 | 1142.6 | 1181.7 | 1121 | 1055.1 | 31.5 | 41.46 | 2.01 | 6.7 |  | 6.01 | 5.64 |  |  | 87898891.252 | 283537.82 | 60816362.773 | 63272.68 | 88601459.192 | 188919.548 | 64456309.176 | 58361.88 | 332875063.14 | 90053.72 | 77768.184 | 8.941 | 74076.564 | 12.884 | 75235.251 | 30.27 | 59623.916 | 40.544 | 286457.904 | 105.681 | 151822.923 | 286352.223 | 12.8833 | 6.01 | 5.64 | 31.5 | 41.46 | 2.01 | 6.7 | 287351.88
2025-06-28 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:26 | 18:29 | 1049.2 | 1069.3 | 961.1 | 963.7 | 1068 | 984 | 990.6 | 990.6 | 1019.1 | 1024.2 | 968.8 | 997.9 | 939.4 | 878.1 | 983.3 | 974.1 | 977.7 | 976.2 | 1052.4 | 1055.7 | 951.1 | 959.8 | 1026.3 | 1093.9 | 1034.6 | 1048.5 | 1013.2 | 1069.1 | 1078.9 | 1063.2 | 1071.1 | 1051.2 | 902.1 | 1201.2 | 971.2 | 1050 | 971.2 | 966 | 871 | 974.5 | 976 | 972.6 | 971.2 | 965.6 | 961.2 | 956.8 | 1030 | 967.8 | 996.8 | 972.9 | 971.2 | 974.8 | 1093.2 | 1098.7 | 1023 | 1100.1 | 1103.6 | 872.2 | 1076.7 | 1091.2 | 991.7 | 1055 | 985.6 | 902 | 1060.5 | 1041.2 | 1056.2 | 1042.6 | 973.6 | 963.7 | 967 | 981.1 | 969.4 | 955.7 | 1072.7 | 1081.1 | 1090.7 | 969.8 | 973.3 | 1061 | 957.8 | 971.2 | 979.2 | 966.9 | 980.2 | 966.2 | 956.2 | 978.3 | 970.4 | 957.2 | 997 | 1018.6 | 961.2 | 854 | 1100.8 | 974.7 | 0 | 972.1 | 958 | 954.2 | 964.6 | 951.6 | 959.4 | 950.3 | 1071 | 967 | 1083.7 | 1051.3 | 939.9 | 1105 | 1032 | 1019.2 | 1057.9 | 1071.5 | 966.9 | 956.1 | 1061.2 | 1054 | 1069.9 | 954.2 | 967.2 | 999 | 1005 | 956 | 941 | 1059 | 956 | 946 | 1090 | 1080.4 | 957.1 | 1047.2 | 1062 | 905 | 1066.5 | 1019.5 | 1065.3 | 1060.3 | 1026.7 | 876.1 | 1049.5 | 1026.7 | 980 | 1074.1 | 952.1 | 1052.3 | 964 | 903.2 | 1045.5 | 1057.4 | 1056.8 | 957.8 | 1074.2 | 948.7 | 945.7 | 950 | 967.6 | 987.5 | 967.9 | 940.5 | 1082.9 | 928 | 1050.5 | 1044.5 | 1080.9 | 983.9 | 942.8 | 1045.1 | 934.3 | 960 | 989.2 | 969.4 | 1052.6 | 893.2 | 1068.2 | 959.2 | 975 | 964.8 | 1071.4 | 956 | 1012 | 1056.2 | 1050.2 | 1010 | 1021.1 | 1081.6 | 978 | 990 | 962.9 | 932.5 | 945.4 | 967.1 | 959.2 | 971.5 | 955.9 | 945 | 795.5 | 949.5 |  |  | 0 | 681.2 | 958.8 |  | 1034 | 971.1 | 956 | 959.1 | 857.8 | 981.2 | 966.3 | 974.1 | 946.8 | 956.8 | 948.3 | 949 | 1062.5 | 1143 | 851 | 841 | 721 | 590 | 741.7 | 849.6 | 1006.4 | 1077.4 | 1014.5 | 1015.6 | 1021.5 | 1034.5 | 1068.2 | 1078.1 | 931.1 | 1012.2 | 909 | 948.6 | 878.9 |  | 1345 | 1021 | 362.5 | 934 | 912 |  |  | 901 | 956 | 978 | 907.7 | 871 | 30.91 | 41.13 | 1.51 | 9.7 |  | 5.07 | 4.65 |  |  | 87963945.817 | 283546.761 | 60876406.429 | 63285.564 | 88665002.114 | 188949.818 | 64504361.702 | 58402.424 | 333111507.545 | 90159.401 | 65054.565 | 8.941 | 60043.656 | 12.884 | 63542.922 | 30.27 | 48052.526 | 40.544 | 236444.405 | 105.681 | 125076.396 | 236338.724 | 13.05 | 5.07 | 4.65 | 30.91 | 41.13 | 1.51 | 9.7 | 238197.7
2025-06-29 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:18 | 18:29 | 913 | 932 | 862 | 859 | 928 | 857 | 861 | 864 | 892 | 896 | 856 | 839.8 | 839 | 807 | 859 | 851.2 | 852 | 851 | 925 | 928 | 849 | 862 | 908 | 969 | 901 | 929 | 902 | 958 | 966 | 944.2 | 952 | 917.2 | 801 | 1072.2 | 849 | 958 | 856 | 829 | 844 | 860 | 836 | 834.1 | 846 | 819.2 | 853 | 856 | 901 | 846 | 882 | 861.2 | 850 | 854 | 973 | 961 | 914.7 | 954.5 | 961.2 | 846.7 | 960 | 933.4 | 856 | 972 | 865 | 788 | 923 | 919 | 928 | 894 | 845 | 848 | 852 | 838 | 839 | 847 | 965 | 953 | 967 | 849 | 845 | 930 | 854 | 860 | 846 | 852 | 838 | 848 | 840 | 843 | 839.8 | 834.2 | 879.2 | 901 | 858 | 831.2 | 948 | 844 | 0 | 847 | 852 | 839 | 833 | 855 | 836 | 852 | 965 | 841 | 983 | 952.6 | 843 | 957 | 921 | 921 | 934.3 | 927.7 | 860 | 836.8 | 945.2 | 931 | 951 | 853 | 834.7 | 899 | 883 | 854 | 828.8 | 958 | 832.3 | 839.7 | 932.5 | 955.7 | 902.7 | 916.6 | 922.6 | 766 | 899 | 900.3 | 892.8 | 903 | 871 | 861 | 919.1 | 905 | 846 | 942.1 | 831.1 | 925.5 | 848.1 | 788 | 921 | 944.2 | 934.1 | 865 | 951.2 | 845 | 852.3 | 840.8 | 856 | 871.2 | 848 | 828 | 944 | 818 | 935 | 922 | 952 | 869 | 826 | 896 | 835.4 | 851.2 | 864 | 865.9 | 939 | 820 | 929.7 | 834 | 846 | 824 | 926 | 845 | 912.7 | 931 | 927 | 872 | 892.7 | 952 | 871.2 | 865.7 | 864.2 | 902 | 821 | 834.2 | 842.7 | 835 | 834 | 829 | 689 | 823 |  |  | 0 | 601 | 856 |  | 926.5 | 849 | 845.7 | 839.7 | 840.9 | 843.7 | 836 | 848.7 | 839.7 | 846.5 | 852 | 832.2 | 961.1 | 1001 | 752.2 | 739 | 629 | 534 | 645 | 750 | 865 | 958 | 901 | 900 | 898 | 934 | 955 | 937.4 | 801 | 866 | 809 | 842.3 | 782.2 |  | 1171.2 | 909.6 | 322 | 835 | 803 |  |  | 788 | 851 | 845 | 809 | 759.7 | 30.09 | 37.22 | 2.43 | 9.3 |  | 4.19 | 3.89 |  |  | 88020668.84 | 283555.702 | 60929965.521 | 63298.448 | 88720828.316 | 188980.088 | 64547622.07 | 58442.968 | 333320660.333 | 90265.082 | 56723.023 | 8.941 | 53559.092 | 12.884 | 55826.202 | 30.27 | 43260.368 | 40.544 | 209152.788 | 105.681 | 110260.29 | 209047.107 | 13.1833 | 4.19 | 3.89 | 30.09 | 37.22 | 2.43 | 9.3 | 210024.2
2025-06-30 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:20 | 18:23 | 739 | 732 | 677 | 673 | 728 | 674 | 677 | 679 | 701 | 704 | 691 | 686 | 681 | 634 | 674 | 673 | 670 | 666 | 730 | 727 | 674 | 676 | 729 | 763 | 733 | 726 | 735 | 755 | 758 | 761 | 759 | 753 | 649 | 864 | 662 | 744 | 673 | 664 | 652 | 672 | 673 | 656 | 687 | 676 | 684 | 673 | 682 | 675.8 | 661 | 659 | 664 | 678 | 751 | 764 | 723 | 763 | 765 | 680 | 756 | 766 | 670 | 768 | 673 | 624 | 727 | 724 | 728 | 734 | 662 | 664 | 674 | 671 | 683 | 679 | 767.8 | 751 | 762 | 669 | 674.7 | 731 | 668 | 673 | 663 | 669 | 674 | 655 | 681 | 655 | 656 | 666 | 681.2 | 723 | 667 | 634 | 756 | 662 | 47.5 | 676 | 683 | 672 | 657.8 | 684.7 | 657.9 | 667 | 755 | 648 | 763.3 | 739 | 671 | 756 | 727 | 743 | 756 | 758 | 672 | 673 | 752 | 732 | 755 | 673 | 654.6 | 708 | 727 | 668 | 669 | 754 | 674 | 684 | 721 | 771 | 739 | 745 | 739 | 612 | 722 | 721 | 711 | 729 | 703 | 682 | 718.6 | 715 | 683 | 709 | 682 | 711.2 | 665.1 | 619.3 | 739 | 734 | 738.9 | 678.2 | 761.2 | 679.3 | 668.7 | 684 | 670 | 685 | 661 | 669.7 | 737 | 649 | 754 | 727 | 731 | 676 | 674 | 701 | 651 | 681 | 698 | 679 | 739 | 668 | 739 | 652.6 | 654 | 654.8 | 724 | 651 | 724 | 731 | 724 | 672.9 | 711 | 736 | 692 | 694 | 645 | 701 | 656.8 | 645 | 656 | 652 | 655 | 658.4 | 544 | 660 |  |  | 0 | 463.6 | 656 |  | 728 | 682 | 653.2 | 654 | 685 | 667 | 668 | 658.1 | 670 | 656.5 | 665 | 661 | 759 | 774 | 587 | 573 | 494 | 414 | 504 | 595 | 704 | 761 | 732 | 721 | 713 | 739 | 759 | 755 | 639 | 676 | 643 | 666 | 612 |  | 934 | 709 | 252 | 661 | 634 |  |  | 639 | 678 | 684 | 636 | 601 | 29.64 | 35.33 | 1.69 | 4.3 |  | 3.23 | 3.03 |  |  | 88065461.3 | 283564.643 | 60972342.552 | 63311.332 | 88764796.416 | 189003.358 | 64582109.651 | 58471.512 | 333486061.493 | 90360.763 | 44792.46 | 8.941 | 42377.031 | 12.884 | 43968.1 | 23.27 | 34487.581 | 28.544 | 165401.16 | 95.681 | 87147.666 | 165305.479 | 13.05 | 3.23 | 3.03 | 29.64 | 35.33 | 1.69 | 4.3 | 166212.4
2025-07-01 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:34 | 18:43 | 588.4 | 599 | 554.2 | 551.4 | 597.2 | 550.8 | 553.6 | 555.2 | 501 | 543 | 566.1 | 562.4 | 528.2 | 520.4 | 552.8 | 553 | 547.5 | 545.4 | 599 | 598 | 553.6 | 557 | 587.3 | 632.2 | 605.4 | 601.2 | 597.6 | 622.9 | 629.4 | 602.5 | 615.2 | 612 | 517.6 | 690 | 544.4 | 590 | 536 | 521.1 | 532 | 536.8 | 526 | 529 | 537.4 | 537.2 | 541.2 | 527.7 | 573 | 539.2 | 561.5 | 549.3 | 542.4 | 547.8 | 593 | 596 | 571 | 596 | 541.2 | 539 | 588 | 590 | 528 | 590 | 534 | 499.3 | 586.1 | 584 | 584 | 569 | 532.2 | 536 | 536.5 | 522.8 | 529.1 | 541.3 | 599 | 588 | 590 | 534 | 534.4 | 567 | 529 | 524.2 | 539.9 | 532.8 | 524.9 | 523.2 | 523.9 | 532.3 | 531 | 526 | 546 | 562.1 | 536 | 523 | 600.4 | 532.1 | 470 | 521 | 539 | 542.7 | 532 | 538 | 533 | 540.7 | 610.8 | 523.2 | 601 | 598.2 | 524 | 604.2 | 580.1 | 581.3 | 590 | 593 | 531 | 524 | 582 | 587 | 602.9 | 532.6 | 538.6 | 556.4 | 574.5 | 533.7 | 535.4 | 589 | 524 | 535.6 | 587.5 | 602 | 572 | 587.3 | 567 | 480 | 572 | 562 | 563 | 568 | 559.8 | 539 | 591.3 | 588.7 | 531.5 | 574.8 | 523 | 582 | 545.4 | 431 | 591 | 590 | 578 | 529 | 614.6 | 529 | 535 | 540.7 | 524 | 538.7 | 529 | 534 | 590 | 519.6 | 603.9 | 531 | 581 | 552.9 | 535.4 | 529 | 532.8 | 545.3 | 547.3 | 549.9 | 591.2 | 546 | 583 | 492.2 | 524 | 523.5 | 592.6 | 519 | 569.6 | 578 | 590 | 549 | 579.2 | 583 | 545 | 538 | 551 | 495 | 529 | 537 | 527 | 525 | 513.8 | 526 | 435.5 | 520.4 |  |  | 0 | 381.2 | 531 |  | 571 | 534 | 527 | 536 | 536 | 527.2 | 485 | 539.4 | 522.8 | 533.8 | 527.3 | 540.5 | 590 | 617.5 | 472 | 451 | 390 | 333.4 | 413 | 473.7 | 558.4 | 597.5 | 568.4 | 573 | 564.5 | 574.5 | 597.6 | 585.9 | 513 | 551.2 | 528 | 538 | 497 |  | 734 | 562 | 198 | 525 | 509 |  |  | 512 | 538 | 543 | 511.7 | 487 | 27.91 | 32.27 | 0.185 | 4.7 | 0.2 | 2.61 | 2.41 |  |  | 88101780.953 | 283573.584 | 61006685.813 | 63324.216 | 88798717.359 | 189026.628 | 64609100.658 | 58500.056 | 333617364.81 | 90456.444 | 36319.653 | 8.941 | 34343.261 | 12.884 | 33920.943 | 23.27 | 26991.007 | 28.544 | 131303.317 | 95.681 | 70641.089 | 131207.636 | 13.15 | 2.61 | 2.41 | 27.91 | 32.27 | 0.185 | 4.7 | 132771
2025-07-02 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:14 | 18:38 | 934 | 952 | 877 | 878 | 940 | 869 | 876 | 875 | 865 | 905 | 896 | 888 | 837 | 822 | 882 | 879 | 881 | 881 | 962 | 962 | 892 | 889 | 937 | 1007 | 964 | 958 | 950 | 989 | 991 | 947 | 958 | 996 | 813 | 1101 | 877 | 985 | 886 | 870 | 846 | 871 | 846 | 839 | 854 | 855 | 860 | 864 | 932 | 858 | 893 | 877 | 851 | 865 | 988 | 968 | 914 | 984 | 956 | 790 | 956 | 964 | 859 | 964 | 801 | 798 | 933 | 940 | 942 | 906 | 865 | 869 | 868 | 849 | 839 | 848 | 959 | 947 | 934 | 852 | 865 | 909 | 836 | 863 | 865 | 863 | 841 | 850 | 841 | 855 | 839 | 844.5 | 881 | 901 | 812 | 852 | 958 | 865 | 788 | 853 | 846 | 853 | 852 | 862 | 842 | 854 | 963 | 778 | 967 | 949 | 875 | 978 | 945 | 935 | 978 | 979 | 879 | 843 | 947 | 942 | 967 | 866 | 878 | 905 | 929 | 867 | 872 | 949 | 849 | 843 | 964 | 939 | 903 | 947 | 924 | 798 | 902 | 897 | 903 | 918 | 904 | 857 | 955 | 938 | 849 | 923 | 845 | 948 | 851 | 793 | 944 | 953 | 945 | 861 | 971 | 854 | 847 | 842 | 845 | 873 | 851 | 851 | 959 | 840 | 950 | 934 | 950 | 871 | 846 | 971 | 831 | 886 | 897 | 882 | 965 | 887 | 901 | 834 | 857 | 831 | 943 | 851 | 907 | 945 | 952 | 878 | 938 | 972 | 872 | 887 | 867 | 911 | 839 | 829.8 | 757 | 831 | 831 | 807 | 702 | 833 |  |  | 407 | 609 | 869 |  | 937 | 846 | 851 | 841 | 854 | 842 | 849 | 869 | 848 | 854 | 851 | 866 | 968 | 964 | 747 | 761 | 632 | 531 | 666 | 755 | 883 | 961 | 910 | 917 | 902 | 909 | 962 | 944 | 819 | 875 | 809 | 857 | 791 |  | 1201 | 921 | 321 | 857 | 816 |  |  | 801 | 861 | 863 | 809 | 771 | 30.38 | 37.35 | 1.48 | 7.1 | 1.2 | 4.34 | 4.07 |  |  | 88159467.883 | 283582.525 | 61061901.317 | 63337.1 | 88855694.683 | 189049.898 | 64652310.868 | 58528.6 | 333830099.275 | 90552.125 | 57686.93 | 8.941 | 55215.504 | 12.884 | 56977.324 | 23.27 | 43210.21 | 28.544 | 212734.465 | 95.681 | 112880.609 | 212638.784 | 13.4 | 4.34 | 4.07 | 30.38 | 37.35 | 1.48 | 7.1 | 213894.3
2025-07-03 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:16 | 18:38 | 1036 | 1059 | 978 | 975 | 1054 | 973 | 956 | 951 | 964 | 1017 | 962 | 955 | 935 | 890 | 976 | 973 | 968 | 967 | 1053 | 1053 | 978 | 978 | 1032 | 1106 | 1062 | 1052 | 1045 | 1088 | 1091 | 1040 | 1046 | 1051 | 902 | 1223 | 957 | 1064 | 929 | 928 | 933 | 964 | 936 | 933.5 | 940 | 945 | 951 | 957 | 1039 | 954 | 988 | 971 | 951 | 963 | 1106 | 1084 | 1004 | 1081 | 1063 | 949 | 1092 | 1106 | 967 | 1062 | 954 | 901 | 1032 | 1044 | 1047 | 1008 | 954 | 963 | 960 | 936 | 970 | 951 | 1064 | 1075 | 1081 | 949 | 954 | 1045 | 971 | 943 | 962 | 950 | 930 | 942 | 927 | 945 | 933 | 929 | 971 | 1010 | 964 | 935 | 1087 | 961 | 933 | 953 | 957 | 949 | 961 | 957 | 947 | 946 | 1067 | 951 | 1084 | 1034.8 | 968 | 1092 | 1048 | 1024 | 1044 | 1055 | 945 | 929 | 1042 | 1044 | 1093 | 968 | 977 | 1015 | 1037 | 957 | 964 | 1054 | 933 | 943 | 1060.2 | 1070.7 | 1023 | 1032.2 | 1040.2 | 857 | 1001 | 1012.7 | 994 | 1028 | 986 | 952 | 1009 | 1023.6 | 958.6 | 1032 | 925.6 | 1038.6 | 961.2 | 821 | 1022.2 | 1034 | 1031 | 953 | 1072 | 957 | 951 | 943 | 946 | 939 | 943 | 928 | 1045 | 934 | 1056 | 939 | 1061 | 965 | 798 | 898 | 923 | 969 | 988 | 967 | 1045 | 959 | 1033 | 923 | 919 | 919 | 1034 | 924 | 1010 | 1034 | 1031 | 989 | 998 | 1033 | 974 | 965 | 990 | 996 | 932 | 934 | 934 | 927 | 935 | 945 | 793 | 946 |  |  | 867 | 687 | 965 |  | 1035 | 934 | 931 | 931 | 946 | 961 | 956 | 953 | 964 | 935 | 964 | 952 | 1049 | 1087 | 831 | 825 | 701 | 590 | 728 | 855 | 1020 | 1066 | 1032 | 1037 | 1002 | 1025 | 1065 | 1085 | 901 | 980 | 901 | 935 | 864 |  | 1302 | 1004 | 356 | 934 | 901 |  |  | 875 | 956 | 944 | 897 | 842 | 31.07 | 39.16 | 2.32 | 5.7 |  | 4.77 | 4.56 |  |  | 88223510.201 | 283591.466 | 61123420.148 | 63349.984 | 88917345.921 | 189073.168 | 64701872.208 | 58557.144 | 334066544.056 | 90647.806 | 64042.318 | 8.941 | 61518.831 | 12.884 | 61651.238 | 23.27 | 49561.34 | 28.544 | 236444.781 | 95.681 | 125539.324 | 236349.1 | 13.3667 | 4.77 | 4.56 | 31.07 | 39.16 | 2.32 | 5.7 | 237266.1
2025-07-04 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:15 | 18:36 | 954 | 961 | 876 | 888 | 954 | 881 | 885 | 883 | 891 | 901 | 872 | 875 | 875.3 | 801 | 860 | 866 | 879 | 890 | 952 | 949 | 882 | 874 | 965 | 1012 | 966 | 978 | 971 | 990 | 1011.6 | 968.3 | 992 | 996 | 829.5 | 1101 | 858.9 | 954.3 | 801 | 871 | 851.1 | 884.2 | 867 | 876 | 852.4 | 855.9 | 866.2 | 876.5 | 954.7 | 872.8 | 910.1 | 897 | 885.3 | 889.1 | 993 | 999.3 | 933.6 | 990 | 956 | 859 | 1007.3 | 995 | 881 | 965 | 856 | 818 | 951.1 | 946.2 | 956 | 924.1 | 859.3 | 867.4 | 872.2 | 854.9 | 876.6 | 867.5 | 968.6 | 949 | 973.6 | 863 | 855.5 | 937.5 | 875.5 | 861 | 868.5 | 855.7 | 842.5 | 855.9 | 844.5 | 867.5 | 856 | 854 | 909 | 912 | 874.9 | 854 | 965 | 858.8 | 848 | 881.8 | 868.3 | 871 | 882.5 | 865.9 | 873.7 | 858.6 | 957.9 | 851 | 977.4 | 948 | 861.5 | 958 | 915.2 | 946.1 | 982 | 984.8 | 876.5 | 845 | 943 | 953 | 971 | 851.3 | 861.8 | 883.5 | 918.5 | 841.5 | 846.3 | 965.8 | 809 | 851 | 945.2 | 939.5 | 883.6 | 922.9 | 933.7 | 798 | 924 | 921.4 | 901 | 934 | 901 | 875.7 | 929.6 | 919.3 | 877.7 | 943 | 846.5 | 933.6 | 853 | 794.5 | 919.7 | 936.1 | 944 | 864.2 | 962.2 | 867.5 | 854.8 | 846.5 | 855.5 | 847 | 851 | 849 | 961 | 853.4 | 967.3 | 944.5 | 1008.3 | 884.6 | 845 | 963.2 | 861.1 | 893.1 | 895.5 | 888.7 | 959 | 919.1 | 935 | 844 | 841.8 | 851 | 934.4 | 838.5 | 932 | 954 | 958.1 | 867 | 934.1 | 966.9 | 897.2 | 887.8 | 890 | 912 | 842 | 841 | 838 | 845 | 836.3 | 842 | 718.5 | 841.6 |  |  | 764.4 | 609 | 863 |  | 934 | 845 | 849 | 855 | 856 | 851 | 847 | 866.8 | 857.8 | 861 | 863.8 | 884.6 | 962 | 956 | 761 | 751 | 654 | 554 | 671 | 764.1 | 912.3 | 976.2 | 921 | 935 | 922.2 | 925.5 | 972.6 | 965 | 823 | 891 | 844 | 869 | 810 |  | 1181 | 941 | 321 | 854 | 834 |  |  | 801 | 878 | 888 | 823 | 790 | 30.97 | 40.04 | 1.49 | 7.5 |  | 4.55 | 4.15 |  |  | 88282690.988 | 283600.407 | 61178438.591 | 63362.868 | 88973969.421 | 189096.438 | 64745685.766 | 58585.688 | 334281509.689 | 90743.487 | 59180.787 | 8.941 | 55018.443 | 12.884 | 56623.5 | 23.27 | 43813.558 | 28.544 | 214965.633 | 95.681 | 114177.405 | 214869.952 | 13.35 | 4.55 | 4.15 | 30.97 | 40.04 | 1.49 | 7.5 | 216167.6
2025-07-05 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:29 | 18:42 | 1150.1 | 1170.7 | 1077.3 | 1072.9 | 1161.3 | 1069.9 | 1073 | 1077.5 | 1036.3 | 1119.9 | 1087.9 | 1085.2 | 1049 | 1013.2 | 1074.1 | 1073.8 | 1047 | 1047.1 | 1137.5 | 1140.1 | 1070.5 | 1080.3 | 1144.2 | 1219.5 | 1153.5 | 1150.9 | 1149.8 | 1202.3 | 1203.2 | 1162.5 | 1195.5 | 1203.8 | 994.8 | 1354 | 1032.7 | 1147.2 | 1020 | 1023 | 1015.2 | 1012 | 1026 | 1012 | 1021.8 | 1034.8 | 1041.3 | 1055.6 | 1142.9 | 1040.5 | 1104.8 | 1090.2 | 1062.2 | 1069.3 | 1226.6 | 1192.5 | 1133 | 1227.9 | 1112 | 1077.4 | 1194.3 | 1208.7 | 1055.8 | 1206.9 | 1065.4 | 990 | 1171 | 1176 | 1175 | 1169 | 1046 | 1054 | 1049 | 1043 | 1049 | 1090 | 1197 | 1193 | 1222 | 1090 | 1091 | 1184 | 1078 | 1101 | 1083 | 1083 | 1070.9 | 1087.8 | 1073.9 | 1075 | 1047 | 1043 | 1140.3 | 1121 | 1114.5 | 1100.9 | 1231 | 1112.3 | 1062 | 1128.9 | 1109.8 | 1115.3 | 1132.9 | 1114.2 | 1129.4 | 1114.5 | 1237.5 | 1100 | 1273 | 1255.5 | 1101.9 | 1252.1 | 1199.9 | 1193.7 | 1247 | 1246 | 1119.8 | 1063 | 1194 | 1204.1 | 1254.8 | 1119.2 | 1113.6 | 1169.1 | 1213.3 | 1090.8 | 1099.5 | 1267 | 1021 | 1009 | 1135.8 | 1135 | 1098 | 1098.9 | 1113 | 934 | 1095 | 1112 | 1097 | 1124.7 | 1071 | 1023 | 1104.4 | 1119 | 1034.4 | 1101 | 1011 | 1114 | 1027.7 | 931 | 1106 | 1110 | 1101 | 1033 | 1162.6 | 1032 | 1023 | 1034.6 | 1019 | 1026.6 | 1060.8 | 1039.5 | 1172.4 | 1034 | 1165 | 1171 | 1190.9 | 1074 | 1056 | 1181 | 1057 | 1074.9 | 1074 | 1082 | 1176 | 1099.7 | 1143 | 1016 | 1035 | 1033 | 1165 | 1067 | 1132 | 1172 | 1174 | 1135.9 | 1120.6 | 1168 | 1091.5 | 1076 | 1023 | 1045 | 1063.3 | 1092 | 1065 | 1045 | 1090.9 | 1045 | 916.4 | 1090.6 |  |  | 962.8 | 764 | 1067 |  | 1159 | 1053 | 1057 | 1080.1 | 1091.9 | 1102.5 | 1098.3 | 1136.7 | 1114.7 | 1074.6 | 1109.7 | 1124.1 | 1185 | 1275.2 | 956 | 959 | 821 | 682 | 855.2 | 1010.3 | 1189.9 | 1299.2 | 1245.3 | 1224.6 | 1201 | 1251.5 | 1288.7 | 1292.8 | 1058.5 | 1157 | 1044.3 | 1101.8 | 1020.2 |  | 1500.5 | 1167.6 | 409 | 1100.8 | 1066.8 |  |  | 1004 | 1064 | 1103 | 1012 | 945.5 | 31.55 | 42.78 | 1.29 | 4.3 |  | 5.37 | 5.13 |  |  | 88353150.305 | 283609.348 | 61249233.387 | 63375.752 | 89042191.268 | 189119.708 | 64803443.715 | 58614.232 | 334547631.737 | 90839.168 | 70459.317 | 8.941 | 70794.796 | 12.884 | 68221.847 | 23.27 | 57757.949 | 28.544 | 266122.048 | 95.681 | 141232.288 | 266026.367 | 13.2167 | 5.37 | 5.13 | 31.55 | 42.78 | 1.29 | 4.3 | 267586.7
2025-07-06 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | 5:15 | 18:27 | 991.3 | 1012.5 | 936.5 | 935.7 | 1003.6 | 925 | 932.6 | 935.2 | 962.2 | 967.9 | 939 | 946.3 | 937 | 873.7 | 928.4 | 923.3 | 925.6 | 923.2 | 1002.8 | 1002.9 | 930.5 | 929.5 | 991 | 1051 | 1012.8 | 1003.9 | 996.8 | 1039.473 | 1046.5 | 1036.2 | 1035.5 | 1045.2 | 882 | 1172 | 917.1 | 1018.8 | 925.8 | 912 | 909 | 913.5 | 915 | 921 | 919 | 929 | 924 | 909.5 | 991 | 925 | 956 | 957 | 925 | 917.3 | 1058.3 | 1026.8 | 991 | 1050.3 | 1058.4 | 942 | 1045.8 | 1058.3 | 917.3 | 1055.4 | 922 | 831 | 1032.2 | 1029.5 | 1037.6 | 1014.4 | 922.3 | 942.3 | 949.8 | 937.7 | 948 | 950.9 | 1080.8 | 1060.7 | 1086.6 | 949.1 | 928.1 | 1019.3 | 921 | 957 | 930.2 | 914.9 | 926 | 932 | 939.8 | 932.4 | 940 | 929.9 | 978.2 | 1023.6 | 963 | 943 | 1058.7 | 943.4 | 909.4 | 964.6 | 957.6 | 939 | 931 | 932 | 945 | 957.8 | 1075.3 | 911 | 1073 | 1075.5 | 950 | 1074.6 | 1027.6 | 1033.6 | 1079.6 | 1076.7 | 955.3 | 923 | 1025 | 1031 | 1076.4 | 949 | 950.6 | 1015.7 | 1036.7 | 926.2 | 938.6 | 1061 | 919 | 925 | 1037.8 | 1043.1 | 991 | 1022 | 1014 | 877.9 | 1016 | 986.7 | 981 | 1024 | 990 | 951 | 1016.9 | 1008.8 | 960 | 1032 | 938.2 | 1020 | 934 | 871 | 989 | 1019 | 1032 | 954 | 1080.4 | 959 | 956.2 | 952.4 | 957.3 | 937.5 | 924.6 | 906.6 | 1022.1 | 925 | 1021 | 1031 | 1046.2 | 943 | 945 | 1029 | 899.7 | 945 | 939 | 951 | 1031.1 | 953.5 | 1029 | 939 | 922 | 915 | 1021 | 926 | 1009 | 1012 | 1029 | 978 | 1005 | 1029 | 953.8 | 959.2 | 957.2 | 1012 | 931 | 937 | 851 | 925 | 942 | 927 | 767.6 | 919.1 |  |  | 838 | 650 | 939 |  | 1034 | 922.5 | 924 | 916.9 | 922.1 | 943.7 | 928.3 | 939 | 944 | 923 | 937.8 | 941 | 1039 | 1099 | 839 | 842 | 717 | 596 | 715 | 838.8 | 1005.8 | 1051 | 1030.7 | 1015.5 | 990 | 1021 | 1077.2 | 1063 | 901 | 953.6 | 911 | 923 | 847 |  | 1250.5 | 1009 | 351 | 923 | 877.9 |  |  | 863 | 931 | 945 | 901 | 831 | 32.64 | 41.48 | 1.41 | 3.9 |  | 4.52 | 4.5 |  |  | 88414777.733 | 283618.289 | 61310077.476 | 63388.636 | 89103661.517 | 189142.978 | 64852126.609 | 58642.776 | 334779897.943 | 90934.849 | 61627.428 | 8.941 | 60844.089 | 12.884 | 61470.249 | 23.27 | 48682.894 | 28.544 | 232266.206 | 95.681 | 122449.692 | 232170.525 | 13.2 | 4.52 | 4.5 | 32.64 | 41.48 | 1.41 | 3.9 | 233878.073
2025-07-07 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-08 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-09 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-10 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-11 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-12 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-13 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-14 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-15 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-16 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-17 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-18 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-19 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-20 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-21 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-22 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-23 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-24 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-25 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-26 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-27 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-28 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-29 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-30 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-07-31 | 2026 | 2025 |  |  | Jul-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-01 | 2026 | 2025 |  |  | Aug-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-02 | 2026 | 2025 |  |  | Aug-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-08-03 | 2026 | 2025 |  |  | Aug-25 | 31 | 66750 | [281 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Formulas:
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Modelling New
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | CC*Bugt (MTD) | CC*Bugt (YTD) | Capacity | 66.755
1 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 | 200.3 | 206.6 |  | 29.1001 |  | 10502 | 66.755 | 76.15% | 6.8867 | 0 | 0 | 0 | 350.0667 | 0 | 0 | 21.85% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
2 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 | 197.9 | 191.7 |  | 33.4 |  | 9693 | 66.755 | 75.74% | 6.1839 | 0 | 0 | 0 | 312.6774 | 0 | 0 | 19.52% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
3 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 | 165.8 | 157.1 |  | 34.8001 |  | 7976.9 | 66.755 | 76.06% | 5.2367 | 0 | 0 | 0 | 265.8967 | 0 | 0 | 16.6% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
4 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 | 141.9 | 135 |  | 33.0999 |  | 6950.5 | 66.755 | 77.13% | 4.3548 | 0 | 0 | 0 | 224.2097 | 0 | 0 | 13.99% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
5 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 | 145 | 143.9 |  | 31.8 |  | 7459 | 66.755 | 77.65% | 4.6419 | 0 | 0 | 0 | 240.6129 | 0 | 0 | 15.02% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
6 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 | 153 | 163.3 |  | 31.1999 |  | 8419.6 | 66.755 | 77.24% | 5.4433 | 0 | 0 | 0 | 280.6533 | 0 | 0 | 17.52% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
7 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 | 153.5 | 177.1 |  | 27.1001 |  | 9198.8 | 66.755 | 77.81% | 5.7129 | 0 | 0 | 0 | 296.7355 | 0 | 0 | 18.52% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
8 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 | 117.4 | 144.5 |  | 20.9 |  | 7717.8 | 66.755 | 80.01% | 4.8167 | 0 | 0 | 0 | 257.26 | 0 | 0 | 16.06% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
9 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 | 103.2 | 132.4 |  | 15.8915 |  | 7215.2 | 66.755 | 81.64% | 4.271 | 0 | 0 | 0 | 232.7484 | 0 | 0 | 14.53% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
10 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 | 102.5 | 127.5 |  | 14.3999 |  | 6983 | 66.755 | 82.04% | 4.1129 | 0 | 0 | 0 | 225.2581 | 0 | 0 | 14.06% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
11 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 | 134.2 | 162.2 |  | 17.8001 |  | 8614.6 | 66.755 | 79.56% | 5.7929 | 0 | 0 | 0 | 307.6643 | 0 | 0 | 19.2% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
12 | March | 3 | 2025-03-01 | 2025 | FY25 | 31 | 185.4 | 207.2 |  | 23.6002 |  | 10739.7 | 66.755 | 77.65% | 6.6839 | 3 | 20.0516 | 20.0516 | 346.4419 | 1039.3258 | 1039.3258 | 21.62% | 2.093% | 21.62% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
13 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 | 167.2997 | 206.6 |  | 29.1001 |  | 10495.2627 | 66.755 | 76.1% | 6.8867 | 30 | 206.6 | 206.6 | 349.8421 | 10495.2627 | 10495.2627 | 21.84% | 21.84% | 21.84% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
14 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 | 203.1012 | 191.7 |  | 33.4 |  | 9688.8168 | 66.755 | 75.71% | 6.1839 | 31 | 191.7 | 398.3 | 312.5425 | 9688.8168 | 20184.0795 | 19.51% | 19.51% | 20.65% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
15 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 | 165.8 | 157.1 |  | 34.8001 |  | 7971.775 | 66.755 | 76.01% | 5.2367 | 30 | 157.1 | 555.4 | 265.7258 | 7971.775 | 28155.8545 | 16.59% | 16.59% | 19.31% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
16 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 | 141.9 | 135 |  | 33.0999 |  | 6947.4741 | 66.755 | 77.09% | 4.3548 | 6 | 26.129 | 581.529 | 224.1121 | 1344.6724 | 29500.5269 | 13.99% | 2.707% | 18.98% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
17 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 | 145 | 143.9 |  | 31.8 |  | 7455.8025 | 66.755 | 77.62% | 4.6419 | 0 | 0 | 581.529 | 240.5098 | 0 | 29500.5269 | 15.01% | 0% | 18.98% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
18 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 | 153 | 163.3 |  | 31.1999 |  | 8414.1736 | 66.755 | 77.19% | 5.4433 | 0 | 0 | 581.529 | 280.4725 | 0 | 29500.5269 | 17.51% | 0% | 18.98% |  | 66.755 |  |  |  | 99.5% | 99.5%
19 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 | 153.5 | 177.1 |  | 27.1001 |  | 9194.8209 | 66.755 | 77.78% | 5.7129 | 0 | 0 | 581.529 | 296.6071 | 0 | 29500.5269 | 18.51% | 0% | 18.98% |  | 66.755 |  |  |  | 99.5% | 99.5%
20 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 | 117.4 | 144.5 |  | 20.9 |  | 7712.8332 | 66.755 | 79.96% | 4.8167 | 0 | 0 | 581.529 | 257.0944 | 0 | 29500.5269 | 16.05% | 0% | 18.98% |  | 66.755 |  |  |  | 99.5% | 99.5%
21 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 | 103.2 | 132.4 |  | 15.8915 |  | 7212.1488 | 66.755 | 81.6% | 4.271 | 0 | 0 | 581.529 | 232.65 | 0 | 29500.5269 | 14.52% | 0% | 18.98% |  | 66.755 |  |  |  | 99.5% | 99.5%
22 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 | 102.5 | 127.5 |  | 14.3999 |  | 6979.9612 | 66.755 | 82.01% | 4.1129 | 0 | 0 | 581.529 | 225.16 | 0 | 29500.5269 | 14.05% | 0% | 18.98% |  | 66.755 |  |  |  | 99.5% | 99.5%
23 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 | 134.2 | 162.2 |  | 17.8001 |  | 8661.6493 | 66.755 | 80% | 5.7929 | 0 | 0 | 581.529 | 309.3446 | 0 | 29500.5269 | 19.31% | 0% | 18.98% |  | 66.755 |  |  |  | 99.5% | 99.5%
24 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 | 185.4 | 207.2 |  | 23.6002 |  | 10735.0943 | 66.755 | 77.61% | 6.6839 | 0 | 0 | 581.529 | 346.2934 | 0 | 29500.5269 | 21.61% | 0% | 18.98% |  | 66.755 |  |  |  | 99.5% | 99.5%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## PA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  |  | 12 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Sr. No. | Date | Financial Year | Calendar Year | 9 | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Inverter Station Number (if Bd in filed) | LT Number (If breakdwon in Below LT Panel) | ACCB Number (If BD below ACCB) | Inverter number (If Inv or Str BD) | String Type(If String BD, No other filed to be inserted) | Equipment (If any BD above LT panel) | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Fault Category | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgement Time | Work Start time on Fault | Work Completion time on fault | Acknow. time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(kWh/m2) | Approximate Energy Loss (KWh) | PTW No. | Job Card No.
1 | 2025-04-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 4249.75 | 6.367% |  |  | I/C trip in overcurrent | 0.48681 | 0.48681 | 0.48889 | 0.48889 | 0 | 0.05 | 0.05 | 0.05 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.0031833 | 0.015 | 48.5103
2 | 2025-04-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 300.375 | 0.45% | Inverter |  | I/C trip in overcurrent | 0.74514 | 0.74514 | 0.75347 | 0.75347 | 0 | 0.2 | 0.2 | 0.2 | Inverter trip in ground fault | closed | 0.0009 | 0.01 | 2.2858
3 | 2025-04-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 300.375 | 0.45% | Inverter |  | Ground Fault | 0.24375 | 0.24375 | 0.75278 | 0.75278 | 0 | 12.2167 | 12.2167 | 12.2167 | Inverter trip in ground fault | closed | 0.054975 | 3.05 | 697.1766
4 | 2025-04-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 300.375 | 0.45% | Inverter |  | Ground Fault | 0.24514 | 0.24514 | 0.42431 | 0.53194 | 0 | 4.3 | 6.8833 | 6.8833 | The inverter tripped due to a ground fault. After performing IR testing, we found a cable fault. Once the cable was repaired, the inverter was successfully charged | closed | 0.030975 | 2.2 | 502.8815
5 | 2025-04-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK5 |  |  | INV2 |  |  | BLK5INV2 | 267 | 0.4% | Inverter |  | Precautionry shutdown | 0.42431 | 0.42431 | 0.42431 | 0.53194 | 0 | 0 | 2.5833 | 2.5833 | The inverter tripped due to a ground fault. After performing IR testing, we found a cable fault. Once the cable was repaired, the inverter was successfully charged | closed | 0.010333 | 4.1 | 833.0562
6 | 2025-04-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 267 | 6.367% | LT Panel |  | ACB Triped in overcurrent | 0.47708 | 0.47708 | 0.48264 | 0.49306 | 0 | 0.13333 | 0.38333 | 0.38333 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.024406 | 0.328 | 66.6445
7 | 2025-04-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 240 | 6.367% | LT Panel |  | ACB Triped in overcurrent | 0.49306 | 0.49306 | 0.49653 | 0.51389 | 0 | 0.083333 | 0.5 | 0.5 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.031833 | 0.348 | 63.5579
8 | 2025-04-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV23 |  |  | BLK2INV23 | 300.375 | 0.45% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.49653 | 0.49306 | 0.58333 | 0.58333 | -0.083333 | 2.0833 | 2.0833 | 2.0833 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0.009375 | 1.8 | 411.4485
9 | 2025-04-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV12 |  |  | BLK2INV12 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.49653 | 0.49306 | 0.58333 | 0.58333 | -0.083333 | 2.0833 | 2.0833 | 2.0833 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0.0083333 | 1.8 | 365.732
10 | 2025-04-10 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 267 | 6.367% |  |  |  | 0.48611 | 0.48611 | 0.48958 | 0.5 | 0 | 0.083333 | 0.33333 | 0.33333 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.021222 | 0.23 | 46.7324
11 | 2025-04-10 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK8 | LT2 |  |  |  |  | BLK8LT2 | 240 | 4.635% | LT Panel |  |  | 0.50347 | 0.50347 | 0.50694 | 0.52083 | 0 | 0.083333 | 0.41667 | 0.41667 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.019313 | 0.24 | 43.833
12 | 2025-04-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 267 | 6.367% | LT Panel |  | I/C trip in overcurrent | 0.53125 | 0.53125 | 0.53472 | 0.55556 | 0 | 0.083333 | 0.58333 | 0.58333 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.037139 | 2.13 | 432.7829
13 | 2025-04-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 240 | 6.367% | LT Panel |  | I/C trip in overcurrent | 0.48889 | 0.48889 | 0.49236 | 0.51389 | 0 | 0.083333 | 0.6 | 0.6 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.0382 | 2.11 | 385.3656
14 | 2025-04-13 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 507 | 6.367% | LT Panel |  | I/C trip in overcurrent | 0.45694 | 0.45694 | 0.46528 | 0.47222 | 0 | 0.2 | 0.36667 | 0.36667 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0.023344 | 1.32 | 509.2852
15 | 2025-04-14 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 507 | 6.367% | LT Panel |  | I/C trip in overcurrent | 0.47917 | 0.47917 | 0.47917 | 0.58333 | 0 | 0 | 2.5 | 2.5 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0 | 2.3 | 887.3909
16 | 2025-04-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 507 | 6.367% | LT Panel |  | I/C trip in overcurrent | 0.45069 | 0.45069 | 0.45764 | 0.45833 | 5 | 0.16667 | 0.18333 | 0.18333 | LT Trip due to over current , after reset LT and charge succesfully | closed | 0 | 0.1 | 38.5822
17 | 2025-04-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.46528 | 0.46181 | 0.58333 | 0.58333 | -0.083333 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.83 | 575.012
18 | 2025-04-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.46528 | 0.46181 | 0.58333 | 0.58333 | -0.083333 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.83 | 516.8647
19 | 2025-04-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.46528 | 0.46181 | 0.58333 | 0.58333 | -0.083333 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.95 | 599.3941
20 | 2025-04-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.46528 | 0.46181 | 0.58333 | 0.58333 | -0.083333 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.95 | 538.7812
[18 empty] | #N/A | [8 empty] | 0 | 0 | 0 | 0 |  | closed |  |  | 0
1724 | 2025-04-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.45486 | 0.45139 | 0.57986 | 0.57986 | -0.083333 | 3 | 3 | 3 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.82 | 572.9801
1725 | 2025-04-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.45486 | 0.45139 | 0.57986 | 0.57986 | -0.083333 | 3 | 3 | 3 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.82 | 515.0383
1726 | 2025-04-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.44653 | 0.44653 | 0.58333 | 0.58333 | 0 | 3.2833 | 3.2833 | 3.2833 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.89 | 587.203
1727 | 2025-04-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.44653 | 0.44653 | 0.58333 | 0.58333 | 0 | 3.2833 | 3.2833 | 3.2833 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | closed | 0 | 2.89 | 527.823
1728 | 2025-04-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.46528 | 0.46528 | 0.59028 | 0.59028 | 0 | 3 | 3 | 3 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted…..12 Times LT2 Trip Some ratio changes on Breaker | closed | 0 | 2.83 | 575.012
1729 | 2025-04-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.46528 | 0.46528 | 0.59028 | 0.59028 | 0 | 3 | 3 | 3 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted…..12 Times LT2 Trip Some ratio changes on Breaker | closed | 0 | 2.83 | 516.8647
1730 | 2025-04-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV30 |  |  | BLK2INV30 | 240 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.47222 | 0.47222 | 0.59028 | 0.59028 | 0 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted…..12 Times LT2 Trip Some ratio changes on Breaker | closed | 0 | 2.72 | 496.7746
1731 | 2025-04-25 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.45833 | 0.45833 | 0.55556 | 0.55556 | 0 | 2.3333 | 2.3333 | 2.3333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted….. | closed | 0 | 2.31 | 421.8931
1732 | 2025-04-25 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 0.45833 | 0.45833 | 0.55556 | 0.55556 | 0 | 2.3333 | 2.3333 | 2.3333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted….. | closed | 0 | 2.31 | 469.3561
1733 | 2025-04-25 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | All_Inv |  |  | BLK2All_Inv | 4605 |  | Inverter |  | All inverter Tripped LT2 | 0.5125 | 0.5125 | 0.52222 | 0.52222 | 0 | 0.23333 | 0.23333 | 0.23333 | All inverter Tripped LT2 | closed | 0 | 0.25 | 876.0902
1734 | 2025-04-27 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK1 |  |  | All_Inv |  |  | BLK1All_Inv | 4381 |  | IDT |  | IDT tripped due to overcurrent | 0.47917 | 0.47917 | 0.4875 | 0.4875 | 0 | 0.2 | 0.2 | 0.2 | IDT tripped due to overcurrent | closed | 0 | 2.12 | 7067.866
1735 | 2025-04-27 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | All_Inv |  |  | BLK2All_Inv | 4520 |  | IDT |  | IDT tripped due to overcurrent | 0.47917 | 0.47917 | 0.4875 | 0.4875 | 0 | 0.2 | 0.2 | 0.2 | IDT tripped due to overcurrent | closed | 0 | 2.12 | 7292.1147
1735 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK8 |  |  | INV5 |  |  | BLK8INV5 | 22.25 | 0.45% | Connectors |  | Found inv string open, connected & rectified | 0.375 | 0.375 | 0.375 | 0.39583 | 0 | 0 | 0.5 | 0.5 | Found inv string open, connected & rectified | closed | 0 | 0.555 | 9.3973
1736 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK8 |  |  | INV10 |  |  | BLK8INV10 | 9.9 | 0.45% | Connectors |  | Found inv string open, connected & rectified | 0.375 | 0.375 | 0.39931 | 0.41319 | 0 | 0.58333 | 0.91667 | 0.91667 | Found inv string open, connected & rectified | closed | 0 | 0.64 | 4.8216
1738 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK8 |  |  | INV11 |  |  | BLK8INV11 | 9.9 | 0.45% | Connectors |  | Found inv string open, connected & rectified | 0.375 | 0.375 | 0.42361 | 0.43403 | 0 | 1.1667 | 1.4167 | 1.4167 | Found inv string open, connected & rectified | closed | 0 | 0.724 | 5.4545
1739 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK8 |  |  | INV12 |  |  | BLK8INV12 | 9.9 | 0.3856% | Connectors |  | Found inv string open, connected & rectified | 0.375 | 0.375 | 0.4375 | 0.44444 | 0 | 1.5 | 1.6667 | 1.6667 | Found inv string open, connected & rectified | closed | 0 | 0.752 | 5.6654
1740 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK8 |  |  | INV13 |  |  | BLK8INV13 | 9.9 | 0.4153% | Connectors |  | Found inv string open, connected & rectified | 0.375 | 0.375 | 0.44792 | 0.45833 | 0 | 1.75 | 2 | 2 | Found inv string open, connected & rectified | closed | 0 | 0.776 | 5.8462
1741 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK3 |  |  | INV6 |  |  | BLK3INV6 | 11.13 | 0.4% | Connectors |  | Found inv string open, connected & rectified | 0.375 | 0.375 | 0.46528 | 0.47222 | 0 | 2.1667 | 2.3333 | 2.3333 | Found inv string open, connected & rectified | closed | 0 | 0.798 | 6.7589
1742 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK3 |  |  | INV20 |  |  | BLK3INV20 | 11.13 | 0.4% | Connectors |  | Found inv string open, connected & rectified | 0.375 | 0.375 | 0.47569 | 0.48264 | 0 | 2.4167 | 2.5833 | 2.5833 | Found inv string open, connected & rectified | closed | 0 | 0.814 | 6.8944
1743 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK1 |  |  | INV17 |  |  | BLK1INV17 | 11.13 | 0.4% | Connectors |  | Found inv string open, connected & rectified | 0.375 | 0.375 | 0.49306 | 0.5 | 0 | 2.8333 | 3 | 3 | Found inv string open, connected & rectified | closed | 0 | 0.839 | 7.1062
1744 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK1 |  |  | INV18 |  |  | BLK1INV18 | 11.13 | 0.4% | String Fuses |  | Replaced the fuse and rectified | 0.375 | 0.375 | 0.50347 | 0.51042 | 0 | 3.0833 | 3.25 | 3.25 | Replaced the fuse and rectified | closed | 0 | 6.3 | 53.3599
1745 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK3 |  |  | INV32 |  |  | BLK3INV32 | 31.9 |  | Cables |  | During Grass cutting cable cut | 0.375 | 0.375 | 0.50347 | 0.5 | 0 | 3.0833 | 3 | 3 | Replaced the fuse and rectified | closed | 0 | 6.3 | 152.9362
1746 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 66.75 | 0.3955% | Cables |  | During Grass cutting cable cut | 0.375 | 0.375 | 0.4375 | 0.4375 | 0 | 1.5 | 1.5 | 1.5 | DC cable damage caused by tractor movement. The cable was replaced with a new one | closed | 0 | 0.7 | 35.5573
1747 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 22.25 | 0.3955% | Cables |  | During Grass cutting cable cut | 0.375 | 0.375 | 0.47917 | 0.47917 | 0 | 2.5 | 2.5 | 2.5 | DC cable damage caused by tractor movement. The cables were replaced with new ones. | closed | 0 | 2.1 | 35.5573
1748 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK1 |  |  | INV24 |  |  | BLK1INV24 | 22.25 | 0.45% | Cables |  | During Grass cutting cable cut | 0.375 | 0.375 | 0.72917 | 0.72917 | 0 | 8.5 | 8.5 | 8.5 | Cable Damged due to tractor movement | closed | 0 | 6.7 | 113.4446
1749 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV28 |  |  | BLK2INV28 | 22.5 | 0.45% | Cables |  | During Grass cutting cable cut | 0.375 | 0.375 | 0.52083 | 0.52083 | 0 | 3.5 | 3.5 | 3.5 | Due to a short circuit caused by tractor movement. The cable was replaced with a new one. | closed | 0 | 3.1 | 53.0791
1750 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV3 |  |  | BLK2INV3 | 22.5 | 0.1667% | Cables |  | During Grass cutting cable cut | 0.375 | 0.375 | 0.5625 | 0.5625 | 0 | 4.5 | 4.5 | 4.5 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 4.1 | 70.2014
1751 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK6 |  |  | INV7 |  |  | BLK6INV7 | 88 | 0.4449% | Cables |  | During Grass cutting cable cut | 0.375 | 0.375 | 0.41667 | 0.45833 | 0 | 1 | 2 | 2 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 0.8 | 53.5737
1752 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 22 | 0.4449% | Cables |  | During Grass cutting cable cut | 0.375 | 0.375 | 0.46875 | 0.47917 | 0 | 2.25 | 2.5 | 2.5 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 1 | 16.7418
1753 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 22.25 | 0.45% | Cables |  | During Grass cutting cable cut | 0.375 | 0.375 | 0.48264 | 0.49306 | 0 | 2.5833 | 2.8333 | 2.8333 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 1.5 | 25.3981
1754 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK6 |  |  | INV8 |  |  | BLK6INV8 | 22 | 0.4449% | Cables |  | During Grass cutting cable cut | 0.375 | 0.375 | 0.49653 | 0.50694 | 0 | 2.9167 | 3.1667 | 3.1667 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 1.7 | 28.461
1755 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK6 |  |  | INV15 |  |  | BLK6INV15 | 22 | 0.412% | Cables |  | During Grass cutting cable cut | 0.375 | 0.375 | 0.51042 | 0.52083 | 0 | 3.25 | 3.5 | 3.5 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 2 | 33.4836
1756 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV24 |  |  | BLK2INV24 | 44.5 | 0.4333% | Cables |  | During Grass cutting cable cut | 0.375 | 0.375 | 0.67014 | 0.68403 | 0 | 7.0833 | 7.4167 | 7.4167 | Cable Damge due to grass cutting activitysame replaced | closed | 0 | 4.6 | 155.7747
1757 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 0.29167 | 0.79167 | 12 | BLK3 |  |  | INV12 |  |  | BLK3INV12 | 300.38 | 0.45% | Inverter |  | inv tripped on system fault | 0.30139 | 0.30417 | 0.45833 | 0.53125 | 0.066667 | 3.7667 | 5.5167 | 5.5167 | Inv Fault System Shudown | closed | 0 | 0.3 | 68.5759
1758 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 0.29167 | 0.79167 | 12 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.2 | 0.45% | Cables |  | cable short | 0.30417 | 0.375 | 0.5 | 0.51042 | 1.7 | 4.7 | 4.95 | 4.95 | Cable Damge due to grass cutting activity same replaced | closed | 0 | 0.293 | 4.9499
1759 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 0.29167 | 0.79167 | 12 | BLK8 |  |  | INV7 |  |  | BLK8INV7 | 22.2 | 0.4333% | Cables |  | cable short | 0.30417 | 0.375 | 0.5125 | 0.51944 | 1.7 | 5 | 5.1667 | 5.1667 | Cable Damge due to grass cutting activity same replaced | closed | 0 | 0.317 | 5.3554
1760 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 0.29167 | 0.79167 | 12 | BLK8 |  |  | INV8 |  |  | BLK8INV8 | 22.2 | 0.4% | Cables |  | mc4 open | 0.30417 | 0.375 | 0.52431 | 0.53472 | 1.7 | 5.2833 | 5.5333 | 5.5333 | MC4 Open FOUND rectified | closed | 0 | 0.326 | 5.5074
1761 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 0.29167 | 0.79167 | 12 | BLK8 |  |  | INV10 |  |  | BLK8INV10 | 22.2 | 0.45% | Cables |  | cable short | 0.30417 | 0.375 | 0.54167 | 0.54861 | 1.7 | 5.7 | 5.8667 | 5.8667 | Cable Damge due to grass cutting activity same replaced | closed | 0 | 0.326 | 5.5074
1762 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 0.29167 | 0.79167 | 12 | BLK8 |  |  | INV11 |  |  | BLK8INV11 | 22.2 | 0.45% | Cables |  | cable cut | 0.30417 | 0.375 | 0.55208 | 0.55903 | 1.7 | 5.95 | 6.1167 | 6.1167 | Cable Damge due to grass cutting activity same replaced | closed | 0 | 0.325 | 5.4905
1763 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV21 |  |  | BLK2INV21 | 22.2 | 0.4% | Connectors |  | Open Found and rectified | 0.30556 | 0.375 | 0.46875 | 0.46875 | 1.6667 | 3.9167 | 3.9167 | 3.9167 | MC4 Found open condition | closed | 0 | 2.3 | 38.8562
1764 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 0.29167 | 0.79167 | 12 | BLK1 |  |  | INV15 |  |  | BLK1INV15 | 22.2 | 0.4% | Connectors |  | Open Found and rectified | 0.30556 | 0.375 | 0.48958 | 0.48958 | 1.6667 | 4.4167 | 4.4167 | 4.4167 | MC4 Found open condition | closed | 0 | 3.5 | 59.129
1765 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV17 |  |  | BLK2INV17 | 22.2 | 0.4% | Connectors |  | Opend Found MC4 Rectified | 0.30556 | 0.375 | 0.54861 | 0.54861 | 1.6667 | 5.8333 | 5.8333 | 5.8333 | MC4 Found opend condition | closed | 0 | 3.1 | 52.3714
1766 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 0.29167 | 0.79167 | 12 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 44.5 | 0.4167% | Connectors |  | two string found Opend Found MC4 Rectified | 0.30556 | 0.375 | 0.64583 | 0.64583 | 1.6667 | 8.1667 | 8.1667 | 8.1667 | 2 MC4 Found OPEN Condition | closed | 0 | 4.1 | 138.8427
1767 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 0.29167 | 0.79167 | 12 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 22.2 | 0.4167% | Connectors |  | Opend Found MC4 Rectified | 0.30556 | 0.375 | 0.68403 | 0.68403 | 1.6667 | 9.0833 | 9.0833 | 9.0833 | MC4 Found opend condition | closed | 0 | 4.9 | 82.7805
1768 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 0.29167 | 0.79167 | 12 | BLK8 |  |  | INV6 |  |  | BLK8INV6 | 22.2 | 0.4333% | Connectors |  | Opend Found MC4 Rectified | 0.30556 | 0.375 | 0.74028 | 0.74028 | 1.6667 | 10.4333 | 10.4333 | 10.4333 | MC4 Found opend condition | closed | 0 | 5.3 | 89.5381
1769 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.22847 | 0.26389 | 12 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 4008 | 5.914% | LT Panel |  | Tripped due to overcurrent fault | 0.53472 | 0.53611 | 0.54167 | 0.54167 | 0.033333 | 0.16667 | 0.16667 | 0.16667 | Reset & Started | closed | 0 | 0.122 | 370.2136
1770 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.22847 | 0.26389 | 12 | BLK8 |  |  | INV27 |  |  | BLK8INV27 | 22.2 | 0.4366% | Connectors |  | Found MC4 connector faulty condition | 0.21944 | 0.375 | 0.39583 | 0.40278 | 3.7333 | 4.2333 | 4.4 | 4.4 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.9 | 15.1273
1771 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.22847 | 0.26389 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 0.21944 | 0.375 | 0.40972 | 0.41667 | 3.7333 | 4.5667 | 4.7333 | 4.7333 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.08 | 1.3446
1772 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.22847 | 0.26389 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 0.21944 | 0.375 | 0.42361 | 0.42708 | 3.7333 | 4.9 | 4.9833 | 4.9833 | MC4 tightned | closed | 0 | 0.107 | 1.7985
1773 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.22847 | 0.26389 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 0.21944 | 0.375 | 0.43056 | 0.43403 | 3.7333 | 5.0667 | 5.15 | 5.15 | MC4 tightned | closed | 0 | 0.12 | 2.017
1774 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.22847 | 0.26389 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 0.21944 | 0.375 | 0.4375 | 0.44444 | 3.7333 | 5.2333 | 5.4 | 5.4 | MC4 tightned | closed | 0 | 0.11 | 1.8489
1775 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.22847 | 0.26389 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 0.21944 | 0.375 | 0.45139 | 0.45833 | 3.7333 | 5.5667 | 5.7333 | 5.7333 | MC4 tightned | closed | 0 | 0.12 | 2.017
1776 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.22847 | 0.26389 | 12 | BLK8 |  |  | INV17 |  |  | BLK8INV17 | 22.2 | 0.2667% | Connectors |  | Found MC4 connector faulty condition | 0.21944 | 0.375 | 0.46528 | 0.47222 | 3.7333 | 5.9 | 6.0667 | 6.0667 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.11 | 1.8489
1777 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.22847 | 0.26389 | 12 | BLK8 |  |  | INV3 |  |  | BLK8INV3 | 22.2 | 0.2818% | Connectors |  | Found MC4 connector faulty condition | 0.21944 | 0.375 | 0.48611 | 0.49306 | 3.7333 | 6.4 | 6.5667 | 6.5667 | MC4 tightned | closed | 0 | 0.9 | 15.1273
1778 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.22847 | 0.26389 | 12 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22.2 | 0.4301% | Connectors |  | Found MC4 connector faulty condition | 0.21944 | 0.375 | 0.5 | 0.50694 | 3.7333 | 6.7333 | 6.9 | 6.9 | 3 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.14 | 2.3531
1779 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.22847 | 0.26389 | 12 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22.2 | 0.4301% | Connectors |  | Found MC4 connector faulty condition | 0.21944 | 0.375 | 0.51389 | 0.52083 | 3.7333 | 7.0667 | 7.2333 | 7.2333 | 2 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.13 | 2.185
1780 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.22847 | 0.26389 | 12 | BLK8 |  |  | INV4 |  |  | BLK8INV4 | 22.2 | 0.4167% | Connectors |  | Found MC4 connector faulty condition | 0.21944 | 0.375 | 0.52431 | 0.52778 | 3.7333 | 7.3167 | 7.4 | 7.4 | MC4 tightned | closed | 0 | 0.13 | 2.185
1781 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK3 |  |  | INV6 |  |  | BLK3INV6 | 267 | 0.4% | Inverter |  | inv tripped on system fault | 0.59722 | 0.59722 | 0.66667 | 0.6875 | 0 | 1.6667 | 2.1667 | 2.1667 | Inv Fault System Shudown | closed | 0 | 0.131 | 26.4818
1782 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK4 |  |  | INV17 |  |  | BLK4INV17 | 289.25 | 0.4333% | Inverter |  | inv tripped on system fault | 0.59722 | 0.59722 | 0.65278 | 0.67361 | 0 | 1.3333 | 1.8333 | 1.8333 | Inv Fault System Shudown | closed | 0 | 0.8228 | 180.1907
1783 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK7 |  |  | INV12 |  |  | BLK7INV12 | 190.35 | 0.4054% | Inverter |  | inv tripped on system fault | 0.59722 | 0.59722 | 0.65972 | 0.68056 | 0 | 1.5 | 2 | 2 | One nos of MC4 connector replaced with new one | closed | 0 | 0.11194 | 16.1325
1784 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK6 |  |  | INV20 |  |  | BLK6INV20 | 264 | 0.3955% | Inverter |  | inv tripped on system fault | 0.59722 | 0.59722 | 0.64583 | 0.67361 | 0 | 1.1667 | 1.8333 | 1.8333 | One nos of MC4 connector replaced with new one | closed | 0 | 0.8227 | 164.4411
1785 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK5 |  |  | INV27 |  |  | BLK5INV27 | 300.38 | 0.4% | Inverter |  | inv tripped on system fault | 0.59722 | 0.59722 | 0.64236 | 0.67222 | 0 | 1.0833 | 1.8 | 1.8 | Inv Fault System Shudown | closed | 0 | 0.7578 | 172.3417
1786 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK5 |  |  | INV13 |  |  | BLK5INV13 | 22.25 | 0.4285% | Connectors |  | Found MC4 connector faulty condition | 0.375 | 0.375 | 0.39583 | 0.40278 | 0 | 0.5 | 0.66667 | 0.66667 | MC4 tightned | closed | 0 | 0.623 | 10.495
1787 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK5 |  |  | INV17 |  |  | BLK5INV17 | 22.25 | 0.4333% | Connectors |  | Found MC4 connector faulty condition | 0.375 | 0.375 | 0.40972 | 0.41667 | 0 | 0.83333 | 1 | 1 | MC4 tightned | closed | 0 | 0.651 | 10.9667
1788 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK5 |  |  | INV12 |  |  | BLK5INV12 | 22.25 | 0.4285% | Connectors |  | Found MC4 connector faulty condition | 0.375 | 0.375 | 0.42361 | 0.43056 | 0 | 1.1667 | 1.3333 | 1.3333 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.666 | 11.2194
1789 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK3 |  |  | INV6 |  |  | BLK3INV6 | 22.25 | 0.4% | Connectors |  | Found MC4 connector faulty condition | 0.375 | 0.375 | 0.4375 | 0.44444 | 0 | 1.5 | 1.6667 | 1.6667 | MC4 tightned | closed | 0 | 0.663 | 11.1688
1790 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK7 |  |  | INV28 |  |  | BLK7INV28 | 22.25 | 0.4% | Connectors |  | Found MC4 connector faulty condition | 0.375 | 0.375 | 0.45139 | 0.45833 | 0 | 1.8333 | 2 | 2 | 2 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.695 | 11.7079
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK2 |  |  | MVP |  |  | BLK2MVP | 4349.2 | 12.5% | IDT |  | IDT tripped on over current fault | 0.44722 | 0.44722 | 0.45417 | 0.45417 | 0 | 0.16667 | 0.16667 | 0.16667 | Normally check the all parameters & charge the idt | closed | 0 | 0.146 | 480.7586
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK2 |  |  | MVP |  |  | BLK2MVP | 4489 | 12.5% | IDT |  | IDT tripped on over current fault | 0.44722 | 0.44722 | 0.45417 | 0.45417 | 0 | 0.16667 | 0.16667 | 0.16667 | Normally check the all parameters & charge the idt | closed | 0 | 0.146 | 496.212
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV4 |  |  | BLK6INV4 | 22 | 0.4449% | Connectors |  | Found MC4 connector faulty condition | 0.375 | 0.375 | 0.40625 | 0.41319 | 0 | 0.75 | 0.91667 | 0.91667 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.0512 | 0.85282
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV14 |  |  | BLK6INV14 | 22 | 0.412% | Connectors |  | Found MC4 connectors open condition | 0.375 | 0.375 | 0.41667 | 0.42361 | 0 | 1 | 1.1667 | 1.1667 | MC4 tightned | closed | 0 | 0.69 | 11.4931
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV18 |  |  | BLK6INV18 | 22 | 0.4449% | Connectors |  | Found MC4 connector faulty condition | 0.375 | 0.375 | 0.42708 | 0.43403 | 0 | 1.25 | 1.4167 | 1.4167 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.82 | 13.6584
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV20 |  |  | BLK6INV20 | 22 | 0.3955% | Connectors |  | Found Y connector shorted | 0.375 | 0.375 | 0.44097 | 0.44792 | 0 | 1.5833 | 1.75 | 1.75 | 1Nos y connector used | closed | 0 | 0.1 | 1.6657
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV23 |  |  | BLK6INV23 | 22 | 0.3955% | Connectors |  | Found Y connector shorted & MC4 1Pair | 0.375 | 0.375 | 0.45139 | 0.45833 | 0 | 1.8333 | 2 | 2 | 1 pair of mc4 connectors & 1NOs of Y connector | closed | 0 | 1.22 | 20.3211
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV26 |  |  | BLK6INV26 | 22 | 0.4449% | Connectors |  | Found MC4 connectors open condition | 0.375 | 0.375 | 0.46528 | 0.47222 | 0 | 2.1667 | 2.3333 | 2.3333 | mc4 tightned | closed | 0 | 1.43 | 23.819
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV27 |  |  | BLK6INV27 | 22 | 0.412% | Connectors |  | Found Y connector shorted | 0.375 | 0.375 | 0.47569 | 0.48264 | 0 | 2.4167 | 2.5833 | 2.5833 | 1Nos y connector used | closed | 0 | 1.65 | 27.4835
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK7 |  |  | INV4 |  |  | BLK7INV4 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 0.375 | 0.375 | 0.49306 | 0.5 | 0 | 2.8333 | 3 | 3 | mc4 tightned | closed | 0 | 2.069 | 34.4626
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 257.4 | 0.2852% | Inverter |  | Inv tripped on excessive leakage current fault | 0.60417 | 0.60417 | 0.61111 | 0.64306 | 0 | 0.16667 | 0.93333 | 0.93333 | 1Nos of y connector used & reset the fault after got the password | closed | 0 | 0.571 | 111.278
1791 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 22.25 | 0.4% | Connectors |  | MC4 found open condition | 0.375 | 0.375 | 0.50694 | 0.51389 | 0 | 3.1667 | 3.3333 | 3.3333 | mc4 tightned | closed | 0 | 2.388 | 40.2281
1792 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK7 |  |  | INV15 |  |  | BLK7INV15 | 247.5 | 0.4% | Inverter |  | Inverter tripped due to ground fault | 0.375 | 0.375 | 0.39583 | 0.40417 | 0 | 0.5 | 0.7 | 0.7 | Checked all string one by one and found one string was grounded and after rectified the same charge the Inverter | closed | 0 | 0.622 | 116.5549
1793 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV10 |  |  | BLK7INV10 | 22 | 0.3856% | Connectors |  | MC4 found open condition | 0.375 | 0.375 | 0.39583 | 0.40556 | 0 | 0.5 | 0.73333 | 0.73333 | mc4 tightned | closed | 0 | 0.1688 | 2.8116
1794 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV25 |  |  | BLK7INV25 | 22 | 0.45% | Connectors |  | Found MC4 connector faulty condition | 0.375 | 0.375 | 0.39583 | 0.41736 | 0 | 0.5 | 1.0167 | 1.0167 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0 | 0.2 | 3.3313
1795 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV17 |  |  | BLK7INV17 | 22 | 0.4% | Connectors |  | Found Y connector shorted |  |  |  | 0.42917 | 0 | 0 | 10.3 | 10.3 | 1Nos y connector used and 1 nos of 15A fuse replaced with new one | closed | 0 | 0.1987 | 3.3097
1796 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22 | 0.3955% | Connectors |  | MC4 found open condition |  |  |  | 0.43958 | 0 | 0 | 10.55 | 10.55 | mc4 tightned | closed | 0 | 0.21 | 3.4979
1797 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV5 |  |  | BLK7INV5 | 22 | 0.3955% | Connectors |  | MC4 found open condition |  |  |  | 0.46528 | 0 | 0 | 11.1667 | 11.1667 | mc4 tightned | closed | 0 | 0.191 | 3.1814
1798 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV16 |  |  | BLK7INV16 | 22 | 0.4% | Connectors |  | MC4 found open condition |  |  |  | 0.47361 | 0 | 0 | 11.3667 | 11.3667 | mc4 tightned | closed | 0 | 0.214 | 3.5645
1799 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK3 |  |  | INV6 |  |  | BLK3INV6 | 22 | 0.4% | Connectors |  | Found Y connector shorted |  |  |  | 0.48472 | 0 | 0 | 11.6333 | 11.6333 | 1Nos y connector used and 1 nos of 15A fuse replaced with new one | closed | 0 | 0.22 | 3.6645
1800 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22 | 0.45% | Connectors |  | Found Y connector shorted |  |  |  | 0.50972 | 0 | 0 | 12.2333 | 12.2333 | 1Nos y connector used and 1 nos of 15A fuse replaced with new one | closed | 0 | 0.218 | 3.6311
1801 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | POWER TRAFO |  |  | 132KV_OC |  |  | POWER TRAFO132KV_OC | 67300 |  | Power Trafo |  | Tripped on REF HV Earth Fault | 0.55069 | 0.55069 | 0.5625 | 0.77083 | 0 | 0.28333 | 5.2833 | 5.2833 | Checked all Parameter & Testing than charged the Power trafo | closed | 0 | 1.46 | 74393.1161
1802 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25903 | 0.77778 | 12.45 | BLK2 |  |  | MVP |  |  | BLK2MVP | 7500 | 12.5% | IDT |  | Tripped on Over current | 0.46528 | 0.46528 | 0.46875 | 0.47222 | 0 | 0.083333 | 0.16667 | 0.16667 | Checked all parameter & charged the IDT | closed | 0 | 0.193 | 1095.9315
1803 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25903 | 0.77778 | 12.45 | BLK1 |  |  | MVP |  |  | BLK1MVP | 7500 | 13.4% | IDT |  | Tripped on Over current | 0.47361 | 0.47361 | 0.47917 | 0.48194 | 0 | 0.13333 | 0.2 | 0.2 | Checked all parameter & charged the IDT | closed | 0 | 0.182 | 1033.4691
1804 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25903 | 0.77778 | 12.45 |  |  |  | MVP |  |  | MVP | 7500 |  | IDT |  | Tripped on Over current | 0.47361 | 0.47361 | 0.47569 | 0.48611 | 0 | 0.05 | 0.3 | 0.3 | Checked all parameter & charged the IDT | closed | 0 | 0.17 | 965.3282
1805 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25903 | 0.77778 | 12.45 |  |  |  | MVP |  |  | MVP | 7500 |  | IDT |  | Tripped on Over current | 0.47361 | 0.47361 | 0.47778 | 0.49028 | 0 | 0.1 | 0.4 | 0.4 | Checked all parameter & charged the IDT | closed | 0 | 0.173 | 982.3635
1806 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25903 | 0.77778 | 12.45 |  |  |  | MVP |  |  | MVP | 7500 |  | IDT |  | Tripped on Over current | 0.53125 | 0.53125 | 0.53542 | 0.53819 | 0 | 0.1 | 0.16667 | 0.16667 | Checked all parameter & charged the IDT | closed | 0 | 0.16 | 908.5442
1807 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25903 | 0.77778 | 12.45 |  |  |  | MVP |  |  | MVP | 7500 |  | IDT |  | Tripped on Over current | 0.53681 | 0.53819 | 0.54514 | 0.54722 | 0.033333 | 0.2 | 0.25 | 0.25 | Checked all parameter & charged the IDT | closed | 0 | 0.153 | 868.7954
1808 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25903 | 0.77778 | 12.45 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 247.5 | 0.3333% | Inverter |  | Manually shutdown | 12:45 | 12:45 | 13:45 | 14:00 | 0 | 1 | 1.25 | 1.25 | Manually tripped | closed | 0.0041667 | 1.1 | 206.126
1809 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.26042 | 0.76667 | 12.15 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 22 | 0.4167% | Connectors |  | MC4 found open condition | 0.26042 | 0.5 | 0.50139 | 0.50625 | 5.75 | 5.7833 | 5.9 | 5.9 | mc4 tightned | closed | 0.024583 | 3.33 | 55.4666
1810 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.26042 | 0.76667 | 12.15 | BLK1 |  |  | INV13 |  |  | BLK1INV13 | 22 | 0.4% | Connectors |  | Found MC4 connector faulty condition | 0.26042 | 0.5 | 0.50972 | 0.5125 | 5.75 | 5.9833 | 6.05 | 6.05 | 1 nos of +ve & -ve MC4 connector replaced with new one | closed | 0.0242 | 3.36 | 55.9663
1811 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.26042 | 0.76667 | 12.15 | BLK3 |  |  | INV10 |  |  | BLK3INV10 | 12 | 0.4% | Connectors |  | MC4 found open condition | 0.26042 | 0.50694 | 0.52083 | 0.525 | 5.9167 | 6.25 | 6.35 | 6.35 | mc4 tightned | closed | 0.0254 | 3.4 | 30.8905
1812 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.26042 | 0.76667 | 12.15 | BLK1 | LT2 |  |  |  |  | BLK1LT2 | 4605.75 | 6.9% | LT Panel |  | Tripped on Over current | 0.46319 | 0.46319 | 0.46806 | 0.47083 | 0 | 0.11667 | 0.18333 | 0.18333 | Checked all parameter & charged the breaker | closed | 0.01265 | 0.18 | 627.6791
1813 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.26042 | 0.76667 | 12.15 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 4008.13 | 5.914% | LT Panel |  | Tripped on Over current | 0.47986 | 0.47986 | 0.48472 | 0.4875 | 0 | 0.11667 | 0.18333 | 0.18333 | Checked all parameter & charged the breaker | closed | 0.010842 | 0.196 | 594.7887
1814 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25347 | 0.75694 | 12.0833 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 4008.13 | 5.914% | LT Panel |  | Tripped on Over current | 0.51181 | 0.51181 | 0.51528 | 0.51736 | 0 | 0.083333 | 0.13333 | 0.13333 | Checked all parameter & charged the breaker | closed | 0.0078851 | 0.16 | 485.5418
1815 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25347 | 0.75694 | 12.0833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 0.25347 | 0.25347 | 0.64236 | 0.64583 | 0 | 9.3333 | 9.4167 | 9.4167 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | closed | 0.037243 | 4.17 | 69.4582
1816 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25347 | 0.75694 | 12.0833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 0.25347 | 0.25347 | 0.64931 | 0.65278 | 0 | 9.5 | 9.5833 | 9.5833 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | closed | 0.037903 | 4.2 | 69.9579
1817 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25347 | 0.75694 | 12.0833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 0.25347 | 0.25347 | 0.66111 | 0.66389 | 0 | 9.7833 | 9.85 | 9.85 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | closed | 0.038957 | 4.12 | 68.6254
1818 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25347 | 0.75694 | 12.0833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 0.25347 | 0.25347 | 0.66667 | 0.67361 | 0 | 9.9167 | 10.0833 | 10.0833 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | closed | 0.03988 | 4.66 | 77.62
1819 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25347 | 0.75694 | 12.0833 | BLK6 |  |  | INV8 |  |  | BLK6INV8 | 22 | 0.4449% | Connectors |  | MC4 found open condition | 0.25347 | 0.25347 | 0.67014 | 0.67569 | 0 | 10 | 10.1333 | 10.1333 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | closed | 0 | 4.73 | 78.7859
1820 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25347 | 0.75694 | 12.0833 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22 | 0.4301% | Connectors |  | Theft cable | 0.25347 | 0.25347 | 0.69792 | 0.70139 | 0 | 10.6667 | 10.75 | 10.75 | 290 meter cable used ,2 pair MC4 connecter ,2 15A fuse replaced with new one | closed | 0.046237 | 4.23 | 70.4576
1821 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25347 | 0.75694 | 12.0833 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22 | 0.4301% | Connectors |  | Theft cable | 0.25347 | 0.25347 | 0.70833 | 0.72222 | 0 | 10.9167 | 11.25 | 11.25 | 276 meter cable used ,2 pair MC4 connecter ,2 15A fuse replaced with new one | closed | 0.048388 | 4.77 | 79.4522
1822 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25347 | 0.75694 | 12.0833 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22 | 0.4301% | Connectors |  | Theft cable | 0.25347 | 0.25347 | 0.72778 | 0.73194 | 0 | 11.3833 | 11.4833 | 11.4833 | 260 meter cable used ,2 pair MC4 connecter ,2 15A fuse replaced with new one | closed | 0.049391 | 4.87 | 81.1179
1823 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.24167 | 0.76042 | 12.45 | BLK1 |  |  | INV8 |  |  | BLK1INV8 | 22 | 0.4% | Connectors |  | MC4 found open condition | 0.24167 | 0.24167 | 0.47917 | 0.48611 | 0 | 5.7 | 5.8667 | 5.8667 | mc4 tightned | closed | 0 | 2.12 | 35.3121
1824 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.24167 | 0.76042 | 12.45 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 22 | 0.4% | Connectors |  | MC4 found open condition | 0.24167 | 0.24167 | 0.47986 | 0.49306 | 0 | 5.7167 | 6.0333 | 6.0333 | mc4 tightned | closed | 0.024133 | 2.48 | 41.3085
1825 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.24167 | 0.76042 | 12.45 | BLK2 |  |  | INV28 |  |  | BLK2INV28 | 22 | 0.45% | Connectors |  | MC4 found open condition | 0.24167 | 0.24167 | 0.48611 | 0.49653 | 0 | 5.8667 | 6.1167 | 6.1167 | mc4 tightned | closed | 0.027525 | 2.31 | 38.4768
1826 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.24167 | 0.76042 | 12.45 | BLK7 |  |  | INV4 |  |  | BLK7INV4 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 0.24167 | 0.24167 | 0.5 | 0.51944 | 0 | 6.2 | 6.6667 | 6.6667 | mc4 tightned | closed | 0.026367 | 2.6 | 43.3073
1827 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.24167 | 0.76042 | 12.45 | BLK7 |  |  | INV26 |  |  | BLK7INV26 | 22 | 0.45% | Connectors |  | MC4 found open condition | 0.24167 | 0.24167 | 0.50694 | 0.52778 | 0 | 6.3667 | 6.8667 | 6.8667 | mc4 tightned | closed | 0.0309 | 2.23 | 37.1443
1828 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.24167 | 0.76042 | 12.45 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | Theft cable | 0.24167 | 0.24167 | 0.67014 | 0.68056 | 0 | 10.2833 | 10.5333 | 10.5333 | St-13 120 mtr cables, 2 pair of MC4 connecter replaced with new one | closed | 0.04166 | 2.44 | 40.6422
1829 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.24167 | 0.76042 | 12.45 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | Theft cable | 0.24167 | 0.24167 | 0.67014 | 0.68056 | 0 | 10.2833 | 10.5333 | 10.5333 | St-14 120 mtr cables, 2 pair of MC4 connecter replaced with new one | closed | 0.04166 | 2.78 | 46.3055
1830 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.24167 | 0.76042 | 12.45 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | Theft cable | 0.24167 | 0.24167 | 0.67014 | 0.68056 | 0 | 10.2833 | 10.5333 | 10.5333 | St-15 120 mtr cables, 2 pair of MC4 connecter replaced with new one | closed | 0.04166 | 2.54 | 42.3079
1831 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.24167 | 0.76042 | 12.45 | BLK7 |  |  | INV32 |  |  | BLK7INV32 | 22 | 0.239% | Connectors |  | I nos of string cable fired by short circuited | 0.45972 | 0.45972 | 0.53125 | 0.72222 | 0 | 1.7167 | 6.3 | 6.3 | St-4 ,50 mtr cables, 2 pair of MC4 connecter replaced with new one | closed | 0 | 2.64 | 43.9735
1832 | 2025-05-12 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25903 | 0.77222 | 12.3167 | BLK2 |  |  | INV11 |  |  | BLK2INV11 | 22 | 0.4% | Connectors |  | Mc4 connecter found open | 0.25903 | 0.25903 | 0.375 | 0.39653 | 0 | 2.7833 | 3.3 | 3.3 | mc4 tightned | closed | 0.0132 | 0.694 | 11.5597
1833 | 2025-05-12 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25903 | 0.77222 | 12.3167 | BLK3 |  |  | INV31 |  |  | BLK3INV31 | 22 | 0.4% | Connectors |  | String cable found faulty | 0.25903 | 0.25903 | 0.42431 | 0.43264 | 0 | 3.9667 | 4.1667 | 4.1667 | mc4 tightned | closed | 0.016667 | 1.47 | 24.4853
1834 | 2025-05-12 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25903 | 0.77222 | 12.3167 | BLK6 |  |  | INV8 |  |  | BLK6INV8 | 22 | 0.4449% | Inverter |  | Inverter tripped due to system fault | 0.41597 | 0.41597 | 0.45833 | 0.47083 | 0 | 1.0167 | 1.3167 | 1.3167 | After checking all parameter restart the inverter | closed | 0.0058584 | 1.13 | 18.822
1835 | 2025-05-12 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25903 | 0.77222 | 12.3167 | BLK8 |  |  | INV15 |  |  | BLK8INV15 | 22 | 0.4004% | Connectors |  | S7-17 half string found grounded | 0.25903 | 0.6875 |  |  | 10.2833 | -6.2167 | -6.2167 | -6.2167 | today will closed this fault | closed | -0.024895 |  | 0
1836 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25208 | 0.77083 | 12.45 | BLK4 |  |  | INV1 |  |  | BLK4INV1 | 22 | 0.45% | Connectors |  | MC4 found open condition | 0.25208 | 0.25208 | 0.38542 | 0.38958 | 0 | 3.2 | 3.3 | 3.3 | mc4 tightned | closed | 0.01485 | 0.788 | 13.1254
1837 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25208 | 0.77083 | 12.45 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22 | 0.45% | Connectors |  | Y connecter faulty | 0.25208 | 0.25208 | 0.54861 | 0.55764 | 0 | 7.1167 | 7.3333 | 7.3333 | Y connecter burrnt & 2 nos of Mc4 replaced with new one | closed | 0.033 | 3.62 | 60.2971
1838 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25208 | 0.77083 | 12.45 | BLK5 |  |  | INV19 |  |  | BLK5INV19 | 22 | 0.4333% | Connectors |  | MC4 found open condition | 0.25208 | 0.25208 | 0.55556 | 0.55972 | 0 | 7.2833 | 7.3833 | 7.3833 | mc4 tightned | closed | 0.031994 | 3.71 | 61.7962
1839 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25208 | 0.77083 | 12.45 | BLK5 |  |  | INV17 |  |  | BLK5INV17 | 22 | 0.4333% | Connectors |  | MC4 found open condition | 0.25208 | 0.25208 | 0.55208 | 0.56319 | 0 | 7.2 | 7.4667 | 7.4667 | mc4 tightned | closed | 0.032356 | 3.61 | 60.1305
1840 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25208 | 0.77083 | 12.45 | BLK5 |  |  | INV4 |  |  | BLK5INV4 | 22 | 0.45% | Connectors |  | MC4 found open condition | 0.25208 | 0.25208 | 0.64236 | 0.64722 | 0 | 9.3667 | 9.4833 | 9.4833 | One nos of MC4 connector replaced with new one | closed | 0.042675 | 5.51 | 91.7781
1841 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25208 | 0.77083 | 12.45 | BLK1 |  |  | MVP |  |  | BLK1MVP | 4338 | 13.4% | LT Panel |  | Tripped on Over current | 0.42361 | 0.42361 | 0.42708 | 0.44028 | 0 | 0.083333 | 0.4 | 0.4 | Tripped due to over current | closed | 0.0536 | 0.33 | 1083.8478
1842 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25208 | 0.77083 | 12.45 | BLK8 |  |  | INV15 |  |  | BLK8INV15 | 22 | 0.4004% | Connectors |  | S7-17 half string found grounded |  |  |  |  | 0 | 0 | 0 | 0 | today will closed this fault | closed | 0 | 6.7 | 111.5995
1842 | 2025-05-14 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.25139 | 0.77292 | 12.5167 | BLK1 |  |  | MVP |  |  | BLK1MVP | 4338 | 13.4% | LT Panel |  | Tripped on Over current | 0.47917 | 0.47917 | 0.48264 | 0.48611 | 0 | 0.083333 | 0.16667 | 0.16667 | Tripped due to over current | closed | 0.022333 | 0.38 | 1248.0672
1843 | 2025-05-15 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.23611 | 0.77361 | 12.9 | BLK3 |  |  | INV12 |  |  | BLK3INV12 | 22.25 | 0.45% | Connectors |  | MC4 found open condition | 0.23611 | 0.375 | 0.40278 | 0.41528 | 3.3333 | 4 | 4.3 | 4.3 | mc4 tightned | closed | 0.01935 | 0.342 | 5.7613
1844 | 2025-05-15 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.23611 | 0.77361 | 12.9 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 19.1 | 0.4065% | String |  | Pending for verification | 0.23611 | 0.375 | 0.78611 | 0.78611 | 3.3333 | 13.2 | 13.2 | 13.2 | Pending for verification | closed | 0.05366 | 6.81 | 98.4794
1845 | 2025-05-15 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.23611 | 0.77361 | 12.9 | BLK8 |  |  | INV15 |  |  | BLK8INV15 | 19.1 | 0.4004% | String |  | mc4 Connector Found open | 0.21875 | 0.375 | 0.78611 | 0.78611 | 3.75 | 13.6167 | 13.6167 | 13.6167 | String cable found faulty | closed | 0.054528 | 6.81 | 98.4794
1850 | 2025-05-16 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21875 | 0.76667 | 13.15 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 19.1 | 0.2852% | String |  | mc4 Connector Found open | 0.21875 | 0.51042 | 0.51042 | 0.51042 | 7 | 7 | 7 | 7 | String Found open restored immidiate | closed | 0.019962 | 2.3 | 33.2603
1851 | 16-May-25 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21875 | 0.76667 | 13.15 | BLK7 |  |  | INV12 |  |  | BLK7INV12 | 19.1 | 0.4054% | String |  | mc4 Connector Found open | 0.21875 | 0.54861 | 0.54861 | 0.54861 | 7.9167 | 7.9167 | 7.9167 | 7.9167 | String Found open restored immidiate | closed | 0.032094 | 3.1 | 44.8291
1852 | 2025-05-17 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:27 | 18:25 | 12.9667 | BLK4 |  |  | INV31 |  |  | BLK4INV31 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:27 | 0.45486 | 0.45486 | 0.45486 | 5.4667 | 5.4667 | 5.4667 | 5.4667 | String Found open restored immidiate | closed | 0.021867 | 0.8 | 11.5688
1853 | 2025-05-17 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:27 | 18:25 | 12.9667 | BLK4 |  |  | INV16 |  |  | BLK4INV16 | 19.1 | 0.45% | String |  | mc4 Connector Found open | 5:27 | 0.46736 | 0.46736 | 0.46736 | 5.7667 | 5.7667 | 5.7667 | 5.7667 | String Found open restored immidiate | closed | 0.02595 | 1.2 | 17.3532
1854 | 2025-05-17 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:27 | 18:25 | 12.9667 | BLK8 |  |  | INV7 |  |  | BLK8INV7 | 19.1 | 0.4333% | String |  | mc4 Connector Found open | 5:27 | 0.75556 | 0.75556 | 0.75556 | 12.6833 | 12.6833 | 12.6833 | 12.6833 | String Found open restored immidiate | closed | 0.054961 | 4.2 | 60.7362
| 2025-05-18 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:23 | 13.15 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 19.1 | 0.3955% | String |  | Y Connector found open same replaced after avrifying load | 5:14 | 0.51528 | 0.51528 | 0.51528 | 7.1333 | 7.1333 | 7.1333 | 7.1333 | String Found open restored immidiate | closed | 0.028213 | 5.1 | 73.7511
1856 | 2025-05-18 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:23 | 13.15 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 22.25 | 0.4449% | String |  | String cut by grass cutting machine same is restored after applying 2 nos Positive and Negative MC4 Connectore | 0.69375 | 0.77083 | 0.77083 | 0.77083 | 1.85 | 1.85 | 1.85 | 1.85 | String Found open restored immidiate | closed | 0.0082315 | 0.3 | 5.0538
1857 | 2025-05-18 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:23 | 13.15 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 19.1 | 0.3955% | String |  | Mc4 Connector found open same is restored after varifying the load | 5:14 | 0.42014 | 0.42014 | 0.42014 | 4.85 | 4.85 | 4.85 | 4.85 | String Found open restored immidiate | closed | 0.019182 | 2.3 | 33.2603
1842 | 2025-05-18 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:23 | 13.15 | BLK8 |  |  | All_Inv |  |  | BLK8All_Inv | 4338 |  | LT Panel |  | Tripped on Over current | 0.5375 | 0.5375 | 0.54444 | 0.54444 | 0 | 0.16667 | 0.16667 | 0.16667 | Tripped due to over current | closed |  | 0.31 | 1018.1601
1859 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK1 |  |  | INV15 |  |  | BLK1INV15 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 0.42708 | 0.42708 | 0.42708 | 5.0167 | 5.0167 | 5.0167 | 5.0167 | mc4 Connector Found open | closed | 0.020067 | 2.3 | 33.2603
1860 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK1 |  |  | INV21 |  |  | BLK1INV21 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 0.43125 | 0.43125 | 0.43125 | 5.1167 | 5.1167 | 5.1167 | 5.1167 | mc4 Connector Found open | closed | 0.020467 | 2.32 | 33.5495
1861 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK3 |  |  | INV10 |  |  | BLK3INV10 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 0.43958 | 0.43958 | 0.43958 | 5.3167 | 5.3167 | 5.3167 | 5.3167 | mc4 Connector Found open | closed | 0.021267 | 2.38 | 34.4172
1862 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK4 |  |  | INV9 |  |  | BLK4INV9 | 22.25 | 0.4% | String |  | Y Connectoor Fuse was failure | 5:14 | 0.45 | 0.45 | 0.45 | 5.5667 | 5.5667 | 5.5667 | 5.5667 |  | closed | 0.022267 | 2.38 | 40.0933
1863 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK2 |  |  | INV11 |  |  | BLK2INV11 | 22.25 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 0.45625 | 0.45625 | 0.45625 | 5.7167 | 5.7167 | 5.7167 | 5.7167 | mc4 Connector Found open | closed | 0.022867 | 2.34 | 39.4195
1864 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK2 |  |  | INV13 |  |  | BLK2INV13 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 0.47222 | 0.47222 | 0.47222 | 6.1 | 6.1 | 6.1 | 6.1 | mc4 Connector Found open | closed | 0.0244 | 2.45 | 35.4294
1865 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK2 |  |  | INV10 |  |  | BLK2INV10 | 22.25 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 0.47778 | 0.47778 | 0.47778 | 6.2333 | 6.2333 | 6.2333 | 6.2333 | mc4 Connector Found open | closed | 0.024933 | 2.45 | 41.2725
1866 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK8 |  |  | MVP |  |  | BLK8MVP | 4338 | 10.55% | LT Panel |  | Tripped on Over current | 0.48958 | 0.48958 | 0.49306 | 0.49306 | 0 | 0.083333 | 0.083333 | 0.083333 | Tripped on Over current | closed | 0.0087908 | 0.3 | 985.3162
1867 | 2025-05-20 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK6 |  |  | INV17 |  |  | BLK6INV17 | 22.25 | 0.412% | String |  | Yconnector Fuse burn | 5:14 | 0.46806 | 0.46806 | 0.46806 | 6 | 6 | 6 | 6 | Y Connectoor Fuse was failure | closed | 0.024719 | 2.3 | 38.7456
1868 | 2025-05-20 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK7 |  |  | INV2 |  |  | BLK7INV2 | 22.25 | 0.3955% | String |  | mc4 Connector Found open | 5:14 | 0.52083 | 0.52083 | 0.52083 | 7.2667 | 7.2667 | 7.2667 | 7.2667 | mc4 Connector Found open | closed | 0.02874 | 2.4 | 40.4302
1869 | 2025-05-20 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK8 |  |  | INV9 |  |  | BLK8INV9 | 22.25 | 0.4333% | String |  | Yconnector Fuse burn | 5:14 | 0.71458 | 0.71458 | 0.71458 | 11.9167 | 11.9167 | 11.9167 | 11.9167 | Y Connectoor Fuse was failure | closed | 0.051639 | 3.4 | 57.2761
1870 | 2025-05-20 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.25 | 0.3856% | String |  | 1 module replaced | 5:14 | 0.65278 | 0.65278 | 0.65278 | 10.4333 | 10.4333 | 10.4333 | 10.4333 | Module replaced | closed | 0.040233 | 4 | 67.3837
1871 | 2025-05-21 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:27 | 13.1833 | BLK8 |  |  | INV14 |  |  | BLK8INV14 | 22.25 | 0.3856% | String |  | Yconnector Fuse burn | 5:14 | 0.42361 | 0.42361 | 0.42361 | 4.9333 | 4.9333 | 4.9333 | 4.9333 | Y Connectoor Fuse was failure | closed | 0.019024 | 1 | 16.8459
1872 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK3 |  |  | INV16 |  |  | BLK3INV16 | 22.25 | 0.4% | String |  | module fixing | 0.21944 | 0.33333 | 0.40972 | 0.42222 | 2.7333 | 4.5667 | 4.8667 | 4.8667 | module fixing, tighten & string rectification | closed | 0.019467 | 0.347 | 5.8455
1873 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK3 |  |  | INV13 |  |  | BLK3INV13 | 22.25 | 0.45% | String |  | module fixing | 0.21944 | 0.33333 | 0.42361 | 0.4375 | 2.7333 | 4.9 | 5.2333 | 5.2333 | module fixing, tighten & string rectification | closed | 0.02355 | 0.347 | 5.8455
1874 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK3 |  |  | INV12 |  |  | BLK3INV12 | 22.25 | 0.45% | String |  | module fixing | 0.21944 | 0.33333 | 0.44097 | 0.44792 | 2.7333 | 5.3167 | 5.4833 | 5.4833 | module fixing, tighten & string rectification | closed | 0.024675 | 0.375 | 6.3172
1875 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | String |  | module fixing | 0.21944 | 0.33333 | 0.42361 | 0.44444 | 2.7333 | 4.9 | 5.4 | 5.4 | module fixing, tighten & string rectification | closed | 0.0243 | 0.396 | 6.671
1876 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK5 |  |  | INV15 |  |  | BLK5INV15 | 22.25 | 0.4% | String |  | module fixing | 0.21944 | 0.33333 | 0.66111 | 0.68056 | 2.7333 | 10.6 | 11.0667 | 11.0667 | module fixing, tighten & string rectification | closed | 0.044267 | 0.389 | 6.5531
1877 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK5 |  |  | INV22 |  |  | BLK5INV22 | 22.25 | 0.4% | String |  | module fixing | 0.21944 | 0.33333 | 0.65278 | 0.67361 | 2.7333 | 10.4 | 10.9 | 10.9 | module fixing, tighten & string rectification | closed | 0.0436 | 0.585 | 9.8549
1878 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22.25 | 0.3955% | String |  | module fixing | 0.21944 | 0.33333 | 0.51042 | 0.52083 | 2.7333 | 6.9833 | 7.2333 | 7.2333 | module fixing, tighten & string rectification | closed | 0.028608 | 0.582 | 9.8043
1879 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK7 |  |  | INV12 |  |  | BLK7INV12 | 20.1 | 0.4054% | String |  | module fixing | 0.21944 | 0.33333 | 0.52431 | 0.53472 | 2.7333 | 7.3167 | 7.5667 | 7.5667 | module fixing, tighten & string rectification | closed | 0.030675 | 0.506 | 7.7004
1880 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK7 |  |  | INV13 |  |  | BLK7INV13 | 20.1 | 0.3667% | String |  | module fixing | 0.21944 | 0.33333 | 0.5 | 0.51181 | 2.7333 | 6.7333 | 7.0167 | 7.0167 | module fixing, tighten & string rectification | closed | 0.025728 | 0.535 | 8.1417
1881 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV2 |  |  | BLK8INV2 | 19.1 | 0.2966% | String |  | module fixing | 0.21944 | 0.33333 | 0.45139 | 0.46597 | 2.7333 | 5.5667 | 5.9167 | 5.9167 | module fixing, tighten & string rectification | closed | 0.017551 | 0.43 | 6.2182
1882 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV2 |  |  | BLK8INV2 | 19.1 | 0.2966% | String |  | module fixing | 0.21944 | 0.33333 | 0.45139 | 0.47361 | 2.7333 | 5.5667 | 6.1 | 6.1 | module fixing, tighten & string rectification | closed | 0.018094 | 0.444 | 6.4207
1883 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV2 |  |  | BLK8INV2 | 19.1 | 0.2966% | String |  | module fixing | 0.21944 | 0.33333 | 0.45139 | 0.48264 | 2.7333 | 5.5667 | 6.3167 | 6.3167 | module fixing, tighten & string rectification | closed | 0.018737 | 0.46 | 6.6521
1884 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV17 |  |  | BLK8INV17 | 31.9 | 0.2667% | String |  | module fixing | 0.21944 | 0.33333 | 0.45833 | 0.47361 | 2.7333 | 5.7333 | 6.1 | 6.1 | module fixing, tighten & string rectification | closed | 0.016267 | 0.444 | 10.7235
1885 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 31.9 | 0.4065% | String |  | module fixing | 0.21944 | 0.33333 | 0.46875 | 0.47917 | 2.7333 | 5.9833 | 6.2333 | 6.2333 | module fixing, tighten & string rectification | closed | 0.02534 | 0.454 | 10.9651
1886 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 31.9 | 0.4065% | String |  | module fixing | 0.21944 | 0.33333 | 0.46875 | 0.48611 | 2.7333 | 5.9833 | 6.4 | 6.4 | module fixing, tighten & string rectification | closed | 0.026017 | 0.465 | 11.2307
1887 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 20.1 | 0.3856% | String |  | module fixing | 0.21944 | 0.33333 | 0.47222 | 0.48611 | 2.7333 | 6.0667 | 6.4 | 6.4 | module fixing, tighten & string rectification | closed | 0.02468 | 0.465 | 7.0764
1888 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21736 | 0.77014 | 13.2667 | BLK2 |  |  | INV10 |  |  | BLK2INV10 | 22.25 | 0.4% | String |  | 2 fuse was fused which was replaced with a new one & restored | 0.21736 | 0.33333 | 0.45139 | 0.46181 | 2.7833 | 5.6167 | 5.8667 | 5.8667 | fuse replaced with a new one & connect the same | closed | 0.023467 | 0.405 | 6.8226
1889 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21736 | 0.77014 | 13.2667 | BLK3 |  |  | INV7 |  |  | BLK3INV7 | 22.25 | 0.4% | String |  | mc4 open so rectify & connect the same | 0.21736 | 0.33333 | 0.45833 | 0.47222 | 2.7833 | 5.7833 | 6.1167 | 6.1167 | mc4 Connector Found open | closed | 0.024467 | 0.424 | 7.1427
1890 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21736 | 0.77014 | 13.2667 | BLK1 |  |  | INV28 |  |  | BLK1INV28 | 22.25 | 0.45% | String |  | mc4 open so rectify & connect the same | 0.21736 | 0.33333 | 0.48264 | 0.49306 | 2.7833 | 6.3667 | 6.6167 | 6.6167 | mc4 Connector Found open | closed | 0.029775 | 0.462 | 7.7828
1891 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21736 | 0.77014 | 13.2667 | BLK5 |  |  | INV15 |  |  | BLK5INV15 | 22.25 | 0.4% | String |  | module fixing | 0.21736 | 0.33333 | 0.50694 | 0.54236 | 2.7833 | 6.95 | 7.8 | 7.8 | module fixing, tighten & string rectification | closed | 0.0312 | 0.533 | 8.9789
1892 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21736 | 0.77014 | 13.2667 | BLK6 |  |  | INV12 |  |  | BLK6INV12 | 22.25 | 0.3955% | String |  | mc4 open so rectify & connect the same | 0.21736 | 0.33333 | 0.72222 | 0.73611 | 2.7833 | 12.1167 | 12.45 | 12.45 | mc4 open so rectify & connect the same | closed | 0.04924 | 0.629 | 10.5961
1893 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21736 | 0.77014 | 13.2667 | BLK6 |  |  | INV8 |  |  | BLK6INV8 | 22.25 | 0.4449% | String |  | String cable found faulty | 0.21736 | 0.33333 | 0.71181 | 0.72569 | 2.7833 | 11.8667 | 12.2 | 12.2 | String cable found faulty | closed | 0.054283 | 0.631 | 10.6298
1894 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21736 | 0.77014 | 13.2667 | BLK6 |  |  | INV14 |  |  | BLK6INV14 | 22.25 | 0.412% | String |  | mc4 open so rectify & connect the same | 0.21736 | 0.33333 | 0.72917 | 0.73958 | 2.7833 | 12.2833 | 12.5333 | 12.5333 | mc4 open so rectify & connect the same | closed | 0.051635 | 0.633 | 10.6635
1895 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21875 | 0.77014 | 13.2333 | BLK6 |  |  | INV26 |  |  | BLK6INV26 | 22.25 | 0.4449% | MCCB |  | Inv MCCB (250Amp) flash-over replaced with a new one & restore | 0.21875 | 0.21875 | 0.44444 | 0.49028 | 0 | 5.4167 | 6.5167 | 6.5167 | Inv MCCB (250Amp) flash-over replaced with a new one & restore | closed | 0.028996 | 2.16 | 36.3872
1896 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21875 | 0.77014 | 13.2333 | BLK6 |  |  | INV25 |  |  | BLK6INV25 | 22.25 | 0.4449% | MCCB |  | Manually shutdown taken for restoretion work of inv 26 | 0.21875 | 0.44306 | 0.44306 | 0.48611 | 5.3833 | 5.3833 | 6.4167 | 6.4167 | Manually shutdown taken for restoretion work of inv 26 | closed | 0.028551 | 0.608 | 10.2423
1897 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21875 | 0.77014 | 13.2333 | BLK3 |  |  | INV29 |  |  | BLK3INV29 | 22.25 | 0.4333% | String |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 0.375 | 0.63542 | 0.64444 | 3.75 | 10 | 10.2167 | 10.2167 | MC4 Connector found open Same is restored after verfying the load | closed | 0.044272 | 4.987 | 84.0106
1898 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21875 | 0.77014 | 13.2333 | BLK3 |  |  | INV24 |  |  | BLK3INV24 | 22.25 | 0.4% | String |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 0.375 | 0.63542 | 0.64722 | 3.75 | 10 | 10.2833 | 10.2833 | MC4 Connector found open Same is restored after verfying the load | closed | 0.041133 | 5.081 | 85.5941
1899 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21875 | 0.77014 | 13.2333 | BLK2 |  |  | INV24 |  |  | BLK2INV24 | 22.25 | 0.4333% | String |  | Found Fuse burn replace with a new one & restore the same | 0.21875 | 0.375 | 0.64583 | 0.66181 | 3.75 | 10.25 | 10.6333 | 10.6333 | Found Fuse burn replace with a new one & restore the same | closed | 0.046078 | 5.123 | 86.3017
1900 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21875 | 0.77014 | 13.2333 | BLK7 |  |  | INV5 |  |  | BLK7INV5 | 22.25 | 0.3955% | String |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 0.375 | 0.68403 | 0.69444 | 3.75 | 11.1667 | 11.4167 | 11.4167 | MC4 Connector found open Same is restored after verfying the load | closed | 0.045154 | 5.325 | 89.7045
1901 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21875 | 0.77014 | 13.2333 | BLK7 |  |  | INV2 |  |  | BLK7INV2 | 22.25 | 0.3955% | String |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 0.375 | 0.68056 | 0.69931 | 3.75 | 11.0833 | 11.5333 | 11.5333 | MC4 Connector found open Same is restored after verfying the load | closed | 0.045615 | 5.416 | 91.2375
1902 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21875 | 0.77014 | 13.2333 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | String |  | Found Fuse burn replace with a new one & restore the same | 0.21875 | 0.375 | 0.70139 | 0.71667 | 3.75 | 11.5833 | 11.95 | 11.95 | Found Fuse burn replace with a new one & restore the same | closed | 0.053775 | 5.44 | 91.6418
1903 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21875 | 0.77014 | 13.2333 | BLK4 |  |  | INV31 |  |  | BLK4INV31 | 22.25 | 0.4% | String |  | Found Fuse burn replace with a new one & restore the same | 0.21875 | 0.375 | 0.71875 | 0.73264 | 3.75 | 12 | 12.3333 | 12.3333 | Found Fuse burn replace with a new one & restore the same | closed | 0.049333 | 5.61 | 94.5056
1904 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.23958 | 0.77153 | 12.7667 | BLK4 |  |  | INV24 |  |  | BLK4INV24 | 22.25 | 0.45% | String |  | Found MC4 Faulty | 0.23958 | 0.375 | 0.47222 | 0.48333 | 3.25 | 5.5833 | 5.85 | 5.85 | 1Pair of MC4 connector replaced with new one | closed | 0.026325 | 2.53 | 42.6202
1905 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.23958 | 0.77153 | 12.7667 | BLK2 |  |  | INV20 |  |  | BLK2INV20 | 44.5 | 0.4% | String |  | Found MC4 Faulty | 0.23958 | 0.375 | 0.42361 | 0.44306 | 3.25 | 4.4167 | 4.8833 | 4.8833 | 1 No of MC4, 1 pcs of Y connector & 1 pair of Fuse replaced with new one | closed | 0.019533 | 1.75 | 58.9607
1906 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.23958 | 0.77153 | 12.7667 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 22.25 | 0.3955% | String |  | Found MC4 Faulty | 0.23958 | 0.375 | 0.47917 | 0.49722 | 3.25 | 5.75 | 6.1833 | 6.1833 | 1Pair of MC4 connector replaced with new one | closed | 0.024455 | 2.82 | 47.5055
1907 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.23958 | 0.77153 | 12.7667 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 11.5 | 0.3955% | String |  | module displaced | 0.23958 | 0.375 | 0.63542 | 0.65 | 3.25 | 9.5 | 9.85 | 9.85 | Fixed with same | closed | 0.038957 | 5.76 | 50.1516
1908 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.23958 | 0.77153 | 12.7667 | BLK8 |  |  | INV2 |  |  | BLK8INV2 | 9.5 | 0.2966% | String |  | module displaced | 0.23958 | 0.375 | 0.63889 | 0.65347 | 3.25 | 9.5833 | 9.9333 | 9.9333 | Fixed with same | closed | 0.029465 | 5.77 | 41.5015
1909 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.23958 | 0.77153 | 12.7667 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 15.75 | 0.4065% | String |  | module displaced | 0.23958 | 0.375 | 0.64236 | 0.65556 | 3.25 | 9.6667 | 9.9833 | 9.9833 | Fixed with same | closed | 0.040584 | 5.77 | 68.8052
1910 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.23958 | 0.77153 | 12.7667 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 11.25 | 0.45% | String |  | module displaced | 0.23958 | 0.375 | 0.40972 | 0.42361 | 3.25 | 4.0833 | 4.4167 | 4.4167 | Fixed with same | closed | 0.019875 | 1.25 | 10.647
1911 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.23958 | 0.77153 | 12.7667 | BLK5 |  |  | INV12 |  |  | BLK5INV12 | 286 | 0.4285% | Inverter |  | Module flyout due to yesterday wind strom impact , same is restored | 0.23958 | 0.375 | 0.28125 | 0.29514 | 3.25 | 1 | 1.3333 | 1.3333 | Reset & Started | closed | 0.0057129 | 0.201 | 43.5238
1912 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.23958 | 0.77153 | 12.7667 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | Inverter |  | Module flyout due to yesterday wind strom impact , same is restored | 0.30556 | 0.375 | 0.30556 | 0.31944 | 1.6667 | 0 | 0.33333 | 0.33333 | Reset & Started | closed | 0.0013333 | 0.349 | 70.5507
1913 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21806 | 0.77153 | 13.2833 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 3947.5 | 5.914% | LT Panel |  | LT1 trippedon over current fault | 0.43611 | 0.43611 | 0.43958 | 0.44444 | 0 | 0.083333 | 0.2 | 0.2 | Check the all parmeter & charged | closed | 0.011828 | 0.113 | 337.7267
1914 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21806 | 0.77153 | 13.2833 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | Inverter |  | Inverter tripped on excessive leakage current fault | 0.47917 | 0.47917 | 0.48264 | 0.50972 | 0 | 0.083333 | 0.73333 | 0.73333 | Reset & Started | closed | 0.0029333 | 0.393 | 79.4454
1915 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21806 | 0.77153 | 13.2833 | BLK5 |  |  | INV23 |  |  | BLK5INV23 | 22.25 | 0.3667% | String |  | Module flyout due to day before yesterday wind strom impact , same is restored | 0.21806 | 0.375 | 0.50347 | 0.52778 | 3.7667 | 6.85 | 7.4333 | 7.4333 | Fixed with same | closed | 0.027256 | 2.319 | 39.0657
1916 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21806 | 0.77153 | 13.2833 | BLK1 |  |  | INV17 |  |  | BLK1INV17 | 22.25 | 0.4% | String |  | MC4 Connector found open Same is restored after verfying the load | 0.21806 | 0.375 | 0.52431 | 0.54167 | 3.7667 | 7.35 | 7.7667 | 7.7667 | MC4 Connector found open Same is restored after verfying the load | closed | 0.031067 | 2.46 | 41.441
1917 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21806 | 0.77153 | 13.2833 | BLK1 | LT2 |  |  |  |  | BLK1LT2 | 4605.75 | 6.9% | LT Panel |  | LT1 trippedon over current fault | 0.55417 | 0.55417 | 0.56181 | 0.56181 | 0 | 0.18333 | 0.18333 | 0.18333 | Check the all parmeter & charged | closed | 0.01265 | 0.111 | 387.0688
1918 | 2025-05-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21528 | 0.77153 | 13.35 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | String |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 0.375 | 0.68403 | 0.68403 | 3.75 | 11.1667 | 11.1667 | 11.1667 | MC4 Connector found open Same is restored after verfying the load | closed | 0.05025 | 5 | 84.2296
1919 | 2025-05-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21528 | 0.77153 | 13.35 | BLK5 |  |  | INV2 |  |  | BLK5INV2 | 22.25 | 0.4% | String |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 0.375 | 0.67292 | 0.67292 | 3.75 | 10.9 | 10.9 | 10.9 | MC4 Connector found open Same is restored after verfying the load | closed | 0.0436 | 4.3 | 72.4375
1920 | 2025-05-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21528 | 0.77153 | 13.35 | BLK5 |  |  | INV32 |  |  | BLK5INV32 | 22.25 | 0.4% | String |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 0.375 | 0.65972 | 0.65972 | 3.75 | 10.5833 | 10.5833 | 10.5833 | MC4 Connector found open Same is restored after verfying the load | closed | 0.042333 | 4.2 | 70.7529
1921 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK1 | LT1 |  |  |  |  | BLK1LT1 | 4338.75 | 6.5% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.54167 | 0.54861 |  |  |  |  | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0 | 1.746 | 5735.5319
1922 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK1 | LT2 |  |  |  |  | BLK1LT2 | 4605.75 | 6.9% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.54167 | 0.54861 |  |  |  |  | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0 | 1.746 | 6088.4877
1923 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK2 | LT1 |  |  |  |  | BLK2LT1 | 4094 | 6.133% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.54167 | 0.54861 | 0 | 1.8167 | 1.9833 | 1.9833 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.12164 | 1.746 | 5411.989
1924 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 4249.75 | 6.367% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.54167 | 0.54861 | 0 | 1.8167 | 1.9833 | 1.9833 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.12627 | 1.746 | 5617.8799
1925 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK3 | LT1 |  |  |  |  | BLK3LT1 | 4483.375 | 6.717% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.54514 | 0.55069 | 0 | 1.9 | 2.0333 | 2.0333 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.13657 | 1.791 | 6079.4667
1926 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK3 | LT2 |  |  |  |  | BLK3LT2 | 4071.75 | 6.1% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.54514 | 0.55069 | 0 | 1.9 | 2.0333 | 2.0333 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.12403 | 1.791 | 5521.3022
1927 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK4 | LT1 |  |  |  |  | BLK4LT1 | 4394.375 | 6.583% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.54514 | 0.55069 | 0 | 1.9 | 2.0333 | 2.0333 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.13386 | 1.791 | 5958.7825
1928 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK4 | LT2 |  |  |  |  | BLK4LT2 | 4260.875 | 6.383% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.54514 | 0.55069 | 0 | 1.9 | 2.0333 | 2.0333 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.12979 | 1.791 | 5777.7562
1929 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK7 | LT1 |  |  |  |  | BLK7LT1 | 3298.1 | 4.941% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.55 | 0.55347 | 0 | 2.0167 | 2.1 | 2.1 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.10376 | 1.725 | 4307.4252
1930 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK7 | LT2 |  |  |  |  | BLK7LT2 | 4071.75 | 6.1% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.55 | 0.55347 | 0 | 2.0167 | 2.1 | 2.1 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.1281 | 1.725 | 5317.8372
1931 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 3947.5 | 5.914% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.55 | 0.55347 | 0 | 2.0167 | 2.1 | 2.1 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.12419 | 1.725 | 5155.5626
1932 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK8 | LT2 |  |  |  |  | BLK8LT2 | 3093.9 | 4.635% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.55 | 0.55347 | 0 | 2.0167 | 2.1 | 2.1 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.097336 | 1.725 | 4040.7334
1933 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK5 | LT1 |  |  |  |  | BLK5LT1 | 4514.875 | 6.764% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.64583 | 0.65208 | 0 | 4.3167 | 4.4667 | 4.4667 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.30212 | 2.152 | 7356.1881
1934 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK5 | LT2 |  |  |  |  | BLK5LT2 | 4349.875 | 6.517% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.64583 | 0.65208 | 0 | 4.3167 | 4.4667 | 4.4667 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | closed | 0.29108 | 2.152 | 7087.3499
1935 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK6 | LT1 |  |  |  |  | BLK6LT1 | 4477 | 6.707% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.77153 | 0.77153 | 0 | 7.3333 | 7.3333 | 7.3333 | Jointing work in progress, It will be restored after joint work. | closed | 0.49186 | 4.381 | 14849.9564
1936 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 4499 | 6.74% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 0.46597 | 0.46597 | 0.77153 | 0.77153 | 0 | 7.3333 | 7.3333 | 7.3333 | Jointing work in progress, It will be restored after joint work. | closed | 0.49427 | 4.381 | 14922.9291
1937 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.2125 | 0.77153 | 13.4167 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 22.25 | 0.3333% | string |  | Inverter was tripped due to excessive leakage current, | 0.55208 | 0.55208 | 0.55556 | 0.52917 | 0 | 0.083333 | -0.55 | -0.55 | we have physically checked all parameter of this inverter & string's then we found that string no-2 MC4 Connector Positive & negative was failure same is restored after replaced it new one. | closed | -0.0018333 | 0.398 | 6.7047
1938 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21458 | 0.76319 | 13.1667 | BLK5 | LT1 |  |  |  |  | BLK5LT1 | 4514.875 | 6.764% | LT Panel |  | HT Cables jointing work has been done of Block-6 O/G Cable, we have to take manually shutdown of incommer-3(Connected Block 5&6) for take load of Block which is connected to block -5 | 0.55556 | 0.55556 | 0.56944 | 0.58056 | 0 | 0.33333 | 0.6 | 0.6 | After connected the load of block-6 to block -5, checked the all parameters then charged the Block 5 | closed | 0.040583 | 0.456 | 1558.7462
1939 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21458 | 0.76319 | 13.1667 | BLK5 | LT2 |  |  |  |  | BLK5LT2 | 4349.875 | 6.517% | LT Panel |  | HT Cables jointing work has been done of Block-6 O/G Cable, we have to take manually shutdown of incommer-3(Connected Block 5&6) for take load of Block which is connected to block -5 | 0.55556 | 0.55556 | 0.56944 | 0.58056 | 0 | 0.33333 | 0.6 | 0.6 | After connected the load of block-6 to block -5, checked the all parameters then charged the Block 5 | closed | 0.0391 | 0.456 | 1501.7805
1940 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21458 | 0.76319 | 13.1667 | BLK6 | LT1 |  |  |  |  | BLK6LT1 | 4477 | 6.707% | LT Panel |  | HT Cable jointing work | 0.21458 | 0.21458 | 0.58333 | 0.59236 | 0 | 8.85 | 9.0667 | 9.0667 | after checking all the parameter & visual inspection of block 6 we charge the ICR | closed | 0.60811 | 4.47 | 15151.6332
1941 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21458 | 0.76319 | 13.1667 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 4499 | 6.74% | LT Panel |  | HT Cable jointing work | 0.21458 | 0.21458 | 0.58333 | 0.59236 | 0 | 8.85 | 9.0667 | 9.0667 | after checking all the parameter & visual inspection of block 6 we charge the ICR | closed | 0.6111 | 4.47 | 15226.0884
1942 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 0.21458 | 0.76319 | 13.1667 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 3947.5 | 5.914% | LT Panel |  | LT-1 was in breakdown under over current | 0.57083 | 0.57639 | 0.60764 | 0.61667 | 0.13333 | 0.88333 | 1.1 | 1.1 | after checking all the parameter & visual inspection of block 8 LT-1 we charge it. | closed | 0.065052 | 0.345 | 1031.1125
1943 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 22.25 | 6.74% | string |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 1900-03-20 10:00 | 0.4375 | 0.4375 | 1924.75 | 5.25 | 5.25 | 5.25 | MC4 Connector found open Same is restored after verfying the load | closed | 0.35385 | 2.2 | 37.061
1944 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 22.25 | 6.74% | string |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 1900-03-20 10:00 | 0.45833 | 0.45833 | 1924.75 | 5.75 | 5.75 | 5.75 | MC4 Connector found open Same is restored after verfying the load | closed | 0.38755 | 2.1 | 35.3764
1945 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 22.25 | 6.74% | string |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 1900-03-20 10:00 | 0.46181 | 0.46181 | 1924.75 | 5.8333 | 5.8333 | 5.8333 | MC4 Connector found open Same is restored after verfying the load | closed | 0.39317 | 2.1 | 35.3764
1946 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK1 | LT1 |  |  |  |  | BLK1LT1 | 22.25 | 6.5% | string |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 1900-03-20 10:00 | 0.60278 | 0.60278 | 1924.75 | 9.2167 | 9.2167 | 9.2167 | MC4 Connector found open Same is restored after verfying the load | closed | 0.59908 | 4.3 | 72.4375
1947 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK1 | LT1 |  |  |  |  | BLK1LT1 | 22.25 | 6.5% | string |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 1900-03-20 10:00 | 0.60972 | 0.60972 | 1924.75 | 9.3833 | 9.3833 | 9.3833 | MC4 Connector found open Same is restored after verfying the load | closed | 0.60992 | 4.4 | 74.1221
1948 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 22.25 | 6.367% | string |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 1900-03-20 10:00 | 0.62014 | 0.62014 | 1924.75 | 9.6333 | 9.6333 | 9.6333 | MC4 Connector found open Same is restored after verfying the load | closed | 0.61332 | 4.5 | 75.8067
1949 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 22.25 | 6.367% | string |  | MC4 Connector found open Same is restored after verfying the load | 0.21875 | 1900-03-20 10:00 | 0.65139 | 0.65139 | 1924.75 | 10.3833 | 10.3833 | 10.3833 | MC4 Connector found open Same is restored after verfying the load | closed | 0.66107 | 5 | 84.2296
1950 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK8 | LT2 |  |  |  |  | BLK8LT2 | 67.25 | 4.635% | string |  | Block8 Inv No 28 3 nos String add after replaced all faulty module(Jakson-335wp),Now Inverter isrunning with total 12.5 String | 0.21875 | 1900-03-20 10:00 | 0.69444 | 0.69444 | 1924.75 | 11.4167 | 11.4167 | 11.4167 | Block8 Inv No 28 3 nos String add after replaced all faulty module(Jakson-335wp),Now Inverter isrunning with total 12.5 String | closed | 0.52917 | 5.3 | 269.8566
1951 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21806 | 0.77292 | 13.3167 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 267 | 0.3955% | Inverter |  | Inv 6 Under breakdown due to insulation fault | 0.21806 | 0.41667 | 0.39722 | 0.39722 | 4.7667 | 4.3 | 4.3 | 4.3 | Inv 6 Under breakdown due to insulation fault | closed | 0.017007 | 2.1 | 426.2119
1952 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21806 | 0.77292 | 13.3167 | BLK6 |  |  | INV24 |  |  | BLK6INV24 | 22.3 | 0.4285% | string |  | MC4 Connector found open Same is restored after verfying the load | 0.21806 | 0.41667 | 0.43056 | 0.43056 | 4.7667 | 5.1 | 5.1 | 5.1 | MC4 Connector found open Same is restored after verfying the load | closed | 0.021852 | 1.3 | 22.0365
1953 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21806 | 0.77292 | 13.3167 | BLK8 |  |  | INV14 |  |  | BLK8INV14 | 22.3 | 0.3856% | string |  | MC4 Connector found open Same is restored after verfying the load | 0.21806 | 0.41667 | 0.44306 | 0.44306 | 4.7667 | 5.4 | 5.4 | 5.4 | MC4 Connector found open Same is restored after verfying the load | closed | 0.020823 | 1.4 | 23.7317
1954 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21806 | 0.77292 | 13.3167 | BLK2 |  |  | INV29 |  |  | BLK2INV29 | 22.3 | 0.45% | string |  | MC4 Connector found open Same is restored after verfying the load | 0.21806 | 0.41667 | 0.47222 | 0.47222 | 4.7667 | 6.1 | 6.1 | 6.1 | MC4 Connector found open Same is restored after verfying the load | closed | 0.02745 | 1.5 | 25.4268
1955 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21806 | 0.77292 | 13.3167 | BLK8 |  |  | INV26 |  |  | BLK8INV26 | 22.3 | 0.4065% | string |  | MC4 Connector found open Same is restored after verfying the load | 0.21806 | 0.41667 | 0.11458 | 0.11458 | 4.7667 | -2.4833 | -2.4833 | -2.4833 | MC4 Connector found open Same is restored after verfying the load | closed | -0.010095 | 1.4 | 23.7317
1956 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21875 | 0.74722 | 12.6833 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.48333 | 0.48333 | 0.48333 | 0.49028 | 0 | 0 | 0.16667 | 0.16667 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.022333 | 0.3 | 2039.7285
1957 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21875 | 0.74722 | 12.6833 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8909 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.48333 | 0.48333 | 0.49028 | 0.49028 | 0 | 0.16667 | 0.16667 | 0.16667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.022134 | 0.3 | 2031.633
1958 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21875 | 0.74722 | 12.6833 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8944.5 | 13.45% | IDT |  | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.48472 | 0.48472 | 0.49167 | 0.49167 | 0 | 0.16667 | 0.16667 | 0.16667 | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.022412 | 0.3 | 2039.7285
1959 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21875 | 0.74722 | 12.6833 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.48472 | 0.48472 | 0.49514 | 0.49514 | 0 | 0.25 | 0.25 | 0.25 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0335 | 0.4 | 2719.638
1960 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21875 | 0.74722 | 12.6833 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.51667 | 0.51667 | 0.52153 | 0.52153 | 0 | 0.11667 | 0.11667 | 0.11667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.014583 | 0.28 | 1887.9113
1961 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21875 | 0.74722 | 12.6833 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.51667 | 0.51667 | 0.52431 | 0.52431 | 0 | 0.18333 | 0.18333 | 0.18333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.024348 | 0.29 | 1978.6815
1963 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21875 | 0.74722 | 12.6833 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8909.25 | 13.45% | IDT |  | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.51667 | 0.51667 | 0.52639 | 0.52639 | 0 | 0.23333 | 0.23333 | 0.23333 | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.031377 | 0.31 | 2099.413
1964 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21875 | 0.74722 | 12.6833 | BLK5 |  |  | INV20 |  |  | BLK5INV20 | 22.5 | 0.4% | string |  | Found Fuse, Y- connector & MC4 burn replace with a new one & restore the same | 0.51667 | 0.51667 | 0.52778 | 0.52778 | 0 | 0.26667 | 0.26667 | 0.26667 | Found Fuse, Y- connector & MC4 burn replace with a new one & restore the same | closed | 0.0010667 | 0.31 | 5.302
1965 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21875 | 0.74722 | 12.6833 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22.5 | 0.45% | string |  | MC4 connector melted causes failure so replaced it with new one | 0.21875 | 0.375 | 0.62917 | 0.62917 | 3.75 | 9.85 | 9.85 | 9.85 | MC4 connector melted causes failure so replaced it with new one | closed | 0.044325 | 5.1 | 87.2264
1966 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.46597 | 0.47639 | 0.47014 | 0.47014 | 0.25 | 0.1 |  |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0 | 0.35 | 2359.8892
1967 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.47222 | 0.47569 | 0.47569 | 0.47569 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011067 | 0.21 | 1432.8383
1968 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.49167 | 0.5 | 0.49653 | 0.49653 | 0.2 | 0.11667 | 0.11667 | 0.11667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.014583 | 0.21 | 1415.9335
1969 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.49167 | 0.49722 | 0.49653 | 0.49653 | 0.13333 | 0.11667 | 0.11667 | 0.11667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.015494 | 0.21 | 1432.8383
1970 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.50625 | 0.51528 | 0.51042 | 0.51042 | 0.21667 | 0.1 | 0.1 | 0.1 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0134 | 0.15 | 1019.8643
1971 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.50625 | 0.51389 | 0.51042 | 0.51042 | 0.18333 | 0.1 | 0.1 | 0.1 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0125 | 0.15 | 1011.3811
1972 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.51042 | 0.51458 | 0.51528 | 0.51528 | 0.1 | 0.11667 | 0.11667 | 0.11667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.015494 | 0.16 | 1091.6863
1973 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.51944 | 0.52361 | 0.52431 | 0.52431 | 0.1 | 0.11667 | 0.11667 | 0.11667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.014583 | 0.16 | 1078.8065
1974 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.52014 | 0.525 | 0.52431 | 0.52431 | 0.11667 | 0.1 | 0.1 | 0.1 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.013281 | 0.14 | 955.2255
1975 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8976 | 13.45% | IDT |  | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.52014 | 0.52639 | 0.52431 | 0.52431 | 0.15 | 0.1 | 0.1 | 0.1 | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.013447 | 0.145 | 989.3407
1976 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK7 | LT1 |  |  |  |  | BLK7LT1 | 4071.75 | 4.941% | LT Panel |  | Block-7 LT1 tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.51736 | 0.52222 | 0.52431 | 0.52431 | 0.11667 | 0.16667 | 0.16667 | 0.16667 | Block-7 LT1 tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.008235 | 0.13 | 402.3644
1977 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK1 |  |  | INV1 |  |  | BLK1INV1 | 289.25 | 0.4333% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 0.51181 | 0.55 | 0.51667 | 0.51667 | 0.91667 | 0.11667 | 0.11667 | 0.11667 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.00050556 | 0.44 | 96.7433
1978 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK1 |  |  | INV2 |  |  | BLK1INV2 | 289.25 | 0.4333% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 0.51181 | 0.55 | 0.51667 | 0.51667 | 0.91667 | 0.11667 | 0.11667 | 0.11667 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.00050556 | 0.44 | 96.7433
1979 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK1 |  |  | INV3 |  |  | BLK1INV3 | 289.25 | 0.4% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 0.51181 | 0.55069 | 0.51667 | 0.51667 | 0.93333 | 0.11667 | 0.11667 | 0.11667 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.00046667 | 0.44 | 96.7433
1980 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | INV1 |  |  | BLK2INV1 | 243.275 | 0.45% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 0.51111 | 0.54097 | 0.51667 | 0.51667 | 0.71667 | 0.13333 | 0.13333 | 0.13333 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.0006 | 0.46 | 85.0649
1981 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 334.55 | 0.3333% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 0.51111 | 0.54514 | 0.51667 | 0.51667 | 0.81667 | 0.13333 | 0.13333 | 0.13333 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.00044444 | 0.46 | 116.9806
1982 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | INV16 |  |  | BLK5INV16 | 289.25 | 0.4333% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 0.51389 | 0.54861 | 0.51667 | 0.51667 | 0.83333 | 0.066667 | 0.066667 | 0.066667 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.00028889 | 0.31 | 68.1601
1983 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | INV22 |  |  | BLK5INV22 | 244.75 | 0.4% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 0.51389 | 0.54861 | 0.51667 | 0.51667 | 0.83333 | 0.066667 | 0.066667 | 0.066667 | As per O2 Team, instruction we have taken manually shutdown for active power control | closed | 0.00026667 | 0.31 | 57.6739
1984 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 31.9 | 0.4065% | String |  | MC4 Connector found melted, Same is restored after verfying the load | 0.22153 | 0.375 | 0.43819 | 0.43819 | 3.6833 | 5.2 | 5.2 | 5.2 | MC4 Connector found melted, Same is restored after verfying the load | closed | 0.021139 | 1.28 | 31.0381
1985 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV15 |  |  | BLK8INV15 | 20.1 | 0.4004% | String |  | MC4 Connector found open Same is restored after verfying the load | 0.22153 | 0.375 | 0.44792 | 0.44792 | 3.6833 | 5.4333 | 5.4333 | 5.4333 | MC4 Connector found open Same is restored after verfying the load | closed | 0.021758 | 1.41 | 21.5432
1986 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV21 |  |  | BLK8INV21 | 20.1 | 0.4004% | String |  | MC4 Connector found open Same is restored after verfying the load | 0.22153 | 0.375 | 0.45833 | 0.45833 | 3.6833 | 5.6833 | 5.6833 | 5.6833 | MC4 Connector found open Same is restored after verfying the load | closed | 0.022759 | 1.56 | 23.835
1987 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV10 |  |  | BLK8INV10 | 20.1 | 0.45% | String |  | MC4 Connector found melted, Same is restored after verfying the load | 0.22153 | 0.375 | 0.63542 | 0.63542 | 3.6833 | 9.9333 | 9.9333 | 9.9333 | MC4 Connector found melted, Same is restored after verfying the load | closed | 0.0447 | 3.7 | 56.5318
1988 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV18 |  |  | BLK8INV18 | 20.1 | 0.3333% | String |  | MC4 Connector found open Same is restored after verfying the load | 0.22153 | 0.375 | 0.64583 | 0.64583 | 3.6833 | 10.1833 | 10.1833 | 10.1833 | MC4 Connector found open Same is restored after verfying the load | closed | 0.033944 | 3.76 | 57.4485
1989 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22.25 | 0.3955% | String |  | Y connector & fuse failure so replaced it with new one | 0.22153 | 0.375 | 0.65625 | 0.65625 | 3.6833 | 10.4333 | 10.4333 | 10.4333 | Y connector & fuse failure so replaced it with new one | closed | 0.041264 | 3.82 | 64.6083
1990 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 22.25 | 0.3955% | String |  | MC4 Connector found melted, Same is restored after verfying the load | 0.22153 | 0.375 | 0.67361 | 0.67361 | 3.6833 | 10.85 | 10.85 | 10.85 | MC4 Connector found melted, Same is restored after verfying the load | closed | 0.042912 | 3.92 | 66.2996
1991 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK3 |  |  | INV28 |  |  | BLK3INV28 | 22.25 | 0.4167% | sTring |  | Y connector & fuse failure so replaced it with new one | 0.22153 | 0.375 | 0.68056 | 0.68056 | 3.6833 | 11.0167 | 11.0167 | 11.0167 | Y connector & fuse failure so replaced it with new one | closed | 0.045903 | 3.95 | 66.807
1992 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK4 |  |  | INV4 |  |  | BLK4INV4 | 22.25 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.22153 | 0.375 | 0.69097 | 0.69097 | 3.6833 | 11.2667 | 11.2667 | 11.2667 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.045067 | 4.01 | 67.8218
1993 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | INV8 |  |  | BLK5INV8 | 22.25 | 0.4333% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.22153 | 0.375 | 0.70486 | 0.70486 | 3.6833 | 11.6 | 11.6 | 11.6 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.050267 | 4.07 | 68.8366
1994 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | INV21 |  |  | BLK5INV21 | 22.25 | 0.4333% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.22153 | 0.375 | 0.71528 | 0.71528 | 3.6833 | 11.85 | 11.85 | 11.85 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.05135 | 4.11 | 69.5131
1995 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK2 |  |  | mvp |  |  | BLK2mvp | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.46736 | 0.46736 | 0.46875 | 0.47083 | 0 | 0.033333 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.010417 | 0.065 | 438.2651
1996 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 18:33 | 13.3833 | BLK5 |  |  | mvp |  |  | BLK5mvp | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.46667 | 0.46667 | 0.46806 | 0.47014 | 0 | 0.033333 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011067 | 0.064 | 436.6745
1997 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 18:33 | 13.3833 | BLK5 |  |  | INV32 |  |  | BLK5INV32 | 22.23 | 0.4% | String |  | Y connector, fuse & mc4 failure | 0.21528 | 0.375 | 0.49653 | 0.50694 | 3.8333 | 6.75 | 7 | 7 | Y connector, fuse & mc4 failure so replaced it with new one | closed | 0.028 | 2.061 | 34.8267
1998 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 18:33 | 13.3833 | BLK5 |  |  | INV29 |  |  | BLK5INV29 | 22.23 | 0.4% | String |  | MC4 Connector found melted | 0.21528 | 0.375 | 0.50694 | 0.51736 | 3.8333 | 7 | 7.25 | 7.25 | MC4 Connector found melted, Same is restored after verfying the load | closed | 0.029 | 2.21 | 37.3445
1999 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 18:33 | 13.3833 | BLK5 |  |  | INV30 |  |  | BLK5INV30 | 22.23 | 0.4% | String |  | MC4 Connecto found open | 0.21528 | 0.375 | 0.51736 | 0.53125 | 3.8333 | 7.25 | 7.5833 | 7.5833 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.030333 | 2.38 | 40.2172
2000 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 18:33 | 13.3833 | BLK5 |  |  | INV28 |  |  | BLK5INV28 | 22.23 | 0.45% | String |  | MC4 Connecto found open | 0.21528 | 0.375 | 0.53125 | 0.54514 | 3.8333 | 7.5833 | 7.9167 | 7.9167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.035625 | 2.54 | 42.9208
2001 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 18:33 | 13.3833 | BLK5 |  |  | INV31 |  |  | BLK5INV31 | 22.23 | 0.4% | String |  | MC4 Connecto found open | 0.21528 | 0.375 | 0.61806 | 0.63194 | 3.8333 | 9.6667 | 10 | 10 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.04 | 3.84 | 64.8882
2002 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 18:33 | 13.3833 | BLK5 |  |  | INV12 |  |  | BLK5INV12 | 22.23 | 0.4285% | String |  | MC4 Connecto found open | 0.21528 | 0.375 | 0.63194 | 0.64583 | 3.8333 | 10 | 10.3333 | 10.3333 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.044275 | 4.08 | 68.9437
2003 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 18:33 | 13.3833 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22.23 | 0.45% | String |  | Found 1 fuse failure | 0.21528 | 0.375 | 0.64236 | 0.65625 | 3.8333 | 10.25 | 10.5833 | 10.5833 | Found 1 fuse failure so replaced it with new one | closed | 0.047625 | 4.22 | 71.3094
2004 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 18:33 | 13.3833 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | String |  | Inverter frequently shutdown on fault of excessive leakage current | 0.33333 | 0.33333 | 0.34375 | 0.40347 | 0 | 0.25 | 1.6833 | 1.6833 | Inverter frequently shutdown on fault of excessive leakage current after reset the fault & verify all parameter charge the inverter | closed | 0.0067333 | 0.65 | 131.9227
2005 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 | 0.775 | 13.5 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.53056 | 0.53056 | 0.53194 | 0.53958 | 0 | 0.033333 | 0.21667 | 0.21667 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.029033 | 0.38 | 2583.6561
2006 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 |  | -5.1 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.53056 | 0.53056 | 0.53194 | 0.53819 | 0 | 0.033333 | 0.18333 | 0.18333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.022917 | 0.38 | 2562.1654
2007 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 |  | -5.1 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.53056 | 0.53056 | 0.53194 | 0.53542 | 0 | 0.033333 | 0.11667 | 0.11667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.015494 | 0.28 | 1910.4511
2008 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 |  | -5.1 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8976 | 13.45% | IDT |  | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.53056 | 0.53056 | 0.53194 | 0.53472 | 0 | 0.033333 | 0.1 | 0.1 | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.013447 | 0.26 | 1773.9903
2009 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 |  | -5.1 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.54444 | 0.54444 | 0.54583 | 0.55486 | 0 | 0.033333 | 0.25 | 0.25 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.03125 | 0.28 | 1887.9113
2010 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 |  | -5.1 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.55 | 0.55 | 0.55139 | 0.55347 | 0 | 0.033333 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011067 | 0.25 | 1705.7599
2011 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 |  | -5.1 | BLK7 |  |  | MVP |  |  | BLK7MVP | 8870.1 | 11.04% | IDT |  | Block-7 LT1 tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.52778 | 0.52778 | 0.52917 | 0.53472 | 0 | 0.033333 | 0.16667 | 0.16667 | Block-7 LT1 tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.018402 | 0.22 | 1483.3589
2012 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 |  | -5.1 | BLK1 |  |  | INV1 |  |  | BLK1INV1 | 289.25 | 0.4333% | Inverter |  | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | 0.44375 | 0.45486 | 0.45486 | 0.45486 | 0.26667 | 0.26667 | 0.26667 | 0.26667 | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | closed | 0.0011556 | 0.31 | 68.1601
2013 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 |  | -5.1 | BLK2 |  |  | INV29 |  |  | BLK2INV29 | 267 | 0.45% | Inverter |  | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | 0.44375 | 0.45486 | 0.45486 | 0.45486 | 0.26667 | 0.26667 | 0.26667 | 0.26667 | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | closed | 0.0012 | 0.31 | 62.917
2014 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 |  | -5.1 | BLK2 |  |  | INV30 |  |  | BLK2INV30 | 298 | 0.4% | Inverter |  | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | 0.44375 | 0.45486 | 0.45486 | 0.45486 | 0.26667 | 0.26667 | 0.26667 | 0.26667 | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | closed | 0.0010667 | 0.31 | 70.222
2015 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 |  | -5.1 | BLK3 |  |  | INV17 |  |  | BLK3INV17 | 22.5 | 0.4333% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.375 | 0.45486 | 0.45486 | 0.45486 | 1.9167 | 1.9167 | 1.9167 | 1.9167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.0083056 | 0.33 | 5.6441
2016 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 |  | -5.1 | BLK4 |  |  | INV21 |  |  | BLK4INV21 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.375 | 0.63194 | 0.63194 | 0.63194 | 6.1667 | 6.1667 | 6.1667 | 6.1667 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.024667 | 0.64 | 10.9461
2017 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 |  | -5.1 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.375 | 0.64583 | 0.64583 | 0.64583 | 6.5 | 6.5 | 6.5 | 6.5 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.026 | 0.61 | 10.433
2018 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 |  | -5.1 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.375 | 0.65972 | 0.65972 | 0.65972 | 6.8333 | 6.8333 | 6.8333 | 6.8333 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.027333 | 0.62 | 10.604
2019 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21319 | 0.775 | 13.4833 | BLK1 |  |  | INV31 |  |  | BLK1INV31 | 22.5 | 0.45% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.21319 | 0.65625 | 0.65625 | 0.67222 | 10.6333 | 10.6333 | 11.0167 | 11.0167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.049575 | 5.23 | 89.4498
2020 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21319 | 0.775 | 13.4833 | BLK1 |  |  | INV8 |  |  | BLK1INV8 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.21319 | 0.68056 | 0.68056 | 0.68542 | 11.2167 | 11.2167 | 11.3333 | 11.3333 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.045333 | 5.32 | 90.9891
2021 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21319 | 0.775 | 13.4833 | BLK1 |  |  | INV8 |  |  | BLK1INV8 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.21319 | 0.67361 | 0.67361 | 0.68681 | 11.05 | 11.05 | 11.3667 | 11.3667 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.045467 | 5.41 | 92.5284
2022 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21319 | 0.775 | 13.4833 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 22.5 | 0.45% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.21319 | 0.67361 | 0.67361 | 0.69653 | 11.05 | 11.05 | 11.6 | 11.6 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.0522 | 5.46 | 93.3835
2023 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21319 | 0.775 | 13.4833 | BLK2 |  |  | INV20 |  |  | BLK2INV20 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.21319 | 0.68056 | 0.68056 | 0.69931 | 11.2167 | 11.2167 | 11.6667 | 11.6667 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.046667 | 5.51 | 94.2387
2024 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21319 | 0.775 | 13.4833 | BLK2 |  |  | INV17 |  |  | BLK2INV17 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.21319 | 0.68889 | 0.68889 | 0.70278 | 11.4167 | 11.4167 | 11.75 | 11.75 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.047 | 5.59 | 95.6069
2025 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21319 | 0.775 | 13.4833 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 22.5 | 0.4167% | String |  | MC4 Connecto found open Same is restored after verfying the load | 0.21319 | 0.69722 | 0.69722 | 0.70556 | 11.6167 | 11.6167 | 11.8167 | 11.8167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.049236 | 6.12 | 104.6716
2026 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21319 | 0.775 | 13.4833 | BLK2 |  |  | INV16 |  |  | BLK2INV16 | 22.5 | 0.4333% | String |  | MC4 connector failure | 0.21319 | 0.70556 | 0.70556 | 0.71389 | 11.8167 | 11.8167 | 12.0167 | 12.0167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.052072 | 6.18 | 105.6978
2027 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21319 | 0.775 | 13.4833 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 22.5 | 0.3333% | String |  | MC4 connector failure | 0.21319 | 0.70833 | 0.70833 | 0.71736 | 11.8833 | 11.8833 | 12.1 | 12.1 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.040333 | 6.26 | 107.0661
2028 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK3 |  |  | INV24 |  |  | BLK3INV24 | 22.5 | 0.4% | String |  | MC4 Connecto found open | 0.21389 | 0.42431 | 0.42431 | 0.43403 | 5.05 | 5.05 | 5.2833 | 5.2833 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.021133 | 0.95 | 16.248
2029 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22.5 | 0.3955% | String |  | MC4 Connecto found open | 0.21389 | 0.43056 | 0.43056 | 0.44792 | 5.2 | 5.2 | 5.6167 | 5.6167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.022214 | 1.2 | 20.5238
2030 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 22.5 | 0.3955% | String |  | MC4 Connecto found open | 0.21389 | 0.45972 | 0.45972 | 0.46528 | 5.9 | 5.9 | 6.0333 | 6.0333 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.023862 | 1.47 | 25.1417
2031 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK8 |  |  | INV10 |  |  | BLK8INV10 | 22.5 | 0.45% | String |  | MC4 Connecto found open | 0.21389 | 0.45972 | 0.45972 | 0.47917 | 5.9 | 5.9 | 6.3667 | 6.3667 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.02865 | 1.88 | 32.154
2032 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 22.5 | 0.4% | String |  | Y connector & fuse failure so replaced it with new one | 0.21389 | 0.49653 | 0.49653 | 0.50694 | 6.7833 | 6.7833 | 7.0333 | 7.0333 | Y connector & fuse failure so replaced it with new one | closed | 0.028133 | 2.29 | 39.1663
2033 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 22.5 | 0.4% | String |  | Y connector & fuse failure so replaced it with new one | 0.21389 | 0.49653 | 0.49653 | 0.51389 | 6.7833 | 6.7833 | 7.2 | 7.2 | Y connector & fuse failure so replaced it with new one | closed | 0.0288 | 2.77 | 47.3759
2034 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK1 |  |  | INV31 |  |  | BLK1INV31 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 0.21389 | 0.375 | 0.67361 | 0.68056 | 3.8667 | 11.0333 | 11.2 | 11.2 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.0504 | 5.88 | 99.4495
2035 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 0.21389 | 0.375 | 0.69444 | 0.70486 | 3.8667 | 11.5333 | 11.7833 | 11.7833 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.053025 | 5.88 | 99.4495
2036 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 0.21389 | 0.375 | 0.375 | 0.40625 | 3.8667 | 3.8667 | 4.6167 | 4.6167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.020775 | 1.19 | 20.1267
2037 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 0.21389 | 0.38889 | 0.38889 | 0.41319 | 4.2 | 4.2 | 4.7833 | 4.7833 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.021525 | 1.22 | 20.6341
2038 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK5 |  |  | INV2 |  |  | BLK5INV2 | 22.25 | 0.4% | String |  | MC4 Connecto found open | 0.21389 | 0.41667 | 0.41667 | 0.42708 | 4.8667 | 4.8667 | 5.1167 | 5.1167 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.020467 | 1.78 | 30.1054
2039 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 0.21389 | 0.42361 | 0.42361 | 0.44097 | 5.0333 | 5.0333 | 5.45 | 5.45 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.024525 | 2.76 | 46.6804
2040 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK5 |  |  | INV12 |  |  | BLK5INV12 | 22.25 | 0.4285% | String |  | MC4 Connecto found open | 0.21389 | 0.45833 | 0.45833 | 0.46528 | 5.8667 | 5.8667 | 6.0333 | 6.0333 | MC4 Connecto found open Same is restored after verfying the load | closed | 0.025851 | 2.98 | 50.4013
2041 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK4 |  |  | INV1 |  |  | BLK4INV1 | 22.25 | 0.45% | String |  | During String current measurement activity we have observed that String-12 is grounded | 0.21389 | 0.50347 | 0.50347 | 0.51042 | 6.95 | 6.95 | 7.1167 | 7.1167 | During String current measurement activity we have observed that String-12 is grounded, so replaced with new one. | closed | 0.032025 | 3.55 | 60.0418
2042 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK3 |  |  | INV24 |  |  | BLK3INV24 | 22.25 | 0.4% | String |  | MC4 Connector melted | 0.21389 | 0.62847 | 0.62847 | 0.63194 | 9.95 | 9.95 | 10.0333 | 10.0333 | MC4 Connector melted so replace it with new one | closed | 0.040133 | 5.11 | 86.4263
2043 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK2 |  |  | INV3 |  |  | BLK2INV3 | 22.25 | 0.1667% | String |  | fuse failure | 0.21389 | 0.63194 | 0.63194 | 0.64583 | 10.0333 | 10.0333 | 10.3667 | 10.3667 | fuse failure so replaced it with new one | closed | 0.017278 | 5.45 | 92.1768
2044 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.775 | 13.4667 | BLK2 |  |  | INV17 |  |  | BLK2INV17 | 22.25 | 0.4% | String |  | MC4 Connector found open | 0.21389 | 0.63889 | 0.63889 | 0.66319 | 10.2 | 10.2 | 10.7833 | 10.7833 | MC4 Connecto found open Same is restored after verfying the load[@[Action taken]] | closed | 0.043133 | 6.11 | 103.3395
2045 | 2025-06-10 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21458 | 0.77639 | 13.4833 | BLK8 |  |  | INV26 |  |  | BLK8INV26 | 271.35 | 0.4065% | Inverter |  | Inv Shut down on the fault of 47 (Relay Card Faulty) | 0.37153 | 0.375 | 0.39931 | 0.47569 | 0.083333 | 0.66667 | 2.5 | 2.5 | after discussion with OEM we replaced the Inv with a new one | closed | 0.010163 | 0.746 | 153.8735
2046 | 2025-06-14 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21389 | 0.77986 | 13.5833 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 264 | 0.3955% | Inverter |  | INVERTER SHUT DOWN on fault of excessive leakage current, restore | 0.32292 | 0.32639 | 0.33681 | 0.34861 | 0.083333 | 0.33333 | 0.61667 | 0.61667 | after checking the all strin found string no 4 &11 floating is not ok, after rectification connected the string & restore | closed | 0.002439 | 0.186 | 37.326
2047 | 2025-06-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21875 | 0.77014 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.51736 | 0.51736 | 0.51875 | 0.52014 | 0 | 0.033333 | 0.066667 | 0.066667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0083333 | 0.0371 | 250.1483
2048 | 2025-06-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21875 | 0.77014 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.51667 | 0.51667 | 0.51944 | 0.52014 | 0 | 0.066667 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011067 | 0.0371 | 253.1348
2049 | 2025-06-16 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.25903 | 0.74514 | 11.6667 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.53611 | 0.53611 | 0.53889 | 0.53958 | 0 | 0.066667 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.010417 | 0.075 | 505.6905
2050 | 2025-06-16 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21875 | 0.77014 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.49653 | 0.49653 | 0.49861 | 0.49931 | 0 | 0.05 | 0.066667 | 0.066667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0088537 | 0.112 | 764.1804
2051 | 2025-06-18 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 | 0.77361 | 13.4667 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.49097 | 0.49097 | 0.49444 | 0.49444 | 0 | 0.083333 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.010417 | 0.101 | 640.5864
2052 | 2025-06-18 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 | 0.77361 | 13.4667 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.5375 | 0.5375 | 0.54028 | 0.54028 | 0 | 0.066667 | 0.066667 | 0.066667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.0088537 | 0.069 | 464.9547
2053 | 2025-06-18 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 | 0.77361 | 13.4667 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 22.25 | 0.3333% | Inverter |  | Inv tripped on fault of string back fedded current | 0.49444 | 0.49444 | 0.5 | 0.51806 | 0 | 0.13333 | 0.56667 | 0.56667 | we have physically checked all parameter of this inverter & string's then we found that all string are healthy same is store. | closed | 0.0018889 | 0.559 | 9.4545
2054 | 2025-06-18 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.2125 | 0.77361 | 13.4667 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | Inverter |  | INV tripped on fault of excessive leakage current | 0.41667 | 0.41806 | 0.42361 | 0.4375 | 0.033333 | 0.16667 | 0.5 | 0.5 | we have physically checked all parameter of this inverter & string's then we found that string no-4,9,11 MC4 Connector Positive & negative was failure same is restored after replaced it new one. | closed | 0.002 | 0.219 | 44.4478
2055 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.225 | 0.74306 | 12.4333 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | Inverter |  | INV tripped on fault of excessive leakage current | 0.33889 | 0.34028 | 0.34722 | 0.37708 | 0.033333 | 0.2 | 0.91667 | 0.91667 | we have physically checked all parameter of this inverter & string's then we found that string no-6,10, MC4 Connector Positive & negative was failure same is restored after replaced it new one. | closed | 0.0036667 | 0.217 | 44.0419
2056 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.225 | 0.74306 | 12.4333 | BLK4 |  |  | MVP |  |  | BLK4MVP | 8655.25 | 12.97% | IDT |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 0.71111 | 0.71111 | 0.34722 | 0.92083 | 0 | -8.7333 | 5.0333 | 5.0333 | after checking the all parameters & verifying the load charge the IDT | closed | 0.65266 | 0 | 0
2057 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.225 | 0.74306 | 12.4333 | BLK4 | LT1 | ACCB1 |  |  |  | BLK4LT1ACCB1 | 534 | 0.8% | ACCB |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 0.71111 | 0.71111 | 0.34722 |  | 0 | -8.7333 | -17.0667 | -17.0667 | MCCB meggaring value is not good | closed | -0.13653 | 0 | 0
2058 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.225 | 0.74306 | 12.4333 | BLK4 | LT1 | ACCB2 |  |  |  | BLK4LT1ACCB2 | 534 | 0.8% | ACCB |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 0.71111 | 0.71111 | 0.34722 | 0.94375 | 0 | -8.7333 | 5.5833 | 5.5833 | After checking the all paramerters & meggaring the MCCB & found MCCB Healthy same is restore | closed | 0.044667 | 0 | 0
2059 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.225 | 0.74306 | 12.4333 | BLK4 | LT1 | ACCB5 |  |  |  | BLK4LT1ACCB5 | 567.375 | 0.85% | ACCB |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 0.71111 | 0.71111 | 0.34722 | 0.94375 | 0 | -8.7333 | 5.5833 | 5.5833 | MCCB meggaring value is not good | closed | 0.047458 | 0 | 0
2060 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.225 | 0.74306 | 12.4333 | BLK4 | LT1 | ACCB6 |  |  |  | BLK4LT1ACCB6 | 567.375 | 0.85% | ACCB |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 0.71111 | 0.71111 | 0.34722 | 0.47917 | 0 | -8.7333 | -5.5667 | -5.5667 | After checking the all paramerters & meggaring the MCCB & found MCCB Healthy same is restore | closed | -0.047317 | 0 | 0
2061 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK4 |  |  | INV1 |  |  | BLK4INV1 | 300.375 | 0.45% | Inverter |  | Due to Block-4 Inverter failure this impact 500 Amp MCCB of this inverter also failure. | 0.23958 | 0.23958 | 0.78125 | 0.83333 | 0 | 13 | 14.25 | 14.25 | It will be restored after rectification of MCCB or Replacment of MCCB. | closed | 0.064125 | 2.4 | 547.9868
2062 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | Due to Block-4 Inverter failure this impact 500 Amp MCCB of this inverter also failure. | 0.23958 | 0.23958 | 0.78125 | 0.83333 | 0 | 13 | 14.25 | 14.25 | It will be restored after rectification of MCCB or Replacment of MCCB. | closed | 0.057 | 2.4 | 487.0994
2063 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK4 |  |  | INV11 |  |  | BLK4INV11 | 300.375 | 0.45% | Inverter |  | Block-4 Inverter No-11 IGBT Failure , it was restored after MCCB replacment work. | 0.23958 | 0.23958 |  |  | 0 | -5.75 | -5.75 | -5.75 | Block-4 Inverter No-11 IGBT Failure , it was restored after MCCB replacment work. | closed | -0.025875 | 2.4 | 547.9868
2064 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK4 |  |  | INV12 |  |  | BLK4INV12 | 267 | 0.4% | Inverter |  | Due to Block-4 Inverter failure this impact 500 Amp MCCB of this inverter also failure. | 0.23958 | 0.23958 |  |  | 0 | -5.75 | -5.75 | -5.75 | It will be restored after rectification of MCCB or Replacment of MCCB. | closed | -0.023 | 2.4 | 487.0994
2065 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 267 | 0.4% | string |  | As per observation we observed that String no -13 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 0.23958 | 0.31597 | 0.4375 | 0.44792 | 1.8333 | 4.75 | 5 | 5 | During VOC we got string no 13 DC cable shorted so isolated the string & charge | closed | 0.02 | 0.64 | 129.8932
2066 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 300.375 | 0.45% | string |  | As per observation we observed that String no -13 &14 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 0.23958 | 0.31597 | 0.45139 | 0.46528 | 1.8333 | 5.0833 | 5.4167 | 5.4167 | During VOC we got string no 13 & 14 DC cable shorted so isolated the string & charge | closed | 0.024375 | 0.827 | 188.8271
2067 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 278.125 | 0.4167% | string |  | As per observation we observed that String no -9 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 0.23958 | 0.31597 | 0.48958 | 0.50417 | 1.8333 | 6 | 6.35 | 6.35 | During VOC we got string np 9 faulty so isolated this string & charge | closed | 0.026458 | 1.26 | 266.3825
2068 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK1 |  |  | INV18 |  |  | BLK1INV18 | 267 | 0.4% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.37153 | 0.38819 | 1.8333 | 3.1667 | 3.5667 | 3.5667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.014267 | 0.236 | 47.8981
2069 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 300.375 | 0.45% | string |  | As per observation we observed that String no -13 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 0.23958 | 0.31597 | 0.46875 | 0.4875 | 1.8333 | 5.5 | 5.95 | 5.95 | As per observation we observed that String no -13 was grounded due to this inverter was in breakdown on exxcusive leakage current. | closed | 0.026775 | 1.03 | 235.1777
2070 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 222.5 | 0.3333% | string |  | As per observation we observed that String no -5 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 0.23958 | 0.31597 | 0.47917 | 0.49722 | 1.8333 | 5.75 | 6.1833 | 6.1833 | As per observation we observed that String no -5 was grounded due to this inverter was in breakdown on exxcusive leakage current. | closed | 0.020611 | 1.51 | 255.3889
2071 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK2 |  |  | INV9 |  |  | BLK2INV9 | 267 | 0.4% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.375 | 0.39167 | 1.8333 | 3.25 | 3.65 | 3.65 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.0146 | 0.267 | 54.1898
2072 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 267 | 0.4% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.36111 | 0.38194 | 1.8333 | 2.9167 | 3.4167 | 3.4167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.013667 | 0.203 | 41.2005
2073 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 278.125 | 0.4167% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.44097 | 0.46111 | 1.8333 | 4.8333 | 5.3167 | 5.3167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.022153 | 0.781 | 165.1148
2074 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 239.25 | 0.3584% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.36806 | 0.38611 | 1.8333 | 3.0833 | 3.5167 | 3.5167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.012605 | 0.222 | 40.3738
2075 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK3 |  |  | INV18 |  |  | BLK3INV18 | 267 | 0.4% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.37847 | 0.39722 | 1.8333 | 3.3333 | 3.7833 | 3.7833 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.015133 | 0.314 | 63.7288
2076 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK5 |  |  | INV4 |  |  | BLK5INV4 | 300.375 | 0.45% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.46875 | 0.48611 | 1.8333 | 5.5 | 5.9167 | 5.9167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.026625 | 1.021 | 233.1227
2077 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK5 |  |  | INV26 |  |  | BLK5INV26 | 289.25 | 0.4333% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.38889 | 0.40486 | 1.8333 | 3.5833 | 3.9667 | 3.9667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.017189 | 0.361 | 79.3735
2078 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 297 | 0.4449% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.35764 | 0.375 | 1.8333 | 2.8333 | 3.25 | 3.25 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.014461 | 0.189 | 42.6691
2079 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK6 |  |  | INV9 |  |  | BLK6INV9 | 275 | 0.412% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.37847 | 0.39236 | 1.8333 | 3.3333 | 3.6667 | 3.6667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.015106 | 0.27 | 56.4406
2080 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 264 | 0.3955% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.39583 | 0.41319 | 1.8333 | 3.75 | 4.1667 | 4.1667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.016479 | 0.414 | 83.0805
2081 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK6 |  |  | INV11 |  |  | BLK6INV11 | 297 | 0.4449% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.41667 | 0.4375 | 1.8333 | 4.25 | 4.75 | 4.75 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.021135 | 0.527 | 118.9768
2082 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK6 |  |  | INV15 |  |  | BLK6INV15 | 275 | 0.412% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.44444 | 0.45972 | 1.8333 | 4.9167 | 5.2833 | 5.2833 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.021767 | 0.766 | 160.124
2083 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK6 |  |  | INV16 |  |  | BLK6INV16 | 297 | 0.4449% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.4375 | 0.45139 | 1.8333 | 4.75 | 5.0833 | 5.0833 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.022618 | 0.663 | 149.6804
2084 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK6 |  |  | INV23 |  |  | BLK6INV23 | 264 | 0.3955% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.39583 | 0.40903 | 1.8333 | 3.75 | 4.0667 | 4.0667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.016084 | 0.388 | 77.8629
2085 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK6 |  |  | INV24 |  |  | BLK6INV24 | 286 | 0.4285% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.40625 | 0.42778 | 1.8333 | 4 | 4.5167 | 4.5167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.019352 | 0.475 | 103.2654
2086 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK6 |  |  | INV31 |  |  | BLK6INV31 | 275 | 0.412% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.39583 | 0.4125 | 1.8333 | 3.75 | 4.15 | 4.15 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.017097 | 0.411 | 85.9151
2087 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK6 |  |  | INV32 |  |  | BLK6INV32 | 275 | 0.412% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.39861 | 0.41875 | 1.8333 | 3.8167 | 4.3 | 4.3 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.017715 | 0.432 | 90.3049
2088 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 264 | 0.3955% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.23958 | 0.31597 | 0.41667 | 0.43264 | 1.8333 | 4.25 | 4.6333 | 4.6333 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.018325 | 0.499 | 100.1381
2089 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK7 |  |  | INV26 |  |  | BLK7INV26 | 300.375 | 0.45% | string |  | As per observation we observed that String no -1,10 & 12 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 0.23958 | 0.31597 | 0.44792 | 0.46528 | 1.8333 | 5 | 5.4167 | 5.4167 | As per observation we observed that String no -1,10 & 12 was grounded due to this inverter was in breakdown on exxcusive leakage current. | closed | 0.024375 | 0.826 | 188.5988
2090 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.23958 | 0.31597 |  | 0.77917 | 1.8333 | -5.75 | 12.95 | 12.95 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0518 | 2.4 | 21.8921
2091 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.23958 | 0.31597 |  | 0.77917 | 1.8333 | -5.75 | 12.95 | 12.95 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.058275 | 2.4 | 40.5916
2092 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.23958 | 0.31597 |  | 0.77917 | 1.8333 | -5.75 | 12.95 | 12.95 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.058275 | 2.4 | 21.8921
2093 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 22.25 | 0.4167% | string |  | 1 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | 0.23958 | 0.31597 | 0.49306 | 0.50694 | 1.8333 | 6.0833 | 6.4167 | 6.4167 | 1 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | closed | 0.026736 | 1.303 | 22.0379
2094 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 22.25 | 0.3333% | string |  | 1 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | 0.23958 | 0.31597 | 0.49306 | 0.50694 | 1.8333 | 6.0833 | 6.4167 | 6.4167 | 1 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | closed | 0.021389 | 1.303 | 22.0379
2095 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22708 | 0.77917 | 13.25 | BLK7 |  |  | INV26 |  |  | BLK7INV26 | 66.75 | 0.45% | string |  | 3 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | 0.23958 | 0.31597 | 0.46181 | 0.47917 | 1.8333 | 5.3333 | 5.75 | 5.75 | 3 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | closed | 0.025875 | 0.951 | 48.2533
2096 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 0.77014 | 13.3167 | BLK3 |  |  | INV16 |  |  | BLK3INV16 | 267 | 0.4% | Inverter |  | During morning after few time of plant start Block-3 inverter-16 Shut down on fault of ecxcessive leakage current, When Done VOC we got that String NO. 8 yconnector & fuse was failure so replace it with new one, restore | 0.29861 | 0.30208 | 0.37639 | 0.39375 | 0.083333 | 1.8667 | 2.2833 | 2.2833 | During morning after few time of plant start Block-3 inverter-16 Shut down on fault of ecxcessive leakage current, When Done VOC we got that String NO. 8 yconnector & fuse was failure so replace it with new one, restore | closed | 0.0091333 | 0.585 | 118.7305
2097 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 0.77014 | 13.3167 | BLK4 |  |  | INV12 |  |  | BLK4INV12 | 267 | 0.4% | Inverter |  | During morning after few time of plant start Block-4 inverter-12 shut down on fault of ecxcessive leakage current, When Done VOC we got that String NO. 13 MC4 connector & fuse was failure so replace it with new one, restore | 0.22431 | 0.22569 | 0.375 | 0.39097 | 0.033333 | 3.6167 | 4 | 4 | During morning after few time of plant start Block-4 inverter-12 shut down on fault of ecxcessive leakage current, When Done VOC we got that String NO. 13 MC4 connector & fuse was failure so replace it with new one, restore | closed | 0.016 | 0.911 | 184.8948
2098 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 0.77014 | 13.3167 | BLK6 |  |  | INV15 |  |  | BLK6INV15 | 275 | 0.412% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.29167 | 0.29861 | 0.31597 | 0.3375 | 0.16667 | 0.58333 | 1.1 | 1.1 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0045318 | 0.341 | 71.2824
2099 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 0.77014 | 13.3167 | BLK4 |  |  | INV11 |  |  | BLK4INV11 | 300.375 | 0.45% | Inverter |  | Restoretion of Inverter & 250 Amp MCCB, after verifying the all parameter connect the same | 0.22431 | 0.22569 | 0.36458 | 0.38403 | 0.033333 | 3.3667 | 3.8333 | 3.8333 | Restoretion of Inverter & 250 Amp MCCB, after verifying the all parameter connect the same | closed | 0.01725 | 0.834 | 190.4254
2100 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 0.77014 | 13.3167 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.50347 | 0.50417 | 0.50486 | 0.50694 | 0.016667 | 0.033333 | 0.083333 | 0.083333 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011167 | 0.102 | 693.5077
2101 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 0.77014 | 13.3167 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.50139 | 0.50208 | 0.50417 | 0.50486 | 0.016667 | 0.066667 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.010417 | 0.104 | 659.6137
2102 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 0.77014 | 13.3167 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.51042 | 0.51111 | 0.51319 | 0.51389 | 0.016667 | 0.066667 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011067 | 0.112 | 754.7091
2103 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 0.77014 | 13.3167 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.23958 | 0.23958 |  | 0.77014 | 0 | -5.75 | 12.7333 | 12.7333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.050933 | 5.19 | 47.3417
2104 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 0.77014 | 13.3167 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.23958 | 0.23958 |  | 0.77014 | 0 | -5.75 | 12.7333 | 12.7333 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0573 | 5.19 | 87.7794
2105 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21528 | 0.77014 | 13.3167 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.23958 | 0.23958 |  | 0.77014 | 0 | -5.75 | 12.7333 | 12.7333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0573 | 5.19 | 47.3417
2106 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.20764 | 0.75833 | 13.2167 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 0.29097 | 0.29514 | 0.30556 | 0.34375 | 0.1 | 0.35 | 1.2667 | 1.2667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.0050667 | 0.42 | 85.2424
2107 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.20764 | 0.75833 | 13.2167 | BLK5 |  |  | INV20 |  |  | BLK5INV20 | 22.25 | 0.4% | string |  | During morining string checking we got that 1 string MC4 connector open, same restore | 0.20764 | 0.375 | 0.40972 | 0.42361 | 4.0167 | 4.85 | 5.1833 | 5.1833 | During morining string checking we got that 1 string MC4 connector open, same restore | closed | 0.020733 | 1.135 | 19.1965
2108 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.20764 | 0.75833 | 13.2167 | BLK6 |  |  | INV32 |  |  | BLK6INV32 | 22.25 | 0.412% | string |  | During morining string checking we got that 1 string MC4 connector open, same restore | 0.20764 | 0.375 | 0.41667 | 0.4375 | 4.0167 | 5.0167 | 5.5167 | 5.5167 | During morining string checking we got that 1 string MC4 connector open, same restore | closed | 0.022728 | 1.219 | 20.6172
2109 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.20764 | 0.75833 | 13.2167 | BLK4 |  |  | INV17 |  |  | BLK4INV17 | 22.25 | 0.4333% | string |  | Morning string checking found that String no 9 , Y connector, fuse & MC4 connector melted | 0.20764 | 0.375 | 0.43403 | 0.44792 | 4.0167 | 5.4333 | 5.7667 | 5.7667 | Morning string checking found that String no 9 , Y connector, fuse & MC4 connector melted, so replace it with new one, restored | closed | 0.024989 | 1.663 | 28.1266
2110 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.20764 | 0.75833 | 13.2167 | BLK4 |  |  | INV12 |  |  | BLK4INV12 | 12 | 0.4% | string |  | Morning string checking found that String no 13 MC4 connector melted | 0.20764 | 0.375 | 0.43958 | 0.45139 | 4.0167 | 5.5667 | 5.85 | 5.85 | Morning string checking found that String no 13 MC4 connector melted, same is replace it with new one, restored | closed | 0.0234 | 1.717 | 15.662
2111 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.20764 | 0.75833 | 13.2167 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.20764 |  |  | 0.75833 | -4.9833 | -4.9833 | 13.2167 | 13.2167 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.052867 | 5.3 | 48.3451
2112 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.20764 | 0.75833 | 13.2167 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.20764 |  |  | 0.75833 | -4.9833 | -4.9833 | 13.2167 | 13.2167 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.059475 | 5.3 | 89.6398
2113 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.20764 | 0.75833 | 13.2167 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.20764 |  |  | 0.75833 | -4.9833 | -4.9833 | 13.2167 | 13.2167 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.059475 | 5.3 | 48.3451
2114 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 278.125 | 0.4167% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22917 | 0.28819 | 0.3125 | 0.34375 | 1.4167 | 2 | 2.75 | 2.75 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.011458 | 0.222 | 46.9341
2115 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22917 | 0.28819 | 0.33333 | 0.35417 | 1.4167 | 2.5 | 3 | 3 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.012 | 0.293 | 59.4667
2116 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 278.125 | 0.4167% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22917 | 0.28819 | 0.34375 | 0.36458 | 1.4167 | 2.75 | 3.25 | 3.25 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.013542 | 0.37 | 78.2234
2117 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | During morning after few time of plant start Block-4 inverter-2 shut down on fault of ecxcessive leakage current & fault 47, When Done VOC we got that String NO. 12 MC4 connector & fuse was failure so replace it with new one & also share Log file of Inverter to OEm after got permission from OEM reset it, restore | 0.22917 | 0.28819 | 0.4375 | 0.45833 | 1.4167 | 5 | 5.5 | 5.5 | During morning after few time of plant start Block-4 inverter-2 shut down on fault of ecxcessive leakage current & fault 47, When Done VOC we got that String NO. 12 MC4 connector & fuse was failure so replace it with new one & also share Log file of Inverter to OEm after got permission from OEM reset it, restore | closed | 0.022 | 1.656 | 336.0986
2118 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK4 |  |  | INV22 |  |  | BLK4INV22 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22917 | 0.28819 | 0.33681 | 0.35069 | 1.4167 | 2.5833 | 2.9167 | 2.9167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.011667 | 0.269 | 54.5957
2119 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK6 |  |  | INV5 |  |  | BLK6INV5 | 264 | 0.3955% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22917 | 0.28819 | 0.30208 | 0.32292 | 1.4167 | 1.75 | 2.25 | 2.25 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0088989 | 0.132 | 26.4894
2120 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 297 | 0.4449% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22917 | 0.28819 | 0.36458 | 0.38542 | 1.4167 | 3.25 | 3.75 | 3.75 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.016685 | 0.564 | 127.33
2121 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 264 | 0.3955% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22917 | 0.28819 | 0.375 | 0.39236 | 1.4167 | 3.5 | 3.9167 | 3.9167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.015491 | 0.639 | 128.233
2122 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK6 |  |  | INV31 |  |  | BLK6INV31 | 275 | 0.412% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22917 | 0.28819 | 0.31944 | 0.34028 | 1.4167 | 2.1667 | 2.6667 | 2.6667 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.010986 | 0.203 | 42.435
2123 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK7 |  |  | INV12 |  |  | BLK7INV12 | 270.6 | 0.4054% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22917 | 0.28819 | 0.34028 | 0.35764 | 1.4167 | 2.6667 | 3.0833 | 3.0833 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0125 | 0.319 | 65.6166
2124 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK7 |  |  | INV17 |  |  | BLK7INV17 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22917 | 0.28819 | 0.36806 | 0.38542 | 1.4167 | 3.3333 | 3.75 | 3.75 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.015 | 0.563 | 114.2654
2125 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK5 |  |  | INV11 |  |  | BLK5INV11 | 286 | 0.4285% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22917 | 0.28819 | 0.45833 | 0.47917 | 1.4167 | 5.5 | 6 | 6 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.025708 | 1.881 | 408.9309
2126 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.22917 |  |  | 0.77083 | -5.5 | -5.5 | 13 | 13 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.052 | 4.58 | 41.7774
2127 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.3 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.22917 |  |  | 0.77083 | -5.5 | -5.5 | 13 | 13 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0585 | 4.58 | 77.6364
2128 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21667 | 0.77083 | 13.3 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.22917 |  |  | 0.77083 | -5.5 | -5.5 | 13 | 13 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0585 | 4.58 | 41.7774
2129 | 2025-06-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21597 | 0.77153 | 13.3333 | Blk4 |  |  | INV13 |  |  | Blk4INV13 | 300.375 | 0.45% | Inverter |  | Block-4 inverter 13 failure on fault of 1616 & 21 in morning, after sharing the log file to OEM, inverter has been replaced with spare one | 0.21597 | 0.25 | 0.5 | 0.53403 | 0.81667 | 6.8167 | 7.6333 | 7.6333 | Block-4 inverter 13 failure on fault of 1616 & 21 in morning, after sharing the log file to OEM, inverter has been replaced with spare one | closed | 0.03435 | 3.4 | 776.3146
2130 | 2025-06-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21597 | 0.77153 | 13.3333 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21597 |  |  | 0.77153 | -5.1833 | -5.1833 | 13.3333 | 13.3333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.053333 | 6.46 | 58.9263
2131 | 2025-06-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21597 | 0.77153 | 13.3333 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21597 |  |  | 0.77153 | -5.1833 | -5.1833 | 13.3333 | 13.3333 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.06 | 6.46 | 109.2591
2132 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21597 | 0.78472 | 13.65 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21597 |  |  | 0.78472 | -5.1833 | -5.1833 | 13.65 | 13.65 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0546 | 6.18 | 56.3722
2133 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21597 | 0.78472 | 13.65 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21597 |  |  | 0.78472 | -5.1833 | -5.1833 | 13.65 | 13.65 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.061425 | 6.18 | 104.5234
2134 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21806 | 0.77778 | 13.4333 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21806 |  |  | 0.77778 | -5.2333 | -5.2333 | 13.4333 | 13.4333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.053733 | 6.3 | 57.4668
2135 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21806 | 0.77778 | 13.4333 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21806 |  |  | 0.77778 | -5.2333 | -5.2333 | 13.4333 | 13.4333 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.06045 | 6.3 | 106.553
2136 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.21806 | 0.77778 | 13.4333 | BLK4 |  |  | INV11 |  |  | BLK4INV11 | 300.375 | 0.45% | Inverter |  | As per obsservation we found that Block-4 Inverter11 running with derating generation, after Discussion with Oem & sharing Log file to OEM, they instructed to change control card, After changing the Control card now its under observation | 0.67708 | 0.67708 | 0.6875 | 0.75347 | 0 | 0.25 | 1.8333 | 1.8333 | As per obsservation we found that Block-4 Inverter11 running with derating generation, after Discussion with Oem & sharing Log file to OEM, they instructed to change control card, After changing the Control card now its under observation | closed | 0.00825 | 0.513 | 117.1322
2137 | 2025-06-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 |  |  | 0 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21806 |  |  | 0.77778 | -5.2333 | -5.2333 | 13.4333 | 13.4333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.053733 | 6.3 | 57.4668
2138 | 2025-06-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 |  |  | 0 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21806 |  |  | 0.77778 | -5.2333 | -5.2333 | 13.4333 | 13.4333 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.06045 | 6.3 | 58.664
2139 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.24167 | 0.77847 | 12.8833 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | Inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 0.24167 | 0.29167 | 0.39583 | 0.77847 | 1.2 | 3.7 | 12.8833 | 12.8833 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | closed | 0.036739 | 5.64 | 816.0693
2140 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.24167 | 0.77847 | 12.8833 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | Inverter shutdown in morining on fault of excessive leakage current, after removing the faulty string inverter fault reset, restore | 0.24167 | 0.29167 | 0.38194 | 0.39931 | 1.2 | 3.3667 | 3.7833 | 3.7833 | Inverter shutdown in morining on fault of excessive leakage current, after removing the faulty string inverter fault reset, restore | closed | 0.015133 | 1.025 | 208.032
2141 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.24167 | 0.77847 | 12.8833 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | 0.73958 | 0.73958 | 0.74306 | 0.77847 | 0 | 0.083333 | 0.93333 | 0.93333 | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | closed | 0.0037333 | 0.0961 | 19.5043
2142 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.24167 | 0.77847 | 12.8833 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.24167 |  |  | 0.77847 | -5.8 | -5.8 | 12.8833 | 12.8833 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.051533 | 5.64 | 51.4464
2143 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.24167 | 0.77847 | 12.8833 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.24167 |  |  | 0.77847 | -5.8 | -5.8 | 12.8833 | 12.8833 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.057975 | 5.64 | 95.3903
2144 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.24167 | 0.77847 | 12.8833 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.52569 | 0.52569 | 0.52847 | 0.52917 | 0 | 0.066667 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.010417 | 0.097 | 615.2166
2145 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22639 | 0.77014 | 13.05 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.22639 |  |  | 0.77014 | -5.4333 | -5.4333 | 13.05 | 13.05 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0522 | 4.65 | 42.416
2146 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22639 | 0.77014 | 13.05 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.22639 |  |  | 0.77014 | -5.4333 | -5.4333 | 13.05 | 13.05 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.058725 | 4.65 | 78.6462
2147 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22639 | 0.77014 | 13.05 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 300.375 | 0.45% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22639 | 0.25694 | 0.30208 | 0.31597 | 0.73333 | 1.8167 | 2.15 | 2.15 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.009675 | 0.189 | 43.154
2148 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22639 | 0.77014 | 13.05 | BLK5 |  |  | INV14 |  |  | BLK5INV14 | 278.125 | 0.4167% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22639 | 0.25694 | 0.30903 | 0.32292 | 0.73333 | 1.9833 | 2.3167 | 2.3167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0096528 | 0.232 | 49.0482
2149 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22639 | 0.77014 | 13.05 | BLK6 |  |  | INV32 |  |  | BLK6INV32 | 275 | 0.412% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22639 | 0.25694 | 0.31944 | 0.34028 | 0.73333 | 2.2333 | 2.7333 | 2.7333 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.011261 | 0.351 | 73.3728
2150 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22639 | 0.77014 | 13.05 | BLK6 |  |  | INV16 |  |  | BLK6INV16 | 297 | 0.4449% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22639 | 0.25694 | 0.34028 | 0.35417 | 0.73333 | 2.7333 | 3.0667 | 3.0667 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.013645 | 0.489 | 110.3978
2151 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22639 | 0.77014 | 13.05 | BLK2 |  |  | INV7 |  |  | BLK2INV7 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22639 | 0.25694 | 0.35069 | 0.36458 | 0.73333 | 2.9833 | 3.3167 | 3.3167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.013267 | 0.455 | 92.3459
2152 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22639 | 0.77014 | 13.05 | BLK3 |  |  | INV30 |  |  | BLK3INV30 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22639 | 0.25694 | 0.28819 | 0.30556 | 0.73333 | 1.4833 | 1.9 | 1.9 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0076 | 0.132 | 26.7905
2153 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22639 | 0.77014 | 13.05 | BLK7 |  |  | INV19 |  |  | BLK7INV19 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.22639 | 0.25694 | 0.36458 | 0.38194 | 0.73333 | 3.3167 | 3.7333 | 3.7333 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.014933 | 0.589 | 119.5423
2154 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22639 | 0.77014 | 13.05 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | 0.22639 |  |  | 0.77014 | -5.4333 | -5.4333 | 13.05 | 13.05 | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | closed | 0.0522 | 4.65 | 943.755
2155 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22639 | 0.77014 | 13.05 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | Inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 0.22639 |  |  | 0.77014 | -5.4333 | -5.4333 | 13.05 | 13.05 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | closed | 0.037214 | 4.65 | 672.8231
2156 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22083 | 0.77014 | 13.1833 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | 0.22083 |  |  | 0.77014 | -5.3 | -5.3 | 13.1833 | 13.1833 | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | closed | 0.052733 | 3.89 | 789.5069
2157 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22083 | 0.77014 | 13.1833 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | Inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 0.22083 |  |  | 0.77014 | -5.3 | -5.3 | 13.1833 | 13.1833 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | closed | 0.037595 | 3.89 | 562.8563
2158 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22083 | 0.77014 | 13.1833 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | String |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.22083 |  |  | 0.77014 | -5.3 | -5.3 | 13.1833 | 13.1833 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.052733 | 3.89 | 35.4835
2159 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22083 | 0.77014 | 13.1833 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | String |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.22083 |  |  | 0.77014 | -5.3 | -5.3 | 13.1833 | 13.1833 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.059325 | 3.89 | 65.7922
2160 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22083 | 0.77014 | 13.1833 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 22.25 | 0.45% | String |  | During String current measurement activity we have observed that String-1 MC4 connector was melted so replace it with spare one. | 0.27778 | 0.29167 | 0.32292 | 0.34375 | 0.33333 | 1.0833 | 1.5833 | 1.5833 | During String current measurement activity we have observed that String-1 MC4 connector was melted so replace it with spare one. | closed | 0.007125 | 0.207 | 3.501
2161 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22083 | 0.77014 | 13.1833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | String |  | During String current measurement activity we have observed that String-10 MC4 connector was melted so replace it with spare one. | 0.27778 | 0.29167 | 0.34375 | 0.36111 | 0.33333 | 1.5833 | 2 | 2 | During String current measurement activity we have observed that String-10 MC4 connector was melted so replace it with spare one. | closed | 0.0079101 | 0.379 | 6.3381
2162 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22083 | 0.77014 | 13.1833 | BLK6 |  |  | INV16 |  |  | BLK6INV16 | 22 | 0.4449% | String |  | During String current measurement activity we have observed that String-5 MC4 connector was melted so replace it with spare one. | 0.27778 | 0.29167 | 0.36111 | 0.375 | 0.33333 | 2 | 2.3333 | 2.3333 | During String current measurement activity we have observed that String-5 MC4 connector was melted so replace it with spare one. | closed | 0.010382 | 0.547 | 9.1476
2163 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22083 | 0.77014 | 13.1833 | BLK2 |  |  | INV12 |  |  | BLK2INV12 | 22.25 | 0.4% | String |  | During String current measurement activity we have observed that String No.-6 MC4 connector was melted so replace it with spare one. | 0.27778 | 0.29167 | 0.38194 | 0.39583 | 0.33333 | 2.5 | 2.8333 | 2.8333 | During String current measurement activity we have observed that String No.-6 MC4 connector was melted so replace it with spare one. | closed | 0.011333 | 0.788 | 13.3276
2164 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22222 | 0.76597 | 13.05 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | String |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.22222 |  |  | 0.76597 | -5.3333 | -5.3333 | 13.05 | 13.05 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0522 | 3.09 | 28.1861
2165 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22222 | 0.76597 | 13.05 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | String |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.22222 |  |  | 0.76597 | -5.3333 | -5.3333 | 13.05 | 13.05 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.058725 | 3.09 | 28.1861
2166 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22222 | 0.76597 | 13.05 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | inverter |  | Inverter IGBT was failure so replace it with spare one | 0.22222 | 0.16319 | 0.17014 | 0.19861 | -1.4167 | -1.25 | -0.56667 | -0.56667 | Inverter IGBT was failure so replace it with spare one | closed | -0.0022667 | 2.79 | 566.253
2167 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22222 | 0.76597 | 13.05 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 0.22222 |  |  | 0.76597 | -5.3333 | -5.3333 | 13.05 | 13.05 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | closed | 0.037214 | 3.09 | 447.1018
2168 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22222 | 0.76597 | 13.05 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | String |  | String no. 13 load shifted to string no. 14 & string no. 6 splited to 2 half string, now restore | 0.22222 | 0.29167 | 0.29861 | 0.30903 | 1.6667 | 1.8333 | 2.0833 | 2.0833 | String no. 13 load shifted to string no. 14 & string no. 6 splited to 2 half string, now restore | closed | 0.009375 | 0.075 | 0.68413
2169 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22222 | 0.76597 | 13.05 | BLK6 |  |  | INV31 |  |  | BLK6INV31 | 275 | 0.412% | String |  | During string monitoring found string no. 1 shows ground fault, rectified now restore | 0.22222 | 0.29167 | 0.31597 | 0.32986 | 1.6667 | 2.25 | 2.5833 | 2.5833 | During string monitoring found string no. 1 shows ground fault, rectified now restore | closed | 0.010643 | 0.121 | 25.2937
2170 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22222 | 0.76597 | 13.05 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 44 | 0.3955% | String |  | During string monitoring found string no. 3& 6 in ground fault now rectified & restore | 0.22222 | 0.29167 | 0.34028 | 0.35417 | 1.6667 | 2.8333 | 3.1667 | 3.1667 | During string monitoring found string no. 3& 6 in ground fault now rectified & restore | closed | 0.012524 | 0.178 | 5.9534
2171 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22222 | 0.76597 | 13.05 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 22 | 0.4% | String |  | During string monitoring found string no. 12 in ground fault now rectified & restore | 0.22222 | 0.29167 | 0.36111 | 0.37153 | 1.6667 | 3.3333 | 3.5833 | 3.5833 | During string monitoring found string no. 12 in ground fault now rectified & restore | closed | 0.014333 | 0.221 | 3.6958
2172 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22222 | 0.76597 | 13.05 | BLK2 |  |  | INV17 |  |  | BLK2INV17 | 22 | 0.4% | String |  | during string monitoring found string no. 7 MC4 connector open, now restore | 0.22222 | 0.29167 | 0.38194 | 0.38889 | 1.6667 | 3.8333 | 4 | 4 | during string monitoring found string no. 7 MC4 connector open, now restore | closed | 0.016 | 0.3 | 5.0169
2173 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22222 | 0.76597 | 13.05 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 22 | 0.4167% | String |  | during string monitoring found string no. 3 MC4 connector open, now restore | 0.22222 | 0.29167 | 0.39236 | 0.39931 | 1.6667 | 4.0833 | 4.25 | 4.25 | during string monitoring found string no. 3 MC4 connector open, now restore | closed | 0.017708 | 0.342 | 5.7193
2174 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22222 | 0.76597 | 13.05 | BLK3 |  |  | INV30 |  |  | BLK3INV30 | 22.25 | 0.4% | String |  | during string monitoring found string no. 1 MC4 connector melted so replace it with spare one, now restore | 0.22222 | 0.29167 | 0.41667 | 0.43403 | 1.6667 | 4.6667 | 5.0833 | 5.0833 | during string monitoring found string no. 1 MC4 connector melted so replace it with spare one, now restore | closed | 0.020333 | 0.39 | 6.5961
2175 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 0.22222 | 0.76597 | 13.05 | BLK5 |  |  | INV3 |  |  | BLK5INV3 | 44.5 | 0.4% | String |  | during string monitoring found string no. 9on ground fault while string no.12 Fuse & y connector melted so replace it with spare one, now restore | 0.22222 | 0.29167 | 0.44444 | 0.45833 | 1.6667 | 5.3333 | 5.6667 | 5.6667 | during string monitoring found string no. 9on ground fault while string no.12 Fuse & y connector melted so replace it with spare one, now restore | closed | 0.022667 | 0.514 | 17.3867
2176 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.23194 | 0.77986 | 13.15 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 264 | 0.3955% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.34028 | 0.34028 | 0.45833 | 0.47917 | 0 | 2.8333 | 3.3333 | 3.3333 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.013184 | 0.975 | 195.6607
2177 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.23194 | 0.77986 | 13.15 | BLK6 |  |  | INV32 |  |  | BLK6INV32 | 275 | 0.412% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.23194 | 0.23194 | 0.375 | 0.39583 | 0 | 3.4333 | 3.9333 | 3.9333 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.016205 | 0.751 | 156.9884
2178 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.23194 | 0.77986 | 13.15 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 297 | 0.4449% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.23194 | 0.23194 | 0.37153 | 0.38542 | 0 | 3.35 | 3.6833 | 3.6833 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.016389 | 0.699 | 157.8079
2179 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.23194 | 0.77986 | 13.15 | BLK6 |  |  | INV18 |  |  | BLK6INV18 | 297 | 0.4449% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.23194 | 0.23194 | 0.40278 | 0.41806 | 0 | 4.1 | 4.4667 | 4.4667 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.019874 | 0.834 | 188.2858
2180 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.23194 | 0.77986 | 13.15 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.23194 | 0.23194 | 0.41667 | 0.43542 | 0 | 4.4333 | 4.8833 | 4.8833 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.019533 | 0.927 | 188.1421
2181 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.23194 | 0.77986 | 13.15 | BLK2 |  |  | INV25 |  |  | BLK2INV25 | 300.375 | 0.45% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.23194 | 0.23194 | 0.36111 | 0.37153 | 0 | 3.1 | 3.35 | 3.35 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.015075 | 0.569 | 129.9185
2182 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.23194 | 0.77986 | 13.15 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 278.125 | 0.4167% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.23194 | 0.23194 | 0.33333 | 0.35208 | 0 | 2.4333 | 2.8833 | 2.8833 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.012014 | 0.398 | 84.143
2183 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.23194 | 0.77986 | 13.15 | BLK5 |  |  | INV22 |  |  | BLK5INV22 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.23194 | 0.23194 | 0.36111 | 0.38125 | 0 | 3.1 | 3.5833 | 3.5833 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.014333 | 0.66 | 133.9523
2184 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.23194 | 0.77986 | 13.15 | BLK7 |  |  | INV21 |  |  | BLK7INV21 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.4375 | 0.44097 | 0.44444 | 0.46111 | 0.083333 | 0.16667 | 0.56667 | 0.56667 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0022667 | 0.241 | 48.9129
2185 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.23194 | 0.77986 | 13.15 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | Inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 0.45486 | 0.45486 | 0.45833 | 0.47986 | 0 | 0.083333 | 0.6 | 0.6 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | closed | 0.001711 | 2.41 | 348.7105
2186 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.23194 | 0.77986 | 13.15 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.23194 | 0.23194 |  | 0.77986 | 0 | -5.5667 | 13.15 | 13.15 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0526 | 2.41 | 21.9833
2187 | 2025-07-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.23194 | 0.77986 | 13.15 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.23194 | 0.23194 |  | 0.77986 | 0 | -5.5667 | 13.15 | 13.15 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.059175 | 2.41 | 21.9833
2188 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK2 |  |  | INV26 |  |  | BLK2INV26 | 300.375 | 0.45% | inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.21806 | 0.25 | 0.32292 | 0.34722 | 0.76667 | 2.5167 | 3.1 | 3.1 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.01395 | 0.345 | 78.7731
2189 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK6 |  |  | INV17 |  |  | BLK6INV17 | 275 | 0.412% | inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.21806 | 0.25 | 0.35764 | 0.37153 | 0.76667 | 3.35 | 3.6833 | 3.6833 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.015175 | 0.456 | 95.3219
2190 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 264 | 0.3955% | inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.21806 | 0.25 | 0.29167 | 0.3125 | 0.76667 | 1.7667 | 2.2667 | 2.2667 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0089648 | 0.147 | 29.4996
2191 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 264 | 0.3955% | inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 0.21806 | 0.25 | 0.31944 | 0.33542 | 0.76667 | 2.4333 | 2.8167 | 2.8167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.01114 | 0.204 | 40.9382
2192 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | inverter |  | During morning after few time of plant start Block-2 inverter-31 shutdown on excessive lekage current, When we got Voc found that String NO. 3,6,9 MC4 connector & fuse was failure so replace it with new one , restore | 0.21806 | 0.25 | 0.40625 | 0.42361 | 0.76667 | 4.5167 | 4.9333 | 4.9333 | During morning after few time of plant start Block-2 inverter-31 shutdown on excessive lekage current, When we got Voc found that String NO. 3,6,9 MC4 connector & fuse was failure so replace it with new one , restore | closed | 0.019733 | 0.698 | 141.6647
2193 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | inverter |  | During morning after few time of plant start Block-4 inverter-2 shutdown on excessive lekage current, When we got Voc found that String NO. 2,5 MC4 connector & fuse was failure so replace it with new one , restore | 0.21806 | 0.25 | 0.42708 | 0.44444 | 0.76667 | 5.0167 | 5.4333 | 5.4333 | During morning after few time of plant start Block-4 inverter-2 shutdown on excessive lekage current, When we got Voc found that String NO. 2,5 MC4 connector & fuse was failure so replace it with new one , restore | closed | 0.021733 | 0.891 | 180.8356
2194 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK4 |  |  | INV11 |  |  | BLK4INV11 | 300.375 | 0.45% | inverter |  | During string monitoring we found that Block-4 Inverter-11 String-6 mc4 connector open, connected the same, restore | 0.21806 | 0.25 | 0.45139 | 0.46528 | 0.76667 | 5.6 | 5.9333 | 5.9333 | During string monitoring we found that Block-4 Inverter-11 String-6 mc4 connector open, connected the same, restore | closed | 0.0267 | 0.563 | 128.5486
2195 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK3 |  |  | INV29 |  |  | BLK3INV29 | 289.25 | 0.4333% | inverter |  | During morning after few time of plant start Block-3 inverter-29 , When we got Voc found that String NO. 1,5 MC4 connector was failure so replace it with new one , restore | 0.21806 | 0.25 | 0.37153 | 0.38889 | 0.76667 | 3.6833 | 4.1 | 4.1 | During morning after few time of plant start Block-3 inverter-29 , When we got Voc found that String NO. 1,5 MC4 connector was failure so replace it with new one , restore | closed | 0.017767 | 0.363 | 79.8133
2196 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | inverter |  | Inverter restoration work completed | 0.21806 | 0.21806 | 0.4375 | 0.45556 | 0 | 5.2667 | 5.7 | 5.7 | Inverter restoration work completed | closed | 0.016255 | 1.56 | 225.7213
2197 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21806 | 0.21806 |  | 0.77639 | 0 | -5.2333 | 13.4 | 13.4 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0536 | 4.07 | 37.1254
2198 | 2025-07-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:14 | 18:38 | 13.4 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21806 | 0.21806 |  | 0.77639 | 0 | -5.2333 | 13.4 | 13.4 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0603 | 4.07 | 37.1254
2199 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21944 | 18:38 | 13.3667 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21944 |  |  | 0.77639 | -5.2667 | -5.2667 | 13.3667 | 13.3667 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.053467 | 4.56 | 41.595
2200 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21944 | 18:38 | 13.3667 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21944 |  |  | 0.77639 | -5.2667 | -5.2667 | 13.3667 | 13.3667 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.06015 | 4.56 | 41.595
2201 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21944 | 18:38 | 13.3667 | BLK5 |  |  | INV22 |  |  | BLK5INV22 | 267 | 0.4% | inverter |  | During morning after few time of plant start Block-5 inverter-22 shutdown on PV reverse current alarm , When we got Voc found that String NO. 7 Y connector was failure, so isolate it and charge the inverter | 0.21944 | 0.25 | 0.27083 | 0.29236 | 0.73333 | 1.2333 | 1.75 | 1.75 | During morning after few time of plant start Block-5 inverter-22 shutdown on PV reverse current alarm , When we got Voc found that String NO. 7 Y connector was failure, so isolate it and charge the inverter | closed | 0.007 | 0.064 | 12.9893
2202 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21944 | 18:38 | 13.3667 | BLK5 |  |  | INV22 |  |  | BLK5INV22 | 22.25 | 0.4% | string |  | String NO. 7 Y connector was melted so replace it with spare one,restore | 0.21944 | 0.25 | 0.39583 | 0.41667 | 0.73333 | 4.2333 | 4.7333 | 4.7333 | String NO. 7 Y connector was melted so replace it with spare one,restore | closed | 0.018933 | 0.909 | 15.3741
2203 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21944 | 18:38 | 13.3667 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 297 | 0.4449% | inverter |  | During morning after few time of plant start Block-6 inverter-6 shutdown on low system isulation alarm , When we got Voc found that String NO. 1,3,6,10,11 was failure, so isolate it and charge the inverter | 0.21944 | 0.25 | 0.30208 | 0.31597 | 0.73333 | 1.9833 | 2.3167 | 2.3167 | During morning after few time of plant start Block-6 inverter-6 shutdown on low system isulation alarm , When we got Voc found that String NO. 1,3,6,10,11 was failure, so isolate it and charge the inverter | closed | 0.010308 | 0.13 | 29.3491
2204 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21944 | 18:38 | 13.3667 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 110 | 0.4449% | string |  | String NO. 1,,3,6,10,11 MC4 Fuse & Y connector was melted so replace it with spare one, restore | 0.21944 | 0.25 | 0.375 | 0.39583 | 0.73333 | 3.7333 | 4.2333 | 4.2333 | String NO. 1,,3,6,10,11 MC4 Fuse & Y connector was melted so replace it with spare one, restore | closed | 0.018836 | 0.713 | 59.618
2205 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21944 | 18:38 | 13.3667 | BLK6 |  |  | INV9 |  |  | BLK6INV9 | 275 | 0.412% | inverter |  | During morning after few time of plant start Block-6 inverter-9 shutdown on low system isulation alarm , When we got Voc found that String NO. 3,4,5,7 was failure, so isolate it and charge the inverter | 0.21944 | 0.25 | 0.32292 | 0.34375 | 0.73333 | 2.4833 | 2.9833 | 2.9833 | During morning after few time of plant start Block-6 inverter-9 shutdown on low system isulation alarm , When we got Voc found that String NO. 3,4,5,7 was failure, so isolate it and charge the inverter | closed | 0.012291 | 0.278 | 58.1129
2206 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21944 | 18:38 | 13.3667 | BLK6 |  |  | INV9 |  |  | BLK6INV9 | 88 | 0.412% | string |  | String NO. 3,4,5,7 MC4 Fuse & Y connector was melted so replace it with spare one, restore | 0.21944 | 0.25 | 0.40625 | 0.42708 | 0.73333 | 4.4833 | 4.9833 | 4.9833 | String NO. 3,4,5,7 MC4 Fuse & Y connector was melted so replace it with spare one, restore | closed | 0.020531 | 1.069 | 71.5081
2207 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21944 | 18:38 | 13.3667 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 264 | 0.3955% | inverter |  | During morning after few time of plant start Block-6 inverter-10 shutdown on low system isulation alarm , When we got Voc found that String NO. 1,3,4,7 was failure, so isolate it and charge the inverter | 0.21944 | 0.25 | 0.35069 | 0.36458 | 0.73333 | 3.15 | 3.4833 | 3.4833 | During morning after few time of plant start Block-6 inverter-10 shutdown on low system isulation alarm , When we got Voc found that String NO. 1,3,4,7 was failure, so isolate it and charge the inverter | closed | 0.013777 | 0.476 | 95.5226
2208 | 2025-07-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21944 | 18:38 | 13.3667 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 88 | 0.3955% | string |  | String NO. 1,3,4,7 MC4 Fuse & Y connector was melted so replace it with spare one, restore | 0.21944 | 0.25 | 0.43403 | 0.44792 | 0.73333 | 5.15 | 5.4833 | 5.4833 | String NO. 1,3,4,7 MC4 Fuse & Y connector was melted so replace it with spare one, restore | closed | 0.021687 | 1.444 | 96.5928
2209 | 2025-07-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21875 | 0.775 | 13.35 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21944 |  |  |  | -5.2667 | -5.2667 | -5.2667 | -5.2667 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | -0.021067 | 4.21 | 38.4024
2210 | 2025-07-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21875 | 0.775 | 13.35 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.21944 |  |  |  | -5.2667 | -5.2667 | -5.2667 | -5.2667 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | -0.0237 | 4.21 | 38.4024
2211 | 2025-07-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21875 | 0.775 | 13.35 | BLK5 |  |  | INV4 |  |  | BLK5INV4 | 22.25 | 0.45% | string |  | String no 3 MC4 was melted so replace it with spare one | 0.21944 | 0.29167 | 0.41319 | 0.43056 | 1.7333 | 4.65 | 5.0667 | 5.0667 | String no 3 MC4 was melted so replace it with spare one | closed | 0.0228 | 1.29 | 21.818
2212 | 2025-07-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21875 | 0.775 | 13.35 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | string |  | String no 8 MC4 was melted so replace it with spare one | 0.21944 | 0.29167 | 0.36458 | 0.38542 | 1.7333 | 3.4833 | 3.9833 | 3.9833 | String no 8 MC4 was melted so replace it with spare one | closed | 0.017925 | 0.78 | 13.1923
2213 | 2025-07-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21875 | 0.775 | 13.35 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22.25 | 0.45% | string |  | String no 8 Y connector, fuse & MC4 was melted so replace it with spare one | 0.21944 | 0.29167 | 0.38889 | 0.40625 | 1.7333 | 4.0667 | 4.4833 | 4.4833 | String no 8 Y connector, fuse & MC4 was melted so replace it with spare one | closed | 0.020175 | 1.014 | 17.15
2214 | 2025-07-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21875 | 0.775 | 13.35 | BLK2 |  |  | INV5 |  |  | BLK2INV5 | 22.25 | 0.4% | string |  | String no 7 MC4 was melted so replace it with spare one | 0.21944 | 0.29167 | 0.42708 | 0.44444 | 1.7333 | 4.9833 | 5.4 | 5.4 | String no 7 MC4 was melted so replace it with spare one | closed | 0.0216 | 1.588 | 26.8581
2215 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.22847 |  |  | 0.77917 | -5.4833 | -5.4833 | 13.2167 | 13.2167 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.052867 | 5.13 | 46.7944
2216 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 0.22847 |  |  | 0.77917 | -5.4833 | -5.4833 | 13.2167 | 13.2167 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.059475 | 5.13 | 46.7944
2217 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK2 |  |  | INV25 |  |  | BLK2INV25 | 66.75 | 0.45% | string |  | String no 1,4,7 MC4 was melted so replace it with spare one | 0.22847 | 0.25 | 0.33333 | 0.34722 | 0.51667 | 2.5167 | 2.85 | 2.85 | String no 1,4,7 MC4 was melted so replace it with spare one | closed | 0.012825 | 0.346 | 17.5559
2218 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK3 |  |  | INV28 |  |  | BLK3INV28 | 22.25 | 0.4167% | string |  | String no 5 on ground fault, rectified | 0.22847 | 0.25 | 0.35069 | 0.35764 | 0.51667 | 2.9333 | 3.1 | 3.1 | String no 5 on ground fault, rectified | closed | 0.012917 | 0.656 | 11.095
2219 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK1 |  |  | INV30 |  |  | BLK1INV30 | 22.25 | 0.45% | string |  | During string monitoring we found that string no 2 MC4 connector open so connect it & restore | 0.22847 | 0.25 | 0.36806 | 0.38194 | 0.51667 | 3.35 | 3.6833 | 3.6833 | During string monitoring we found that string no 2 MC4 connector open so connect it & restore | closed | 0.016575 | 0.753 | 12.7356
2220 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK6 |  |  | INV31 |  |  | BLK6INV31 | 44 | 0.412% | string |  | String no.4 & 6 on ground fault due to MC4 Connector & Y-connector was melted, rectified | 0.22847 | 0.25 | 0.38889 | 0.40278 | 0.51667 | 3.85 | 4.1833 | 4.1833 | String no.4 & 6 on ground fault due to MC4 Connector & Y-connector was melted, rectified | closed | 0.017235 | 1.221 | 40.8379
2221 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK6 |  |  | INV32 |  |  | BLK6INV32 | 110 | 0.412% | string |  | String no.1,6,10,11 & 12 on ground fault due to MC4 Connector was melted, rectified | 0.22847 | 0.25 | 0.40972 | 0.42361 | 0.51667 | 4.35 | 4.6833 | 4.6833 | String no.1,6,10,11 & 12 on ground fault due to MC4 Connector was melted, rectified | closed | 0.019295 | 1.345 | 112.4631
2222 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK6 |  |  | INV18 |  |  | BLK6INV18 | 22 | 0.4449% | string |  | During string monitoring we found that string no 5 MC4 connector was melted so replace it with spare one & restore | 0.22847 | 0.25 | 0.43056 | 0.44792 | 0.51667 | 4.85 | 5.2667 | 5.2667 | During string monitoring we found that string no 5 MC4 connector was melted so replace it with spare one & restore | closed | 0.023434 | 1.456 | 24.3489
2223 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK6 |  |  | INV17 |  |  | BLK6INV17 | 22 | 0.412% | string |  | During string monitoring we found that string no 6 MC4 connector was melted so replace it with spare one & restore | 0.22847 | 0.25 | 0.45486 | 0.47222 | 0.51667 | 5.4333 | 5.85 | 5.85 | During string monitoring we found that string no 6 MC4 connector was melted so replace it with spare one & restore | closed | 0.024101 | 1.657 | 27.7102
2224 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.50694 | 0.50694 | 0.50972 | 0.51042 | 0 | 0.066667 | 0.083333 | 0.083333 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011167 | 0.106 | 720.7041
2225 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.50694 | 0.50694 | 0.51111 | 0.51181 | 0 | 0.1 | 0.11667 | 0.11667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.014583 | 0.14 | 887.9415
2226 | 2025-07-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 5:29 | 18:42 | 13.2167 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 0.50694 | 0.50694 | 0.51181 | 0.5125 | 0 | 0.11667 | 0.13333 | 0.13333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.017707 | 0.159 | 1071.4173
2227 | 2025-07-06 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21875 | 0.76875 | 13.2 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 264 | 0.3955% | inverter |  | Inverter shutdown on fault of excessive leakage current, after identify the string, isolate the string & charge the inverter | 0.21875 | 0.25694 | 0.29861 | 0.3125 | 0.91667 | 1.9167 | 2.25 | 2.25 | Inverter shutdown on fault of excessive leakage current, after identify the string, isolate the string & charge the inverter | closed | 0.0088989 | 0.156 | 31.3057
2228 | 2025-07-06 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21875 | 0.76875 | 13.2 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22.25 | 0.3955% | string |  | during VOC we found that sring no 9 in ground fault so rectify it & connect to the inverter, restore | 0.21875 | 0.25694 | 0.32292 | 0.34375 | 0.91667 | 2.5 | 3 | 3 | during VOC we found that sring no 9 in ground fault so rectify it & connect to the inverter, restore | closed | 0.011865 | 0.37 | 6.2579
2229 | 2025-07-06 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21875 | 0.76875 | 13.2 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | String 13 cable failure so for minimize the generation lost its load is connected with string no 14 while string no 5 seprated to 2v half string & connected to inverter | 0.21875 | 0.21875 | 0.42361 | 0.45347 | 0 | 4.9167 | 5.6333 | 5.6333 | String 13 cable failure so for minimize the generation lost its load is connected with string no 14 while string no 5 seprated to 2v half string & connected to inverter | closed | 0.022533 | 1.564 | 14.2664
2230 | 2025-07-06 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 31 | 0.21875 | 0.76875 | 13.2 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | string |  | String 14 cable failure so for minimize the generation lost its load is connected with string no 15 while string no 6 seprated to 2v half string & connected to inverter | 0.21875 | 0.21875 | 0.46528 | 0.48611 | 0 | 5.9167 | 6.4167 | 6.4167 | String 14 cable failure so for minimize the generation lost its load is connected with string no 15 while string no 6 seprated to 2v half string & connected to inverter | closed | 0.028875 | 2.241 | 20.4418
Formulas:
Days = DAY(EOMONTH(PA[[#This Row],[Date]], 0))
Days = DAY(EOMONTH(PA!$[Date], 0))
Sunrise Time (POA>20 W/m2) = XLOOKUP(PA[[#This Row],[Date]],RD[Date],RD[Sunrise Time (POA>20 W/m2)],0)
Sunset Time (POA<20 W/m2) = XLOOKUP(PA[[#This Row],[Financial Year]],RD[Finacial Year],RD[Sunset Time (POA<20 W/m2)],0)

## Basic Data (hidden)
Equipment | Affected DC Capacity | Plant Equivalent Weightage | Fault Category Plant BD sheet | IS Number | LT Number | String Type | Equipment | Inverter Number | Status | Plant capacity | LT Number
BLK1INV1 | 289.25 | 0.4333% | Module | BLK1 | ACCB1 | Str_Typ1(445*50) | Tx | INV1 | Open | 66750 | LT1
BLK1INV2 | 289.25 | 0.4333% | Cables | BLK2 | ACCB2 | Str_Typ2 (330*60) | MVP | INV2 | Close |  | LT2
BLK1INV3 | 267 | 0.4% | String Fuses | BLK3 | ACCB3 | Str_Typ3(335*60) | Aux_Tx | INV3
BLK1INV4 | 267 | 0.4% | ACCB | BLK4 | ACCB4 | Str_Typ4(440*60) | MCR_MVP_IC_1 | INV4
BLK1INV5 | 289.25 | 0.4333% | Inverter | BLK5 | ACCB5 |  | MCR_MVP_IC_2 | INV5
BLK1INV6 | 267 | 0.4% | IDT | BLK6 | ACCB6 |  | MCR_MVP_IC_3 | INV6
BLK1INV7 | 267 | 0.4% | PTR | BLK7 | ACCB7 |  | MCR_MVP_IC_4 | INV7
BLK1INV8 | 267 | 0.4% | MV Panel | BLK8 | ACCB8 |  | MCR_MVP_OG | INV8
BLK1INV9 | 278.125 | 0.4167% | Metering System Plant |  |  |  | PWR_Tx | INV9
BLK1INV10 | 278.125 | 0.4167% | Grid System |  |  |  | Line_Bay1 | INV10
BLK1INV11 | 267 | 0.4% | Metering System Grid |  |  |  |  | INV11
BLK1INV12 | 267 | 0.4% | WMS |  |  |  |  | INV12
BLK1INV13 | 267 | 0.4% | MMS |  |  |  |  | INV13
BLK1INV14 | 244.75 | 0.3667% | Battery Charger_MCR |  |  |  |  | INV14
BLK1INV15 | 267 | 0.4% | IC_UPS |  |  |  |  | INV15
BLK1INV16 | 267 | 0.4% | IC_Auxiliary Tranformer |  |  |  |  | INV16
BLK1INV17 | 267 | 0.4% | IC_Auxiliary DB |  |  |  |  | INV17
BLK1INV18 | 267 | 0.4% | IC_SCADA Panel |  |  |  |  | INV18
BLK1INV19 | 289.25 | 0.4333% | Connectors |  |  |  |  | INV19
BLK1INV20 | 289.25 | 0.4333% | LT Panel |  |  |  |  | INV20
BLK1INV21 | 267 | 0.4% | SS |  |  |  |  | INV21
BLK1INV22 | 267 | 0.4% | Force Majeure |  |  |  |  | INV22
BLK1INV23 | 289.25 | 0.4333% | [5 empty] | INV23
BLK1INV24 | 300.375 | 0.45% | [5 empty] | INV24
BLK1INV25 | 289.25 | 0.4333% | [5 empty] | INV25
BLK1INV26 | 289.25 | 0.4333% | [5 empty] | INV26
BLK1INV27 | 289.25 | 0.4333% | [5 empty] | INV27
BLK1INV28 | 300.375 | 0.45% | [5 empty] | INV28
BLK1INV29 | 300.375 | 0.45% | [5 empty] | INV29
BLK1INV30 | 300.375 | 0.45% | [5 empty] | INV30
BLK1INV31 | 300.375 | 0.45% | [5 empty] | INV31
BLK1INV32 | 300.375 | 0.45% | [5 empty] | INV31
BLK2INV1 | 300.375 | 0.45% | [5 empty] | INV32
BLK2INV2 | 222.5 | 0.3333% | [5 empty] | All_Inv
BLK2INV3 | 111.25 | 0.1667%
BLK2INV4 | 267 | 0.4%
BLK2INV5 | 267 | 0.4%
BLK2INV6 | 267 | 0.4%
BLK2INV7 | 267 | 0.4%
BLK2INV8 | 267 | 0.4%
BLK2INV9 | 267 | 0.4%
BLK2INV10 | 267 | 0.4%
BLK2INV11 | 267 | 0.4%
BLK2INV12 | 267 | 0.4%
BLK2INV13 | 267 | 0.4%
BLK2INV14 | 267 | 0.4%
BLK2INV15 | 267 | 0.4%
BLK2INV16 | 289.25 | 0.4333%
BLK2INV17 | 267 | 0.4%
BLK2INV18 | 278.125 | 0.4167%
BLK2INV19 | 278.125 | 0.4167%
BLK2INV20 | 267 | 0.4%
BLK2INV21 | 267 | 0.4%
BLK2INV22 | 300.375 | 0.45%
BLK2INV23 | 300.375 | 0.45%
BLK2INV24 | 289.25 | 0.4333%
BLK2INV25 | 300.375 | 0.45%
BLK2INV26 | 300.375 | 0.45%
BLK2INV27 | 267 | 0.4%
BLK2INV28 | 300.375 | 0.45%
BLK2INV29 | 300.375 | 0.45%
BLK2INV30 | 267 | 0.4%
BLK2INV31 | 267 | 0.4%
BLK2INV32 | 239.25 | 0.3584%
BLK3INV1 | 267 | 0.4%
BLK3INV2 | 289.25 | 0.4333%
BLK3INV3 | 289.25 | 0.4333%
BLK3INV4 | 289.25 | 0.4333%
BLK3INV5 | 289.25 | 0.4333%
BLK3INV6 | 267 | 0.4%
BLK3INV7 | 267 | 0.4%
BLK3INV8 | 267 | 0.4%
BLK3INV9 | 267 | 0.4%
BLK3INV10 | 267 | 0.4%
BLK3INV11 | 267 | 0.4%
BLK3INV12 | 300.375 | 0.45%
BLK3INV13 | 300.375 | 0.45%
BLK3INV14 | 300.375 | 0.45%
BLK3INV15 | 267 | 0.4%
BLK3INV16 | 267 | 0.4%
BLK3INV17 | 289.25 | 0.4333%
BLK3INV18 | 267 | 0.4%
BLK3INV19 | 267 | 0.4%
BLK3INV20 | 267 | 0.4%
BLK3INV21 | 267 | 0.4%
BLK3INV22 | 267 | 0.4%
BLK3INV23 | 267 | 0.4%
BLK3INV24 | 267 | 0.4%
BLK3INV25 | 267 | 0.4%
BLK3INV26 | 267 | 0.4%
BLK3INV27 | 267 | 0.4%
BLK3INV28 | 278.125 | 0.4167%
BLK3INV29 | 289.25 | 0.4333%
BLK3INV30 | 267 | 0.4%
BLK3INV31 | 267 | 0.4%
BLK4INV1 | 300.375 | 0.45%
BLK4INV2 | 267 | 0.4%
BLK4INV3 | 267 | 0.4%
BLK4INV4 | 267 | 0.4%
BLK4INV5 | 267 | 0.4%
BLK4INV6 | 267 | 0.4%
BLK4INV7 | 267 | 0.4%
BLK4INV8 | 267 | 0.4%
BLK4INV9 | 267 | 0.4%
BLK4INV10 | 267 | 0.4%
BLK4INV11 | 300.375 | 0.45%
BLK4INV12 | 267 | 0.4%
BLK4INV13 | 300.375 | 0.45%
BLK4INV14 | 267 | 0.4%
BLK4INV15 | 267 | 0.4%
BLK4INV16 | 300.375 | 0.45%
BLK4INV17 | 289.25 | 0.4333%
BLK4INV18 | 289.25 | 0.4333%
BLK4INV19 | 300.375 | 0.45%
BLK4INV20 | 300.375 | 0.45%
BLK4INV21 | 267 | 0.4%
BLK4INV22 | 267 | 0.4%
BLK4INV23 | 267 | 0.4%
BLK4INV24 | 300.375 | 0.45%
BLK4INV25 | 300.375 | 0.45%
BLK4INV26 | 267 | 0.4%
BLK4INV27 | 267 | 0.4%
BLK4INV28 | 300.375 | 0.45%
BLK4INV29 | 300.375 | 0.45%
BLK4INV30 | 267 | 0.4%
BLK4INV31 | 267 | 0.4%
BLK5INV1 | 300.375 | 0.45%
BLK5INV2 | 267 | 0.4%
BLK5INV3 | 267 | 0.4%
BLK5INV4 | 300.375 | 0.45%
BLK5INV5 | 300.375 | 0.45%
BLK5INV6 | 289.25 | 0.4333%
BLK5INV7 | 289.25 | 0.4333%
BLK5INV8 | 289.25 | 0.4333%
BLK5INV9 | 244.75 | 0.3667%
BLK5INV10 | 286 | 0.4285%
BLK5INV11 | 286 | 0.4285%
BLK5INV12 | 286 | 0.4285%
BLK5INV13 | 286 | 0.4285%
BLK5INV14 | 278.125 | 0.4167%
BLK5INV15 | 267 | 0.4%
BLK5INV16 | 289.25 | 0.4333%
BLK5INV17 | 289.25 | 0.4333%
BLK5INV18 | 267 | 0.4%
BLK5INV19 | 289.25 | 0.4333%
BLK5INV20 | 267 | 0.4%
BLK5INV21 | 289.25 | 0.4333%
BLK5INV22 | 267 | 0.4%
BLK5INV23 | 244.75 | 0.3667%
BLK5INV24 | 267 | 0.4%
BLK5INV25 | 267 | 0.4%
BLK5INV26 | 289.25 | 0.4333%
BLK5INV27 | 267 | 0.4%
BLK5INV28 | 300.375 | 0.45%
BLK5INV29 | 267 | 0.4%
BLK5INV30 | 267 | 0.4%
BLK5INV31 | 267 | 0.4%
BLK5INV32 | 267 | 0.4%
BLK6INV1 | 267 | 0.4%
BLK6INV2 | 264 | 0.3955%
BLK6INV3 | 264 | 0.3955%
BLK6INV4 | 297 | 0.4449%
BLK6INV5 | 264 | 0.3955%
BLK6INV6 | 297 | 0.4449%
BLK6INV7 | 297 | 0.4449%
BLK6INV8 | 297 | 0.4449%
BLK6INV9 | 275 | 0.412%
BLK6INV10 | 264 | 0.3955%
BLK6INV11 | 297 | 0.4449%
BLK6INV12 | 264 | 0.3955%
BLK6INV13 | 275 | 0.412%
BLK6INV14 | 275 | 0.412%
BLK6INV15 | 275 | 0.412%
BLK6INV16 | 297 | 0.4449%
BLK6INV17 | 275 | 0.412%
BLK6INV18 | 297 | 0.4449%
BLK6INV19 | 264 | 0.3955%
BLK6INV20 | 264 | 0.3955%
BLK6INV21 | 264 | 0.3955%
BLK6INV22 | 297 | 0.4449%
BLK6INV23 | 264 | 0.3955%
BLK6INV24 | 286 | 0.4285%
BLK6INV25 | 297 | 0.4449%
BLK6INV26 | 297 | 0.4449%
BLK6INV27 | 275 | 0.412%
BLK6INV28 | 286 | 0.4285%
BLK6INV29 | 297 | 0.4449%
BLK6INV30 | 275 | 0.412%
BLK6INV31 | 275 | 0.412%
BLK6INV32 | 275 | 0.412%
BLK7INV1 | 286 | 0.4285%
BLK7INV2 | 264 | 0.3955%
BLK7INV3 | 264 | 0.3955%
BLK7INV4 | 264 | 0.3955%
BLK7INV5 | 264 | 0.3955%
BLK7INV6 | 264 | 0.3955%
BLK7INV7 | 264 | 0.3955%
BLK7INV8 | 220 | 0.3296%
BLK7INV9 | 264 | 0.3955%
BLK7INV10 | 257.4 | 0.3856%
BLK7INV11 | 190.35 | 0.2852%
BLK7INV12 | 270.6 | 0.4054%
BLK7INV13 | 244.75 | 0.3667%
BLK7INV14 | 267 | 0.4%
BLK7INV15 | 267 | 0.4%
BLK7INV16 | 267 | 0.4%
BLK7INV17 | 267 | 0.4%
BLK7INV18 | 267 | 0.4%
BLK7INV19 | 267 | 0.4%
BLK7INV20 | 267 | 0.4%
BLK7INV21 | 267 | 0.4%
BLK7INV22 | 267 | 0.4%
BLK7INV23 | 267 | 0.4%
BLK7INV24 | 267 | 0.4%
BLK7INV25 | 300.375 | 0.45%
BLK7INV26 | 300.375 | 0.45%
BLK7INV27 | 267 | 0.4%
BLK7INV28 | 267 | 0.4%
BLK7INV29 | 267 | 0.4%
BLK7INV30 | 267 | 0.4%
BLK7INV31 | 267 | 0.4%
BLK7INV32 | 159.5 | 0.239%
BLK8INV1 | 267 | 0.4%
BLK8INV2 | 198 | 0.2966%
BLK8INV3 | 188.1 | 0.2818%
BLK8INV4 | 278.125 | 0.4167%
BLK8INV5 | 300.375 | 0.45%
BLK8INV6 | 289.25 | 0.4333%
BLK8INV7 | 289.25 | 0.4333%
BLK8INV8 | 267 | 0.4%
BLK8INV9 | 289.25 | 0.4333%
BLK8INV10 | 300.375 | 0.45%
BLK8INV11 | 300.375 | 0.45%
BLK8INV12 | 257.4 | 0.3856%
BLK8INV13 | 277.2 | 0.4153%
BLK8INV14 | 257.4 | 0.3856%
BLK8INV15 | 267.3 | 0.4004%
BLK8INV16 | 188.1 | 0.2818%
BLK8INV17 | 178 | 0.2667%
BLK8INV18 | 222.5 | 0.3333%
BLK8INV19 | 287.1 | 0.4301%
BLK8INV20 | 257.4 | 0.3856%
BLK8INV21 | 267.3 | 0.4004%
BLK8INV22 | 257.4 | 0.3856%
BLK8INV23 | 271.35 | 0.4065%
BLK8INV24 | 271.35 | 0.4065%
BLK8INV25 | 261.3 | 0.3915%
BLK8INV26 | 271.35 | 0.4065%
BLK8INV27 | 291.45 | 0.4366%
BLK8INV28 | 257.4 | 0.3856%
BLK1LT1 | 4338.75 | 6.5%
BLK1LT2 | 4605.75 | 6.9%
BLK2LT1 | 4094 | 6.133%
BLK2LT2 | 4249.75 | 6.367%
BLK3LT1 | 4483.375 | 6.717%
BLK3LT2 | 4071.75 | 6.1%
BLK4LT1 | 4394.375 | 6.583%
BLK4LT2 | 4260.875 | 6.383%
BLK5LT1 | 4514.875 | 6.764%
BLK5LT2 | 4349.875 | 6.517%
BLK6LT1 | 4477 | 6.707%
BLK6LT2 | 4499 | 6.74%
BLK7LT1 | 3298.1 | 4.941%
BLK7LT2 | 4071.75 | 6.1%
BLK8LT1 | 3947.5 | 5.914%
BLK8LT2 | 3093.9 | 4.635%
BLK1LT1ACCB1 | 578.5 | 0.8667%
BLK1LT1ACCB2 | 534 | 0.8%
BLK1LT1ACCB3 | 556.25 | 0.8333%
BLK1LT1ACCB4 | 534 | 0.8%
BLK1LT1ACCB5 | 556.25 | 0.8333%
BLK1LT1ACCB6 | 534 | 0.8%
BLK1LT1ACCB7 | 511.75 | 0.7667%
BLK1LT1ACCB8 | 534 | 0.8%
BLK1LT2ACCB1 | 534 | 0.8%
BLK1LT2ACCB2 | 578.5 | 0.8667%
BLK1LT2ACCB3 | 534 | 0.8%
BLK1LT2ACCB4 | 589.625 | 0.8833%
BLK1LT2ACCB5 | 578.5 | 0.8667%
BLK1LT2ACCB6 | 589.625 | 0.8833%
BLK1LT2ACCB7 | 600.75 | 0.9%
BLK1LT2ACCB8 | 600.75 | 0.9%
BLK2LT1ACCB1 | 333.75 | 0.5%
BLK2LT1ACCB2 | 534 | 0.8%
BLK2LT1ACCB3 | 534 | 0.8%
BLK2LT1ACCB4 | 534 | 0.8%
BLK2LT1ACCB5 | 534 | 0.8%
BLK2LT1ACCB6 | 534 | 0.8%
BLK2LT1ACCB7 | 534 | 0.8%
BLK2LT1ACCB8 | 556.25 | 0.8333%
BLK2LT2ACCB1 | 556.25 | 0.8333%
BLK2LT2ACCB2 | 534 | 0.8%
BLK2LT2ACCB3 | 600.75 | 0.9%
BLK2LT2ACCB4 | 589.625 | 0.8833%
BLK2LT2ACCB5 | 567.375 | 0.85%
BLK2LT2ACCB6 | 600.75 | 0.9%
BLK2LT2ACCB7 | 534 | 0.8%
BLK2LT2ACCB8 | 267 | 0.4%
BLK3LT1ACCB1 | 578.5 | 0.8667%
BLK3LT1ACCB2 | 556.25 | 0.8333%
BLK3LT1ACCB3 | 534 | 0.8%
BLK3LT1ACCB4 | 534 | 0.8%
BLK3LT1ACCB5 | 567.375 | 0.85%
BLK3LT1ACCB6 | 600.75 | 0.9%
BLK3LT1ACCB7 | 534 | 0.8%
BLK3LT1ACCB8 | 578.5 | 0.8667%
BLK3LT2ACCB1 | 534 | 0.8%
BLK3LT2ACCB2 | 534 | 0.8%
BLK3LT2ACCB3 | 534 | 0.8%
BLK3LT2ACCB4 | 534 | 0.8%
BLK3LT2ACCB5 | 545.125 | 0.8167%
BLK3LT2ACCB6 | 556.25 | 0.8333%
BLK3LT2ACCB7 | 567.375 | 0.85%
BLK3LT2ACCB8 | 267 | 0.4%
BLK4LT1ACCB1 | 534 | 0.8%
BLK4LT1ACCB2 | 534 | 0.8%
BLK4LT1ACCB3 | 534 | 0.8%
BLK4LT1ACCB4 | 534 | 0.8%
BLK4LT1ACCB5 | 567.375 | 0.85%
BLK4LT1ACCB6 | 567.375 | 0.85%
BLK4LT1ACCB7 | 534 | 0.8%
BLK4LT1ACCB8 | 589.625 | 0.8833%
BLK4LT2ACCB1 | 589.625 | 0.8833%
BLK4LT2ACCB2 | 567.375 | 0.85%
BLK4LT2ACCB3 | 534 | 0.8%
BLK4LT2ACCB4 | 600.75 | 0.9%
BLK4LT2ACCB5 | 534 | 0.8%
BLK4LT2ACCB6 | 600.75 | 0.9%
BLK4LT2ACCB7 | 534 | 0.8%
BLK4LT2ACCB8 | 300.375 | 0.45%
BLK5LT1ACCB1 | 534 | 0.8%
BLK5LT1ACCB2 | 600.75 | 0.9%
BLK5LT1ACCB3 | 578.5 | 0.8667%
BLK5LT1ACCB4 | 534 | 0.8%
BLK5LT1ACCB5 | 572 | 0.8569%
BLK5LT1ACCB6 | 572 | 0.8569%
BLK5LT1ACCB7 | 545.125 | 0.8167%
BLK5LT1ACCB8 | 578.5 | 0.8667%
BLK5LT2ACCB1 | 556.25 | 0.8333%
BLK5LT2ACCB2 | 556.25 | 0.8333%
BLK5LT2ACCB3 | 511.75 | 0.7667%
BLK5LT2ACCB4 | 534 | 0.8%
BLK5LT2ACCB5 | 556.25 | 0.8333%
BLK5LT2ACCB6 | 567.375 | 0.85%
BLK5LT2ACCB7 | 534 | 0.8%
BLK5LT2ACCB8 | 534 | 0.8%
BLK6LT1ACCB1 | 528 | 0.791%
BLK6LT1ACCB2 | 561 | 0.8404%
BLK6LT1ACCB3 | 594 | 0.8899%
BLK6LT1ACCB4 | 572 | 0.8569%
BLK6LT1ACCB5 | 561 | 0.8404%
BLK6LT1ACCB6 | 539 | 0.8075%
BLK6LT1ACCB7 | 550 | 0.824%
BLK6LT1ACCB8 | 572 | 0.8569%
BLK6LT2ACCB1 | 561 | 0.8404%
BLK6LT2ACCB2 | 528 | 0.791%
BLK6LT2ACCB3 | 561 | 0.8404%
BLK6LT2ACCB4 | 583 | 0.8734%
BLK6LT2ACCB5 | 572 | 0.8569%
BLK6LT2ACCB6 | 583 | 0.8734%
BLK6LT2ACCB7 | 550 | 0.824%
BLK6LT2ACCB8 | 561 | 0.8404%
BLK7LT1ACCB1 | 528 | 0.791%
BLK7LT1ACCB2 | 528 | 0.791%
BLK7LT1ACCB3 | 528 | 0.791%
BLK7LT1ACCB4 | 484 | 0.7251%
BLK7LT1ACCB5 |  | 0%
BLK7LT1ACCB6 | 447.75 | 0.6708%
BLK7LT1ACCB7 | 270.5 | 0.4052%
BLK7LT1ACCB8 | 511.75 | 0.7667%
BLK7LT2ACCB1 | 534 | 0.8%
BLK7LT2ACCB2 | 534 | 0.8%
BLK7LT2ACCB3 | 534 | 0.8%
BLK7LT2ACCB4 | 534 | 0.8%
BLK7LT2ACCB5 | 534 | 0.8%
BLK7LT2ACCB6 | 600.75 | 0.9%
BLK7LT2ACCB7 | 534 | 0.8%
BLK7LT2ACCB8 | 267 | 0.4%
BLK8LT1ACCB1 | 386.1 | 0.5784%
BLK8LT1ACCB2 | 578.5 | 0.8667%
BLK8LT1ACCB3 | 578.5 | 0.8667%
BLK8LT1ACCB4 | 556.25 | 0.8333%
BLK8LT1ACCB5 | 600.75 | 0.9%
BLK8LT1ACCB6 | 534.6 | 0.8009%
BLK8LT1ACCB7 | 524.7 | 0.7861%
BLK8LT1ACCB8 | 188.1 | 0.2818%
BLK8LT2ACCB1 | 400.5 | 0.6%
BLK8LT2ACCB2 | 544.5 | 0.8157%
BLK8LT2ACCB3 | 524.7 | 0.7861%
BLK8LT2ACCB4 | 542.7 | 0.813%
BLK8LT2ACCB5 | 532.65 | 0.798%
BLK8LT2ACCB6 | 548.85 | 0.8222%
BLK1TX | 8944.5 | 13.4%
BLK2TX | 8343.75 | 12.5%
BLK3TX | 8555.125 | 12.82%
BLK4TX | 8655.25 | 12.97%
BLK5TX | 8864.75 | 13.28%
BLK6TX | 8976 | 13.45%
BLK7TX | 7369.85 | 11.04%
BLK8TX | 7041.4 | 10.55%
MCR_MVP_IC_1 | 17288.25 | 25.9%
MCR_MVP_IC_2 | 17210.375 | 25.78%
MCR_MVP_IC_3 | 17840.75 | 26.73%
MCR_MVP_IC_4 | 14411.25 | 21.59%
MCR_MVP_OG | 66750.25 | 100%
PWR_TX | 66750.25 | 100%
132KV_OC | 66750.25 | 100%
Line_Bay1 | 66750.25 | 100%
Str_Typ1(445*50) | 22.25 | 0.03333%
Str_Typ2 (330*60) | 19.8 | 0.02966%
Str_Typ3(335*60) | 20.1 | 0.03011%
Str_Typ4(440*60) | 22 | 0.03296%
BLK1MVP | 8944.5 | 13.4%
BLK2MVP | 8343.75 | 12.5%
BLK3MVP | 8555.125 | 12.82%
BLK4MVP | 8655.25 | 12.97%
BLK5MVP | 8864.75 | 13.28%
BLK6MVP | 8976 | 13.45%
BLK7MVP | 7369.85 | 11.04%
BLK8MVP | 7041.4 | 10.55%
BLK1Aux_Tx | 8944.5 | 13.4%
BLK2Aux_Tx | 8343.75 | 12.5%
BLK3Aux_Tx | 8555.125 | 12.82%
BLK4Aux_Tx | 8655.25 | 12.97%
BLK5Aux_Tx | 8864.75 | 13.28%
BLK6Aux_Tx | 8976 | 13.45%
BLK7Aux_Tx | 7369.85 | 11.04%
BLK8Aux_Tx | 7041.4 | 10.55%
All_Inv | 66750.25 | 100%

## GA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
Sr. No. | Date | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Breakdown Description | Fault Time | Work Completion time on fault | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(kWh/m2) | Approximate Energy Loss (KWh)
1 |  | 1900 | 1900 | Year-2 | Year-2 | 1899-12-31 | 31 | 0 | 0 | 0 |  | 0 | 0% |  |  |  | 0 |  |  | 0
2 |  | 1900 | 1900 | Year-2 | Year-2 | 1899-12-31 | 31 | 0 | 0 | 0 |  | 0 | 0% |  |  |  | 0 |  |  | 0
3 |  | 1900 | 1900 | Year-2 | Year-2 | 1899-12-31 | 31 | 0 | 0 | 0 |  | 0 | 0% |  |  |  | 0 |  |  | 0
4 |  | 1900 | 1900 | Year-2 | Year-2 | 1899-12-31 | 31 | 0 | 0 | 0 |  | 0 | 0% |  |  |  | 0 |  |  | 0
[6 empty] | 1899-12-31 | [10 empty] | 0 |  |  | 0
[6 empty] | 1899-12-31 | [10 empty] | 0 |  |  | 0
[6 empty] | 1899-12-31 | [10 empty] | 0 |  |  | 0
Formulas:
Month Year = GA[[#This Row],[Date]]-DAY(GA[[#This Row],[Date]])+1
Days = DAY(EOMONTH(GA[[#This Row],[Month Year]],0))
Sunrise Time (POA>20 W/m2) = XLOOKUP(GA[[#This Row],[Date]],RD[Date],RD[Sunrise Time (POA>20 W/m2)],0)
Sunset Time (POA<20 W/m2) = XLOOKUP(GA[[#This Row],[Date]],RD[Date],RD[Sunset Time (POA<20 W/m2)],0)

## Inv_SY_B
| 289.25 | 289.25 | 267 | 267 | 289.25 | 267 | 267 | 267 | 278.125 | 278.125 | 267 | 267 | 267 | 244.75 | 267 | 267 | 267 | 267 | 289.25 | 289.25 | 267 | 267 | 289.25 | 300.375 | 289.25 | 289.25 | 289.25 | 300.375 | 300.375 | 300.375 | 300.375 | 300.375 | 254.4 | 334.55 | 267 | 298.9 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 289.25 | 267 | 278.125 | 278.125 | 267 | 267 | 300.375 | 300.375 | 289.25 | 300.375 | 300.375 | 267 | 300.375 | 300.375 | 267 | 298.9 | 267 | 239.25 | 289.25 | 289.25 | 289.25 | 289.25 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 300.375 | 300.375 | 267 | 267 | 289.25 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 278.125 | 289.25 | 267 | 267 | 300.375 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 267 | 300.375 | 298.9 | 267 | 300.375 | 289.25 | 289.25 | 300.375 | 300.375 | 267 | 267 | 298.9 | 300.375 | 300.375 | 267 | 267 | 300.375 | 300.375 | 267 | 267 | 300.375 | 267 | 267 | 300.375 | 300.375 | 289.25 | 289.25 | 289.25 | 244.75 | 286 | 286 | 286 | 286 | 278.125 | 267 | 289.25 | 289.25 | 267 | 289.25 | 267 | 289.25 | 267 | 244.75 | 289.25 | 289.25 | 289.25 | 267 | 300.375 | 267 | 267 | 267 | 267 | 267 | 264 | 264 | 297 | 264 | 297 | 297 | 297 | 275 | 264 | 297 | 264 | 275 | 275 | 275 | 297 | 275 | 297 | 264 | 264 | 264 | 297 | 264 | 286 | 297 | 297 | 275 | 286 | 297 | 275 | 275 | 275 | 286 | 264 | 264 | 264 | 264 | 264 | 264 | 220 | 264 | 0 | 0 | 257.4 | 190.35 | 270.6 | 0 | 292.6 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 300.375 | 223.3 | 223.3 | 191.4 | 159.5 | 207.9 | 239.8 | 278.125 | 300.375 | 289.25 | 289.25 | 278.125 | 289.25 | 300.375 | 300.375 | 257.4 | 277.2 | 257.4 | 267.3 | 247.5 | 0 | 353.3 | 287.1 | 100.5 | 267.3 | 257.4 | 0 | 0 | 239.25 | 255.2 | 261 | 257.4 | 241.2 | 67019.4
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261
Date | BLK1_INV1 | BLK1_INV2 | BLK1_INV3 | BLK1_INV4 | BLK1_INV5 | BLK1_INV6 | BLK1_INV7 | BLK1_INV8 | BLK1_INV9 | BLK1_INV10 | BLK1_INV11 | BLK1_INV12 | BLK1_INV13 | BLK1_INV14 | BLK1_INV15 | BLK1_INV16 | BLK1_INV17 | BLK1_INV18 | BLK1_INV19 | BLK1_INV20 | BLK1_INV21 | BLK1_INV22 | BLK1_INV23 | BLK1_INV24 | BLK1_INV25 | BLK1_INV26 | BLK1_INV27 | BLK1_INV28 | BLK1_INV29 | BLK1_INV30 | BLK1_INV31 | BLK1_INV32 | BLK2_INV1 | BLK2_INV2 | BLK2_INV3 | BLK2_INV4 | BLK2_INV5 | BLK2_INV6 | BLK2_INV7 | BLK2_INV8 | BLK2_INV9 | BLK2_INV10 | BLK2_INV11 | BLK2_INV12 | BLK2_INV13 | BLK2_INV14 | BLK2_INV15 | BLK2_INV16 | BLK2_INV17 | BLK2_INV18 | BLK2_INV19 | BLK2_INV20 | BLK2_INV21 | BLK2_INV22 | BLK2_INV23 | BLK2_INV24 | BLK2_INV25 | BLK2_INV26 | BLK2_INV27 | BLK2_INV28 | BLK2_INV29 | BLK2_INV30 | BLK2_INV31 | BLK2_INV32 | BLK3_INV1 | BLK3_INV2 | BLK3_INV3 | BLK3_INV4 | BLK3_INV5 | BLK3_INV6 | BLK3_INV7 | BLK3_INV8 | BLK3_INV9 | BLK3_INV10 | BLK3_INV11 | BLK3_INV12 | BLK3_INV13 | BLK3_INV14 | BLK3_INV15 | BLK3_INV16 | BLK3_INV17 | BLK3_INV18 | BLK3_INV19 | BLK3_INV20 | BLK3_INV21 | BLK3_INV22 | BLK3_INV23 | BLK3_INV24 | BLK3_INV25 | BLK3_INV26 | BLK3_INV27 | BLK3_INV28 | BLK3_INV29 | BLK3_INV30 | BLK3_INV31 | BLK4_INV1 | BLK4_INV2 | BLK4_INV3 | BLK4_INV4 | BLK4_INV5 | BLK4_INV6 | BLK4_INV7 | BLK4_INV8 | BLK4_INV9 | BLK4_INV10 | BLK4_INV11 | BLK4_INV12 | BLK4_INV13 | BLK4_INV14 | BLK4_INV15 | BLK4_INV16 | BLK4_INV17 | BLK4_INV18 | BLK4_INV19 | BLK4_INV20 | BLK4_INV21 | BLK4_INV22 | BLK4_INV23 | BLK4_INV24 | BLK4_INV25 | BLK4_INV26 | BLK4_INV27 | BLK4_INV28 | BLK4_INV29 | BLK4_INV30 | BLK4_INV31 | BLK5_INV1 | BLK5_INV2 | BLK5_INV3 | BLK5_INV4 | BLK5_INV5 | BLK5_INV6 | BLK5_INV7 | BLK5_INV8 | BLK5_INV9 | BLK5_INV10 | BLK5_INV11 | BLK5_INV12 | BLK5_INV13 | BLK5_INV14 | BLK5_INV15 | BLK5_INV16 | BLK5_INV17 | BLK5_INV18 | BLK5_INV19 | BLK5_INV20 | BLK5_INV21 | BLK5_INV22 | BLK5_INV23 | BLK5_INV24 | BLK5_INV25 | BLK5_INV26 | BLK5_INV27 | BLK5_INV28 | BLK5_INV29 | BLK5_INV30 | BLK5_INV31 | BLK5_INV32 | BLK6_INV1 | BLK6_INV2 | BLK6_INV3 | BLK6_INV4 | BLK6_INV5 | BLK6_INV6 | BLK6_INV7 | BLK6_INV8 | BLK6_INV9 | BLK6_INV10 | BLK6_INV11 | BLK6_INV12 | BLK6_INV13 | BLK6_INV14 | BLK6_INV15 | BLK6_INV16 | BLK6_INV17 | BLK6_INV18 | BLK6_INV19 | BLK6_INV20 | BLK6_INV21 | BLK6_INV22 | BLK6_INV23 | BLK6_INV24 | BLK6_INV25 | BLK6_INV26 | BLK6_INV27 | BLK6_INV28 | BLK6_INV29 | BLK6_INV30 | BLK6_INV31 | BLK6_INV32 | BLK7_INV1 | BLK7_INV2 | BLK7_INV3 | BLK7_INV4 | BLK7_INV5 | BLK7_INV6 | BLK7_INV7 | BLK7_INV8 | BLK7_INV9 | BLK7_INV10 | BLK7_INV11 | BLK7_INV12 | BLK7_INV13 | BLK7_INV14 | BLK7_INV15 | BLK7_INV16 | BLK7_INV17 | BLK7_INV18 | BLK7_INV19 | BLK7_INV20 | BLK7_INV21 | BLK7_INV22 | BLK7_INV23 | BLK7_INV24 | BLK7_INV25 | BLK7_INV26 | BLK7_INV27 | BLK7_INV28 | BLK7_INV29 | BLK7_INV30 | BLK7_INV31 | BLK7_INV32 | BLK8_INV1 | BLK8_INV2 | BLK8_INV3 | BLK8_INV4 | BLK8_INV5 | BLK8_INV6 | BLK8_INV7 | BLK8_INV8 | BLK8_INV9 | BLK8_INV10 | BLK8_INV11 | BLK8_INV12 | BLK8_INV13 | BLK8_INV14 | BLK8_INV15 | BLK8_INV16 | BLK8_INV17 | BLK8_INV18 | BLK8_INV19 | BLK8_INV20 | BLK8_INV21 | BLK8_INV22 | BLK8_INV23 | BLK8_INV24 | BLK8_INV25 | BLK8_INV26 | BLK8_INV27 | BLK8_INV28 | Plnat
2025-06-05 | 4.4114 | 4.6638 | 4.6629 | 4.6629 | 4.643 | 4.6704 | 4.6929 | 4.5993 | 4.6526 | 4.6706 | 4.7865 | 4.764 | 4.6816 | 4.8049 | 4.6891 | 4.6592 | 4.4607 | 4.6292 | 4.6742 | 4.6707 | 4.6966 | 4.5131 | 4.5635 | 4.7141 | 4.726 | 4.6845 | 4.6534 | 4.6309 | 4.7041 | 4.6009 | 4.1748 | 4.2913 | 4.7681 | 4.3312 | 4.5393 | 4.7574 | 4.6704 | 4.6442 | 4.7079 | 4.7865 | 4.6966 | 4.6592 | 4.7228 | 4.2622 | 4.7154 | 4.7603 | 4.7295 | 4.4831 | 4.6849 | 4.6058 | 4.7228 | 4.5431 | 4.814 | 4.7507 | 4.6949 | 4.7674 | 4.7873 | 4.794 | 4.7274 | 4.794 | 4.5431 | 4.5734 | 4.6966 | 4.0042 | 4.9127 | 4.8228 | 4.9542 | 4.5324 | 4.9101 | 4.8614 | 4.9363 | 4.9288 | 5.0112 | 4.9026 | 4.9938 | 4.8772 | 4.9705 | 4.7865 | 4.6929 | 4.8297 | 4.9401 | 4.9213 | 4.8839 | 5.1685 | 4.9176 | 4.8727 | 4.9738 | 4.9401 | 4.9251 | 4.8989 | 4.8863 | 4.6569 | 5.0487 | 5.0225 | 4.4112 | 4.3333 | 4.8165 | 4.9326 | 4.8614 | 4.8876 | 5.0187 | 4.8801 | 4.9625 | 4.8427 | 4.9072 | 4.9476 | 5.1203 | 4.8344 | 4.9363 | 4.7973 | 4.9162 | 4.4875 | 4.8506 | 4.8772 | 4.9064 | 4.4569 | 4.811 | 4.9205 | 4.8906 | 4.9288 | 4.9738 | 4.6608 | 4.5809 | 4.9139 | 4.9588 | 4.1715 | 4.1386 | 4.2097 | 4.6642 | 4.6042 | 4.4425 | 4.6327 | 4.6119 | 4.666 | 4.9021 | 4.507 | 4.6748 | 4.2692 | 4.6993 | 4.6742 | 4.5601 | 4.4978 | 4.6479 | 4.6914 | 4.5206 | 4.605 | 4.6367 | 4.7109 | 4.6223 | 4.6742 | 4.7087 | 4.6779 | 4.7607 | 4.7004 | 4.6142 | 4.573 | 4.6966 | 4.5805 | 4.9621 | 4.8106 | 4.9091 | 4.7879 | 4.8384 | 4.7508 | 4.8788 | 4.9091 | 4.7083 | 4.8081 | 4.9356 | 4.7345 | 4.8182 | 4.9382 | 4.7744 | 4.8291 | 4.7677 | 4.8939 | 4.947 | 4.822 | 4.8451 | 5.0189 | 4.8881 | 4.7542 | 4.9663 | 4.9636 | 4.9476 | 4.798 | 4.9636 | 4.9636 | 4.7964 | 4.9371 | 4.7955 | 4.8371 | 4.7273 | 4.8485 | 4.8106 | 4.8598 | 4.8455 | 4.9242 |  |  | 4.3939 | 4.7176 | 4.6711 |  | 4.6241 | 4.8614 | 4.9438 | 4.8052 | 4.9064 | 4.8951 | 4.9663 | 4.9625 | 4.9663 | 4.9963 | 4.9363 | 4.9401 | 4.8872 | 4.9771 | 5.3292 | 5.1993 | 4.7179 | 5.1724 | 4.6417 | 4.7206 | 4.8899 | 4.8506 | 4.8539 | 4.7087 | 4.6526 | 4.7606 | 4.8173 | 4.6342 | 4.7786 | 4.6789 | 4.6542 | 4.856 | 4.8889 |  | 4.8061 | 4.7266 | 4.8557 | 4.856 | 5.2797 |  |  | 5.605 | 4.6395 | 5.0192 | 4.6542 | 4.6517 | 4.7646
2025-06-06 | 4.7537 | 4.8608 | 4.6779 | 4.8652 | 4.8228 | 4.8539 | 4.8539 | 4.4607 | 4.8324 | 4.8575 | 4.9363 | 4.9139 | 4.839 | 4.9683 | 4.839 | 4.8202 | 4.5993 | 4.7828 | 4.7986 | 4.7986 | 4.8352 | 4.6517 | 4.7191 | 4.8539 | 4.8539 | 4.809 | 4.7813 | 4.7707 | 4.834 | 4.7541 | 4.228 | 4.4345 | 4.8428 | 4.7168 | 4.6105 | 4.8377 | 4.8464 | 4.7303 | 4.8015 | 4.8727 | 4.7865 | 4.7528 | 4.8165 | 4.3221 | 4.7978 | 4.8427 | 4.8055 | 4.5693 | 4.5987 | 4.5375 | 4.8315 | 4.6292 | 4.9005 | 4.8273 | 4.7848 | 4.8772 | 4.8706 | 4.8689 | 4.7973 | 4.8506 | 4.8577 | 4.8879 | 4.7491 | 4.046 | 4.8332 | 4.7952 | 4.8021 | 4.4183 | 4.8202 | 4.6816 | 4.7378 | 4.8277 | 4.8315 | 4.8315 | 4.7374 | 4.6176 | 4.6708 | 4.6816 | 4.5206 | 4.522 | 4.5281 | 4.7865 | 4.8277 | 4.5281 | 4.7453 | 4.8315 | 4.7378 | 4.8427 | 4.6629 | 4.6667 | 4.6778 | 4.4806 | 4.8352 | 4.8502 | 4.3546 | 4.3146 | 4.6816 | 4.8502 | 4.794 | 4.8127 | 4.9438 | 4.8052 | 4.9026 | 4.7978 | 4.8972 | 4.8727 | 5.1203 | 4.811 | 4.8689 | 4.7308 | 4.8643 | 4.7571 | 4.794 | 4.8273 | 4.8127 | 4.3596 | 4.7942 | 4.8672 | 4.8473 | 4.8652 | 4.9139 | 4.6608 | 4.5243 | 4.8502 | 4.8876 | 4.3213 | 4.3034 | 4.3745 | 4.8473 | 4.784 | 4.6188 | 4.8228 | 4.8021 | 4.858 | 5.1224 | 4.7378 | 4.9161 | 4.5 | 4.9474 | 4.9101 | 4.7502 | 4.6811 | 4.8839 | 4.9058 | 4.7528 | 4.9715 | 4.8352 | 4.8948 | 4.8124 | 4.8643 | 4.8954 | 4.8652 | 4.9571 | 4.8876 | 4.8015 | 4.7528 | 4.8689 | 4.7753 | 4.9167 | 4.6932 | 4.8586 | 4.7614 | 4.8114 | 4.7172 | 4.7542 | 4.9018 | 4.625 | 4.7576 | 4.8409 | 4.6909 | 4.7345 | 4.8727 | 4.7071 | 4.7345 | 4.7845 | 4.8409 | 4.928 | 4.7614 | 4.7172 | 4.9735 | 4.8182 | 4.7172 | 4.9158 | 4.9745 | 4.9021 | 4.7508 | 5.0109 | 4.9455 | 4.7673 | 4.9615 | 4.8674 | 4.7576 | 4.7008 | 4.7992 | 4.8068 | 4.8409 | 4.9182 | 4.9167 |  |  | 4.4716 | 4.7912 | 4.745 |  | 4.7676 | 4.8801 | 4.8727 | 4.764 | 4.8277 | 4.8502 | 4.8801 | 4.8689 | 4.8801 | 4.9476 | 4.8727 | 4.8801 | 4.8473 | 4.9438 | 5.3381 | 5.2127 | 5.1097 | 4.8903 | 4.7042 | 4.804 | 4.8144 | 4.8073 | 4.7675 | 4.8021 | 4.7101 | 4.809 | 4.774 | 4.6542 | 4.8446 | 4.7258 | 4.7708 | 4.8223 | 4.8121 |  | 4.7495 | 4.8694 | 4.7861 | 4.8148 | 4.7086 |  |  | 4.9028 | 4.7414 | 4.8659 | 4.5765 | 4.5937 | 4.7823
2025-06-07 | 5.0614 | 5.1858 | 4.9888 | 5.1985 | 5.1409 | 5.1723 | 5.1723 | 4.7753 | 5.1344 | 5.1596 | 5.2622 | 5.2285 | 5.1573 | 5.2952 | 5.1461 | 5.1311 | 4.8989 | 5.0974 | 5.0994 | 5.1167 | 5.1648 | 4.9551 | 5.0441 | 5.1802 | 5.1893 | 5.1305 | 5.1063 | 5.1003 | 5.1469 | 5.0803 | 4.3612 | 4.7407 | 5.3577 | 5.0157 | 4.8951 | 5.1288 | 5.1386 | 5.03 | 5.1049 | 5.1985 | 5.1049 | 5.0487 | 5.1348 | 4.6554 | 5.1461 | 5.176 | 5.1478 | 4.8914 | 4.8863 | 4.8288 | 5.1423 | 4.9288 | 5.2301 | 5.1536 | 5.0821 | 5.2002 | 5.1835 | 5.1798 | 5.1003 | 5.1569 | 5.1685 | 5.1924 | 5.1049 | 4.5977 | 5.0303 | 4.9611 | 4.9853 | 4.7329 | 4.97 | 4.9588 | 4.985 | 4.9625 | 5.0112 | 4.9738 | 4.9938 | 4.9105 | 4.9605 | 4.9738 | 4.8277 | 4.8297 | 4.9401 | 5.161 | 5.0637 | 4.8989 | 5.0375 | 5.0262 | 4.9738 | 5.0337 | 4.9888 | 4.9775 | 4.9798 | 5.0579 | 5.0487 | 5.0225 | 4.6941 | 4.6442 | 5.0674 | 5.1723 | 5.1124 | 5.1348 | 5.2697 | 5.1273 | 5.2135 | 5.0936 | 5.1968 | 5.176 | 5.3566 | 5.1221 | 5.1985 | 5.0004 | 5.1927 | 4.9957 | 5.0137 | 5.1402 | 5.161 | 4.6816 | 5.0987 | 5.1569 | 5.1236 | 5.1835 | 5.2509 | 5.0004 | 4.8539 | 5.1723 | 5.206 | 4.6109 | 4.573 | 4.6442 | 5.1569 | 5.0836 | 4.8989 | 5.1132 | 5.1063 | 5.1767 | 5.4126 | 5.049 | 5.2343 | 4.7867 | 5.2099 | 5.1461 | 5.0406 | 4.9196 | 5.1873 | 5.1893 | 5.0225 | 5.0717 | 5.0936 | 5.1726 | 5.1029 | 5.1478 | 5.1893 | 5.1536 | 5.2335 | 5.1798 | 5.1049 | 5.0562 | 5.206 | 5.0824 | 5.2197 | 5.0076 | 5.3131 | 5.1629 | 5.3468 | 5.2626 | 5.0842 | 5.4473 | 5.1629 | 5.2626 | 5.5985 | 5.1273 | 5.12 | 5.3745 | 5.0842 | 5.0836 | 5.0774 | 5.2955 | 5.3333 | 5.1629 | 5.2626 | 5.3409 | 5.1678 | 5.0438 | 5.2626 | 5.32 | 5.2517 | 5.0606 | 5.4473 | 5.3745 | 5.4473 | 5.2797 | 5.1515 | 5.1136 | 5.053 | 5.1818 | 5.1705 | 5.1932 | 5.2682 | 5.2992 |  |  | 4.7747 | 5.243 | 5.0443 |  | 5.082 | 5.1873 | 5.1723 | 5.0262 | 5.1461 | 5.1948 | 5.206 | 5.1985 | 5.2097 | 5.2659 | 5.2172 | 5.2434 | 5.1935 | 5.2967 | 5.6964 | 5.5755 | 5.2142 | 6.3323 | 5.1371 | 5.5963 | 5.1056 | 5.0137 | 4.9957 | 5.0303 | 5.0013 | 5.1167 | 5.0603 | 5.0037 | 5.0505 | 5.0289 | 5.1243 | 5.2076 | 5.2444 |  | 5.0524 | 5.1794 | 5.1741 | 4.9832 | 5.0389 |  |  | 5.0073 | 5.1136 | 5.2261 | 4.899 | 5.0539 | 5.1091
2025-06-08 | 4.903 | 5.0164 | 4.9004 | 5.0266 | 4.9822 | 5.0116 | 5.0142 | 5.0262 | 4.9776 | 5.0049 | 4.9022 | 5.0824 | 5.0011 | 5.1363 | 5.0049 | 4.9813 | 4.8629 | 4.9577 | 4.9753 | 4.977 | 5.0225 | 4.9105 | 4.8837 | 5.0234 | 5.0475 | 4.9867 | 4.9639 | 4.9491 | 5.0134 | 4.9315 | 4.6782 | 4.799 | 4.9969 | 4.8848 | 4.8738 | 4.9957 | 5.0105 | 4.891 | 4.9959 | 5.0528 | 4.9581 | 4.9146 | 5.0097 | 4.9655 | 5.0397 | 5.0513 | 5.0337 | 4.9798 | 4.9611 | 4.8784 | 5.0337 | 5.036 | 5.1246 | 5.05 | 4.9411 | 5.0387 | 5.0314 | 5.0375 | 4.967 | 5.0267 | 5.0281 | 5.0646 | 4.8075 | 5.4073 | 4.986 | 4.9549 | 5.0258 | 4.8823 | 4.9524 | 4.9858 | 5.0146 | 4.9925 | 5.1067 | 4.9431 | 5.0687 | 4.9608 | 5.0504 | 5.0079 | 4.9479 | 4.9258 | 5.0228 | 5.0434 | 4.9798 | 5.0494 | 5.0307 | 5.0419 | 5.0554 | 4.7079 | 4.9712 | 4.9124 | 4.942 | 4.883 | 5.1221 | 5.1258 | 4.9721 | 4.7236 | 4.9221 | 5.024 | 4.961 | 4.9828 | 5.1116 | 4.9753 | 5.0663 | 4.9494 | 5.0577 | 5.0288 | 5.2528 | 4.9528 | 5.0416 | 4.8786 | 5.0137 | 4.8532 | 4.9019 | 4.9924 | 5.0116 | 4.7562 | 4.9679 | 5.0151 | 4.9861 | 5.0333 | 5.0876 | 4.9655 | 4.9888 | 5.0139 | 5.0464 | 4.9988 | 4.4745 | 4.5521 | 5.0327 | 4.9591 | 4.8436 | 4.9825 | 4.9673 | 5.0374 | 5.3007 | 4.935 | 5.0986 | 4.6962 | 5.0934 | 5.0345 | 4.9131 | 4.8436 | 5.0603 | 5.0593 | 4.912 | 4.9483 | 4.9727 | 5.0435 | 4.9639 | 5.0071 | 5.0562 | 5.0255 | 5.0986 | 5.039 | 4.9633 | 4.9172 | 4.9607 | 5.0015 | 4.9663 | 4.9826 | 4.998 | 4.9716 | 5.0071 | 4.9411 | 4.9882 | 5.4585 | 4.9678 | 4.9731 | 5.0057 | 4.8927 | 4.9069 | 5.0524 | 4.8599 | 4.8782 | 5.0114 | 5.0057 | 4.9977 | 4.9845 | 4.9879 | 5.017 | 4.9818 | 5.0114 | 5.0384 | 5.1109 | 5.0388 | 5.0384 | 4.9073 | 4.8698 | 4.8818 | 4.8895 | 5.008 | 4.9958 | 4.6069 | 4.9674 | 5.014 | 4.6417 | 5.1341 | 5.1379 |  |  | 4.636 | 4.8826 | 4.9095 |  | 5.0154 | 4.8558 | 5.0232 | 4.9228 | 4.9985 | 5.0127 | 5.0528 | 5.0434 | 5.0509 | 5.1135 | 5.0899 | 5.1071 | 5.0477 | 5.1635 | 5.5087 | 5.2548 | 5.256 | 5.4307 | 4.8538 | 4.8849 | 4.9693 | 4.9442 | 4.8854 | 4.8785 | 5.0377 | 4.9594 | 4.9208 | 5.0307 | 5.0443 | 5.0905 | 5.1336 | 5.1455 | 5.0723 |  | 5.0931 | 4.8798 | 4.9264 | 4.85 | 4.9161 |  |  | 5.0508 | 5.0721 | 5.0716 | 4.8217 | 5.0394 | 4.9881
2025-06-09 | 5.0506 | 5.0932 | 4.961 | 5.1652 | 5.107 | 5.1547 | 5.0805 | 5.112 | 5.0725 | 5.1114 | 5.1809 | 5.1558 | 5.0787 | 5.0296 | 5.0723 | 5.0532 | 5.0419 | 5.0345 | 5.0503 | 5.0596 | 5.0948 | 5.1049 | 5.0558 | 5.0996 | 5.1305 | 5.0645 | 5.042 | 5.0304 | 5.0986 | 5.0077 | 5.0307 | 4.9988 | 5.0456 | 4.9341 | 4.8142 | 5.0572 | 5.0734 | 4.9528 | 5.027 | 5.1079 | 5.0772 | 4.9652 | 5.0603 | 5.015 | 5.0929 | 5.1019 | 5.0921 | 5.0356 | 5.0689 | 4.9916 | 5.1217 | 5.1139 | 5.0976 | 5.1203 | 5.0434 | 5.064 | 5.103 | 5.1071 | 5.049 | 5.0963 | 5.1007 | 5.1352 | 5.1213 | 5.4667 | 5.1105 | 5.0787 | 5.1488 | 4.9715 | 5.009 | 5.0644 | 5.094 | 5.073 | 5.0974 | 4.9873 | 5.1362 | 5.0337 | 5.1239 | 5.0652 | 5.0154 | 4.9857 | 5.085 | 5.1079 | 5.0431 | 5.1075 | 5.0981 | 5.1146 | 5.1206 | 4.8764 | 5.0397 | 4.9873 | 5.0298 | 4.9476 | 5.0899 | 5.1476 | 5.0883 | 4.7846 | 4.9865 | 5.0959 | 5.0232 | 5.0577 | 5.0787 | 5.0476 | 5.0749 | 5.0221 | 5.1506 | 5.1157 | 4.9971 | 5.0582 | 5.1191 | 4.9382 | 5.1035 | 4.9476 | 4.9358 | 5.058 | 5.0801 | 4.7809 | 5.0194 | 5.0983 | 5.0753 | 5.1232 | 5.1764 | 4.9581 | 4.9768 | 5.0978 | 5.133 | 5.1612 | 4.9348 | 5.0075 | 5.092 | 5.0294 | 4.8494 | 5.052 | 5.0368 | 4.9969 | 5.0839 | 4.985 | 5.1874 | 4.8472 | 5.1092 | 5.0599 | 4.9867 | 4.9182 | 5.1438 | 5.2003 | 5.0655 | 5.0901 | 5.1075 | 5.1367 | 5.0506 | 5.0869 | 5.1426 | 5.1041 | 5.0836 | 5.121 | 5.0397 | 4.9854 | 5.0363 | 5.0109 | 5.0511 | 5.0462 | 5.1364 | 5.0436 | 5.1566 | 5.0879 | 5.1047 | 5.0335 | 5.0307 | 5.1822 | 5.0549 | 5.016 | 5.06 | 5.0425 | 5.1239 | 5.0669 | 5.0539 | 5.0777 | 5.0129 | 5.0515 | 5.0572 | 5.0318 | 4.9979 | 5.0404 | 5.1374 | 5.0524 | 5.0273 | 5.0471 | 5.0524 | 5.0767 | 5.0353 | 5.0168 | 5.1015 | 5.0833 | 4.9739 | 5.0644 | 5.1011 | 5.139 | 5.2141 | 5.2193 |  |  | 4.7323 | 4.9462 | 4.9523 |  | 5.0824 | 4.9637 | 5.1187 | 4.9536 | 5.0835 | 5.0876 | 5.1337 | 5.1243 | 5.1255 | 5.1663 | 5.1659 | 5.1948 | 5.1392 | 5.2248 | 5.3789 | 5.365 | 5.3422 | 5.2871 | 4.9856 | 5.0088 | 5.0542 | 5.0221 | 4.9704 | 4.9694 | 5.1254 | 5.032 | 5.0031 | 4.9971 | 5.0987 | 5.0224 | 4.9662 | 5.0333 | 5.0707 |  | 5.0538 | 4.9955 | 4.9851 | 4.9495 | 4.9907 |  |  | 5.2247 | 5.2202 | 5.1916 | 4.9153 | 4.9295 | 5.0649
2025-06-10 | 5.3815 | 5.5032 | 5.5213 | 5.5052 | 5.4717 | 5.5165 | 5.4895 | 5.5109 | 5.4623 | 5.4943 | 5.33 | 5.4086 | 5.4921 | 5.4427 | 5.4865 | 5.4629 | 5.4498 | 5.4266 | 5.3756 | 5.3936 | 5.4779 | 5.4963 | 5.442 | 5.2864 | 5.4562 | 5.3895 | 5.3625 | 5.351 | 5.4136 | 5.327 | 5.3303 | 5.3147 | 5.3711 | 5.2716 | 5.3446 | 5.4386 | 5.4184 | 5.2794 | 5.3764 | 5.4506 | 5.3397 | 5.485 | 5.4663 | 5.3371 | 5.4461 | 5.4554 | 5.4372 | 5.3577 | 5.3875 | 5.3091 | 5.4491 | 5.4378 | 5.5384 | 5.4489 | 5.414 | 5.4412 | 5.2767 | 5.3599 | 5.4375 | 5.4202 | 5.4303 | 5.4637 | 5.4434 | 5.4382 | 5.4493 | 5.4112 | 5.4043 | 5.2733 | 5.3127 | 5.4007 | 5.43 | 5.4067 | 5.4502 | 5.4536 | 5.4272 | 5.3333 | 5.4372 | 5.3491 | 5.336 | 5.376 | 5.4142 | 5.4352 | 5.37 | 5.4382 | 5.4262 | 5.4438 | 5.4566 | 5.4157 | 5.3749 | 5.321 | 5.3138 | 5.3729 | 5.4045 | 5.364 | 5.4309 | 5.3165 | 5.3011 | 5.4326 | 5.3307 | 5.3974 | 5.2476 | 5.3865 | 5.4835 | 5.3685 | 5.3137 | 5.4633 | 5.3973 | 5.4038 | 5.4869 | 5.297 | 5.4648 | 5.2933 | 5.3237 | 5.4052 | 5.4476 | 5.5491 | 5.3071 | 5.4379 | 5.3859 | 5.4401 | 5.4652 | 5.2837 | 5.297 | 5.4996 | 5.4978 | 5.4958 | 5.3097 | 5.4187 | 5.5048 | 5.4405 | 5.452 | 5.478 | 5.3625 | 5.3569 | 5.4479 | 5.4017 | 5.4444 | 5.3888 | 5.4332 | 5.3936 | 5.4047 | 5.2933 | 5.3895 | 5.3763 | 5.4423 | 5.4468 | 5.3858 | 5.4705 | 5.3867 | 5.4264 | 5.4759 | 5.4427 | 5.3806 | 5.373 | 5.4464 | 5.3363 | 5.339 | 5.3577 | 5.3072 | 5.2962 | 5.4582 | 5.3451 | 5.4515 | 5.3906 | 5.3785 | 5.3167 | 5.3602 | 5.3741 | 5.3318 | 5.3084 | 5.3178 | 5.2938 | 5.4249 | 5.2618 | 5.3576 | 5.3375 | 5.3617 | 5.3223 | 5.3754 | 5.3508 | 5.3643 | 5.4007 | 5.3684 | 5.3058 | 5.3395 | 5.5593 | 5.2913 | 5.2709 | 5.2996 | 5.349 | 5.4398 | 5.4061 | 5.2773 | 5.2992 | 5.4439 | 5.4837 | 5.3468 | 5.3451 |  |  | 5.0606 | 5.3118 | 5.2997 |  | 5.4053 | 5.285 | 5.4472 | 5.3712 | 5.4243 | 5.4378 | 5.4745 | 5.3524 | 5.4652 | 5.4333 | 5.2779 | 5.4101 | 5.4412 | 5.4039 | 5.6162 | 5.6162 | 5.6818 | 5.3987 | 5.2963 | 5.3053 | 5.4875 | 5.4166 | 5.3853 | 5.2899 | 5.3792 | 5.4088 | 5.4049 | 5.3303 | 5.3294 | 5.2854 | 5.3539 | 5.3651 | 5.3782 |  | 5.319 | 5.2773 | 5.3841 | 5.3651 | 5.3139 |  |  | 5.4867 | 5.4976 | 4.4192 | 5.3477 | 5.2973 | 5.3908
2025-06-11 | 5.0275 | 5.1457 | 4.9524 | 5.1461 | 5.1118 | 5.0903 | 5.133 | 5.0978 | 5.1063 | 5.1376 | 5.1352 | 5.0603 | 5.1386 | 5.2629 | 5.1423 | 5.1225 | 5.1169 | 5.1067 | 5.1319 | 5.1419 | 5.167 | 5.1708 | 5.0133 | 5.0973 | 5.0721 | 5.134 | 5.1122 | 5.0993 | 5.1352 | 5.1143 | 5.1456 | 5.0743 | 5.0303 | 5.0175 | 4.9996 | 5.0723 | 5.0588 | 4.9667 | 5.0213 | 5.0854 | 4.991 | 4.936 | 5.0262 | 4.9816 | 5.0697 | 5.0884 | 5.0742 | 5.0105 | 5.042 | 4.9625 | 5.0925 | 5.0846 | 5.1789 | 5.0873 | 5.0458 | 5.0573 | 5.1536 | 5.0978 | 5.1103 | 5.064 | 5.0745 | 5.1114 | 5.0861 | 5.1122 | 5.106 | 5.078 | 5.144 | 4.9984 | 5.0277 | 5.0393 | 5.0719 | 5.0513 | 5.1573 | 4.9816 | 5.064 | 5.0623 | 5.0707 | 5.0663 | 4.9888 | 4.958 | 5.0685 | 5.0876 | 5.0191 | 5.0775 | 5.0659 | 5.0839 | 5.1 | 5.0112 | 5.0165 | 4.9727 | 5.0387 | 4.948 | 5.0981 | 5.1266 | 5.1052 | 4.9835 | 4.9427 | 5.091 | 5.0202 | 5.1262 | 5.1007 | 5.0633 | 5.1386 | 4.9693 | 4.9452 | 5.1509 | 4.9808 | 5.0555 | 5.0607 | 4.9844 | 5.0168 | 4.986 | 4.9475 | 5.1386 | 5.0382 | 5.1929 | 5.0759 | 5.1655 | 4.9971 | 5.0757 | 5.0794 | 4.9971 | 4.9814 | 5.0981 | 5.0813 | 5.1306 | 4.9476 | 5.0663 | 5.1522 | 5.0836 | 5.0925 | 5.1084 | 5.1011 | 5.1714 | 5.0909 | 5.0486 | 5.1283 | 5.101 | 5.1933 | 5.164 | 5.0482 | 4.9732 | 5.0843 | 5.0444 | 5.0513 | 5.0807 | 5.0963 | 5.055 | 5.1156 | 5.0244 | 5.1001 | 5.0607 | 5.1509 | 5.0678 | 5.0547 | 5.0607 | 5.0768 | 5.0172 | 4.9629 | 5.0019 | 4.9906 | 4.9678 | 4.9343 | 4.9869 | 4.9414 | 4.9716 | 5.0057 | 4.9545 | 4.9716 | 5.044 | 4.9789 | 4.9862 | 4.9478 | 4.9705 | 4.9545 | 4.9678 | 4.983 | 4.9602 | 4.9535 | 4.9678 | 5.1091 | 5.0007 | 5.0061 | 4.9785 | 5.1451 | 4.9882 | 4.9862 | 5.0953 | 5.0116 | 5.1465 | 5.078 | 5.0436 | 4.9742 | 5.0485 | 5.0841 | 5.1174 | 5.005 | 5.0121 |  |  | 4.7238 | 4.9913 | 4.9586 |  | 5.069 | 5.0232 | 5.0933 | 5.0022 | 5.0655 | 5.0787 | 5.115 | 5.1045 | 5.1056 | 5.164 | 5.006 | 5.1948 | 5.1219 | 5.1309 | 5.2893 | 5.0654 | 5.0742 | 5.1611 | 5.0515 | 5.0546 | 5.1258 | 5.1036 | 5.032 | 4.9407 | 5.1613 | 5.0527 | 4.9545 | 4.9525 | 4.9542 | 4.9693 | 5 | 5.0247 | 5.0149 |  | 5.5338 | 4.9955 | 5.1851 | 4.9495 | 4.9635 |  |  | 5.3333 | 5.3491 | 5.3686 | 4.9425 | 5.1169 | 5.0623
2025-06-12 | 4.5673 | 4.6769 | 4.6187 | 4.6809 | 4.6482 | 4.6895 | 4.682 | 4.6858 | 4.645 | 4.6698 | 4.6142 | 4.6105 | 4.6693 | 4.6333 | 4.6689 | 4.6551 | 4.6453 | 4.6315 | 4.6742 | 4.6669 | 4.6865 | 4.5393 | 4.6707 | 4.6342 | 4.6603 | 4.6773 | 4.6527 | 4.6608 | 4.7008 | 4.6365 | 4.6246 | 4.6489 | 4.6997 | 4.53 | 4.6861 | 4.5393 | 4.7139 | 4.5779 | 4.5697 | 4.6416 | 4.6311 | 4.5479 | 4.5783 | 4.5375 | 4.6101 | 4.627 | 4.6188 | 4.5693 | 4.5853 | 4.5206 | 4.63 | 4.6277 | 4.7208 | 4.6246 | 4.613 | 4.6885 | 4.7001 | 4.7049 | 4.6445 | 4.6309 | 4.7186 | 4.6035 | 4.6303 | 4.6228 | 4.6327 | 4.5978 | 4.6659 | 4.5438 | 4.5816 | 4.5768 | 4.6097 | 4.5888 | 4.6854 | 4.6037 | 4.6209 | 4.6618 | 4.7407 | 4.7022 | 4.6453 | 4.5787 | 4.6592 | 4.6255 | 4.6772 | 4.6554 | 4.5929 | 4.6079 | 4.7172 | 4.6816 | 4.5708 | 4.536 | 4.5893 | 4.6852 | 4.6217 | 4.603 | 4.6345 | 4.6723 | 4.6086 | 4.618 | 4.6689 | 4.6648 | 4.6217 | 4.6678 | 4.6592 | 4.5404 | 4.5626 | 4.7064 | 4.6176 | 4.6173 | 4.7019 | 4.5979 | 4.6634 | 4.5746 | 4.5586 | 4.6548 | 4.6708 | 4.688 | 4.6109 | 4.6608 | 4.6469 | 4.6446 | 4.7296 | 4.5893 | 4.5986 | 4.6689 | 4.7079 | 4.6908 | 4.5805 | 4.6034 | 4.6901 | 4.6176 | 4.6213 | 4.6392 | 4.6282 | 4.6962 | 4.6643 | 4.6035 | 4.6573 | 4.6573 | 4.6778 | 4.6768 | 4.5632 | 4.5739 | 4.6554 | 4.6707 | 4.5562 | 4.6085 | 4.6303 | 4.7305 | 4.6704 | 4.7291 | 4.6638 | 4.6993 | 4.7334 | 4.6929 | 4.6315 | 4.6071 | 4.6273 | 4.6438 | 4.661 | 4.6799 | 4.5673 | 4.6648 | 4.564 | 4.5943 | 4.5761 | 4.6382 | 4.7178 | 4.6279 | 4.6947 | 4.6524 | 4.6236 | 4.6164 | 4.601 | 4.6596 | 4.6313 | 4.6648 | 4.7311 | 4.6758 | 4.6108 | 4.6837 | 4.5916 | 4.5842 | 4.6108 | 4.6524 | 4.6196 | 4.6178 | 4.6167 | 4.6135 | 4.6855 | 4.6364 | 4.6966 | 4.6477 | 4.5909 | 4.7136 | 4.6917 | 4.7348 | 4.6955 | 4.6326 |  |  | 4.256 | 4.5674 | 4.5536 |  | 4.5892 | 4.5356 | 4.6787 | 4.5393 | 4.6685 | 4.6034 | 4.5985 | 4.6378 | 4.7019 | 4.6918 | 4.5794 | 4.6903 | 4.6256 | 4.7178 | 4.7246 | 4.9069 | 4.7074 | 4.7335 | 4.5455 | 4.5413 | 4.6375 | 4.6202 | 4.5487 | 4.5739 | 4.6785 | 4.5677 | 4.6009 | 4.5643 | 4.7086 | 4.5491 | 4.6659 | 4.5342 | 4.5293 |  | 4.9674 | 4.6743 | 4.7363 | 4.5342 | 4.7863 |  |  | 4.9154 | 4.9216 | 4.887 | 4.526 | 4.5605 | 4.6409
2025-06-13 | 4.0736 | 4.1777 | 4.1187 | 4.1715 | 4.15 | 4.1843 | 4.1775 | 4.1809 | 4.1417 | 4.1507 | 4.2588 | 4.2221 | 4.1596 | 4.2742 | 4.167 | 4.1569 | 4.1491 | 4.1404 | 4.1736 | 4.1711 | 4.1933 | 4.2034 | 4.2562 | 4.233 | 4.2437 | 4.1929 | 4.1801 | 4.1884 | 4.2254 | 4.1608 | 4.1798 | 4.1984 | 4.204 | 4.0927 | 4.1929 | 4.0853 | 4.2206 | 4.1184 | 4.206 | 4.2689 | 4.1813 | 4.136 | 4.2266 | 4.1843 | 4.2356 | 4.2337 | 4.2258 | 4.1918 | 4.1187 | 4.0964 | 4.1588 | 4.176 | 4.286 | 4.2161 | 4.1158 | 4.1964 | 4.1958 | 4.2026 | 4.1478 | 4.2044 | 4.2442 | 4.2666 | 4.1434 | 4.2257 | 4.2634 | 4.1815 | 4.2278 | 4.0999 | 4.0921 | 4.2112 | 4.2382 | 4.2176 | 4.3 | 4.0865 | 4.2187 | 4.1588 | 4.2034 | 4.1723 | 4.1727 | 4.1006 | 4.2199 | 4.2273 | 4.1918 | 4.2513 | 4.2228 | 4.2142 | 4.2472 | 4.2101 | 4.194 | 4.1667 | 4.1294 | 4.0812 | 4.2861 | 4.2787 | 4.2573 | 4.1921 | 4.1536 | 4.2356 | 4.1974 | 4.2011 | 4.1985 | 4.2022 | 4.2655 | 4.121 | 4.0859 | 4.2318 | 4.1348 | 4.0826 | 4.2408 | 4.1378 | 4.1919 | 4.0833 | 4.0716 | 4.1491 | 4.2075 | 4.2427 | 4.1198 | 4.1272 | 4.1172 | 4.2015 | 4.2517 | 4.0836 | 4.0949 | 4.2195 | 4.2453 | 4.0746 | 4.0798 | 4.1071 | 4.2014 | 4.1315 | 4.1241 | 4.1352 | 4.1286 | 4.1986 | 4.1538 | 4.1245 | 4.1993 | 4.2161 | 4.2093 | 4.1539 | 4.075 | 4.0726 | 4.1876 | 4.1863 | 4.1423 | 4.1034 | 4.1315 | 4.2264 | 4.1836 | 4.2258 | 4.2213 | 4.2022 | 4.2367 | 4.209 | 4.1566 | 4.1236 | 4.1779 | 4.1966 | 4.2197 | 4.2087 | 4.2286 | 4.1318 | 4.1717 | 4.2273 | 4.1886 | 4.2393 | 4.1977 | 4.2542 | 4.2348 | 4.0782 | 4.1367 | 4.0767 | 4.1485 | 4.176 | 4.1178 | 4.2314 | 4.2273 | 4.1795 | 4.1785 | 4.2083 | 4.128 | 4.1623 | 4.1865 | 4.1127 | 4.1993 | 4.2121 | 4.1964 | 4.2145 | 4.0836 | 4.1073 | 4.1705 | 4.186 | 4.0833 | 4.2235 | 4.2386 | 4.2083 | 4.1364 | 4.1288 |  |  | 3.871 | 4.1082 | 4.0987 |  | 4.149 | 4.0865 | 4.2599 | 4.0865 | 4.1985 | 4.1918 | 4.206 | 4.206 | 4.1884 | 4.2217 | 4.2135 | 4.176 | 4.2127 | 4.2314 | 4.2723 | 4.4156 | 4.2894 | 4.1818 | 4.1419 | 4.0913 | 4.2075 | 4.1665 | 4.0868 | 4.1901 | 4.2754 | 4.3405 | 4.1039 | 4.1052 | 4.1026 | 4.1706 | 4.0793 | 4.1119 | 4.1111 |  | 4.1311 | 4.0968 | 4.1891 | 4.1571 | 4.1033 |  |  | 4.4514 | 4.4005 | 4.4054 | 4.1006 | 4.1522 | 4.1794
2025-06-14 | 4.5843 | 4.6811 | 4.5056 | 4.6929 | 4.6258 | 4.6667 | 4.633 | 4.6442 | 4.6022 | 4.6418 | 4.7191 | 4.7041 | 4.6292 | 4.7436 | 4.633 | 4.618 | 4.588 | 4.5843 | 4.5912 | 4.6016 | 4.6442 | 4.6592 | 4.7053 | 4.6575 | 4.6638 | 4.6188 | 4.5912 | 4.5843 | 4.6575 | 4.5743 | 4.5976 | 4.6109 | 4.6108 | 4.5225 | 4.5843 | 4.4898 | 4.618 | 4.5019 | 4.573 | 4.6367 | 4.5581 | 4.5243 | 4.5843 | 4.5281 | 4.5843 | 4.5993 | 4.5739 | 4.5356 | 4.6022 | 4.5231 | 4.6255 | 4.6142 | 4.6608 | 4.5843 | 4.5774 | 4.6975 | 4.6375 | 4.6479 | 4.5843 | 4.6509 | 4.6255 | 4.6671 | 4.5693 | 4.5434 | 4.5877 | 4.5532 | 4.6188 | 4.4944 | 4.5506 | 4.5281 | 4.5618 | 4.5356 | 4.6404 | 4.5655 | 4.6375 | 4.5543 | 4.6275 | 4.5843 | 4.5356 | 4.5393 | 4.5993 | 4.6142 | 4.5543 | 4.6217 | 4.5581 | 4.5693 | 4.5993 | 4.5543 | 4.5056 | 4.4719 | 4.5411 | 4.6016 | 4.6517 | 4.6142 | 4.561 | 4.5318 | 4.5094 | 4.603 | 4.5506 | 4.5618 | 4.6891 | 4.5431 | 4.6367 | 4.5243 | 4.5876 | 4.6105 | 4.6975 | 4.5701 | 4.6217 | 4.5643 | 4.6016 | 4.5774 | 4.6109 | 4.6409 | 4.5918 | 4.6929 | 4.6102 | 4.6509 | 4.5876 | 4.6667 | 4.7266 | 4.501 | 4.4911 | 4.6142 | 4.6367 | 4.4977 | 4.4944 | 4.5468 | 4.6142 | 4.551 | 4.5497 | 4.567 | 4.5566 | 4.621 | 4.6189 | 4.5385 | 4.6888 | 4.6678 | 4.6346 | 4.6404 | 4.5186 | 4.5324 | 4.6442 | 4.6569 | 4.5056 | 4.5601 | 4.5655 | 4.6251 | 4.567 | 4.6016 | 4.6327 | 4.6105 | 4.6908 | 4.6292 | 4.5393 | 4.5056 | 4.4906 | 4.5356 | 4.6326 | 4.5417 | 4.6128 | 4.4735 | 4.596 | 4.5657 | 4.6633 | 4.5818 | 4.6023 | 4.6566 | 4.6326 | 4.5527 | 4.6473 | 4.5491 | 4.6667 | 4.6873 | 4.4815 | 4.5758 | 4.625 | 4.5379 | 4.7508 | 4.6818 | 4.6014 | 4.6734 | 4.5387 | 4.7673 | 4.6294 | 4.6296 | 4.6364 | 4.64 | 4.5455 | 4.6259 | 4.6098 | 4.6098 | 4.5038 | 4.6477 | 4.6061 | 4.1705 | 4.6727 | 4.7273 |  |  | 4.2541 | 4.6283 | 4.49 |  | 4.5557 | 4.4981 | 4.6105 | 4.5169 | 4.5843 | 4.5955 | 4.6479 | 4.618 | 4.6404 | 4.7228 | 4.6217 | 4.6704 | 4.6042 | 4.6975 | 4.7783 | 4.7962 | 4.6332 | 4.7436 | 4.5262 | 4.583 | 4.6526 | 4.5776 | 4.5601 | 4.4667 | 4.5339 | 4.6016 | 4.571 | 4.4977 | 4.5416 | 4.531 | 4.6581 | 4.5754 | 4.5374 |  | 4.6844 | 4.5315 | 4.6866 | 4.4856 | 4.5765 |  |  | 4.8109 | 4.7884 | 4.8084 | 4.4872 | 4.5066 | 4.5982
2025-06-15 | 3.3566 | 3.4264 | 3.3745 | 3.4109 | 3.4164 | 3.4318 | 3.4393 | 3.4472 | 3.4204 | 3.4298 | 3.5026 | 3.4835 | 3.4184 | 3.5587 | 3.4135 | 3.4045 | 3.3873 | 3.4195 | 3.3846 | 3.3915 | 3.361 | 3.3925 | 3.4517 | 3.3818 | 3.368 | 3.3915 | 3.357 | 3.3991 | 3.3768 | 3.4024 | 3.4024 | 3.4091 | 3.3416 | 3.291 | 3.3745 | 3.3489 | 3.3933 | 3.3371 | 3.3745 | 3.3637 | 3.3453 | 3.3689 | 3.3745 | 3.3745 | 3.3933 | 3.3292 | 3.4261 | 3.3745 | 3.3834 | 3.3769 | 3.3745 | 3.3865 | 3.3658 | 3.3858 | 3.357 | 3.3658 | 3.3761 | 3.3858 | 3.3328 | 3.3691 | 3.3895 | 3.376 | 3.3861 | 3.348 | 3.4627 | 3.4358 | 3.4821 | 3.3953 | 3.4393 | 3.4172 | 3.4506 | 3.4281 | 3.5165 | 3.4431 | 3.493 | 3.4304 | 3.487 | 3.4573 | 3.418 | 3.461 | 3.4685 | 3.4787 | 3.4378 | 3.4899 | 3.4356 | 3.4513 | 3.4775 | 3.4423 | 3.4105 | 3.3809 | 3.4287 | 3.4918 | 3.518 | 3.491 | 3.4477 | 3.4184 | 3.3985 | 3.5401 | 3.4685 | 3.5101 | 3.5243 | 3.4805 | 3.5247 | 3.4124 | 3.4327 | 3.4416 | 3.3991 | 3.4988 | 3.4494 | 3.4327 | 3.4883 | 3.4645 | 3.5316 | 3.5153 | 3.5341 | 3.561 | 3.4788 | 3.5729 | 3.5462 | 3.5551 | 3.5944 | 3.4127 | 3.3691 | 3.5532 | 3.5783 | 3.9654 | 3.3371 | 3.3461 | 3.3738 | 3.3505 | 3.3518 | 3.3646 | 3.3684 | 3.4259 | 3.3951 | 3.3601 | 3.4769 | 3.4497 | 3.4341 | 3.3757 | 3.3393 | 3.357 | 3.3393 | 3.3895 | 3.3371 | 3.3915 | 3.3371 | 3.363 | 3.3269 | 3.3545 | 3.3649 | 3.3562 | 3.4207 | 3.3554 | 3.3633 | 3.3371 | 3.3446 | 3.3296 | 3.3386 | 3.3485 | 3.337 | 3.4129 | 3.3704 | 3.3535 | 3.3475 | 3.4218 | 3.4129 | 3.3663 | 3.4511 | 3.3891 | 3.3665 | 3.3491 | 3.3976 | 3.3855 | 3.3401 | 3.4508 | 3.3527 | 3.4129 | 3.4589 | 3.4023 | 3.3892 | 3.4192 | 3.4411 | 3.4971 | 3.3395 | 3.3387 | 3.3807 | 3.3625 | 3.4535 | 3.3738 | 3.4943 | 3.5239 | 3.7216 | 3.5136 | 3.4905 | 3.5223 | 3.5891 | 3.5936 |  |  | 3.1935 | 3.4163 | 3.4287 |  | 3.501 | 3.3738 | 3.4993 | 3.4251 | 3.4712 | 3.4884 | 3.5135 | 3.5004 | 3.5105 | 3.5787 | 3.4918 | 3.53 | 3.475 | 3.5449 | 3.5871 | 3.5737 | 3.4274 | 3.4796 | 3.366 | 3.4374 | 3.5419 | 3.5459 | 3.5461 | 3.4942 | 3.5416 | 3.5298 | 3.5159 | 3.3688 | 3.4693 | 3.4102 | 3.3877 | 3.3771 | 3.3709 |  | 3.5154 | 3.4866 | 3.4726 | 3.3707 | 3.5004 |  |  | 3.5569 | 3.5306 | 3.5785 | 3.3722 | 3.3997 | 3.431
2025-06-16 | 4.484 | 4.5736 | 4.5438 | 4.5472 | 4.5549 | 4.5846 | 4.5959 | 4.5985 | 4.5494 | 4.5652 | 4.6831 | 4.6513 | 4.5816 | 4.7122 | 4.5865 | 4.5798 | 4.5607 | 4.5363 | 4.5494 | 4.5497 | 4.579 | 4.5955 | 4.6579 | 4.5849 | 4.6029 | 4.5442 | 4.5238 | 4.5267 | 4.5713 | 4.5087 | 4.5127 | 4.4927 | 4.489 | 4.4361 | 4.53 | 4.4674 | 4.4708 | 4.4356 | 4.5787 | 4.5539 | 4.5895 | 4.4981 | 4.5202 | 4.467 | 4.5195 | 4.5345 | 4.5027 | 4.5375 | 4.4707 | 4.444 | 4.5285 | 4.5101 | 4.573 | 4.5067 | 4.4698 | 4.5457 | 4.5546 | 4.5685 | 4.5 | 4.5596 | 4.5532 | 4.5855 | 4.5199 | 4.5977 | 4.585 | 4.5521 | 4.6005 | 4.4882 | 4.5622 | 4.5442 | 4.573 | 4.5498 | 4.6629 | 4.5779 | 4.6289 | 4.546 | 4.6342 | 4.588 | 4.536 | 4.5749 | 4.6082 | 4.6243 | 4.5648 | 4.6285 | 4.5629 | 4.5712 | 4.6034 | 4.5622 | 4.5131 | 4.4865 | 4.5343 | 4.5808 | 4.6551 | 4.6311 | 4.5556 | 4.5427 | 4.5213 | 4.6431 | 4.5772 | 4.5951 | 4.7019 | 4.5861 | 4.6457 | 4.5446 | 4.6189 | 4.6375 | 4.6545 | 4.5667 | 4.63 | 4.5783 | 4.5981 | 4.531 | 4.6116 | 4.5816 | 4.6191 | 4.6461 | 4.5393 | 4.5786 | 4.557 | 4.6165 | 4.676 | 4.4744 | 4.4914 | 4.6131 | 4.6506 | 4.6439 | 4.409 | 4.3828 | 4.3645 | 4.3998 | 4.3965 | 4.4239 | 4.4173 | 4.4127 | 4.3706 | 4.4105 | 4.4091 | 4.4052 | 4.3901 | 4.3307 | 4.3692 | 4.3475 | 4.412 | 4.4114 | 4.3524 | 4.4218 | 4.4217 | 4.4045 | 4.3941 | 4.3872 | 4.3838 | 4.3895 | 4.3878 | 4.3895 | 4.4064 | 4.3772 | 4.3588 | 4.3895 | 4.5936 | 4.508 | 4.5653 | 4.4523 | 4.5303 | 4.5047 | 4.5909 | 4.5389 | 4.5386 | 4.5842 | 4.6568 | 4.4604 | 4.5411 | 4.4527 | 4.5613 | 4.5873 | 4.5465 | 4.5504 | 4.6045 | 4.5121 | 4.6643 | 4.653 | 4.5329 | 4.6007 | 4.4717 | 4.64 | 4.578 | 4.5798 | 4.6211 | 4.6211 | 4.6469 | 4.5497 | 4.6208 | 4.5799 | 4.5492 | 4.6277 | 4.6277 | 4.642 | 4.7027 | 4.7326 |  |  | 4.3411 | 4.4423 | 4.5466 |  | 4.5663 | 4.4311 | 4.609 | 4.4805 | 4.5978 | 4.5974 | 4.6367 | 4.6292 | 4.6446 | 4.6899 | 4.6221 | 4.6517 | 4.6006 | 4.6931 | 4.8768 | 4.7918 | 4.7074 | 4.7273 | 4.4829 | 4.5183 | 4.6145 | 4.5999 | 4.558 | 4.5407 | 4.658 | 4.5687 | 4.5743 | 4.4677 | 4.4406 | 4.4625 | 4.4716 | 4.4291 | 4.5374 |  | 4.4735 | 4.4521 | 4.5871 | 4.4598 | 4.4328 |  |  | 4.7732 | 4.7179 | 4.728 | 4.4911 | 4.5647 | 4.5466
2025-06-17 | 3.1509 | 3.228 | 3.2404 | 3.2506 | 3.1955 | 3.2176 | 3.212 | 3.2221 | 3.1957 | 3.2144 | 3.2674 | 3.2479 | 3.2049 | 3.2972 | 3.1944 | 3.1547 | 3.1712 | 3.1592 | 3.1461 | 3.1634 | 3.2022 | 3.1993 | 3.2612 | 3.209 | 3.2118 | 3.1634 | 3.1478 | 3.1604 | 3.1694 | 3.1377 | 3.1677 | 3.1587 | 3.1659 | 3.1218 | 3.1491 | 3.1666 | 3.1618 | 3.097 | 3.1573 | 3.2112 | 3.1288 | 3.1019 | 3.1607 | 3.1315 | 3.1704 | 3.182 | 3.1651 | 3.1378 | 3.154 | 3.1062 | 3.1861 | 3.1753 | 3.2293 | 3.1727 | 3.1634 | 3.2336 | 3.2136 | 3.2086 | 3.1547 | 3.1807 | 3.1948 | 3.2151 | 3.1906 | 3.3973 | 3.1827 | 3.1592 | 3.1945 | 3.1105 | 3.1521 | 3.1446 | 3.1644 | 3.1434 | 3.2247 | 3.1225 | 3.193 | 3.1278 | 3.1943 | 3.1603 | 3.1236 | 3.1841 | 3.1715 | 3.1846 | 3.1457 | 3.1858 | 3.1382 | 3.1562 | 3.1787 | 3.1551 | 3.1169 | 3.1041 | 3.1277 | 3.1582 | 3.2157 | 3.197 | 3.1634 | 3.1277 | 3.1206 | 3.2004 | 3.1768 | 3.1839 | 3.2581 | 3.1704 | 3.2109 | 3.1255 | 3.2097 | 3.1846 | 3.2639 | 3.175 | 3.212 | 3.1521 | 3.1651 | 3.1077 | 3.1694 | 3.177 | 3.191 | 3.2217 | 3.1502 | 3.1464 | 3.1407 | 3.173 | 3.2401 | 3.1094 | 3.1427 | 3.1906 | 3.2075 | 3.1577 | 3.1521 | 3.1318 | 3.207 | 3.1554 | 3.1454 | 3.1485 | 3.1485 | 3.2102 | 3.1538 | 3.149 | 3.2538 | 3.2045 | 3.2363 | 3.1236 | 3.108 | 3.0911 | 3.2079 | 3.2201 | 3.161 | 3.115 | 3.1547 | 3.1967 | 3.1547 | 3.182 | 3.2045 | 3.1809 | 3.2176 | 3.1929 | 3.1476 | 3.1228 | 3.1303 | 3.1404 | 3.1568 | 3.1023 | 3.137 | 3.1553 | 3.1451 | 3.1051 | 3.2067 | 3.1327 | 3.1242 | 3.1596 | 3.1939 | 3.1309 | 3.116 | 3.1236 | 3.1414 | 3.1476 | 3.1832 | 3.1492 | 3.1708 | 3.1129 | 3.2098 | 3.2011 | 3.1143 | 3.1562 | 3.1037 | 3.2865 | 3.1706 | 3.1687 | 3.1938 | 3.1975 | 3.1876 | 3.1105 | 3.178 | 3.1477 | 3.1841 | 3.1985 | 3.1894 | 3.2091 | 3.2432 | 3.2761 |  |  | 3.054 | 3.1573 | 3.1135 |  | 3.1962 | 3.115 | 3.1667 | 3.1423 | 3.1708 | 3.1757 | 3.2172 | 3.1974 | 3.2221 | 3.2288 | 3.1951 | 3.2266 | 3.2063 | 3.2746 | 3.3811 | 3.3632 | 3.2968 | 3.3292 | 3.1313 | 3.1172 | 3.2058 | 3.1854 | 3.0908 | 3.1073 | 3.2399 | 3.1997 | 3.173 | 3.1094 | 3.1119 | 3.1133 | 3.1197 | 3.1089 | 3.103 |  | 3.2579 | 3.1383 | 3.3333 | 3.1089 | 3.1119 |  |  | 3.3396 | 3.3503 | 3.3257 | 3.1119 | 3.1302 | 3.1767
2025-06-18 | 3.8548 | 3.9277 | 3.9453 | 3.9345 | 3.9495 | 3.9431 | 3.9918 | 3.9906 | 3.9385 | 3.9637 | 4.0655 | 4.0442 | 3.9599 | 4.0666 | 3.9742 | 3.7944 | 3.9569 | 3.9607 | 3.9779 | 3.9841 | 3.9963 | 3.9933 | 3.9672 | 4.001 | 4.0283 | 3.9737 | 3.943 | 3.9494 | 3.9967 | 4.0466 | 4.0666 | 4.013 | 3.7107 | 3.3221 | 3.6933 | 3.7334 | 3.6933 | 3.7015 | 3.7494 | 3.7285 | 3.6723 | 3.7195 | 3.6742 | 3.7243 | 3.761 | 3.7116 | 3.7376 | 3.7322 | 3.7181 | 3.7303 | 3.7438 | 3.7285 | 3.7427 | 3.7367 | 3.7379 | 3.7437 | 3.7946 | 3.7573 | 3.7403 | 3.759 | 3.7562 | 3.716 | 3.7494 | 3.9331 | 3.9132 | 3.8831 | 3.9239 | 3.8216 | 3.9105 | 3.9105 | 3.9341 | 3.9135 | 4.0266 | 3.8659 | 3.975 | 3.9194 | 3.9864 | 3.961 | 3.9532 | 3.9706 | 3.824 | 3.8989 | 3.9438 | 4.0097 | 3.9618 | 3.9607 | 3.9708 | 3.9375 | 3.8846 | 3.8554 | 3.8472 | 3.8918 | 4.0082 | 3.9985 | 3.8682 | 3.9322 | 3.9105 | 3.9914 | 3.9397 | 3.961 | 4.0566 | 3.9517 | 4.0131 | 3.9199 | 3.9507 | 3.9558 | 4.0523 | 3.912 | 3.9745 | 3.9208 | 3.9243 | 3.841 | 3.8768 | 3.9045 | 3.9753 | 3.9828 | 3.8521 | 3.9088 | 3.9013 | 3.9464 | 3.9783 | 3.8152 | 3.8279 | 3.9412 | 3.9749 | 3.9517 | 3.9251 | 3.9363 | 3.9907 | 3.9394 | 3.9488 | 3.9575 | 3.9813 | 3.933 | 3.8524 | 3.9752 | 4.0881 | 4.0423 | 4.0608 | 3.8217 | 3.925 | 3.8724 | 3.9876 | 4.0162 | 3.8524 | 3.9194 | 3.9633 | 4.0057 | 3.9402 | 3.9748 | 3.9627 | 3.9449 | 3.974 | 3.9562 | 3.9082 | 3.894 | 3.9127 | 3.9079 | 3.9432 | 3.983 | 4.0333 | 3.9364 | 4 | 3.9744 | 3.8721 | 3.9855 | 3.9826 | 3.9566 | 3.9394 | 3.8953 | 3.9898 | 3.8887 | 4.0098 | 4.0058 | 3.9663 | 4.0572 | 4.072 | 4.011 | 4.0071 | 3.9697 | 4.0059 | 3.9596 | 3.9603 | 4.0036 | 3.9266 | 3.9697 | 4.0778 | 4.0956 | 4.0509 | 3.993 | 3.939 | 3.8727 | 3.8295 | 3.9326 | 3.9455 | 3.875 | 4.0091 | 4.0254 |  |  | 3.6134 | 3.9086 | 3.8385 |  | 3.8397 | 3.8277 | 3.9401 | 3.639 | 3.9285 | 3.9566 | 3.9667 | 3.9648 | 3.9678 | 3.8277 | 3.9453 | 3.979 | 3.9144 | 3.9757 | 4.0349 | 4.0349 | 4.0282 | 4.0376 | 3.8528 | 3.8048 | 3.9364 | 3.8782 | 3.8538 | 3.8334 | 3.9533 | 3.9039 | 3.8592 | 3.8485 | 3.9277 | 3.8059 | 3.8112 | 3.9057 | 3.8182 |  | 3.9004 | 3.8349 | 4.0995 | 3.9319 | 3.8112 |  |  | 4.0334 | 4.0713 | 4.1034 | 3.8112 | 3.8599 | 3.9144
2025-06-19 | 3.4192 | 3.4019 | 3.4165 | 3.4142 | 3.3825 | 3.3993 | 3.4131 | 3.4131 | 3.3805 | 3.4042 | 3.4431 | 3.4573 | 3.4019 | 3.4905 | 3.4082 | 3.3146 | 3.394 | 3.3801 | 3.3812 | 3.3905 | 3.4191 | 3.4157 | 3.33 | 3.4224 | 3.4379 | 3.3933 | 3.3718 | 3.3814 | 3.4111 | 3.4107 | 3.3928 | 3.4224 | 3.4536 | 3.3272 | 3.4184 | 3.4577 | 3.4109 | 3.3169 | 3.3539 | 3.4251 | 3.3764 | 3.3457 | 3.3831 | 3.4213 | 3.3895 | 3.406 | 3.3798 | 3.3753 | 3.3489 | 3.3978 | 3.385 | 3.3749 | 3.4297 | 3.3881 | 3.3494 | 3.4071 | 3.4204 | 3.4251 | 3.3854 | 3.4294 | 3.4146 | 3.4624 | 3.3715 | 3.6447 | 3.3836 | 3.3632 | 3.3874 | 3.3099 | 3.379 | 3.3652 | 3.3809 | 3.3577 | 3.4517 | 3.3963 | 3.477 | 3.3958 | 3.47 | 3.4236 | 3.3738 | 3.4247 | 3.409 | 3.4228 | 3.3738 | 3.4206 | 3.3599 | 3.3783 | 3.3948 | 3.37 | 3.3255 | 3.3783 | 3.3359 | 3.3494 | 3.4393 | 3.424 | 3.3498 | 3.3685 | 3.3712 | 3.4337 | 3.4161 | 3.4079 | 3.479 | 3.4037 | 3.4434 | 3.3588 | 3.4231 | 3.4034 | 3.5466 | 3.3831 | 3.4154 | 3.3668 | 3.3628 | 3.3224 | 3.3964 | 3.3914 | 3.4124 | 3.4266 | 3.3663 | 3.3332 | 3.3458 | 3.3622 | 3.4285 | 3.3325 | 3.3658 | 3.3824 | 3.4124 | 3.4031 | 3.3742 | 3.3903 | 3.46 | 3.4214 | 3.4192 | 3.4223 | 3.4216 | 3.4889 | 3.5308 | 3.4262 | 3.5587 | 3.5063 | 3.5545 | 3.339 | 3.3839 | 3.377 | 3.5015 | 3.5219 | 3.3652 | 3.357 | 3.4498 | 3.495 | 3.4292 | 3.4596 | 3.4707 | 3.4303 | 3.4593 | 3.4367 | 3.3944 | 3.3798 | 3.4165 | 3.391 | 3.4598 | 3.3962 | 3.4431 | 3.353 | 3.4367 | 3.4212 | 3.469 | 3.4062 | 3.4038 | 3.4354 | 3.4905 | 3.3196 | 3.3971 | 3.3178 | 3.4212 | 3.4178 | 3.5168 | 3.4602 | 3.4837 | 3.4189 | 3.5185 | 3.5144 | 3.421 | 3.4569 | 3.4155 | 3.4545 | 3.4755 | 3.4852 | 3.5011 | 3.5109 | 3.4556 | 3.3983 | 3.3424 | 3.3678 | 3.3754 | 3.353 | 3.3625 | 3.3564 | 3.4295 | 3.4405 |  |  | 3.2129 | 3.379 | 3.3296 |  | 3.3571 | 3.3303 | 3.3468 | 3.0704 | 3.3423 | 3.3506 | 3.3903 | 3.3753 | 3.3981 | 3.4303 | 3.3858 | 3.4157 | 3.3894 | 3.4593 | 3.5925 | 3.6202 | 3.6087 | 3.5266 | 3.3632 | 3.3453 | 3.3578 | 3.3405 | 3.3245 | 3.3815 | 3.3841 | 3.3836 | 3.4131 | 3.3691 | 3.4577 | 3.3387 | 3.458 | 3.3247 | 3.4485 |  | 3.4319 | 3.349 | 3.4866 | 3.3711 | 3.4266 |  |  | 3.5298 | 3.5368 | 3.5728 | 3.4235 | 3.3769 | 3.409
2025-06-20 | 1.9706 | 2.0086 | 2.0191 | 2.0094 | 1.944 | 2.0097 | 2.0105 | 2.0124 | 1.2261 | 2.0088 | 2.0502 | 2.0371 | 2.0015 | 2.0511 | 2.0049 | 1.9162 | 1.994 | 1.9846 | 2.0145 | 2.0076 | 2.0082 | 2.0146 | 1.9599 | 2.0255 | 2.028 | 2.0118 | 2 | 2.0045 | 2.0411 | 1.9333 | 1.9592 | 1.4449 | 2.0393 | 1.2913 | 2.0165 | 2.0418 | 2.0247 | 1.9674 | 1.9974 | 2.0262 | 1.9963 | 1.9573 | 2.0097 | 1.9899 | 2.0079 | 2.0105 | 1.535 | 1.9805 | 1.9869 | 1.4058 | 2.0019 | 2.0041 | 2.0348 | 2.0065 | 1.9838 | 2.0245 | 2.0211 | 2.0199 | 1.9988 | 2.0388 | 2.0172 | 2.0582 | 1.9989 | 2.1785 | 1.9865 | 1.9748 | 2.0363 | 2.0259 | 1.9708 | 1.967 | 1.9794 | 1.9614 | 2.0266 | 1.9929 | 2.0271 | 1.9965 | 2.0238 | 1.9974 | 1.9749 | 2.0211 | 2.0004 | 1.7757 | 1.9775 | 2.0015 | 1.9648 | 1.9772 | 1.9562 | 1.9753 | 1.9412 | 1.9052 | 1.9545 | 1.9675 | 1.9865 | 1.9899 | 2.0208 | 0 | 0 | 2.0075 | 1.9955 | 1.9569 | 2.0479 | 1.9479 | 2.0191 | 1.9663 | 2.0315 | 0 | 0 | 2.0107 | 2.0086 | 2.0072 | 2.01 | 2.0363 | 2.0022 | 1.9868 | 1.985 | 2.0124 | 1.907 | 1.9942 | 2.0032 | 1.988 | 2.027 | 1.7711 | 1.7278 | 2.0045 | 2.0236 | 1.9952 | 2.0375 | 1.9816 | 1.8923 | 1.4782 | 2.0038 | 1.9997 | 2.001 | 2.0478 | 2.0731 | 2.0136 | 2.0822 | 2.0423 | 2.0764 | 2.0562 | 2.0363 | 1.9965 | 2.0154 | 2.0339 | 1.9502 | 1.9371 | 2.0191 | 2.0425 | 2.0104 | 2.0135 | 2.0131 | 1.7382 | 2.0418 | 2.0292 | 1.9895 | 1.9749 | 2.0206 | 1.9981 | 2.0413 | 2.0106 | 2.0428 | 1.9807 | 1.5845 | 1.7643 | 2.0522 | 2.0251 | 1.7155 | 1.5185 | 1.3485 | 1.9251 | 2.0131 | 1.9171 | 1.4633 | 1.4 | 2.0138 | 1.9852 | 2.0402 | 2.0042 | 2.0721 | 2.0678 | 1.4825 | 1.4973 | 2.0077 | 2.1291 | 2.0458 | 2.0478 | 2.0302 | 2.02 | 1.6309 | 1.157 | 1.9788 | 1.9523 | 1.9811 | 1.9432 | 1.978 | 1.4811 | 2.0109 | 2.0394 |  |  | 1.8221 | 1.949 | 1.9734 |  | 1.9788 | 1.9101 | 1.9513 | 1.9442 | 1.9749 | 1.9978 | 2.0045 | 1.9176 | 2.003 | 2.03 | 1.9835 | 1.5019 | 1.9942 | 2.0395 | 2.2082 | 2.1406 | 2.129 | 2.1649 | 1.9125 | 1.96 | 1.9319 | 1.9885 | 1.9703 | 1.9547 | 1.9578 | 1.9965 | 1.9782 | 1.9559 | 2.0319 | 1.9297 | 2.0357 | 1.9978 | 1.9127 |  | 2.0125 | 1.968 | 2 | 1.8975 | 1.9021 |  |  | 2.0397 | 1.971 | 2.046 | 1.9106 | 1.9693 | 1.9546
2025-06-21 | 4.019 | 3.9931 | 4.0037 | 3.9873 | 4.0778 | 4.0037 | 3.9663 | 4.0157 | 3.8975 | 4.0647 | 3.9738 | 4.0487 | 4.0539 | 4.0245 | 4.0536 | 3.8787 | 4.0251 | 4.0127 | 4.0353 | 4.0356 | 3.997 | 3.9738 | 3.9564 | 4.0629 | 3.9793 | 4.0377 | 4.0097 | 4.002 | 4.0573 | 3.8818 | 3.8652 | 3.6654 | 4.0256 | 3.876 | 3.9906 | 4.0214 | 3.9685 | 3.9228 | 4.0165 | 4.0689 | 3.9693 | 3.9262 | 4.0217 | 3.9693 | 4.0408 | 3.9139 | 3.8693 | 3.9895 | 4.028 | 4.0424 | 3.9363 | 4.0719 | 4.1305 | 4.0646 | 3.9582 | 3.9284 | 4.0576 | 4.0464 | 3.973 | 4.017 | 4.0232 | 4.0535 | 3.9738 | 4.1881 | 4.0138 | 4.0201 | 3.9965 | 4.0211 | 3.9625 | 4.0112 | 4 | 4.0127 | 4.0618 | 3.9738 | 4.0609 | 3.9983 | 4.0769 | 4.0517 | 4.0588 | 3.6508 | 3.9963 | 3.973 | 4.0622 | 4.03 | 4.0412 | 4.0112 | 4.0225 | 4.0112 | 3.9813 | 3.9693 | 3.9587 | 4.0024 | 3.985 | 4.0296 | 4.038 | 3.8772 | 3.8689 | 3.9116 | 3.8614 | 3.8566 | 3.9285 | 3.8801 | 3.8712 | 3.8876 | 3.8985 | 3.4757 | 3.5256 | 3.8608 | 3.8517 | 3.8938 | 3.9205 | 3.9378 | 3.8738 | 3.8632 | 3.9034 | 3.903 | 3.8675 | 3.8585 | 3.8918 | 3.8839 | 3.8757 | 3.5995 | 3.6022 | 3.8839 | 3.8607 | 3.9318 | 3.9738 | 3.9513 | 3.8851 | 3.8655 | 3.9703 | 3.8825 | 3.9647 | 4.0482 | 3.9825 | 3.9671 | 4.035 | 4.0059 | 4.0413 | 3.8801 | 3.9388 | 3.9105 | 4.0337 | 4.0162 | 3.9135 | 3.8755 | 3.9816 | 4.027 | 3.9053 | 3.9848 | 3.9962 | 3.9333 | 3.9461 | 3.906 | 3.8727 | 3.873 | 3.8783 | 3.9228 | 3.9773 | 4.0311 | 3.9428 | 3.9394 | 3.9276 | 4.0128 | 4.0037 | 4.0327 | 3.9958 | 3.9889 | 3.9814 | 4.0131 | 3.9636 | 4.0156 | 3.4545 | 3.8836 | 4.0067 | 3.9811 | 4.0038 | 4.0189 | 4.0438 | 3.9962 | 3.8776 | 4.003 | 4.0333 | 3.8945 | 3.9441 | 3.9865 | 3.9309 | 4.0116 | 3.9309 | 3.8811 | 3.9811 | 3.9902 | 3.947 | 4.0284 | 4.0114 | 3.9811 | 3.9409 | 3.9545 |  |  | 3.6946 | 3.8681 | 3.9132 |  | 4.0615 | 3.9596 | 3.8614 | 3.9101 | 4.0307 | 3.9974 | 3.9738 | 3.9476 | 4.0112 | 3.9064 | 3.8989 | 3.8764 | 4.04 | 3.9983 | 4.0349 | 4.0349 | 4.1223 | 4.2069 | 3.8899 | 3.9883 | 3.9587 | 4.0323 | 4.0048 | 3.9927 | 3.9587 | 4.0432 | 4.008 | 3.9737 | 3.8889 | 3.8997 | 3.8928 | 3.8661 | 3.9131 |  | 3.9343 | 3.8732 | 3.99 | 3.8721 | 3.8889 |  |  | 4.1379 | 3.9577 | 4.1379 | 3.8539 | 3.8702 | 3.9595
2025-06-22 | 4.2541 | 4.2458 | 4.2288 | 4.2479 | 4.2213 | 4.2734 | 4.2622 | 4.2884 | 4.2787 | 4.2787 | 4.221 | 4.2959 | 4.1772 | 4.2737 | 4.2809 | 4.1199 | 4.2472 | 4.3165 | 4.3077 | 4.2558 | 4.2434 | 4.2509 | 4.2417 | 4.2613 | 4.2558 | 4.2835 | 4.2652 | 4.278 | 4.3213 | 4.1248 | 4.1798 | 3.9883 | 4.2846 | 4.1232 | 4.3101 | 4.2824 | 4.3228 | 4.2539 | 4.3112 | 4.2959 | 4.236 | 4.2532 | 4.2472 | 4.1985 | 4.2996 | 4.2285 | 4.1521 | 4.2734 | 4.1931 | 3.9673 | 4.3146 | 4.309 | 4.3313 | 4.2946 | 4.2714 | 4.2547 | 4.2314 | 4.2397 | 4.228 | 4.2946 | 4.2622 | 4.3158 | 4.2963 | 4.3887 | 4.2489 | 4.2558 | 4.308 | 4.2016 | 4.2397 | 4.2551 | 4.2659 | 4.2472 | 4.1985 | 4.2888 | 4.228 | 4.268 | 4.2757 | 4.2899 | 4.2798 | 4.3274 | 4.236 | 4.2288 | 4.2524 | 4.3056 | 4.3109 | 4.2925 | 4.2839 | 4.2835 | 4.2094 | 4.1768 | 4.2057 | 4.1452 | 4.236 | 4.2221 | 4.241 | 4.2659 | 4.2401 | 4.221 | 4.2925 | 4.2816 | 4.2509 | 4.2824 | 4.2472 | 4.2011 | 4.2687 | 4.2528 | 4.0682 | 4.2392 | 4.2944 | 4.2247 | 4.2244 | 3.9758 | 4.2234 | 4.252 | 4.3026 | 4.2745 | 4.1285 | 4.1558 | 4.1861 | 4.203 | 4.2903 | 3.9497 | 3.8665 | 4.2442 | 4.2809 | 4.245 | 4.2801 | 4.2693 | 4.1315 | 4.2121 | 4.2506 | 4.1521 | 4.2911 | 4.2942 | 4.2622 | 4.3042 | 4.3042 | 4.2797 | 4.2427 | 4.1236 | 4.2648 | 4.1957 | 4.2397 | 4.2662 | 4.2547 | 3.9713 | 4.1985 | 4.2533 | 4.2742 | 4.26 | 4.2627 | 4.297 | 4.2873 | 4.2476 | 4.2506 | 4.2277 | 4.2513 | 4.279 | 4.2792 | 4.2909 | 4.2458 | 4.2121 | 4.2212 | 4.2508 | 4.2121 | 4.3138 | 4.2189 | 4.2189 | 4.1742 | 4.192 | 4.1876 | 4.2015 | 4.2626 | 4.1895 | 4.2694 | 4.1705 | 4.2413 | 4.2697 | 4.3098 | 4.3091 | 4.1902 | 4.2061 | 4.2785 | 4.2909 | 4.278 | 4.2811 | 4.2182 | 4.2545 | 4.2767 | 3.993 | 4.1288 | 4.2083 | 4.2538 | 4.1705 | 4.1523 | 4.2322 | 4.2518 | 4.2587 |  |  | 3.9666 | 4.208 | 4.2166 |  | 4.1432 | 4.1985 | 4.1558 | 4.2011 | 4.1648 | 4.1427 | 4.2045 | 4.2 | 4.2288 | 4.1929 | 4.2266 | 4.1551 | 4.227 | 4.3223 | 4.3439 | 4.2991 | 4.3521 | 4.3135 | 4.1919 | 4.1747 | 4.1341 | 4.1608 | 4.1431 | 4.1822 | 4.1546 | 4.1901 | 4.1395 | 4.16 | 4.2778 | 4.1681 | 4.2863 | 4.2312 | 4.2747 |  | 4.246 | 4.2598 | 4.1891 | 4.1489 | 4.1608 |  |  | 4.3469 | 4.3143 | 4.3793 | 4.1608 | 4.2745 | 4.2332
2025-06-23 | 3.6889 | 3.6418 | 3.6629 | 3.6446 | 3.6273 | 3.6476 | 3.6427 | 3.6446 | 3.3496 | 3.6426 | 3.6742 | 3.6936 | 3.6745 | 3.6404 | 3.6262 | 3.6247 | 3.6161 | 3.7386 | 3.6142 | 3.6086 | 3.63 | 3.6404 | 3.6166 | 3.6604 | 3.6564 | 3.6242 | 3.6615 | 3.6225 | 3.6548 | 3.6328 | 3.6921 | 3.3625 | 3.6761 | 3.6826 | 3.6345 | 3.5831 | 3.6581 | 3.7116 | 3.6749 | 3.6625 | 3.6045 | 3.7075 | 3.7419 | 3.7251 | 3.6532 | 3.6682 | 3.2878 | 3.5921 | 3.6315 | 3.2755 | 3.6315 | 3.6442 | 3.6288 | 3.6335 | 3.5751 | 3.6621 | 3.6604 | 3.6326 | 3.6201 | 3.6767 | 3.6558 | 3.6132 | 3.6457 | 3.72 | 3.638 | 3.6557 | 3.6093 | 3.5889 | 3.6554 | 3.6483 | 3.6532 | 3.6221 | 3.5993 | 3.5993 | 3.5955 | 3.6571 | 3.5888 | 3.6813 | 3.6442 | 3.7058 | 3.6727 | 3.6176 | 3.6479 | 3.7041 | 3.6352 | 3.6446 | 3.6513 | 3.6285 | 3.5809 | 3.5419 | 3.5951 | 3.516 | 3.5768 | 3.588 | 3.5655 | 3.5884 | 2.7903 | 3.6899 | 3.5805 | 3.5955 | 3.633 | 3.588 | 3.5618 | 3.5453 | 3.5955 | 3.5618 | 3.5955 | 3.6112 | 3.5618 | 3.5256 | 3.6135 | 3.6398 | 3.5622 | 3.5323 | 3.5618 | 3.6105 | 3.2352 | 3.6288 | 3.5256 | 3.6536 | 3.5805 | 3.461 | 3.3828 | 3.5618 | 3.6217 | 3.6255 | 3.521 | 3.6109 | 3.5955 | 3.4823 | 3.5575 | 3.5239 | 3.6111 | 3.5138 | 3.5664 | 3.6038 | 3.0409 | 3.5979 | 3.5596 | 3.4981 | 3.5941 | 3.5277 | 3.6045 | 3.6024 | 3.5453 | 3.6093 | 3.6142 | 3.5792 | 3.6764 | 3.6667 | 3.6232 | 3.6375 | 3.5988 | 3.6045 | 3.6479 | 3.6037 | 3.6146 | 3.5693 | 3.6337 | 3.5951 | 3.6347 | 3.4883 | 3.3313 | 3.3273 | 3.532 | 3.6145 | 3.5606 | 3.3421 | 3.5606 | 3.5098 | 3.6058 | 3.5222 | 3.569 | 3.5636 | 3.6236 | 3.614 | 3.5644 | 3.5769 | 3.5744 | 3.6023 | 3.5664 | 3.5051 | 3.6061 | 3.6 | 3.5822 | 3.6118 | 3.5309 | 3.6033 | 3.3455 | 3.5315 | 3.5989 | 3.5447 | 3.5644 | 3.567 | 3.6235 | 3.5265 | 3.5455 | 3.5265 |  |  | 3.3411 | 3.2356 | 3.524 |  | 3.6408 | 3.5337 | 3.3757 | 3.5255 | 3.594 | 3.6247 | 3.6592 | 3.6558 | 3.5243 | 3.6483 | 3.6614 | 3.5243 | 3.5955 | 3.6621 | 3.717 | 3.6677 | 3.6468 | 3.7053 | 3.5642 | 3.6163 | 3.7124 | 3.6658 | 3.6353 | 3.6812 | 3.7131 | 3.7082 | 3.6977 | 3.6375 | 3.6581 | 3.539 | 3.6127 | 3.5226 | 3.5418 |  | 3.6824 | 3.5528 | 3.7015 | 3.4942 | 3.5043 |  |  | 3.9415 | 3.7226 | 3.6935 | 3.4887 | 3.5705 | 3.5923
2025-06-24 | 4.8927 | 5.0137 | 5.0404 | 4.97 | 4.9649 | 5.0124 | 5.0101 | 5.0345 | 5.0013 | 5.0333 | 5.0974 | 5.0861 | 4.8202 | 5.1718 | 5.024 | 5.021 | 4.9801 | 4.9689 | 4.9787 | 4.9777 | 5.0288 | 5.0521 | 4.9148 | 5.049 | 5.0586 | 5.0143 | 4.8716 | 4.9711 | 5.0254 | 4.8439 | 4.8456 | 4.831 | 4.945 | 5.0776 | 4.9105 | 4.9455 | 4.8067 | 4.8397 | 4.9326 | 4.9798 | 4.8955 | 4.8783 | 4.9667 | 4.9322 | 5.0004 | 5.0221 | 4.8709 | 4.9225 | 4.9377 | 4.8719 | 4.9884 | 4.9831 | 5.058 | 4.9911 | 4.9141 | 5.0071 | 4.9994 | 5.0082 | 4.9375 | 5.0054 | 4.9933 | 5.0335 | 4.9801 | 5.3889 | 5.0237 | 4.9787 | 5.0202 | 4.8619 | 4.9742 | 4.9652 | 4.97 | 4.9337 | 5.061 | 4.9517 | 4.9661 | 4.8613 | 4.9934 | 4.9775 | 4.9382 | 5.0009 | 5.0281 | 5.0438 | 4.9727 | 5.0213 | 4.9798 | 4.9993 | 4.9876 | 4.9809 | 4.8757 | 4.8457 | 4.8629 | 4.8443 | 5.0494 | 4.8715 | 4.9385 | 4.909 | 4.824 | 5.0483 | 4.9273 | 4.9996 | 5.1026 | 4.9573 | 4.9914 | 4.9067 | 4.9988 | 4.8596 | 5.1156 | 2.4975 | 5.0382 | 4.9774 | 5.0031 | 4.9615 | 4.9608 | 4.9971 | 5.0491 | 5.0315 | 4.8394 | 4.9478 | 4.9538 | 4.9981 | 5.0663 | 4.7527 | 4.6464 | 5.0109 | 4.9034 | 4.9235 | 4.9116 | 4.8404 | 4.9455 | 4.9012 | 4.875 | 4.808 | 4.8944 | 4.9075 | 5.0441 | 4.814 | 4.9755 | 5.0196 | 4.9715 | 4.9401 | 4.8754 | 4.8477 | 4.9258 | 4.9825 | 4.8071 | 4.8971 | 4.8386 | 4.9397 | 4.8885 | 4.874 | 4.9805 | 4.9195 | 4.9238 | 4.9154 | 4.8277 | 4.8356 | 4.8037 | 4.8816 | 5.0269 | 4.936 | 4.9795 | 4.8564 | 4.8687 | 4.8727 | 4.8956 | 4.9651 | 4.8966 | 4.9067 | 4.8788 | 4.8244 | 4.972 | 4.8636 | 4.862 | 4.9836 | 4.9842 | 4.9583 | 4.9682 | 4.8773 | 4.9013 | 5.0576 | 4.857 | 4.8926 | 4.8519 | 5.1636 | 5.0035 | 4.9657 | 4.9873 | 4.9091 | 4.8502 | 4.9301 | 4.9936 | 4.9587 | 4.8409 | 4.9322 | 4.9693 | 4.8527 | 5.0145 | 4.8864 |  |  | 4.5688 | 4.8385 | 4.8485 |  | 4.892 | 4.8581 | 4.8831 | 4.8824 | 4.9648 | 4.9727 | 5.0034 | 5.0041 | 4.9955 | 4.8281 | 4.9633 | 5 | 4.9615 | 4.9858 | 5.1232 | 4.9306 | 4.9321 | 5.0219 | 4.9264 | 4.8595 | 4.9762 | 4.9848 | 4.9386 | 4.922 | 5.0175 | 4.9628 | 4.9598 | 4.9149 | 4.8368 | 4.8308 | 4.8271 | 4.9502 | 4.9661 |  | 5.0977 | 4.8805 | 5.2189 | 4.8672 | 4.831 |  |  | 5.4378 | 5.0047 | 4.9847 | 4.8302 | 4.886 | 4.9387
2025-06-25 | 4.8356 | 4.8443 | 4.9667 | 4.9622 | 4.9158 | 4.9378 | 4.9539 | 4.8734 | 4.9111 | 4.9219 | 4.9142 | 4.9049 | 4.7345 | 4.8629 | 4.9322 | 4.927 | 4.9064 | 4.8846 | 4.874 | 4.8961 | 4.9483 | 4.9502 | 4.8353 | 4.9548 | 4.9649 | 4.9044 | 4.7402 | 4.8769 | 4.9005 | 4.7314 | 4.7457 | 4.7191 | 4.934 | 4.8516 | 4.8603 | 4.8953 | 4.9045 | 4.7993 | 4.8801 | 4.9614 | 4.8453 | 4.8015 | 4.8933 | 4.8528 | 4.9311 | 4.9363 | 4.8799 | 4.8708 | 4.8762 | 4.7227 | 4.9184 | 4.9101 | 4.8929 | 4.9202 | 4.7976 | 4.8846 | 4.8742 | 4.8678 | 4.8922 | 4.8759 | 4.9449 | 4.8906 | 4.9202 | 5.261 | 4.9414 | 4.8992 | 4.9587 | 4.8121 | 4.9157 | 4.8963 | 4.9157 | 4.8678 | 4.9404 | 4.9165 | 4.9538 | 4.8516 | 4.9605 | 4.9232 | 4.8715 | 4.9611 | 4.9476 | 4.8727 | 4.8906 | 4.9517 | 4.8824 | 4.9064 | 4.8996 | 4.8895 | 4.7858 | 4.7468 | 4.8068 | 4.7589 | 4.9816 | 4.8356 | 4.8849 | 4.8667 | 4.8813 | 4.9685 | 4.9079 | 4.9356 | 4.9479 | 4.8798 | 4.9255 | 4.8734 | 4.9445 | 4.8318 | 4.9615 | 4.7313 | 4.903 | 4.8879 | 4.9141 | 4.911 | 4.8476 | 4.8812 | 4.9596 | 4.7461 | 4.7461 | 4.8533 | 4.8832 | 4.9311 | 4.9404 | 4.6795 | 4.5546 | 4.9311 | 4.8322 | 4.8842 | 4.8322 | 4.8438 | 4.7068 | 4.821 | 4.8474 | 4.8035 | 4.8232 | 4.9164 | 4.899 | 4.8049 | 4.8605 | 4.9413 | 4.8694 | 4.7648 | 4.7772 | 4.7426 | 4.8813 | 4.8439 | 4.736 | 4.8152 | 4.797 | 4.8936 | 4.8498 | 4.8913 | 4.8439 | 4.8622 | 4.9488 | 4.8655 | 4.776 | 4.767 | 4.767 | 4.8648 | 4.8322 | 4.7409 | 4.764 | 4.7523 | 4.7407 | 4.7104 | 4.8559 | 4.7902 | 4.7394 | 4.8199 | 4.7898 | 4.7764 | 4.7913 | 4.7746 | 4.7623 | 4.8415 | 4.7751 | 4.7795 | 4.825 | 4.8087 | 4.7529 | 4.8663 | 4.7524 | 4.7253 | 4.8569 | 4.9535 | 4.8136 | 4.7771 | 4.8498 | 4.8378 | 4.8145 | 4.7399 | 4.8458 | 4.7413 | 4.7898 | 4.7879 | 4.9027 | 4.8027 | 4.8691 | 4.8864 |  |  | 4.5625 | 4.7386 | 4.813 |  | 4.8452 | 4.7644 | 4.8232 | 4.7607 | 4.8809 | 4.903 | 4.9476 | 4.9543 | 4.8318 | 4.7622 | 4.9345 | 4.8315 | 4.9352 | 5.0497 | 5.1679 | 5.0291 | 5.0522 | 4.9467 | 4.81 | 4.7631 | 4.9129 | 4.8706 | 4.7917 | 4.7934 | 4.942 | 4.8211 | 4.8633 | 4.7654 | 4.7552 | 4.7662 | 4.7436 | 4.7437 | 4.8667 |  | 5.0637 | 4.7638 | 5.005 | 4.7759 | 4.7809 |  |  | 5.2723 | 4.9177 | 5.0307 | 4.7883 | 4.9362 | 4.8608
2025-06-26 | 4.8885 | 4.92 | 5.0157 | 5.0034 | 4.9352 | 4.9742 | 4.9449 | 4.9648 | 4.923 | 4.9395 | 5.006 | 4.9727 | 4.8303 | 4.952 | 4.8996 | 4.8921 | 4.861 | 4.8386 | 4.8318 | 4.847 | 4.9064 | 4.9161 | 4.7965 | 4.9002 | 4.902 | 4.8446 | 4.735 | 4.808 | 4.84 | 4.808 | 4.7387 | 4.7767 | 4.9033 | 5.0052 | 4.8345 | 4.8598 | 4.8693 | 4.7625 | 4.8375 | 4.9243 | 4.8139 | 4.7689 | 4.8457 | 4.8056 | 4.8993 | 4.9255 | 4.8916 | 4.8412 | 4.914 | 4.7507 | 4.9453 | 4.9341 | 4.8999 | 4.9215 | 4.7665 | 4.8979 | 4.8586 | 4.9315 | 4.8556 | 4.9072 | 4.9067 | 4.9512 | 4.897 | 5.3007 | 4.9276 | 4.8792 | 4.9428 | 4.8263 | 4.9094 | 4.8828 | 4.9199 | 4.8805 | 4.8775 | 4.873 | 4.8496 | 4.772 | 4.8952 | 4.873 | 4.8337 | 4.8868 | 4.9056 | 4.9266 | 4.8734 | 4.9247 | 4.8592 | 4.8955 | 4.9034 | 4.9052 | 4.7955 | 4.7678 | 4.827 | 4.7765 | 4.9674 | 4.9195 | 4.8593 | 4.833 | 4.8228 | 4.9464 | 4.8521 | 4.8985 | 4.9109 | 4.8303 | 4.8794 | 4.8191 | 4.8416 | 4.5749 | 4.9705 | 4.8026 | 4.921 | 4.8446 | 4.8515 | 4.8965 | 4.8649 | 4.8856 | 4.9367 | 4.7607 | 4.8019 | 4.7647 | 4.8087 | 4.9071 | 4.9678 | 4.6642 | 4.5057 | 4.8865 | 4.903 | 4.8866 | 4.83 | 4.8255 | 4.7644 | 4.8216 | 4.8107 | 4.8114 | 4.8277 | 4.9128 | 4.857 | 4.8014 | 4.8888 | 4.8993 | 4.8582 | 4.8697 | 4.7965 | 4.7748 | 4.9004 | 4.9286 | 4.7633 | 4.8283 | 4.7966 | 4.8813 | 4.7865 | 4.8532 | 4.8764 | 4.8131 | 4.9125 | 4.8311 | 4.7513 | 4.7869 | 4.7449 | 4.8318 | 4.8848 | 4.8148 | 4.8185 | 4.7943 | 4.7848 | 4.829 | 4.8455 | 4.804 | 4.7936 | 4.8859 | 4.8485 | 4.9273 | 4.8836 | 4.8415 | 4.7865 | 4.8767 | 4.7845 | 4.8148 | 4.8174 | 4.8902 | 4.8185 | 4.928 | 4.8409 | 4.7862 | 4.7492 | 4.9858 | 4.8885 | 4.8306 | 4.8873 | 4.8876 | 4.8705 | 4.7941 | 4.8932 | 4.8689 | 4.8716 | 4.8845 | 4.8864 | 4.8409 | 4.8636 | 4.9284 |  |  | 4.5882 | 4.8106 | 4.8141 |  | 4.9306 | 4.8161 | 4.8367 | 4.8 | 4.8727 | 4.8532 | 4.9854 | 4.9554 | 4.873 | 4.8315 | 4.9139 | 4.9622 | 4.9382 | 5.05 | 5.1545 | 5.0766 | 5.0914 | 5.0094 | 4.8066 | 4.9041 | 4.9316 | 4.9162 | 4.8781 | 4.8729 | 4.9298 | 4.9151 | 4.9844 | 4.9265 | 4.8221 | 4.8618 | 4.7933 | 4.8253 | 4.8117 |  | 5.0977 | 4.7948 | 5.1065 | 4.7729 | 4.7883 |  |  | 5.2706 | 5.0102 | 5.0617 | 4.7622 | 5.0004 | 4.8712
2025-06-27 | 4.4543 | 4.4636 | 4.4569 | 4.4981 | 4.4944 | 4.485 | 4.4255 | 4.4873 | 4.3222 | 4.3506 | 4.4573 | 4.4895 | 4.2873 | 4.3309 | 4.4442 | 4.461 | 4.4232 | 4.4176 | 4.3271 | 4.3357 | 4.373 | 4.3888 | 4.3488 | 4.3316 | 4.3831 | 4.3755 | 4.223 | 4.4038 | 4.3865 | 4.2277 | 4.2131 | 4.2517 | 4.3333 | 4.3539 | 4.2801 | 4.2673 | 4.3131 | 4.2322 | 4.303 | 4.3921 | 4.2719 | 4.2438 | 4.309 | 4.2708 | 4.3682 | 4.3843 | 4.1901 | 4.3307 | 4.3865 | 4.1988 | 4.3861 | 4.3933 | 4.3316 | 4.3735 | 4.1901 | 4.3319 | 4.3685 | 4.4157 | 4.3239 | 4.3466 | 4.3723 | 4.3874 | 4.3431 | 4.604 | 4.3526 | 4.3761 | 4.3969 | 4.3264 | 4.3165 | 4.3243 | 4.3517 | 4.3884 | 4.3659 | 4.3558 | 4.3436 | 4.285 | 4.3273 | 4.385 | 4.3742 | 4.3658 | 4.3577 | 4.3356 | 4.3813 | 4.394 | 4.3794 | 4.3401 | 4.3401 | 4.3221 | 4.3251 | 4.2805 | 4.3017 | 4.2385 | 4.3708 | 4.3655 | 4.3832 | 4.3858 | 2.864 | 4.3918 | 4.3831 | 4.3738 | 4.3539 | 4.3936 | 4.424 | 4.2236 | 4.3452 | 4.415 | 4.3772 | 4.2081 | 4.3888 | 4.3829 | 4.4007 | 4.3519 | 4.3472 | 4.3972 | 4.3154 | 4.206 | 4.1957 | 4.2467 | 4.268 | 4.403 | 4.4487 | 4.1155 | 4.0866 | 4.3236 | 4.3592 | 4.2547 | 4.3221 | 4.2734 | 4.2184 | 4.2247 | 4.2116 | 4.2555 | 4.2655 | 4.3375 | 4.3014 | 4.2378 | 4.2857 | 4.2657 | 4.2416 | 4.2239 | 4.261 | 4.2216 | 4.2266 | 4.2545 | 4.2363 | 4.2562 | 4.2363 | 4.2272 | 4.2576 | 4.2199 | 4.2392 | 4.2064 | 4.271 | 4.2127 | 4.2363 | 4.2139 | 4.2903 | 4.2715 | 4.3216 | 4.2402 | 4.2525 | 4.2856 | 4.2185 | 4.2249 | 4.3145 | 4.2767 | 4.2788 | 4.2 | 4.2928 | 4.2633 | 4.2695 | 4.2044 | 4.2532 | 4.3004 | 4.2226 | 4.2519 | 4.2932 | 4.2466 | 4.2138 | 4.3189 | 4.2378 | 4.2226 | 4.2576 | 4.4211 | 4.2892 | 4.2673 | 4.3011 | 4.3033 | 4.356 | 4.2308 | 4.2883 | 4.3023 | 4.2466 | 4.3117 | 4.2845 | 4.2163 | 4.3459 | 4.258 |  |  | 0.0003885 | 4.238 | 4.2458 |  | 4.3681 | 4.3404 | 4.3861 | 4.2258 | 4.3861 | 4.3457 | 4.3734 | 4.4 | 4.3251 | 4.239 | 4.3116 | 4.3311 | 4.4018 | 4.4964 | 4.5862 | 4.5678 | 4.5517 | 4.3962 | 4.265 | 4.3424 | 4.489 | 4.4155 | 4.363 | 4.3834 | 4.5142 | 4.4425 | 4.3955 | 4.3246 | 4.2389 | 4.2828 | 4.2774 | 4.2705 | 4.2493 |  | 4.5896 | 4.2532 | 4.3363 | 4.2353 | 4.2409 |  |  | 4.6859 | 4.4773 | 4.5276 | 4.3551 | 4.3744 | 4.3209
2025-06-28 | 3.6273 | 3.6968 | 3.5996 | 3.6094 | 3.6923 | 3.6854 | 3.7101 | 3.7101 | 3.6642 | 3.6825 | 3.6285 | 3.7375 | 3.5184 | 3.5877 | 3.6828 | 3.6483 | 3.6618 | 3.6562 | 3.6384 | 3.6498 | 3.5622 | 3.5948 | 3.5481 | 3.6418 | 3.5768 | 3.6249 | 3.5029 | 3.5592 | 3.5918 | 3.5396 | 3.5659 | 3.4996 | 3.546 | 3.5905 | 3.6375 | 3.5129 | 3.6375 | 3.618 | 3.2622 | 3.6498 | 3.6554 | 3.6427 | 3.6375 | 3.6165 | 3.6 | 3.5835 | 3.5609 | 3.6247 | 3.584 | 3.4981 | 3.6375 | 3.6509 | 3.6395 | 3.6578 | 3.5367 | 3.6624 | 3.6741 | 3.2667 | 3.5845 | 3.6328 | 3.7142 | 3.5296 | 3.6914 | 3.7701 | 3.6664 | 3.5997 | 3.6515 | 3.6045 | 3.6464 | 3.6094 | 3.6217 | 3.6745 | 3.6307 | 3.5794 | 3.5712 | 3.5992 | 3.6311 | 3.6322 | 3.6453 | 3.6681 | 3.5873 | 3.6375 | 3.6674 | 3.6213 | 3.6712 | 3.6187 | 3.5813 | 3.664 | 3.6345 | 3.585 | 3.5847 | 3.5215 | 3.6 | 3.1985 | 3.6648 | 3.6506 | 0 | 3.6408 | 3.588 | 3.5738 | 3.6127 | 3.564 | 3.5933 | 3.5592 | 3.5655 | 3.6217 | 3.6078 | 3.5172 | 3.5202 | 3.6787 | 3.5678 | 3.5236 | 3.5219 | 3.5672 | 3.6213 | 3.5809 | 3.5504 | 3.5089 | 3.5619 | 3.5738 | 3.6225 | 3.3258 | 3.3458 | 3.5805 | 3.5243 | 3.5256 | 3.5805 | 3.5431 | 3.6288 | 3.5968 | 3.3089 | 3.6204 | 3.6716 | 3.6977 | 3.729 | 3.5647 | 3.7248 | 3.7073 | 3.6915 | 3.2813 | 3.6283 | 3.5495 | 3.6704 | 3.7134 | 3.5659 | 3.638 | 3.6105 | 3.6903 | 3.6145 | 3.6557 | 3.6536 | 3.5873 | 3.5762 | 3.5532 | 3.5419 | 3.5581 | 3.624 | 3.6985 | 3.6663 | 3.5625 | 3.6461 | 3.5152 | 3.537 | 3.5168 | 3.6394 | 3.5778 | 3.5712 | 3.5189 | 3.539 | 3.4909 | 3.5971 | 3.5251 | 3.5441 | 3.248 | 3.5966 | 3.6333 | 3.6932 | 3.6545 | 3.6074 | 3.6212 | 3.5385 | 3.5562 | 3.536 | 3.6727 | 3.5703 | 3.6418 | 3.5564 | 3.6 | 3.5015 | 3.2605 | 3.5811 | 3.6633 | 3.6333 | 3.6799 | 3.6208 | 3.5795 | 3.6159 | 3.5966 |  |  | 0 | 3.5787 | 3.5432 |  | 3.5338 | 3.6371 | 3.5805 | 3.5921 | 3.2127 | 3.6749 | 3.6191 | 3.6483 | 3.5461 | 3.5835 | 3.5517 | 3.5543 | 3.5372 | 3.8052 | 3.811 | 3.7662 | 3.767 | 3.6991 | 3.5676 | 3.543 | 3.6185 | 3.5868 | 3.5073 | 3.5111 | 3.6728 | 3.5765 | 3.5562 | 3.5892 | 3.6173 | 3.6515 | 3.5315 | 3.5488 | 3.5511 |  | 3.807 | 3.5563 | 3.607 | 3.4942 | 3.5431 |  |  | 3.7659 | 3.7461 | 3.7471 | 3.5264 | 3.6111 | 3.5963
2025-06-29 | 3.1564 | 3.2221 | 3.2285 | 3.2172 | 3.2083 | 3.2097 | 3.2247 | 3.236 | 3.2072 | 3.2216 | 3.206 | 3.1453 | 3.1423 | 3.2972 | 3.2172 | 3.188 | 3.191 | 3.1873 | 3.1979 | 3.2083 | 3.1798 | 3.2285 | 3.1392 | 3.226 | 3.115 | 3.2118 | 3.1184 | 3.1893 | 3.216 | 3.1434 | 3.1694 | 3.0535 | 3.1486 | 3.2049 | 3.1798 | 3.2051 | 3.206 | 3.1049 | 3.161 | 3.221 | 3.1311 | 3.124 | 3.1685 | 3.0682 | 3.1948 | 3.206 | 3.115 | 3.1685 | 3.1712 | 3.0964 | 3.1835 | 3.1985 | 3.2393 | 3.1993 | 3.1623 | 3.1777 | 3.2 | 3.1712 | 3.196 | 3.1074 | 3.206 | 3.2519 | 3.2397 | 3.2936 | 3.191 | 3.1772 | 3.2083 | 3.0908 | 3.1648 | 3.176 | 3.191 | 3.1386 | 3.1423 | 3.1723 | 3.2127 | 3.1727 | 3.2193 | 3.1798 | 3.1648 | 3.2152 | 3.1985 | 3.221 | 3.1685 | 3.191 | 3.1386 | 3.176 | 3.1461 | 3.1573 | 3.1453 | 3.1243 | 3.1612 | 3.115 | 3.2135 | 3.1131 | 3.1561 | 3.161 | 0 | 3.1723 | 3.191 | 3.1423 | 3.1199 | 3.2022 | 3.1311 | 3.191 | 3.2127 | 3.1498 | 3.2726 | 3.187 | 3.1573 | 3.186 | 3.1841 | 3.1841 | 3.1104 | 3.0885 | 3.221 | 3.1341 | 3.1623 | 3.0995 | 3.166 | 3.1948 | 3.1262 | 2.9929 | 2.9397 | 3.1985 | 3.1041 | 3.1893 | 3.1172 | 3.1449 | 3.1045 | 3.1817 | 3.1208 | 3.1689 | 3.1896 | 3.1297 | 3.1434 | 3.1479 | 3.1217 | 3.1573 | 3.1317 | 3.2247 | 3.1775 | 3.1288 | 3.1685 | 3.257 | 3.1127 | 3.1997 | 3.1764 | 3.2196 | 3.1841 | 3.2643 | 3.2294 | 3.2397 | 3.1667 | 3.1648 | 3.1921 | 3.1491 | 3.206 | 3.2629 | 3.2121 | 3.1364 | 3.1785 | 3.0985 | 3.1481 | 3.1044 | 3.2054 | 3.16 | 3.1288 | 3.0168 | 3.1644 | 3.0953 | 3.1418 | 3.1487 | 3.1616 | 2.9818 | 3.1303 | 3.1591 | 3.2045 | 3.1212 | 3.1178 | 3.2008 | 3.1913 | 3.1347 | 3.1212 | 3.1709 | 3.1213 | 3.2054 | 3.168 | 3.148 | 3.1425 | 3.1538 | 3.1098 | 3.1598 | 3.192 | 3.1629 | 3.1591 | 3.1402 | 3.1318 | 3.1174 |  |  | 0 | 3.1573 | 3.1633 |  | 3.1664 | 3.1798 | 3.1674 | 3.1449 | 3.1494 | 3.1599 | 3.1311 | 3.1787 | 3.1449 | 3.1704 | 3.191 | 3.1169 | 3.1997 | 3.3325 | 3.3686 | 3.3094 | 3.2863 | 3.348 | 3.1025 | 3.1276 | 3.1101 | 3.1893 | 3.115 | 3.1115 | 3.2288 | 3.229 | 3.1794 | 3.1208 | 3.1119 | 3.1241 | 3.143 | 3.1511 | 3.1604 |  | 3.315 | 3.1682 | 3.204 | 3.1238 | 3.1197 |  |  | 3.2936 | 3.3346 | 3.2375 | 3.143 | 3.1497 | 3.1708
2025-06-30 | 2.5549 | 2.5307 | 2.5356 | 2.5206 | 2.5169 | 2.5243 | 2.5356 | 2.5431 | 2.5204 | 2.5312 | 2.588 | 2.5693 | 2.5506 | 2.5904 | 2.5243 | 2.5206 | 2.5094 | 2.4944 | 2.5238 | 2.5134 | 2.5243 | 2.5318 | 2.5203 | 2.5402 | 2.5341 | 2.5099 | 2.5411 | 2.5135 | 2.5235 | 2.5335 | 2.5268 | 2.5069 | 2.5511 | 2.5826 | 2.4794 | 2.4891 | 2.5206 | 2.4869 | 2.4419 | 2.5169 | 2.5206 | 2.4569 | 2.573 | 2.5318 | 2.5618 | 2.5206 | 2.3578 | 2.5311 | 2.3766 | 2.3694 | 2.4869 | 2.5393 | 2.5002 | 2.5435 | 2.4996 | 2.5402 | 2.5468 | 2.5468 | 2.5169 | 2.5501 | 2.5094 | 2.5694 | 2.5206 | 2.6082 | 2.5134 | 2.503 | 2.5169 | 2.5376 | 2.4794 | 2.4869 | 2.5243 | 2.5131 | 2.5581 | 2.5431 | 2.5561 | 2.5002 | 2.5368 | 2.5056 | 2.527 | 2.5272 | 2.5019 | 2.5206 | 2.4831 | 2.5056 | 2.5243 | 2.4532 | 2.5506 | 2.4532 | 2.4569 | 2.4944 | 2.4493 | 2.4996 | 2.4981 | 2.3745 | 2.5169 | 2.4794 | 0.1779 | 2.5318 | 2.5581 | 2.5169 | 2.4637 | 2.5644 | 2.464 | 2.4981 | 2.5135 | 2.427 | 2.5412 | 2.4724 | 2.5131 | 2.5169 | 2.5134 | 2.5687 | 2.5169 | 2.5235 | 2.5169 | 2.5206 | 2.5159 | 2.437 | 2.5135 | 2.5206 | 2.4517 | 2.3571 | 2.4203 | 2.5019 | 2.5056 | 2.5102 | 2.5243 | 2.5618 | 2.4003 | 2.5668 | 2.5549 | 2.5756 | 2.5549 | 2.5005 | 2.5245 | 2.521 | 2.486 | 2.549 | 2.5276 | 2.5543 | 2.4844 | 2.4719 | 2.5581 | 2.4512 | 2.5543 | 2.4588 | 2.491 | 2.5303 | 2.5549 | 2.5376 | 2.5545 | 2.5401 | 2.5342 | 2.5442 | 2.5045 | 2.5618 | 2.5094 | 2.5655 | 2.5038 | 2.5367 | 2.4815 | 2.4583 | 2.5387 | 2.4478 | 2.4613 | 2.4582 | 2.553 | 2.3603 | 2.4659 | 2.4764 | 2.5382 | 2.4691 | 2.4882 | 2.4291 | 2.4882 | 2.472 | 2.4773 | 2.4803 | 2.4377 | 2.4659 | 2.5315 | 2.4613 | 2.4377 | 2.4469 | 2.486 | 2.4781 | 2.5164 | 2.5236 | 2.3455 | 2.451 | 2.4879 | 2.4432 | 2.4848 | 2.4697 | 2.4811 | 2.4939 | 2.4727 | 2.5 |  |  | 0 | 2.4355 | 2.4242 |  | 2.488 | 2.5543 | 2.4464 | 2.4494 | 2.5655 | 2.4981 | 2.5019 | 2.4648 | 2.5094 | 2.4588 | 2.4906 | 2.4757 | 2.5268 | 2.5768 | 2.6288 | 2.5661 | 2.581 | 2.5956 | 2.4242 | 2.4812 | 2.5312 | 2.5335 | 2.5307 | 2.4927 | 2.5636 | 2.5549 | 2.5268 | 2.5135 | 2.4825 | 2.4387 | 2.4981 | 2.4916 | 2.4727 |  | 2.6436 | 2.4695 | 2.5075 | 2.4729 | 2.4631 |  |  | 2.6708 | 2.6567 | 2.6207 | 2.4709 | 2.4917 | 2.4986
2025-07-01 | 2.0342 | 2.0709 | 2.0757 | 2.0652 | 2.0646 | 2.0629 | 2.0734 | 2.0794 | 1.8013 | 1.9524 | 2.1202 | 2.1064 | 1.9783 | 2.1263 | 2.0704 | 2.0712 | 2.0506 | 2.0427 | 2.0709 | 2.0674 | 2.0734 | 2.0861 | 2.0304 | 2.1047 | 2.093 | 2.0785 | 2.066 | 2.0737 | 2.0954 | 2.0058 | 2.0481 | 2.0375 | 2.0346 | 2.0625 | 2.039 | 1.9739 | 2.0075 | 1.9517 | 1.9925 | 2.0105 | 1.97 | 1.9813 | 2.0127 | 2.012 | 2.027 | 1.9764 | 1.981 | 2.0195 | 2.0189 | 1.975 | 2.0315 | 2.0517 | 1.9742 | 1.9842 | 1.9741 | 1.9842 | 1.8017 | 2.0187 | 1.9576 | 1.9642 | 1.9775 | 1.9739 | 2 | 2.0869 | 2.0263 | 2.019 | 2.019 | 1.9672 | 1.9933 | 2.0075 | 2.0094 | 1.9581 | 1.9816 | 2.0273 | 1.9942 | 1.9576 | 1.9642 | 2 | 2.0015 | 1.9602 | 1.9813 | 1.9633 | 2.0221 | 1.9955 | 1.9659 | 1.9596 | 1.9622 | 1.9936 | 1.9888 | 1.97 | 1.9631 | 1.9433 | 2.0075 | 1.9588 | 1.9988 | 1.9929 | 1.7603 | 1.9513 | 2.0187 | 2.0326 | 1.9925 | 2.015 | 1.9963 | 2.0251 | 2.0335 | 1.9596 | 2.0008 | 2.0013 | 1.9625 | 2.0115 | 2.0055 | 2.0097 | 1.9642 | 1.9742 | 1.9888 | 1.9625 | 1.9471 | 1.9542 | 2.0072 | 1.9948 | 2.0172 | 1.8524 | 1.9126 | 1.9989 | 2.0052 | 1.9609 | 1.9625 | 2.006 | 1.9559 | 2.0042 | 1.9775 | 2.0304 | 1.9602 | 1.9612 | 2 | 1.965 | 1.9685 | 1.986 | 2.0128 | 2.0187 | 2.0443 | 2.0353 | 1.9906 | 1.9872 | 1.9588 | 2.0121 | 2.0427 | 1.761 | 2.0432 | 2.0398 | 1.9983 | 1.9813 | 2.0461 | 1.9813 | 2.0037 | 2.0251 | 1.9625 | 2.0176 | 2.0038 | 2.0227 | 1.9865 | 1.9682 | 2.0333 | 1.7879 | 1.9562 | 2.0105 | 2.028 | 1.7811 | 2.0182 | 1.9829 | 1.9902 | 1.9996 | 1.9906 | 1.9855 | 1.963 | 1.8644 | 1.9848 | 1.983 | 1.9953 | 1.9659 | 1.9916 | 1.9461 | 1.9865 | 1.9964 | 2.0252 | 1.963 | 1.9818 | 1.9564 | 2.0036 | 1.7308 | 2.0038 | 2.0341 | 1.9962 | 1.9886 | 1.9462 | 1.9924 | 1.9795 | 1.9712 |  |  | 0 | 2.0026 | 1.9623 |  | 1.9515 | 2 | 1.9738 | 2.0075 | 2.0075 | 1.9745 | 1.8165 | 2.0202 | 1.9581 | 1.9993 | 1.9749 | 2.0243 | 1.9642 | 2.0558 | 2.1137 | 2.0197 | 2.0376 | 2.0903 | 1.9865 | 1.9754 | 2.0077 | 1.9892 | 1.9651 | 1.981 | 2.0297 | 1.9862 | 1.9895 | 1.9506 | 1.993 | 1.9885 | 2.0513 | 2.0127 | 2.0081 |  | 2.0776 | 1.9575 | 1.9701 | 1.9641 | 1.9775 |  |  | 2.14 | 2.1082 | 2.0805 | 1.988 | 2.0191 | 1.9964
2025-07-02 | 3.229 | 3.2913 | 3.2846 | 3.2884 | 3.2498 | 3.2547 | 3.2809 | 3.2772 | 3.1101 | 3.2539 | 3.3558 | 3.3258 | 3.1348 | 3.3585 | 3.3034 | 3.2921 | 3.2996 | 3.2996 | 3.3258 | 3.3258 | 3.3408 | 3.3296 | 3.2394 | 3.3525 | 3.3328 | 3.312 | 3.2844 | 3.2926 | 3.2992 | 3.1527 | 3.1893 | 3.3159 | 3.1958 | 3.291 | 3.2846 | 3.2954 | 3.3184 | 3.2584 | 3.1685 | 3.2622 | 3.1685 | 3.1423 | 3.1985 | 3.2022 | 3.221 | 3.236 | 3.2221 | 3.2135 | 3.2108 | 3.1533 | 3.1873 | 3.2397 | 3.2892 | 3.2226 | 3.1599 | 3.2759 | 3.1827 | 2.9588 | 3.1827 | 3.2093 | 3.2172 | 3.2252 | 3 | 3.3354 | 3.2256 | 3.2498 | 3.2567 | 3.1322 | 3.2397 | 3.2547 | 3.2509 | 3.1798 | 3.1423 | 3.176 | 3.1927 | 3.1527 | 3.1094 | 3.191 | 3.2397 | 3.1426 | 3.1311 | 3.2322 | 3.2397 | 3.2322 | 3.1498 | 3.1835 | 3.1498 | 3.2022 | 3.1423 | 3.1629 | 3.1676 | 3.115 | 3.0412 | 3.191 | 3.1893 | 3.2397 | 2.9513 | 3.1948 | 3.1685 | 3.1948 | 3.191 | 3.2285 | 3.1536 | 3.1985 | 3.206 | 2.9139 | 3.2193 | 3.175 | 3.2772 | 3.2559 | 3.2671 | 3.2325 | 3.2559 | 3.2593 | 3.2921 | 3.1573 | 3.1683 | 3.1361 | 3.2193 | 3.2434 | 3.2884 | 3.0129 | 3.0928 | 3.2472 | 3.2659 | 3.1594 | 3.1798 | 3.1573 | 3.2093 | 3.1261 | 3.1219 | 3.274 | 3.1945 | 3.2605 | 3.1538 | 3.1364 | 3.1573 | 3.2098 | 3.2503 | 3.2097 | 3.3016 | 3.2429 | 3.1798 | 3.191 | 3.1648 | 3.2774 | 3.1873 | 3.24 | 3.2636 | 3.2947 | 3.2671 | 3.2247 | 3.2326 | 3.1985 | 3.1723 | 3.1536 | 3.1648 | 3.2697 | 3.2235 | 3.2235 | 3.229 | 3.1818 | 3.1987 | 3.1448 | 3.1987 | 3.1673 | 3.2045 | 3.2694 | 3.1477 | 3.2218 | 3.2618 | 3.2073 | 3.2492 | 3.2255 | 3.0337 | 3.1591 | 3.2462 | 3.1477 | 3.1751 | 3.2235 | 3.1713 | 3.1818 | 3.2054 | 3.1927 | 3.2797 | 3.2727 | 3.1709 | 3.2255 | 3.1527 | 3.1853 | 3.178 | 3.1432 | 2.8674 | 3.1477 | 3.1477 | 3.0568 | 3.1909 | 3.1553 |  |  | 1.5812 | 3.1994 | 3.2114 |  | 3.2023 | 3.1685 | 3.1873 | 3.1498 | 3.1985 | 3.1536 | 3.1798 | 3.2547 | 3.176 | 3.1985 | 3.1873 | 3.2434 | 3.2226 | 3.2093 | 3.3453 | 3.408 | 3.302 | 3.3292 | 3.2035 | 3.1485 | 3.1748 | 3.1993 | 3.1461 | 3.1703 | 3.2431 | 3.1426 | 3.2027 | 3.1427 | 3.1818 | 3.1566 | 3.143 | 3.2061 | 3.196 |  | 3.3994 | 3.2079 | 3.194 | 3.2061 | 3.1702 |  |  | 3.348 | 3.3738 | 3.3065 | 3.143 | 3.1965 | 3.2028
2025-07-03 | 3.5817 | 3.6612 | 3.6629 | 3.6517 | 3.6439 | 3.6442 | 3.5805 | 3.5618 | 3.4661 | 3.6566 | 3.603 | 3.5768 | 3.5019 | 3.6364 | 3.6554 | 3.6442 | 3.6255 | 3.6217 | 3.6404 | 3.6404 | 3.6629 | 3.6629 | 3.5678 | 3.6821 | 3.6716 | 3.637 | 3.6128 | 3.6221 | 3.6321 | 3.4623 | 3.4823 | 3.499 | 3.5456 | 3.6557 | 3.5843 | 3.5597 | 3.4794 | 3.4757 | 3.4944 | 3.6105 | 3.5056 | 3.4963 | 3.5206 | 3.5393 | 3.5618 | 3.5843 | 3.592 | 3.573 | 3.5524 | 3.4912 | 3.5618 | 3.6067 | 3.6821 | 3.6088 | 3.471 | 3.5988 | 3.5389 | 3.5543 | 3.6355 | 3.6821 | 3.6217 | 3.553 | 3.573 | 3.7659 | 3.5678 | 3.6093 | 3.6197 | 3.4849 | 3.573 | 3.6067 | 3.5955 | 3.5056 | 3.633 | 3.5618 | 3.5422 | 3.5789 | 3.5988 | 3.5543 | 3.573 | 3.6128 | 3.6367 | 3.5318 | 3.603 | 3.5581 | 3.4831 | 3.5281 | 3.4719 | 3.5393 | 3.4944 | 3.4794 | 3.4912 | 3.4918 | 3.6105 | 3.5019 | 3.6188 | 3.5993 | 3.4944 | 3.5693 | 3.5843 | 3.5543 | 3.5993 | 3.5843 | 3.5468 | 3.5431 | 3.5522 | 3.5618 | 3.6088 | 3.462 | 3.6255 | 3.6355 | 3.6232 | 3.5402 | 3.4757 | 3.5123 | 3.5393 | 3.4794 | 3.4861 | 3.4757 | 3.6388 | 3.6255 | 3.6592 | 3.3791 | 3.4524 | 3.5843 | 3.6105 | 3.5089 | 3.4944 | 3.5318 | 3.5296 | 3.5645 | 3.5367 | 3.5685 | 3.5962 | 3.5015 | 3.5 | 3.5409 | 3.4755 | 3.5944 | 3.5452 | 3.5655 | 3.4883 | 3.5388 | 3.5903 | 3.5678 | 3.4667 | 3.5907 | 3.6 | 3.3544 | 3.534 | 3.5748 | 3.5644 | 3.5693 | 3.5689 | 3.5843 | 3.5618 | 3.5318 | 3.5431 | 3.5169 | 3.572 | 3.5152 | 3.5185 | 3.5379 | 3.5556 | 3.1616 | 3.5724 | 3.5091 | 3.0227 | 3.0236 | 3.4962 | 3.5236 | 3.5927 | 3.5164 | 3.5185 | 3.4873 | 3.4781 | 3.4962 | 3.4811 | 3.4811 | 3.4815 | 3.5 | 3.5315 | 3.4815 | 3.4714 | 3.5964 | 3.4895 | 3.4781 | 3.5418 | 3.5091 | 3.6 | 3.4825 | 3.5303 | 3.5379 | 3.5379 | 3.5114 | 3.5417 | 3.5795 | 3.6045 | 3.5833 |  |  | 3.3683 | 3.6091 | 3.5661 |  | 3.5373 | 3.4981 | 3.4869 | 3.4869 | 3.5431 | 3.5993 | 3.5805 | 3.5693 | 3.6105 | 3.5019 | 3.6105 | 3.5655 | 3.4923 | 3.6188 | 3.7215 | 3.6946 | 3.6625 | 3.6991 | 3.5017 | 3.5655 | 3.6674 | 3.5489 | 3.5678 | 3.5851 | 3.6027 | 3.5436 | 3.5456 | 3.6122 | 3.5004 | 3.5354 | 3.5004 | 3.4979 | 3.4909 |  | 3.6853 | 3.497 | 3.5423 | 3.4942 | 3.5004 |  |  | 3.6573 | 3.7461 | 3.6169 | 3.4848 | 3.4909 | 3.5537
2025-07-04 | 3.2982 | 3.3224 | 3.2809 | 3.3258 | 3.2982 | 3.2996 | 3.3146 | 3.3071 | 3.2036 | 3.2396 | 3.2659 | 3.2772 | 3.2783 | 3.2727 | 3.221 | 3.2434 | 3.2921 | 3.3333 | 3.2913 | 3.2809 | 3.3034 | 3.2734 | 3.3362 | 3.3691 | 3.3397 | 3.3812 | 3.357 | 3.2959 | 3.3678 | 3.2236 | 3.3025 | 3.3159 | 3.2606 | 3.291 | 3.2169 | 3.1927 | 3 | 3.2622 | 3.1876 | 3.3116 | 3.2472 | 3.2809 | 3.1925 | 3.2056 | 3.2442 | 3.2828 | 3.3006 | 3.2689 | 3.2723 | 3.2252 | 3.3157 | 3.33 | 3.3059 | 3.3268 | 3.2277 | 3.2959 | 3.1827 | 3.2172 | 3.3535 | 3.3125 | 3.2996 | 3.2285 | 3.206 | 3.419 | 3.2882 | 3.2712 | 3.3051 | 3.1948 | 3.2184 | 3.2487 | 3.2667 | 3.2019 | 3.2831 | 3.2491 | 3.2246 | 3.1594 | 3.2413 | 3.2322 | 3.2041 | 3.2411 | 3.279 | 3.2247 | 3.2528 | 3.2049 | 3.1554 | 3.2056 | 3.1629 | 3.2491 | 3.206 | 3.1985 | 3.2683 | 3.153 | 3.2768 | 3.1985 | 3.2127 | 3.2165 | 3.176 | 3.3026 | 3.2521 | 3.2622 | 3.3052 | 3.2431 | 3.2723 | 3.2157 | 3.189 | 3.1873 | 3.2539 | 3.1716 | 3.2266 | 3.1893 | 3.164 | 3.2709 | 3.2692 | 3.2786 | 3.2828 | 3.1648 | 3.1549 | 3.1727 | 3.2326 | 3.1884 | 3.2277 | 2.9413 | 3.0578 | 3.1517 | 3.1697 | 3.2153 | 3.03 | 3.1873 | 3.1467 | 3.1278 | 3.0548 | 3.1907 | 3.228 | 3.2605 | 3.2308 | 3.2217 | 3.1503 | 3.2657 | 3.2396 | 3.2798 | 3.2138 | 3.1782 | 3.2873 | 3.2602 | 3.1704 | 3.2277 | 3.1948 | 3.2462 | 3.1796 | 3.2363 | 3.2636 | 3.2367 | 3.2033 | 3.2491 | 3.2015 | 3.1704 | 3.2041 | 3.1723 | 3.2235 | 3.2159 | 3.2357 | 3.2326 | 3.2569 | 3.1801 | 3.3949 | 3.2167 | 3.2008 | 3.2431 | 3.2617 | 3.2476 | 3.2564 | 3.2316 | 3.229 | 3.3422 | 3.1481 | 3.197 | 3.1886 | 3.2235 | 3.1461 | 3.1761 | 3.2587 | 3.2121 | 3.2259 | 3.1527 | 3.2661 | 3.2556 | 3.2625 | 3.2284 | 3.2364 | 3.1888 | 3.1894 | 3.1856 | 3.1742 | 3.2008 | 3.1678 | 3.1894 | 3.2659 | 3.1879 |  |  | 2.9697 | 3.1994 | 3.1892 |  | 3.1921 | 3.1648 | 3.1798 | 3.2022 | 3.206 | 3.1873 | 3.1723 | 3.2464 | 3.2127 | 3.2247 | 3.2352 | 3.3131 | 3.2027 | 3.1827 | 3.408 | 3.3632 | 3.4169 | 3.4734 | 3.2275 | 3.1864 | 3.2802 | 3.2499 | 3.1841 | 3.2325 | 3.3158 | 3.1997 | 3.238 | 3.2127 | 3.1974 | 3.2143 | 3.2789 | 3.251 | 3.2727 |  | 3.3428 | 3.2776 | 3.194 | 3.1949 | 3.2401 |  |  | 3.348 | 3.4404 | 3.4023 | 3.1974 | 3.2753 | 3.2378
2025-07-05 | 3.9761 | 4.0474 | 4.0348 | 4.0184 | 4.0149 | 4.0071 | 4.0187 | 4.0356 | 3.726 | 4.0266 | 4.0745 | 4.0644 | 3.9288 | 4.1397 | 4.0228 | 4.0217 | 3.9213 | 3.9217 | 3.9326 | 3.9416 | 4.0094 | 4.0461 | 3.9557 | 4.0599 | 3.9879 | 3.9789 | 3.9751 | 4.0027 | 4.0057 | 3.8702 | 3.98 | 4.0077 | 3.9104 | 4.0472 | 3.8678 | 3.8381 | 3.8202 | 3.8315 | 3.8022 | 3.7903 | 3.8427 | 3.7903 | 3.827 | 3.8757 | 3.9 | 3.9536 | 3.9513 | 3.897 | 3.9723 | 3.9198 | 3.9783 | 4.0049 | 4.0836 | 3.97 | 3.917 | 4.0879 | 3.702 | 4.0352 | 3.976 | 4.024 | 3.9543 | 4.0378 | 3.9903 | 4.1379 | 4.0484 | 4.0657 | 4.0622 | 4.0415 | 3.9176 | 3.9476 | 3.9288 | 3.9064 | 3.9288 | 4.0824 | 3.985 | 3.9717 | 4.0682 | 4.0824 | 4.0861 | 4.0933 | 4.0375 | 4.1236 | 4.0562 | 4.0562 | 4.0109 | 4.0742 | 4.0221 | 4.0262 | 3.9213 | 3.9064 | 4.1 | 3.8755 | 4.1742 | 4.1232 | 4.0982 | 4.1659 | 3.9775 | 4.2281 | 4.1566 | 4.1772 | 4.2431 | 4.173 | 4.23 | 4.1742 | 4.1199 | 4.1199 | 4.238 | 4.2004 | 4.127 | 4.1685 | 4.1483 | 4.1269 | 4.1515 | 4.1481 | 4.194 | 3.9813 | 3.9946 | 4.0087 | 4.1774 | 4.1918 | 4.1708 | 3.8921 | 4.0393 | 4.0854 | 4.118 | 4.2181 | 3.824 | 3.779 | 3.7813 | 3.7786 | 3.796 | 3.7991 | 3.8479 | 3.8161 | 3.8287 | 3.8881 | 3.8357 | 3.9325 | 3.8508 | 3.8315 | 3.8182 | 3.8686 | 3.8742 | 3.8064 | 3.7865 | 3.8513 | 3.8491 | 3.8039 | 3.8237 | 3.8375 | 3.8064 | 3.8689 | 3.8705 | 3.8652 | 3.8315 | 3.8749 | 3.8165 | 3.8449 | 4.0182 | 3.9375 | 3.9475 | 3.9167 | 3.9226 | 3.9428 | 4.0098 | 3.9055 | 4 | 3.9764 | 4.0038 | 3.9087 | 3.9055 | 3.9345 | 3.9596 | 3.9989 | 3.8485 | 3.8485 | 3.9205 | 3.9129 | 3.9226 | 4.0417 | 3.958 | 3.9461 | 3.9529 | 4.1305 | 3.9182 | 3.9327 | 3.9691 | 3.9127 | 3.72 | 3.6538 | 4.0277 | 4.1364 | 4.0341 | 3.9583 | 4.1322 | 3.9583 | 4.1655 | 4.1311 |  |  | 3.7405 | 4.0137 | 3.9431 |  | 3.961 | 3.9438 | 3.9588 | 4.0453 | 4.0895 | 4.1292 | 4.1135 | 4.2573 | 4.1749 | 4.0247 | 4.1562 | 4.2101 | 3.9451 | 4.2454 | 4.2812 | 4.2947 | 4.2894 | 4.2759 | 4.1135 | 4.2131 | 4.2783 | 4.3253 | 4.3053 | 4.2337 | 4.3182 | 4.3267 | 4.2903 | 4.304 | 4.1123 | 4.1739 | 4.0571 | 4.122 | 4.122 |  | 4.2471 | 4.0669 | 4.0697 | 4.1182 | 4.1445 |  |  | 4.1964 | 4.1693 | 4.2261 | 3.9316 | 3.92 | 4.0087
2025-07-06 | 3.4271 | 3.5004 | 3.5075 | 3.5045 | 3.4697 | 3.4644 | 3.4929 | 3.5026 | 3.4596 | 3.4801 | 3.5169 | 3.5442 | 3.5094 | 3.5698 | 3.4772 | 3.4581 | 3.4667 | 3.4577 | 3.4669 | 3.4672 | 3.485 | 3.4813 | 3.4261 | 3.499 | 3.5015 | 3.4707 | 3.4462 | 3.4606 | 3.484 | 3.4497 | 3.4474 | 3.4797 | 3.467 | 3.5032 | 3.4348 | 3.4085 | 3.4674 | 3.4157 | 3.4045 | 3.4213 | 3.427 | 3.4494 | 3.4419 | 3.4794 | 3.4607 | 3.4064 | 3.4261 | 3.4644 | 3.4373 | 3.4409 | 3.4644 | 3.4356 | 3.5233 | 3.4184 | 3.4261 | 3.4966 | 3.5236 | 3.5281 | 3.4816 | 3.5233 | 3.4356 | 3.5309 | 3.4532 | 3.4734 | 3.5685 | 3.5592 | 3.5872 | 3.507 | 3.4543 | 3.5292 | 3.5573 | 3.512 | 3.5506 | 3.5614 | 3.5982 | 3.5313 | 3.6175 | 3.5547 | 3.476 | 3.5239 | 3.4494 | 3.5843 | 3.4839 | 3.4266 | 3.4682 | 3.4906 | 3.5199 | 3.4921 | 3.5206 | 3.4828 | 3.5171 | 3.5388 | 3.6067 | 3.5318 | 3.5246 | 3.5333 | 3.406 | 3.6127 | 3.5865 | 3.5169 | 3.4869 | 3.4906 | 3.5393 | 3.5873 | 3.5799 | 3.412 | 3.5722 | 3.5982 | 3.5581 | 3.5775 | 3.5526 | 3.5734 | 3.5942 | 3.5845 | 3.5779 | 3.4569 | 3.4292 | 3.4324 | 3.5835 | 3.5543 | 3.5603 | 3.3814 | 3.4514 | 3.4689 | 3.5154 | 3.5323 | 3.4419 | 3.4644 | 3.455 | 3.4727 | 3.4261 | 3.5333 | 3.5056 | 3.5869 | 3.5524 | 3.45 | 3.4301 | 3.5804 | 3.5596 | 3.5618 | 3.5156 | 3.4876 | 3.5955 | 3.5678 | 3.5139 | 3.5264 | 3.4981 | 3.5587 | 3.4192 | 3.5229 | 3.5678 | 3.573 | 3.5968 | 3.5918 | 3.5813 | 3.567 | 3.5854 | 3.5112 | 3.5023 | 3.4341 | 3.4414 | 3.5038 | 3.4377 | 3.4714 | 3.5226 | 3.4291 | 3.5795 | 3.4646 | 3.408 | 3.4364 | 3.4145 | 3.4582 | 3.4717 | 3.4673 | 3.4646 | 3.5568 | 3.4924 | 3.4659 | 3.4377 | 3.5076 | 3.528 | 3.4074 | 3.4646 | 3.5564 | 3.514 | 3.4646 | 3.4684 | 3.488 | 3.4807 | 3.5385 | 3.5265 | 3.5492 | 3.2235 | 3.5038 | 3.5682 | 3.5114 | 3.4891 | 3.4814 |  |  | 3.2556 | 3.4148 | 3.4701 |  | 3.5338 | 3.4551 | 3.4607 | 3.4341 | 3.4536 | 3.5345 | 3.4768 | 3.5169 | 3.5356 | 3.4569 | 3.5124 | 3.5243 | 3.459 | 3.6588 | 3.7573 | 3.7707 | 3.7461 | 3.7367 | 3.4392 | 3.4979 | 3.6164 | 3.499 | 3.5634 | 3.5108 | 3.5596 | 3.5298 | 3.5862 | 3.5389 | 3.5004 | 3.4401 | 3.5392 | 3.453 | 3.4222 |  | 3.5395 | 3.5145 | 3.4925 | 3.453 | 3.4106 |  |  | 3.6071 | 3.6481 | 3.6207 | 3.5004 | 3.4453 | 3.5031
2025-07-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2025-07-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
Formulas:
Date = [Date, row above]+1

## Inv_SY
| 289.25 | 289.25 | 267 | 267 | 289.25 | 267 | 267 | 267 | 278.125 | 278.125 | 267 | 267 | 267 | 244.75 | 267 | 267 | 267 | 267 | 289.25 | 289.25 | 267 | 267 | 289.25 | 300.375 | 289.25 | 289.25 | 289.25 | 300.375 | 300.375 | 300.375 | 300.375 | 300.375 | 254.4 | 334.55 | 267 | 298.9 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 289.25 | 267 | 278.125 | 278.125 | 267 | 267 | 300.375 | 300.375 | 289.25 | 300.375 | 300.375 | 267 | 300.375 | 300.375 | 267 | 298.9 | 267 | 239.25 | 289.25 | 289.25 | 289.25 | 289.25 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 300.375 | 300.375 | 267 | 267 | 289.25 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 278.125 | 289.25 | 267 | 267 | 300.375 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 267 | 300.375 | 298.9 | 267 | 300.375 | 289.25 | 289.25 | 300.375 | 300.375 | 267 | 267 | 298.9 | 300.375 | 300.375 | 267 | 267 | 300.375 | 300.375 | 267 | 267 | 300.375 | 267 | 267 | 300.375 | 300.375 | 289.25 | 289.25 | 289.25 | 244.75 | 286 | 286 | 286 | 286 | 278.125 | 267 | 289.25 | 289.25 | 267 | 289.25 | 267 | 289.25 | 267 | 244.75 | 289.25 | 289.25 | 289.25 | 267 | 300.375 | 267 | 267 | 267 | 267 | 267 | 264 | 264 | 297 | 264 | 297 | 297 | 297 | 275 | 264 | 297 | 264 | 275 | 275 | 275 | 297 | 275 | 297 | 264 | 264 | 264 | 297 | 264 | 286 | 297 | 297 | 275 | 286 | 297 | 275 | 275 | 275 | 286 | 264 | 264 | 264 | 264 | 264 | 264 | 220 | 264 | 0 | 0 | 257.4 | 190.35 | 270.6 | 0 | 292.6 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 300.375 | 223.3 | 223.3 | 191.4 | 159.5 | 207.9 | 239.8 | 278.125 | 300.375 | 289.25 | 289.25 | 278.125 | 289.25 | 300.38 | 300.375 | 257.4 | 277.2 | 257.4 | 267.3 | 247.5 | 0 | 353.2 | 287.1 | 100.5 | 267.3 | 257.4 | 0 | 0 | 239.25 | 255.2 | 261 | 257.4 | 241.2 | 67019.305
Date | BLK1_INV1 | BLK1_INV2 | BLK1_INV3 | BLK1_INV4 | BLK1_INV5 | BLK1_INV6 | BLK1_INV7 | BLK1_INV8 | BLK1_INV9 | BLK1_INV10 | BLK1_INV11 | BLK1_INV12 | BLK1_INV13 | BLK1_INV14 | BLK1_INV15 | BLK1_INV16 | BLK1_INV17 | BLK1_INV18 | BLK1_INV19 | BLK1_INV20 | BLK1_INV21 | BLK1_INV22 | BLK1_INV23 | BLK1_INV24 | BLK1_INV25 | BLK1_INV26 | BLK1_INV27 | BLK1_INV28 | BLK1_INV29 | BLK1_INV30 | BLK1_INV31 | BLK1_INV32 | BLK2_INV1 | BLK2_INV2 | BLK2_INV3 | BLK2_INV4 | BLK2_INV5 | BLK2_INV6 | BLK2_INV7 | BLK2_INV8 | BLK2_INV9 | BLK2_INV10 | BLK2_INV11 | BLK2_INV12 | BLK2_INV13 | BLK2_INV14 | BLK2_INV15 | BLK2_INV16 | BLK2_INV17 | BLK2_INV18 | BLK2_INV19 | BLK2_INV20 | BLK2_INV21 | BLK2_INV22 | BLK2_INV23 | BLK2_INV24 | BLK2_INV25 | BLK2_INV26 | BLK2_INV27 | BLK2_INV28 | BLK2_INV29 | BLK2_INV30 | BLK2_INV31 | BLK2_INV32 | BLK3_INV1 | BLK3_INV2 | BLK3_INV3 | BLK3_INV4 | BLK3_INV5 | BLK3_INV6 | BLK3_INV7 | BLK3_INV8 | BLK3_INV9 | BLK3_INV10 | BLK3_INV11 | BLK3_INV12 | BLK3_INV13 | BLK3_INV14 | BLK3_INV15 | BLK3_INV16 | BLK3_INV17 | BLK3_INV18 | BLK3_INV19 | BLK3_INV20 | BLK3_INV21 | BLK3_INV22 | BLK3_INV23 | BLK3_INV24 | BLK3_INV25 | BLK3_INV26 | BLK3_INV27 | BLK3_INV28 | BLK3_INV29 | BLK3_INV30 | BLK3_INV31 | BLK4_INV1 | BLK4_INV2 | BLK4_INV3 | BLK4_INV4 | BLK4_INV5 | BLK4_INV6 | BLK4_INV7 | BLK4_INV8 | BLK4_INV9 | BLK4_INV10 | BLK4_INV11 | BLK4_INV12 | BLK4_INV13 | BLK4_INV14 | BLK4_INV15 | BLK4_INV16 | BLK4_INV17 | BLK4_INV18 | BLK4_INV19 | BLK4_INV20 | BLK4_INV21 | BLK4_INV22 | BLK4_INV23 | BLK4_INV24 | BLK4_INV25 | BLK4_INV26 | BLK4_INV27 | BLK4_INV28 | BLK4_INV29 | BLK4_INV30 | BLK4_INV31 | BLK5_INV1 | BLK5_INV2 | BLK5_INV3 | BLK5_INV4 | BLK5_INV5 | BLK5_INV6 | BLK5_INV7 | BLK5_INV8 | BLK5_INV9 | BLK5_INV10 | BLK5_INV11 | BLK5_INV12 | BLK5_INV13 | BLK5_INV14 | BLK5_INV15 | BLK5_INV16 | BLK5_INV17 | BLK5_INV18 | BLK5_INV19 | BLK5_INV20 | BLK5_INV21 | BLK5_INV22 | BLK5_INV23 | BLK5_INV24 | BLK5_INV25 | BLK5_INV26 | BLK5_INV27 | BLK5_INV28 | BLK5_INV29 | BLK5_INV30 | BLK5_INV31 | BLK5_INV32 | BLK6_INV1 | BLK6_INV2 | BLK6_INV3 | BLK6_INV4 | BLK6_INV5 | BLK6_INV6 | BLK6_INV7 | BLK6_INV8 | BLK6_INV9 | BLK6_INV10 | BLK6_INV11 | BLK6_INV12 | BLK6_INV13 | BLK6_INV14 | BLK6_INV15 | BLK6_INV16 | BLK6_INV17 | BLK6_INV18 | BLK6_INV19 | BLK6_INV20 | BLK6_INV21 | BLK6_INV22 | BLK6_INV23 | BLK6_INV24 | BLK6_INV25 | BLK6_INV26 | BLK6_INV27 | BLK6_INV28 | BLK6_INV29 | BLK6_INV30 | BLK6_INV31 | BLK6_INV32 | BLK7_INV1 | BLK7_INV2 | BLK7_INV3 | BLK7_INV4 | BLK7_INV5 | BLK7_INV6 | BLK7_INV7 | BLK7_INV8 | BLK7_INV9 | BLK7_INV10 | BLK7_INV11 | BLK7_INV12 | BLK7_INV13 | BLK7_INV14 | BLK7_INV15 | BLK7_INV16 | BLK7_INV17 | BLK7_INV18 | BLK7_INV19 | BLK7_INV20 | BLK7_INV21 | BLK7_INV22 | BLK7_INV23 | BLK7_INV24 | BLK7_INV25 | BLK7_INV26 | BLK7_INV27 | BLK7_INV28 | BLK7_INV29 | BLK7_INV30 | BLK7_INV31 | BLK7_INV32 | BLK8_INV1 | BLK8_INV2 | BLK8_INV3 | BLK8_INV4 | BLK8_INV5 | BLK8_INV6 | BLK8_INV7 | BLK8_INV8 | BLK8_INV9 | BLK8_INV10 | BLK8_INV11 | BLK8_INV12 | BLK8_INV13 | BLK8_INV14 | BLK8_INV15 | BLK8_INV16 | BLK8_INV17 | BLK8_INV18 | BLK8_INV19 | BLK8_INV20 | BLK8_INV21 | BLK8_INV22 | BLK8_INV23 | BLK8_INV24 | BLK8_INV25 | BLK8_INV26 | BLK8_INV27 | BLK8_INV28
2025-06-05 | -7.413% | -2.116% | -2.135% | -2.135% | -2.552% | -1.977% | -1.506% | -3.471% | -2.352% | -1.974% | 0.4594% | -0.01223% | -1.742% | 0.8453% | -1.584% | -2.213% | -6.379% | -2.842% | -1.899% | -1.971% | -1.427% | -5.279% | -4.221% | -1.06% | -0.8104% | -1.681% | -2.334% | -2.807% | -1.27% | -3.436% | -12.38% | -9.934% | 0.07249% | -9.097% | -4.729% | -0.1508% | -1.977% | -2.528% | -1.191% | 0.4594% | -1.427% | -2.213% | -0.8769% | -10.55% | -1.034% | -0.09084% | -0.7378% | -5.908% | -1.672% | -3.333% | -0.8769% | -4.65% | 1.036% | -0.2917% | -1.463% | 0.05764% | 0.4769% | 0.6166% | -0.7808% | 0.6166% | -4.65% | -4.013% | -1.427% | -15.96% | 3.108% | 1.221% | 3.979% | -4.874% | 3.053% | 2.032% | 3.604% | 3.446% | 5.176% | 2.896% | 4.809% | 2.363% | 4.32% | 0.4594% | -1.506% | 1.366% | 3.682% | 3.289% | 2.503% | 8.477% | 3.211% | 2.267% | 4.39% | 3.682% | 3.368% | 2.818% | 2.553% | -2.262% | 5.962% | 5.412% | -7.419% | -9.052% | 1.088% | 3.525% | 2.032% | 2.582% | 5.333% | 2.425% | 4.154% | 1.639% | 2.992% | 3.839% | 7.464% | 1.464% | 3.604% | 0.6865% | 3.18% | -5.817% | 1.804% | 2.363% | 2.975% | -6.458% | 0.9727% | 3.272% | 2.643% | 3.446% | 4.39% | -2.178% | -3.855% | 3.132% | 4.075% | -12.45% | -13.14% | -11.65% | -2.108% | -3.366% | -6.76% | -2.77% | -3.205% | -2.07% | 2.885% | -5.407% | -1.885% | -10.4% | -1.371% | -1.899% | -4.293% | -5.599% | -2.449% | -1.536% | -5.122% | -3.35% | -2.685% | -1.127% | -2.987% | -1.899% | -1.173% | -1.82% | -0.08211% | -1.349% | -3.157% | -4.021% | -1.427% | -3.864% | 4.145% | 0.965% | 3.032% | 0.488% | 1.548% | -0.2893% | 2.396% | 3.032% | -1.182% | 0.912% | 3.588% | -0.6314% | 1.124% | 3.643% | 0.2053% | 1.353% | 0.06399% | 2.714% | 3.827% | 1.203% | 1.689% | 5.337% | 2.592% | -0.2187% | 4.233% | 4.177% | 3.839% | 0.7% | 4.177% | 4.177% | 0.6661% | 3.619% | 0.647% | 1.521% | -0.784% | 1.76% | 0.965% | 1.998% | 1.696% | 3.35% |  |  | -7.78% | -0.9865% | -1.963% |  | -2.95% | 2.032% | 3.761% | 0.8524% | 2.975% | 2.739% | 4.233% | 4.154% | 4.233% | 4.861% | 3.604% | 3.682% | 2.573% | 4.46% | 11.85% | 9.123% | -0.9814% | 8.559% | -2.581% | -0.924% | 2.629% | 1.804% | 1.874% | -1.173% | -2.352% | -0.08479% | 1.106% | -2.737% | 0.2923% | -1.799% | -2.317% | 1.917% | 2.608% |  | 0.8707% | -0.7986% | 1.912% | 1.917% | 10.81% |  |  | 17.64% | -2.626% | 5.342% | -2.317% | -2.369%
2025-06-06 | -0.5984% | 1.643% | -2.183% | 1.733% | 0.8475% | 1.498% | 1.498% | -6.725% | 1.047% | 1.573% | 3.221% | 2.751% | 1.185% | 3.89% | 1.185% | 0.7932% | -3.827% | 0.01008% | 0.3414% | 0.3414% | 1.107% | -2.731% | -1.321% | 1.498% | 1.498% | 0.5583% | -0.02005% | -0.2423% | 1.08% | -0.5903% | -11.59% | -7.273% | 1.265% | -1.37% | -3.592% | 1.159% | 1.341% | -1.086% | 0.4017% | 1.89% | 0.08839% | -0.6165% | 0.7149% | -9.623% | 0.3233% | 1.263% | 0.486% | -4.454% | -3.84% | -5.118% | 1.028% | -3.201% | 2.473% | 0.9412% | 0.05225% | 1.985% | 1.846% | 1.811% | 0.3146% | 1.428% | 1.576% | 2.209% | -0.6948% | -15.4% | 1.064% | 0.2691% | 0.4137% | -7.611% | 0.7932% | -2.104% | -0.9297% | 0.9499% | 1.028% | 1.028% | -0.9384% | -3.445% | -2.331% | -2.104% | -5.472% | -5.442% | -5.315% | 0.08839% | 0.9499% | -5.315% | -0.7731% | 1.028% | -0.9297% | 1.263% | -2.496% | -2.418% | -2.186% | -6.309% | 1.107% | 1.42% | -8.944% | -9.779% | -2.104% | 1.42% | 0.245% | 0.6366% | 3.378% | 0.48% | 2.516% | 0.3233% | 2.403% | 1.89% | 7.067% | 0.5998% | 1.811% | -1.078% | 1.715% | -0.5261% | 0.245% | 0.9412% | 0.6366% | -8.84% | 0.25% | 1.777% | 1.359% | 1.733% | 2.751% | -2.54% | -5.394% | 1.42% | 2.203% | -9.64% | -10.01% | -8.526% | 1.359% | 0.03618% | -3.418% | 0.8475% | 0.4137% | 1.584% | 7.111% | -0.9311% | 2.798% | -5.903% | 3.453% | 2.673% | -0.6707% | -2.117% | 2.125% | 2.582% | -0.6165% | 3.956% | 1.107% | 2.352% | 0.6306% | 1.715% | 2.366% | 1.733% | 3.656% | 2.203% | 0.4017% | -0.6165% | 1.811% | -0.1466% | 2.81% | -1.863% | 1.595% | -0.4376% | 0.6097% | -1.362% | -0.5872% | 2.499% | -3.289% | -0.5168% | 1.226% | -1.911% | -0.9984% | 1.891% | -1.573% | -0.9984% | 0.04647% | 1.226% | 3.048% | -0.4376% | -1.362% | 3.998% | 0.7505% | -1.362% | 2.792% | 4.02% | 2.505% | -0.6576% | 4.781% | 3.412% | -0.314% | 3.748% | 1.78% | -0.5168% | -1.705% | 0.3545% | 0.5129% | 1.226% | 2.842% | 2.81% |  |  | -6.496% | 0.1858% | -0.7795% |  | -0.3072% | 2.046% | 1.89% | -0.3815% | 0.9499% | 1.42% | 2.046% | 1.811% | 2.046% | 3.456% | 1.89% | 2.046% | 1.359% | 3.378% | 11.62% | 9% | 6.847% | 2.258% | -1.633% | 0.454% | 0.6711% | 0.5235% | -0.3092% | 0.4137% | -1.509% | 0.5583% | -0.1727% | -2.679% | 1.303% | -1.181% | -0.2406% | 0.8366% | 0.6238% |  | -0.6855% | 1.821% | 0.07904% | 0.6801% | -1.54% |  |  | 2.52% | -0.8555% | 1.748% | -4.302% | -3.944%
2025-06-07 | -0.9336% | 1.502% | -2.355% | 1.751% | 0.6227% | 1.237% | 1.237% | -6.533% | 0.4955% | 0.9881% | 2.997% | 2.337% | 0.9441% | 3.643% | 0.7242% | 0.431% | -4.114% | -0.2288% | -0.1893% | 0.149% | 1.091% | -3.014% | -1.272% | 1.392% | 1.57% | 0.4197% | -0.05396% | -0.1718% | 0.7405% | -0.5627% | -14.64% | -7.209% | 4.867% | -1.828% | -4.187% | 0.3864% | 0.5776% | -1.548% | -0.08215% | 1.751% | -0.08215% | -1.182% | 0.5043% | -8.879% | 0.7242% | 1.311% | 0.7581% | -4.261% | -4.36% | -5.486% | 0.6509% | -3.528% | 2.37% | 0.8708% | -0.5276% | 1.783% | 1.457% | 1.384% | -0.1718% | 0.936% | 1.164% | 1.631% | -0.08215% | -10.01% | -1.543% | -2.896% | -2.422% | -7.362% | -2.721% | -2.941% | -2.428% | -2.868% | -1.915% | -2.648% | -2.257% | -3.886% | -2.909% | -2.648% | -5.507% | -5.467% | -3.308% | 1.017% | -0.8885% | -4.114% | -1.402% | -1.622% | -2.648% | -1.475% | -2.355% | -2.575% | -2.531% | -1.001% | -1.182% | -1.695% | -8.122% | -9.099% | -0.8152% | 1.237% | 0.06446% | 0.5043% | 3.143% | 0.3577% | 2.044% | -0.3021% | 1.718% | 1.311% | 4.846% | 0.2554% | 1.751% | -2.127% | 1.638% | -2.219% | -1.866% | 0.6102% | 1.017% | -8.366% | -0.203% | 0.936% | 0.2844% | 1.457% | 2.777% | -2.127% | -4.994% | 1.237% | 1.897% | -9.751% | -10.49% | -9.099% | 0.936% | -0.4976% | -4.114% | 0.08138% | -0.05396% | 1.324% | 5.941% | -1.177% | 2.451% | -6.309% | 1.973% | 0.7242% | -1.34% | -3.708% | 1.531% | 1.57% | -1.695% | -0.7306% | -0.3021% | 1.244% | -0.1216% | 0.7581% | 1.57% | 0.8708% | 2.435% | 1.384% | -0.08215% | -1.035% | 1.897% | -0.522% | 2.165% | -1.986% | 3.994% | 1.053% | 4.653% | 3.006% | -0.4872% | 6.62% | 1.053% | 3.006% | 9.579% | 0.3564% | 0.214% | 5.196% | -0.4872% | -0.4977% | -0.619% | 3.648% | 4.39% | 1.053% | 3.006% | 4.538% | 1.15% | -1.278% | 3.006% | 4.129% | 2.793% | -0.9485% | 6.62% | 5.196% | 6.62% | 3.34% | 0.8309% | 0.08945% | -1.097% | 1.424% | 1.202% | 1.646% | 3.114% | 3.722% |  |  | -6.545% | 2.621% | -1.267% |  | -0.5293% | 1.531% | 1.237% | -1.622% | 0.7242% | 1.677% | 1.897% | 1.751% | 1.97% | 3.07% | 2.117% | 2.63% | 1.653% | 3.673% | 11.5% | 9.129% | 2.058% | 23.94% | 0.5484% | 9.537% | -0.06749% | -1.866% | -2.219% | -1.543% | -2.108% | 0.149% | -0.9537% | -2.061% | -1.146% | -1.57% | 0.2986% | 1.929% | 2.65% |  | -1.11% | 1.376% | 1.273% | -2.464% | -1.374% |  |  | -1.992% | 0.08945% | 2.29% | -4.112% | -1.08%
2025-06-08 | -1.705% | 0.5688% | -1.758% | 0.7726% | -0.1174% | 0.4723% | 0.5249% | 0.7651% | -0.2092% | 0.3387% | -1.72% | 1.891% | 0.2621% | 2.971% | 0.3371% | -0.1359% | -2.509% | -0.6089% | -0.256% | -0.2214% | 0.6901% | -1.555% | -2.093% | 0.7084% | 1.193% | -0.02731% | -0.4848% | -0.78% | 0.5082% | -1.134% | -6.213% | -3.79% | 0.1765% | -2.071% | -2.291% | 0.1523% | 0.4498% | -1.945% | 0.1569% | 1.298% | -0.6014% | -1.472% | 0.4348% | -0.4513% | 1.035% | 1.268% | 0.9153% | -0.1659% | -0.5408% | -2.199% | 0.9153% | 0.9604% | 2.737% | 1.242% | -0.9422% | 1.015% | 0.8686% | 0.9904% | -0.4222% | 0.7752% | 0.8027% | 1.534% | -3.62% | 8.405% | -0.04117% | -0.665% | 0.7559% | -2.12% | -0.7141% | -0.04579% | 0.5324% | 0.08937% | 2.379% | -0.9018% | 1.616% | -0.5464% | 1.249% | 0.3972% | -0.8042% | -1.247% | 0.6976% | 1.111% | -0.1659% | 1.231% | 0.8552% | 1.08% | 1.351% | -5.617% | -0.3386% | -1.517% | -0.9228% | -2.107% | 2.687% | 2.762% | -0.3194% | -5.302% | -1.322% | 0.7201% | -0.5414% | -0.1059% | 2.477% | -0.256% | 1.569% | -0.7741% | 1.396% | 0.8177% | 5.307% | -0.7062% | 1.073% | -2.195% | 0.5133% | -2.703% | -1.728% | 0.0877% | 0.4723% | -4.649% | -0.4044% | 0.5416% | -0.03911% | 0.9078% | 1.997% | -0.4529% | 0.01428% | 0.5174% | 1.171% | 0.2145% | -10.29% | -8.741% | 0.8953% | -0.5797% | -2.897% | -0.1105% | -0.4154% | 0.989% | 6.268% | -1.064% | 2.216% | -5.852% | 2.112% | 0.9303% | -1.504% | -2.897% | 1.448% | 1.428% | -1.525% | -0.7966% | -0.3086% | 1.112% | -0.4848% | 0.3816% | 1.366% | 0.7501% | 2.217% | 1.02% | -0.4963% | -1.42% | -0.5489% | 0.2696% | -0.4363% | -0.1098% | 0.199% | -0.33% | 0.3813% | -0.9417% | 0.003284% | 9.432% | -0.4059% | -0.3005% | 0.3534% | -1.911% | -1.627% | 1.289% | -2.569% | -2.203% | 0.469% | 0.3534% | 0.194% | -0.07181% | -0.003467% | 0.5813% | -0.125% | 0.469% | 1.009% | 2.463% | 1.018% | 1.009% | -1.619% | -2.37% | -2.13% | -1.976% | 0.399% | 0.156% | -7.641% | -0.4135% | 0.5205% | -6.944% | 2.928% | 3.004% |  |  | -7.058% | -2.114% | -1.576% |  | 0.5479% | -2.651% | 0.7051% | -1.307% | 0.2095% | 0.4948% | 1.298% | 1.111% | 1.261% | 2.515% | 2.042% | 2.387% | 1.196% | 3.518% | 10.44% | 5.348% | 5.372% | 8.875% | -2.692% | -2.068% | -0.375% | -0.8801% | -2.058% | -2.197% | 0.9946% | -0.5749% | -1.347% | 0.8552% | 1.127% | 2.055% | 2.919% | 3.157% | 1.689% |  | 2.106% | -2.17% | -1.237% | -2.768% | -1.443% |  |  | 1.258% | 1.685% | 1.676% | -3.335% | 1.029%
2025-06-09 | -0.2811% | 0.5585% | -2.05% | 1.98% | 0.8315% | 1.773% | 0.3088% | 0.9299% | 0.1511% | 0.9178% | 2.291% | 1.795% | 0.2718% | -0.6962% | 0.1461% | -0.231% | -0.4529% | -0.6008% | -0.2879% | -0.1036% | 0.5898% | 0.7894% | -0.1787% | 0.6859% | 1.296% | -0.00805% | -0.4517% | -0.6813% | 0.6662% | -1.128% | -0.6747% | -1.306% | -0.3808% | -2.582% | -4.949% | -0.1515% | 0.1683% | -2.213% | -0.7487% | 0.8486% | 0.2422% | -1.969% | -0.09053% | -0.9853% | 0.5528% | 0.7303% | 0.538% | -0.5786% | 0.08014% | -1.446% | 1.122% | 0.9669% | 0.6465% | 1.093% | -0.4244% | -0.0174% | 0.7516% | 0.8338% | -0.3132% | 0.6202% | 0.7081% | 1.388% | 1.115% | 7.933% | 0.8998% | 0.2718% | 1.657% | -1.844% | -1.104% | -0.009188% | 0.575% | 0.1609% | 0.6415% | -1.532% | 1.409% | -0.6156% | 1.166% | 0.005601% | -0.9779% | -1.564% | 0.3975% | 0.8486% | -0.4307% | 0.8412% | 0.6563% | 0.9817% | 1.1% | -3.721% | -0.4972% | -1.532% | -0.6936% | -2.315% | 0.4937% | 1.632% | 0.4624% | -5.533% | -1.547% | 0.612% | -0.8226% | -0.1423% | 0.2718% | -0.3419% | 0.1979% | -0.8448% | 1.692% | 1.004% | -1.339% | -0.1317% | 1.07% | -2.502% | 0.7633% | -2.315% | -2.548% | -0.1357% | 0.3014% | -5.607% | -0.898% | 0.6596% | 0.2061% | 1.152% | 2.202% | -2.108% | -1.74% | 0.6489% | 1.344% | 1.902% | -2.568% | -1.133% | 0.5347% | -0.701% | -4.254% | -0.2538% | -0.5541% | -1.342% | 0.3757% | -1.578% | 2.419% | -4.298% | 0.8752% | -0.09792% | -1.544% | -2.895% | 1.558% | 2.675% | 0.013% | 0.4971% | 0.8412% | 1.417% | -0.2811% | 0.4356% | 1.535% | 0.7746% | 0.3704% | 1.107% | -0.4972% | -1.569% | -0.5638% | -1.067% | -0.2714% | -0.3687% | 1.411% | -0.421% | 1.81% | 0.454% | 0.7864% | -0.6206% | -0.6753% | 2.315% | -0.1967% | -0.9652% | -0.09645% | -0.4411% | 1.165% | 0.03997% | -0.2174% | 0.2521% | -1.027% | -0.264% | -0.151% | -0.6529% | -1.322% | -0.4833% | 1.431% | -0.2472% | -0.7426% | -0.3504% | -0.2472% | 0.2338% | -0.5847% | -0.9497% | 0.7232% | 0.3642% | -1.797% | -0.009692% | 0.7157% | 1.464% | 2.946% | 3.049% |  |  | -6.566% | -2.344% | -2.222% |  | 0.3451% | -1.998% | 1.063% | -2.198% | 0.3679% | 0.4493% | 1.359% | 1.174% | 1.196% | 2.002% | 1.995% | 2.564% | 1.468% | 3.157% | 6.199% | 5.925% | 5.476% | 4.388% | -1.566% | -1.108% | -0.2109% | -0.8456% | -1.865% | -1.885% | 1.195% | -0.6497% | -1.22% | -1.339% | 0.6672% | -0.8395% | -1.948% | -0.6237% | 0.115% |  | -0.2193% | -1.37% | -1.576% | -2.278% | -1.465% |  |  | 3.155% | 3.067% | 2.501% | -2.953% | -2.673%
2025-06-10 | -0.1719% | 2.086% | 2.422% | 2.123% | 1.502% | 2.332% | 1.832% | 2.228% | 1.327% | 1.92% | -1.128% | 0.331% | 1.88% | 0.9632% | 1.776% | 1.338% | 1.095% | 0.6645% | -0.2809% | 0.05256% | 1.616% | 1.957% | 0.9504% | -1.936% | 1.213% | -0.02439% | -0.5246% | -0.7382% | 0.4229% | -1.183% | -1.121% | -1.411% | -0.3655% | -2.211% | -0.857% | 0.8874% | 0.5116% | -2.066% | -0.2665% | 1.109% | -0.9474% | 1.748% | 1.401% | -0.996% | 1.026% | 1.199% | 0.8606% | -0.6139% | -0.06056% | -1.515% | 1.081% | 0.8729% | 2.739% | 1.077% | 0.4309% | 0.9355% | -2.115% | -0.5722% | 0.8675% | 0.5464% | 0.734% | 1.353% | 0.9771% | 0.8807% | 1.085% | 0.3796% | 0.2514% | -2.179% | -1.448% | 0.1851% | 0.727% | 0.2963% | 1.102% | 1.165% | 0.6761% | -1.065% | 0.8613% | -0.7737% | -1.017% | -0.2745% | 0.4352% | 0.8243% | -0.3846% | 0.8799% | 0.6575% | 0.9841% | 1.22% | 0.463% | -0.2943% | -1.295% | -1.428% | -0.3322% | 0.2546% | -0.4958% | 0.744% | -1.378% | -1.663% | 0.7757% | -1.114% | 0.1226% | -2.656% | -0.07891% | 1.721% | -0.4124% | -1.43% | 1.345% | 0.1203% | 0.242% | 1.783% | -1.739% | 1.374% | -1.807% | -1.245% | 0.2685% | 1.054% | 2.936% | -1.552% | 0.8737% | -0.08971% | 0.9146% | 1.38% | -1.986% | -1.739% | 2.019% | 1.985% | 1.948% | -1.503% | 0.5186% | 2.115% | 0.9231% | 1.136% | 1.617% | -0.5246% | -0.6284% | 1.06% | 0.2036% | 0.9949% | -0.03635% | 0.7865% | 0.0531% | 0.2578% | -1.807% | -0.02333% | -0.2681% | 0.9563% | 1.04% | -0.0928% | 1.479% | -0.0757% | 0.6618% | 1.579% | 0.9632% | -0.1885% | -0.329% | 1.033% | -1.01% | -0.9613% | -0.6139% | -1.55% | -1.754% | 1.252% | -0.8476% | 1.127% | -0.003676% | -0.2285% | -1.374% | -0.5666% | -0.3097% | -1.094% | -1.529% | -1.353% | -1.798% | 0.6334% | -2.392% | -0.6158% | -0.9882% | -0.5385% | -1.269% | -0.2847% | -0.7422% | -0.4904% | 0.1837% | -0.4159% | -1.576% | -0.9509% | 3.126% | -1.846% | -2.223% | -1.691% | -0.7758% | 0.909% | 0.2836% | -2.105% | -1.698% | 0.9863% | 1.724% | -0.8153% | -0.8476% |  |  | -6.125% | -1.465% | -1.689% |  | 0.2701% | -1.962% | 1.047% | -0.3638% | 0.6228% | 0.8729% | 1.554% | -0.7111% | 1.38% | 0.7895% | -2.094% | 0.3588% | 0.9355% | 0.2438% | 4.182% | 4.182% | 5.399% | 0.1479% | -1.753% | -1.586% | 1.794% | 0.4784% | -0.1014% | -1.871% | -0.214% | 0.3347% | 0.2623% | -1.121% | -1.138% | -1.956% | -0.6835% | -0.4756% | -0.2335% |  | -1.332% | -2.106% | -0.1241% | -0.4756% | -1.426% |  |  | 1.78% | 1.983% | -18.02% | -0.7988% | -1.735%
2025-06-11 | -0.6871% | 1.649% | -2.17% | 1.655% | 0.9793% | 0.553% | 1.396% | 0.701% | 0.8706% | 1.488% | 1.441% | -0.03885% | 1.507% | 3.964% | 1.581% | 1.189% | 1.078% | 0.8786% | 1.375% | 1.573% | 2.07% | 2.144% | -0.9671% | 0.692% | 0.1939% | 1.416% | 0.9861% | 0.7314% | 1.442% | 1.027% | 1.646% | 0.2382% | -0.6321% | -0.8846% | -1.237% | 0.1975% | -0.06844% | -1.888% | -0.8083% | 0.4569% | -1.408% | -2.495% | -0.7121% | -1.593% | 0.1461% | 0.516% | 0.2349% | -1.023% | -0.4008% | -1.97% | 0.5974% | 0.4421% | 2.303% | 0.4947% | -0.3251% | -0.09721% | 1.803% | 0.701% | 0.9484% | 0.03431% | 0.2423% | 0.9708% | 0.4716% | 0.9869% | 0.8632% | 0.31% | 1.614% | -1.261% | -0.6825% | -0.4532% | 0.1905% | -0.2164% | 1.877% | -1.593% | 0.03431% | 0.001432% | 0.1658% | 0.07953% | -1.452% | -2.06% | 0.1239% | 0.5012% | -0.8527% | 0.3015% | 0.07213% | 0.4273% | 0.7454% | -1.008% | -0.9045% | -1.77% | -0.4647% | -2.258% | 0.7084% | 1.271% | 0.8478% | -1.556% | -2.362% | 0.5678% | -0.8305% | 1.263% | 0.7602% | 0.02034% | 1.507% | -1.837% | -2.313% | 1.752% | -1.61% | -0.1329% | -0.03145% | -1.537% | -0.8988% | -1.507% | -2.267% | 1.507% | -0.4754% | 2.58% | 0.2702% | 2.04% | -1.288% | 0.2645% | 0.3385% | -1.288% | -1.597% | 0.7084% | 0.3755% | 1.35% | -2.266% | 0.07953% | 1.777% | 0.4223% | 0.5969% | 0.911% | 0.7676% | 2.156% | 0.5658% | -0.2699% | 1.305% | 0.7661% | 2.589% | 2.011% | -0.2773% | -1.759% | 0.4347% | -0.3524% | -0.2164% | 0.3647% | 0.6714% | -0.1444% | 1.054% | -0.7485% | 0.7471% | -0.03145% | 1.751% | 0.1091% | -0.1498% | -0.03145% | 0.2867% | -0.8897% | -1.963% | -1.193% | -1.416% | -1.866% | -2.527% | -1.489% | -2.387% | -1.79% | -1.118% | -2.128% | -1.791% | -0.3608% | -1.647% | -1.503% | -2.261% | -1.812% | -2.128% | -1.866% | -1.567% | -2.016% | -2.148% | -1.866% | 0.925% | -1.217% | -1.11% | -1.654% | 1.636% | -1.463% | -1.503% | 0.652% | -1% | 1.664% | 0.3114% | -0.3695% | -1.739% | -0.2722% | 0.4311% | 1.09% | -1.131% | -0.9906% |  |  | -6.687% | -1.401% | -2.048% |  | 0.1337% | -0.7713% | 0.6122% | -1.186% | 0.06473% | 0.3237% | 1.041% | 0.8342% | 0.8564% | 2.011% | -1.112% | 2.617% | 1.179% | 1.356% | 4.485% | 0.06157% | 0.2355% | 1.953% | -0.2133% | -0.1509% | 1.254% | 0.8169% | -0.5983% | -2.401% | 1.957% | -0.1885% | -2.129% | -2.169% | -2.136% | -1.836% | -1.23% | -0.7423% | -0.9347% |  | 9.315% | -1.319% | 2.426% | -2.228% | -1.951% |  |  | 5.355% | 5.667% | 6.051% | -2.366% | 1.08%
2025-06-12 | -1.585% | 0.7763% | -0.4777% | 0.862% | 0.158% | 1.048% | 0.8862% | 0.9669% | 0.08918% | 0.6238% | -0.5745% | -0.6552% | 0.6118% | -0.1637% | 0.6037% | 0.3051% | 0.09532% | -0.2033% | 0.7167% | 0.5603% | 0.983% | -2.189% | 0.6422% | -0.1441% | 0.4187% | 0.7838% | 0.2549% | 0.4298% | 1.291% | -0.09389% | -0.3521% | 0.1715% | 1.267% | -2.39% | 0.975% | -2.189% | 1.572% | -1.357% | -1.535% | 0.01461% | -0.2114% | -2.003% | -1.349% | -2.229% | -0.6633% | -0.3001% | -0.4752% | -1.543% | -1.197% | -2.591% | -0.2356% | -0.284% | 1.721% | -0.3521% | -0.6018% | 1.025% | 1.276% | 1.378% | 0.07828% | -0.2158% | 1.675% | -0.8048% | -0.2275% | -0.3903% | -0.1772% | -0.9296% | 0.5379% | -2.092% | -1.277% | -1.382% | -0.6714% | -1.123% | 0.9588% | -0.8005% | -0.431% | 0.4513% | 2.151% | 1.322% | 0.09532% | -1.339% | 0.3939% | -0.3324% | 0.7813% | 0.3132% | -1.035% | -0.7117% | 1.645% | 0.8781% | -1.511% | -2.261% | -1.112% | 0.9551% | -0.4131% | -0.8166% | -0.1369% | 0.6764% | -0.6956% | -0.4938% | 0.6037% | 0.515% | -0.4131% | 0.5795% | 0.3939% | -2.164% | -1.686% | 1.411% | -0.5028% | -0.5092% | 1.314% | -0.926% | 0.4858% | -1.429% | -1.772% | 0.3007% | 0.6441% | 1.015% | -0.6462% | 0.4298% | 0.1285% | 0.07917% | 1.911% | -1.113% | -0.9117% | 0.6037% | 1.443% | 1.075% | -1.301% | -0.8086% | 1.061% | -0.5028% | -0.423% | -0.03567% | -0.2741% | 1.192% | 0.5051% | -0.8058% | 0.3544% | 0.3544% | 0.7942% | 0.7732% | -1.675% | -1.444% | 0.3132% | 0.6422% | -1.825% | -0.6987% | -0.2275% | 1.932% | 0.6348% | 1.901% | 0.4932% | 1.257% | 1.994% | 1.12% | -0.2033% | -0.7279% | -0.2921% | 0.06303% | 0.4329% | 0.841% | -1.585% | 0.5145% | -1.657% | -1.005% | -1.396% | -0.05846% | 1.657% | -0.279% | 1.159% | 0.2471% | -0.3719% | -0.5286% | -0.8594% | 0.4038% | -0.2065% | 0.5145% | 1.943% | 0.7512% | -0.649% | 0.9226% | -1.062% | -1.222% | -0.649% | 0.2471% | -0.4593% | -0.4967% | -0.5208% | -0.5913% | 0.9602% | -0.09764% | 1.2% | 0.1472% | -1.077% | 1.567% | 1.094% | 2.024% | 1.176% | -0.1793% |  |  | -8.293% | -1.584% | -1.881% |  | -1.114% | -2.269% | 0.8136% | -2.189% | 0.5957% | -0.8086% | -0.9135% | -0.06609% | 1.314% | 1.096% | -1.325% | 1.064% | -0.3306% | 1.656% | 1.803% | 5.731% | 1.433% | 1.996% | -2.057% | -2.146% | -0.07351% | -0.4454% | -1.987% | -1.444% | 0.8097% | -1.578% | -0.8615% | -1.651% | 1.459% | -1.979% | 0.5386% | -2.298% | -2.405% |  | 7.036% | 0.7204% | 2.056% | -2.298% | 3.134% |  |  | 5.914% | 6.049% | 5.302% | -2.475% | -1.732%
2025-06-13 | -2.53% | -0.03968% | -1.451% | -0.1872% | -0.7014% | 0.1175% | -0.04381% | 0.03684% | -0.902% | -0.6869% | 1.901% | 1.023% | -0.474% | 2.268% | -0.2947% | -0.5367% | -0.7249% | -0.931% | -0.1389% | -0.1968% | 0.3326% | 0.5745% | 1.838% | 1.284% | 1.54% | 0.3243% | 0.01823% | 0.2171% | 1.101% | -0.4441% | 0.009957% | 0.456% | 0.5898% | -2.074% | 0.3236% | -2.25% | 0.9868% | -1.46% | 0.6373% | 2.143% | 0.0458% | -1.039% | 1.13% | 0.1175% | 1.345% | 1.3% | 1.11% | 0.2967% | -1.453% | -1.986% | -0.4919% | -0.07966% | 2.551% | 0.8782% | -1.52% | 0.4082% | 0.3923% | 0.5566% | -0.7548% | 0.5994% | 1.551% | 2.088% | -0.8593% | 1.109% | 2.012% | 0.05132% | 1.16% | -1.901% | -2.087% | 0.7627% | 1.408% | 0.9151% | 2.887% | -2.221% | 0.9419% | -0.4919% | 0.5755% | -0.1693% | -0.1603% | -1.884% | 0.9688% | 1.148% | 0.2967% | 1.722% | 1.041% | 0.8344% | 1.623% | 0.7358% | 0.3505% | -0.3037% | -1.194% | -2.348% | 2.555% | 2.376% | 1.866% | 0.3057% | -0.6173% | 1.345% | 0.4311% | 0.5208% | 0.458% | 0.5476% | 2.062% | -1.397% | -2.236% | 1.256% | -1.065% | -2.314% | 1.471% | -0.9937% | 0.2995% | -2.298% | -2.579% | -0.7229% | 0.6731% | 1.515% | -1.426% | -1.249% | -1.488% | 0.5297% | 1.731% | -2.292% | -2.021% | 0.9599% | 1.578% | -2.507% | -2.383% | -1.729% | 0.5277% | -1.145% | -1.322% | -1.057% | -1.214% | 0.4597% | -0.6105% | -1.313% | 0.4771% | 0.8787% | 0.7154% | -0.6084% | -2.496% | -2.554% | 0.1981% | 0.1671% | -0.8862% | -1.818% | -1.146% | 1.124% | 0.101% | 1.11% | 1.003% | 0.5476% | 1.372% | 0.709% | -0.5457% | -1.334% | -0.03485% | 0.4132% | 0.9652% | 0.7023% | 1.179% | -1.138% | -0.1828% | 1.146% | 0.22% | 1.434% | 0.4395% | 1.791% | 1.328% | -2.421% | -1.02% | -2.456% | -0.7387% | -0.08037% | -1.472% | 1.246% | 1.146% | 0.004458% | -0.02172% | 0.6933% | -1.23% | -0.4084% | 0.1716% | -1.594% | 0.4771% | 0.7839% | 0.4069% | 0.8419% | -2.29% | -1.723% | -0.2131% | 0.1585% | -2.298% | 1.056% | 1.418% | 0.6933% | -1.029% | -1.21% |  |  | -7.378% | -1.702% | -1.931% |  | -0.7262% | -2.221% | 1.928% | -2.221% | 0.458% | 0.2967% | 0.6373% | 0.6373% | 0.2161% | 1.014% | 0.8165% | -0.07966% | 0.7986% | 1.245% | 2.223% | 5.652% | 2.634% | 0.05884% | -0.8964% | -2.106% | 0.6724% | -0.3087% | -2.215% | 0.2581% | 2.298% | 3.856% | -1.806% | -1.774% | -1.837% | -0.2087% | -2.395% | -1.615% | -1.633% |  | -1.156% | -1.975% | 0.232% | -0.532% | -1.819% |  |  | 6.509% | 5.291% | 5.408% | -1.884% | -0.6509%
2025-06-14 | -0.3021% | 1.803% | -2.013% | 2.06% | 0.6001% | 1.49% | 0.7568% | 1.001% | 0.08886% | 0.949% | 2.63% | 2.304% | 0.6753% | 3.163% | 0.7568% | 0.431% | -0.2207% | -0.3021% | -0.1517% | 0.07383% | 1.001% | 1.327% | 2.329% | 1.291% | 1.427% | 0.4498% | -0.1517% | -0.3021% | 1.291% | -0.5193% | -0.0125% | 0.2771% | 0.2759% | -1.646% | -0.3021% | -2.357% | 0.431% | -2.094% | -0.5465% | 0.8382% | -0.8723% | -1.605% | -0.3021% | -1.524% | -0.3021% | 0.0237% | -0.5277% | -1.361% | 0.08886% | -1.631% | 0.5939% | 0.3495% | 1.363% | -0.3021% | -0.4525% | 2.16% | 0.8563% | 1.083% | -0.3021% | 1.146% | 0.5939% | 1.5% | -0.6279% | -1.192% | -0.2269% | -0.9788% | 0.4498% | -2.257% | -1.035% | -1.524% | -0.7908% | -1.361% | 0.9197% | -0.7094% | 0.8563% | -0.9537% | 0.6391% | -0.3021% | -1.361% | -1.28% | 0.0237% | 0.3495% | -0.9537% | 0.5124% | -0.8723% | -0.6279% | 0.0237% | -0.9537% | -2.013% | -2.746% | -1.24% | 0.07383% | 1.164% | 0.3495% | -0.8089% | -1.442% | -1.931% | 0.1052% | -1.035% | -0.7908% | 1.979% | -1.198% | 0.8382% | -1.605% | -0.2297% | 0.2681% | 2.16% | -0.6105% | 0.5124% | -0.7365% | 0.07383% | -0.4525% | 0.2771% | 0.9287% | -0.1392% | 2.06% | 0.2626% | 1.146% | -0.2297% | 1.49% | 2.793% | -2.112% | -2.329% | 0.3495% | 0.8382% | -2.185% | -2.257% | -1.117% | 0.3495% | -1.026% | -1.054% | -0.678% | -0.9036% | 0.4976% | 0.4506% | -1.298% | 1.971% | 1.515% | 0.7926% | 0.9197% | -1.731% | -1.43% | 1.001% | 1.277% | -2.013% | -0.8284% | -0.7094% | 0.5865% | -0.678% | 0.07383% | 0.7505% | 0.2681% | 2.015% | 0.6753% | -1.28% | -2.013% | -2.338% | -1.361% | 0.7484% | -1.229% | 0.3182% | -2.711% | -0.04788% | -0.7069% | 1.417% | -0.3554% | 0.08942% | 1.27% | 0.7484% | -0.9881% | 1.068% | -1.067% | 1.49% | 1.938% | -2.538% | -0.4872% | 0.5837% | -1.311% | 3.32% | 1.819% | 0.07041% | 1.636% | -1.293% | 3.678% | 0.6787% | 0.6844% | 0.8308% | 0.9099% | -1.146% | 0.6027% | 0.2542% | 0.2542% | -2.052% | 1.078% | 0.1718% | -9.302% | 1.622% | 2.808% |  |  | -7.483% | 0.6558% | -2.352% |  | -0.9233% | -2.176% | 0.2681% | -1.768% | -0.3021% | -0.05775% | 1.083% | 0.431% | 0.9197% | 2.712% | 0.5124% | 1.571% | 0.1323% | 2.16% | 3.918% | 4.308% | 0.7626% | 3.162% | -1.565% | -0.33% | 1.184% | -0.4469% | -0.8284% | -2.858% | -1.397% | 0.07383% | -0.5917% | -2.185% | -1.231% | -1.46% | 1.304% | -0.4954% | -1.322% |  | 1.876% | -1.449% | 1.923% | -2.448% | -0.4703% |  |  | 4.626% | 4.137% | 4.573% | -2.414% | -1.991%
2025-06-15 | -2.167% | -0.1316% | -1.645% | -0.5859% | -0.4239% | 0.02538% | 0.2437% | 0.4729% | -0.3078% | -0.03531% | 2.089% | 1.532% | -0.3676% | 3.724% | -0.5095% | -0.7715% | -1.274% | -0.3349% | -1.351% | -1.149% | -2.038% | -1.121% | 0.6039% | -1.434% | -1.835% | -1.149% | -2.157% | -0.9292% | -1.579% | -0.8321% | -0.8321% | -0.6381% | -2.605% | -4.08% | -1.645% | -2.391% | -1.099% | -2.736% | -1.645% | -1.961% | -2.496% | -1.809% | -1.645% | -1.645% | -1.099% | -2.966% | -0.1417% | -1.645% | -1.387% | -1.576% | -1.645% | -1.295% | -1.9% | -1.317% | -2.157% | -1.9% | -1.599% | -1.317% | -2.86% | -1.802% | -1.208% | -1.601% | -1.306% | -2.419% | 0.9264% | 0.1404% | 1.491% | -1.039% | 0.2437% | -0.4003% | 0.5712% | -0.08378% | 2.492% | 0.3529% | 1.807% | -0.01707% | 1.632% | 0.7677% | -0.3785% | 0.876% | 1.095% | 1.39% | 0.2% | 1.717% | 0.1345% | 0.593% | 1.357% | 0.331% | -0.5968% | -1.459% | -0.06675% | 1.773% | 2.536% | 1.75% | 0.4875% | -0.3676% | -0.9462% | 3.18% | 1.095% | 2.307% | 2.722% | 1.444% | 2.733% | -0.5423% | 0.05086% | 0.3092% | -0.9292% | 1.978% | 0.5384% | 0.05086% | 1.672% | 0.9768% | 2.933% | 2.457% | 3.006% | 3.791% | 1.393% | 4.136% | 3.36% | 3.617% | 4.763% | -0.5313% | -1.802% | 3.562% | 4.294% | 15.58% | -2.736% | -2.474% | -1.667% | -2.346% | -2.308% | -1.935% | -1.824% | -0.1463% | -1.045% | -2.064% | 1.34% | 0.5446% | 0.09044% | -1.612% | -2.671% | -2.157% | -2.671% | -1.21% | -2.736% | -1.149% | -2.736% | -1.98% | -3.034% | -2.228% | -1.925% | -2.18% | -0.2985% | -2.202% | -1.972% | -2.736% | -2.518% | -2.955% | -2.691% | -2.404% | -2.738% | -0.5271% | -1.766% | -2.257% | -2.433% | -0.2666% | -0.5271% | -1.884% | 0.5879% | -1.22% | -1.878% | -2.386% | -0.9712% | -1.326% | -2.649% | 0.5769% | -2.283% | -0.5271% | 0.8149% | -0.8363% | -1.218% | -0.3431% | 0.2948% | 1.927% | -2.666% | -2.689% | -1.464% | -1.994% | 0.6555% | -1.667% | 1.847% | 2.708% | 8.471% | 2.41% | 1.736% | 2.664% | 4.609% | 4.739% |  |  | -6.922% | -0.4263% | -0.06667% |  | 2.042% | -1.667% | 1.99% | -0.1711% | 1.172% | 1.674% | 2.405% | 2.023% | 2.318% | 4.305% | 1.772% | 2.885% | 1.283% | 3.321% | 4.551% | 4.159% | -0.1045% | 1.418% | -1.892% | 0.189% | 3.234% | 3.35% | 3.355% | 1.843% | 3.224% | 2.881% | 2.477% | -1.812% | 1.118% | -0.606% | -1.26% | -1.57% | -1.75% |  | 2.462% | 1.621% | 1.215% | -1.755% | 2.023% |  |  | 3.672% | 2.903% | 4.301% | -1.713% | -0.9122%
2025-06-16 | -1.378% | 0.5918% | -0.06214% | 0.012% | 0.1812% | 0.8358% | 1.083% | 1.141% | 0.06043% | 0.4084% | 3.002% | 2.302% | 0.7699% | 3.64% | 0.8769% | 0.7287% | 0.3085% | -0.2269% | 0.05952% | 0.06713% | 0.7122% | 1.075% | 2.447% | 0.8422% | 1.238% | -0.05454% | -0.5032% | -0.4392% | 0.5419% | -0.8346% | -0.7468% | -1.186% | -1.268% | -2.431% | -0.3669% | -1.743% | -1.668% | -2.443% | 0.704% | 0.1603% | 0.9428% | -1.067% | -0.5811% | -1.751% | -0.5976% | -0.2681% | -0.967% | -0.2022% | -1.671% | -2.257% | -0.3999% | -0.8035% | 0.5786% | -0.8786% | -1.689% | -0.02187% | 0.1758% | 0.4815% | -1.025% | 0.2857% | 0.1438% | 0.8541% | -0.5893% | 1.123% | 0.8427% | 0.1204% | 1.185% | -1.286% | 0.3415% | -0.0539% | 0.5804% | 0.06966% | 2.557% | 0.6875% | 1.809% | -0.01455% | 1.926% | 0.9099% | -0.2351% | 0.6222% | 1.355% | 1.709% | 0.3992% | 1.8% | 0.358% | 0.5392% | 1.248% | 0.3415% | -0.7376% | -1.322% | -0.2717% | 0.7515% | 2.384% | 1.857% | 0.1978% | -0.08685% | -0.5564% | 2.121% | 0.671% | 1.066% | 3.414% | 0.8687% | 2.178% | -0.04567% | 1.589% | 1.997% | 2.373% | 0.4421% | 1.832% | 0.6957% | 1.132% | -0.3435% | 1.428% | 0.7689% | 1.594% | 2.187% | -0.1613% | 0.703% | 0.2271% | 1.536% | 2.846% | -1.589% | -1.215% | 1.462% | 2.286% | 2.138% | -3.028% | -3.604% | -4.005% | -3.229% | -3.301% | -2.701% | -2.845% | -2.947% | -3.871% | -2.995% | -3.025% | -3.11% | -3.443% | -4.749% | -3.902% | -4.381% | -2.962% | -2.974% | -4.272% | -2.746% | -2.748% | -3.127% | -3.355% | -3.507% | -3.583% | -3.456% | -3.493% | -3.456% | -3.085% | -3.728% | -4.131% | -3.456% | 1.032% | -0.851% | 0.4107% | -2.076% | -0.3594% | -0.9223% | 0.9735% | -0.1702% | -0.1762% | 0.8254% | 2.423% | -1.898% | -0.1222% | -2.066% | 0.3219% | 0.8936% | -0.003979% | 0.08211% | 1.273% | -0.7593% | 2.588% | 2.34% | -0.303% | 1.188% | -1.648% | 2.053% | 0.689% | 0.7292% | 1.637% | 1.637% | 2.205% | 0.06609% | 1.632% | 0.7319% | 0.05712% | 1.782% | 1.782% | 2.098% | 3.433% | 4.089% |  |  | -4.521% | -2.294% | -0.001811% |  | 0.4323% | -2.542% | 1.371% | -1.454% | 1.124% | 1.116% | 1.981% | 1.816% | 2.154% | 3.151% | 1.66% | 2.31% | 1.186% | 3.222% | 7.263% | 5.391% | 3.536% | 3.973% | -1.401% | -0.6224% | 1.492% | 1.172% | 0.2496% | -0.1306% | 2.449% | 0.4853% | 0.6078% | -1.735% | -2.333% | -1.851% | -1.65% | -2.585% | -0.2039% |  | -1.608% | -2.079% | 0.889% | -1.91% | -2.504% |  |  | 4.984% | 3.766% | 3.988% | -1.222% | 0.3966%
2025-06-17 | -0.8125% | 1.614% | 2.006% | 2.325% | 0.5914% | 1.287% | 1.11% | 1.429% | 0.5971% | 1.186% | 2.855% | 2.242% | 0.8862% | 3.794% | 0.5561% | -0.6937% | -0.1749% | -0.5522% | -0.9648% | -0.4207% | 0.8037% | 0.7093% | 2.659% | 1.016% | 1.103% | -0.4207% | -0.9104% | -0.5142% | -0.2312% | -1.227% | -0.2836% | -0.5666% | -0.3411% | -1.729% | -0.8705% | -0.3181% | -0.4697% | -2.509% | -0.6111% | 1.087% | -1.507% | -2.356% | -0.505% | -1.425% | -0.1985% | 0.167% | -0.3663% | -1.224% | -0.7158% | -2.221% | 0.2967% | -0.04522% | 1.655% | -0.1264% | -0.4207% | 1.791% | 1.163% | 1.004% | -0.6924% | 0.1251% | 0.5679% | 1.209% | 0.4382% | 6.943% | 0.1888% | -0.5513% | 0.5588% | -2.086% | -0.7762% | -1.012% | -0.3871% | -1.047% | 1.511% | -1.708% | 0.5128% | -1.541% | 0.5548% | -0.5168% | -1.672% | 0.2323% | -0.1631% | 0.2495% | -0.9766% | 0.2849% | -1.212% | -0.6465% | 0.06089% | -0.6819% | -1.884% | -2.285% | -1.542% | -0.5839% | 1.228% | 0.6386% | -0.4199% | -1.543% | -1.767% | 0.7447% | 0.001942% | 0.226% | 2.56% | -0.1985% | 1.075% | -1.613% | 1.037% | 0.2495% | 2.745% | -0.05485% | 1.11% | -0.7762% | -0.3663% | -2.173% | -0.2312% | 0.009802% | 0.45% | 1.417% | -0.8342% | -0.9543% | -1.133% | -0.116% | 1.994% | -2.118% | -1.07% | 0.4382% | 0.9687% | -0.598% | -0.7762% | -1.413% | 0.953% | -0.6714% | -0.9866% | -0.8886% | -0.8886% | 1.054% | -0.72% | -0.8741% | 2.428% | 0.876% | 1.876% | -1.672% | -2.162% | -2.695% | 0.9805% | 1.364% | -0.4932% | -1.944% | -0.6937% | 0.63% | -0.6928% | 0.167% | 0.8744% | 0.1316% | 1.288% | 0.5089% | -0.9177% | -1.696% | -1.46% | -1.142% | -0.6264% | -2.343% | -1.249% | -0.6741% | -0.9947% | -2.256% | 0.9449% | -1.385% | -1.652% | -0.539% | 0.5421% | -1.442% | -1.911% | -1.671% | -1.111% | -0.9154% | 0.203% | -0.8649% | -0.1852% | -2.01% | 1.04% | 0.7687% | -1.964% | -0.645% | -2.298% | 3.457% | -0.1916% | -0.2528% | 0.5383% | 0.6528% | 0.3437% | -2.085% | 0.04133% | -0.9126% | 0.2321% | 0.6852% | 0.399% | 1.019% | 2.092% | 3.13% |  |  | -3.863% | -0.6099% | -1.992% |  | 0.6124% | -1.943% | -0.3164% | -1.083% | -0.1867% | -0.03343% | 1.275% | 0.6504% | 1.429% | 1.641% | 0.5796% | 1.57% | 0.932% | 3.08% | 6.434% | 5.87% | 3.779% | 4.799% | -1.429% | -1.874% | 0.914% | 0.2718% | -2.706% | -2.184% | 1.989% | 0.722% | -0.116% | -2.118% | -2.041% | -1.997% | -1.796% | -2.136% | -2.32% |  | 2.554% | -1.21% | 4.93% | -2.136% | -2.041% |  |  | 5.127% | 5.465% | 4.689% | -2.041% | -1.465%
2025-06-18 | -1.523% | 0.3402% | 0.7891% | 0.5117% | 0.8966% | 0.7317% | 1.976% | 1.947% | 0.6154% | 1.258% | 3.86% | 3.315% | 1.162% | 3.887% | 1.526% | -3.067% | 1.086% | 1.181% | 1.621% | 1.78% | 2.09% | 2.014% | 1.347% | 2.212% | 2.91% | 1.515% | 0.7288% | 0.8933% | 2.101% | 3.377% | 3.887% | 2.518% | -5.205% | -15.13% | -5.65% | -4.626% | -5.65% | -5.44% | -4.215% | -4.751% | -6.186% | -4.98% | -6.138% | -4.856% | -3.918% | -5.181% | -4.517% | -4.655% | -5.015% | -4.703% | -4.358% | -4.751% | -4.388% | -4.541% | -4.509% | -4.363% | -3.061% | -4.014% | -4.448% | -3.971% | -4.043% | -5.07% | -4.215% | 0.4776% | -0.03076% | -0.7991% | 0.243% | -2.371% | -0.1007% | -0.1007% | 0.5021% | -0.02414% | 2.865% | -1.239% | 1.548% | 0.1279% | 1.837% | 1.191% | 0.9901% | 1.435% | -2.311% | -0.3973% | 0.7509% | 2.435% | 1.21% | 1.181% | 1.44% | 0.5882% | -0.7609% | -1.507% | -1.718% | -0.5783% | 2.397% | 2.148% | -1.182% | 0.4543% | -0.1007% | 1.966% | 0.6456% | 1.191% | 3.631% | 0.9518% | 2.521% | 0.1385% | 0.9273% | 1.057% | 3.521% | -0.06175% | 1.535% | 0.1619% | 0.2519% | -1.877% | -0.9607% | -0.2548% | 1.555% | 1.746% | -1.592% | -0.1443% | -0.3356% | 0.8178% | 1.631% | -2.534% | -2.211% | 0.6839% | 1.545% | 0.9529% | 0.2725% | 0.5595% | 1.948% | 0.6382% | 0.8789% | 1.1% | 1.709% | 0.4743% | -1.583% | 1.552% | 4.437% | 3.267% | 3.738% | -2.368% | 0.2695% | -1.073% | 1.87% | 2.601% | -1.584% | 0.1282% | 1.248% | 2.332% | 0.6581% | 1.541% | 1.232% | 0.7796% | 1.523% | 1.067% | -0.1581% | -0.5217% | -0.04327% | -0.1677% | 0.7346% | 1.751% | 3.038% | 0.5604% | 2.186% | 1.532% | -1.083% | 1.814% | 1.741% | 1.076% | 0.6378% | -0.4894% | 1.926% | -0.6566% | 2.436% | 2.335% | 1.326% | 3.647% | 4.025% | 2.467% | 2.367% | 1.412% | 2.338% | 1.154% | 1.171% | 2.279% | 0.3103% | 1.412% | 4.174% | 4.629% | 3.487% | 2.007% | 0.6281% | -1.065% | -2.168% | 0.4636% | 0.7926% | -1.007% | 2.418% | 2.834% |  |  | -7.689% | -0.1492% | -1.94% |  | -1.909% | -2.215% | 0.6552% | -7.037% | 0.3586% | 1.076% | 1.335% | 1.287% | 1.363% | -2.215% | 0.7891% | 1.65% | 0.0003133% | 1.565% | 3.078% | 3.078% | 2.907% | 3.147% | -1.574% | -2.8% | 0.5603% | -0.9267% | -1.55% | -2.071% | 0.992% | -0.2692% | -1.411% | -1.684% | 0.34% | -2.772% | -2.637% | -0.2224% | -2.459% |  | -0.3592% | -2.032% | 4.728% | 0.4466% | -2.637% |  |  | 3.04% | 4.008% | 4.829% | -2.637% | -1.394%
2025-06-19 | 0.2984% | -0.2086% | 0.219% | 0.1531% | -0.7766% | -0.2864% | 0.1201% | 0.1201% | -0.8366% | -0.1405% | 0.999% | 1.417% | -0.2095% | 2.39% | -0.02271% | -2.769% | -0.4402% | -0.8467% | -0.8171% | -0.5433% | 0.2959% | 0.197% | -2.318% | 0.3923% | 0.8461% | -0.4622% | -1.091% | -0.8089% | 0.0603% | 0.05053% | -0.4768% | 0.3923% | 1.308% | -2.401% | 0.2739% | 1.428% | 0.05419% | -2.703% | -1.616% | 0.4717% | -0.9566% | -1.857% | -0.7588% | 0.3618% | -0.572% | -0.08863% | -0.8577% | -0.9895% | -1.765% | -0.3303% | -0.7039% | -1.001% | 0.6072% | -0.6135% | -1.75% | -0.05689% | 0.3337% | 0.4717% | -0.6917% | 0.5974% | 0.1641% | 1.565% | -1.099% | 6.914% | -0.7461% | -1.344% | -0.6346% | -2.906% | -0.8797% | -1.286% | -0.8247% | -1.506% | 1.252% | -0.3743% | 1.994% | -0.3889% | 1.789% | 0.4277% | -1.033% | 0.4607% | -0.0007381% | 0.4058% | -1.033% | 0.3398% | -1.44% | -0.9016% | -0.4182% | -1.143% | -2.451% | -0.9016% | -2.144% | -1.75% | 0.8892% | 0.4387% | -1.737% | -1.187% | -1.11% | 0.7244% | 0.208% | -0.0337% | 2.054% | -0.1545% | 1.01% | -1.473% | 0.4119% | -0.1655% | 4.035% | -0.761% | 0.186% | -1.239% | -1.355% | -2.541% | -0.3694% | -0.5159% | 0.09814% | 0.5156% | -1.252% | -2.225% | -1.854% | -1.374% | 0.5706% | -2.244% | -1.268% | -0.7808% | 0.09814% | -0.1741% | -1.022% | -0.5501% | 1.496% | 0.363% | 0.2984% | 0.3897% | 0.3694% | 2.342% | 3.572% | 0.5048% | 4.392% | 2.854% | 4.268% | -2.055% | -0.736% | -0.9388% | 2.713% | 3.31% | -1.286% | -1.527% | 1.197% | 2.522% | 0.5925% | 1.485% | 1.81% | 0.6255% | 1.476% | 0.8123% | -0.4292% | -0.8577% | 0.219% | -0.5281% | 1.491% | -0.3755% | 0.9998% | -1.642% | 0.8122% | 0.3578% | 1.76% | -0.08308% | -0.1533% | 0.7726% | 2.391% | -2.622% | -0.3497% | -2.675% | 0.3578% | 0.2583% | 3.163% | 1.502% | 2.191% | 0.2912% | 3.212% | 3.091% | 0.351% | 1.405% | 0.1899% | 1.336% | 1.951% | 2.234% | 2.701% | 2.989% | 1.368% | -0.3157% | -1.953% | -1.209% | -0.9867% | -1.642% | -1.364% | -1.542% | 0.6023% | 0.9245% |  |  | -5.753% | -0.8793% | -2.328% |  | -1.522% | -2.308% | -1.824% | -9.933% | -1.956% | -1.715% | -0.5501% | -0.9895% | -0.3193% | 0.6255% | -0.6819% | 0.197% | -0.5745% | 1.476% | 5.382% | 6.196% | 5.857% | 3.451% | -1.345% | -1.869% | -1.501% | -2.01% | -2.48% | -0.807% | -0.7311% | -0.7461% | 0.1189% | -1.17% | 1.427% | -2.061% | 1.438% | -2.472% | 1.158% |  | 0.6721% | -1.76% | 2.275% | -1.112% | 0.5151% |  |  | 3.543% | 3.749% | 4.804% | 0.4239% | -0.943%
2025-06-20 | 0.8219% | 2.768% | 3.303% | 2.804% | -0.5401% | 2.824% | 2.862% | 2.958% | -37.27% | 2.776% | 4.893% | 4.222% | 2.402% | 4.938% | 2.574% | -1.961% | 2.019% | 1.54% | 3.068% | 2.714% | 2.747% | 3.073% | 0.2735% | 3.628% | 3.758% | 2.927% | 2.325% | 2.555% | 4.429% | -1.09% | 0.2388% | -26.08% | 4.336% | -33.93% | 3.168% | 4.465% | 3.59% | 0.6582% | 2.191% | 3.667% | 2.134% | 0.1409% | 2.824% | 1.808% | 2.728% | 2.862% | -21.47% | 1.329% | 1.654% | -28.07% | 2.421% | 2.536% | 4.105% | 2.657% | 1.494% | 3.577% | 3.407% | 3.341% | 2.266% | 4.31% | 3.207% | 5.304% | 2.268% | 11.46% | 1.636% | 1.034% | 4.183% | 3.652% | 0.8307% | 0.6391% | 1.271% | 0.3517% | 3.686% | 1.961% | 3.714% | 2.146% | 3.543% | 2.191% | 1.041% | 3.404% | 2.345% | -9.153% | 1.176% | 2.402% | 0.5241% | 1.156% | 0.08338% | 1.061% | -0.6831% | -2.523% | -0.001698% | 0.6627% | 1.636% | 1.808% | 3.39% | -100% | -100% | 2.709% | 2.095% | 0.1217% | 4.778% | -0.3382% | 3.303% | 0.6008% | 3.935% | -100% | -100% | 2.873% | 2.766% | 2.692% | 2.838% | 4.183% | 2.436% | 1.653% | 1.559% | 2.958% | -2.433% | 2.027% | 2.487% | 1.712% | 3.705% | -9.385% | -11.6% | 2.555% | 3.533% | 2.078% | 4.242% | 1.386% | -3.185% | -24.37% | 2.52% | 2.308% | 2.378% | 4.771% | 6.064% | 3.023% | 6.529% | 4.49% | 6.234% | 5.2% | 4.183% | 2.148% | 3.111% | 4.059% | -0.2232% | -0.8939% | 3.303% | 4.499% | 2.856% | 3.015% | 2.997% | -11.07% | 4.463% | 3.82% | 1.789% | 1.041% | 3.379% | 2.23% | 4.438% | 2.868% | 4.513% | 1.337% | -18.93% | -9.733% | 4.995% | 3.609% | -12.23% | -22.31% | -31.01% | -1.507% | 2.995% | -1.917% | -25.13% | -28.37% | 3.032% | 1.57% | 4.38% | 2.539% | 6.012% | 5.794% | -24.15% | -23.39% | 2.722% | 8.93% | 4.669% | 4.772% | 3.87% | 3.349% | -16.56% | -40.81% | 1.24% | -0.1165% | 1.356% | -0.5816% | 1.201% | -24.22% | 2.883% | 4.341% |  |  | -6.778% | -0.2818% | 0.964% |  | 1.241% | -2.274% | -0.1657% | -0.5298% | 1.041% | 2.21% | 2.555% | -1.89% | 2.479% | 3.858% | 1.482% | -23.16% | 2.027% | 4.344% | 12.98% | 9.52% | 8.928% | 10.76% | -2.154% | 0.2771% | -1.161% | 1.738% | 0.8042% | 0.008207% | 0.1639% | 2.148% | 1.21% | 0.06848% | 3.955% | -1.274% | 4.154% | 2.21% | -2.14% |  | 2.963% | 0.6859% | 2.325% | -2.919% | -2.684% |  |  | 4.357% | 0.8418% | 4.678% | -2.246% | 0.7557%
2025-06-21 | 1.504% | 0.8493% | 1.119% | 0.7023% | 2.989% | 1.119% | 0.1726% | 1.421% | -1.564% | 2.659% | 0.3618% | 2.254% | 2.386% | 1.643% | 2.377% | -2.041% | 1.658% | 1.346% | 1.915% | 1.923% | 0.9483% | 0.3618% | -0.07621% | 2.613% | 0.5001% | 1.976% | 1.268% | 1.074% | 2.47% | -1.961% | -2.381% | -7.426% | 1.669% | -2.109% | 0.7875% | 1.565% | 0.2294% | -0.9246% | 1.44% | 2.764% | 0.2483% | -0.8395% | 1.573% | 0.2483% | 2.055% | -1.152% | -2.277% | 0.7591% | 1.732% | 2.095% | -0.5841% | 2.84% | 4.32% | 2.655% | -0.03256% | -0.7838% | 2.479% | 2.197% | 0.3429% | 1.453% | 1.61% | 2.376% | 0.3618% | 5.774% | 1.373% | 1.53% | 0.9366% | 1.557% | 0.07804% | 1.308% | 1.024% | 1.346% | 2.585% | 0.3618% | 2.563% | 0.9819% | 2.966% | 2.329% | 2.509% | -7.795% | 0.9294% | 0.3429% | 2.594% | 1.781% | 2.064% | 1.308% | 1.592% | 1.308% | 0.551% | 0.2483% | -0.02033% | 1.085% | 0.6456% | 1.771% | 1.982% | -2.079% | -2.287% | -1.208% | -2.476% | -2.599% | -0.7827% | -2.003% | -2.23% | -1.814% | -1.541% | -12.22% | -10.96% | -2.491% | -2.722% | -1.658% | -0.9843% | -0.5477% | -2.163% | -2.432% | -1.417% | -1.426% | -2.322% | -2.55% | -1.709% | -1.908% | -2.116% | -9.091% | -9.024% | -1.908% | -2.495% | -0.6997% | 0.3618% | -0.2057% | -1.877% | -2.373% | 0.273% | -1.945% | 0.1333% | 2.242% | 0.5824% | 0.1939% | 1.907% | 1.174% | 2.068% | -2.003% | -0.5215% | -1.238% | 1.875% | 1.434% | -1.161% | -2.119% | 0.5605% | 1.705% | -1.368% | 0.6398% | 0.9279% | -0.6598% | -0.3382% | -1.35% | -2.192% | -2.183% | -2.05% | -0.9246% | 0.45% | 1.808% | -0.4217% | -0.5067% | -0.8043% | 1.347% | 1.118% | 1.851% | 0.9187% | 0.7433% | 0.5552% | 1.355% | 0.1056% | 1.419% | -12.75% | -1.915% | 1.194% | 0.5456% | 1.12% | 1.502% | 2.129% | 0.9283% | -2.067% | 1.1% | 1.866% | -1.639% | -0.389% | 0.6838% | -0.721% | 1.318% | -0.721% | -1.979% | 0.5456% | 0.7752% | -0.3154% | 1.741% | 1.311% | 0.5456% | -0.4684% | -0.124% |  |  | -6.688% | -2.306% | -1.169% |  | 2.578% | 0.00237% | -2.476% | -1.246% | 1.8% | 0.9577% | 0.3618% | -0.3003% | 1.308% | -1.341% | -1.53% | -2.098% | 2.033% | 0.9819% | 1.906% | 1.906% | 4.112% | 6.249% | -1.758% | 0.7291% | -0.02033% | 1.84% | 1.146% | 0.8406% | -0.02033% | 2.115% | 1.226% | 0.3597% | -1.782% | -1.509% | -1.684% | -2.359% | -1.17% |  | -0.6345% | -2.178% | 0.7727% | -2.207% | -1.782% |  |  | 4.508% | -0.04487% | 4.508% | -2.665% | -2.253%
2025-06-22 | 0.4948% | 0.2988% | -0.1021% | 0.3492% | -0.2811% | 0.9508% | 0.6854% | 1.305% | 1.075% | 1.075% | -0.2879% | 1.482% | -1.323% | 0.9588% | 1.128% | -2.677% | 0.3315% | 1.968% | 1.761% | 0.5356% | 0.243% | 0.4199% | 0.2008% | 0.6657% | 0.5356% | 1.189% | 0.7561% | 1.059% | 2.081% | -2.559% | -1.261% | -5.783% | 1.215% | -2.599% | 1.818% | 1.162% | 2.119% | 0.4907% | 1.844% | 1.482% | 0.06604% | 0.473% | 0.3315% | -0.8187% | 1.57% | -0.1109% | -1.914% | 0.9508% | -0.9468% | -6.281% | 1.924% | 1.791% | 2.317% | 1.452% | 0.9032% | 0.5084% | -0.0421% | 0.1545% | -0.1207% | 1.452% | 0.6854% | 1.953% | 1.49% | 3.675% | 0.3723% | 0.5356% | 1.769% | -0.7466% | 0.1545% | 0.5173% | 0.7738% | 0.3315% | -0.8187% | 1.314% | -0.1207% | 0.823% | 1.004% | 1.34% | 1.101% | 2.226% | 0.06604% | -0.1021% | 0.4553% | 1.712% | 1.836% | 1.402% | 1.199% | 1.19% | -0.5621% | -1.332% | -0.6496% | -2.078% | 0.06604% | -0.2613% | 0.186% | 0.7738% | 0.1634% | -0.2879% | 1.402% | 1.145% | 0.4199% | 1.163% | 0.3315% | -0.7568% | 0.8387% | 0.4642% | -3.896% | 0.1429% | 1.446% | -0.1994% | -0.2076% | -6.08% | -0.2308% | 0.4455% | 1.641% | 0.9773% | -2.473% | -1.827% | -1.112% | -0.7125% | 1.349% | -6.695% | -8.662% | 0.2607% | 1.128% | 0.2803% | 1.11% | 0.8535% | -2.401% | -0.4982% | 0.4131% | -1.914% | 1.369% | 1.441% | 0.6869% | 1.678% | 1.678% | 1.1% | 0.2253% | -2.588% | 0.748% | -0.8854% | 0.1545% | 0.7806% | 0.5084% | -6.186% | -0.8187% | 0.4762% | 0.9685% | 0.6336% | 0.699% | 1.508% | 1.279% | 0.3403% | 0.4111% | -0.1286% | 0.4288% | 1.084% | 1.087% | 1.364% | 0.2984% | -0.497% | -0.2822% | 0.4177% | -0.497% | 1.905% | -0.3359% | -0.3379% | -1.392% | -0.9723% | -1.075% | -0.749% | 0.6961% | -1.032% | 0.8552% | -1.481% | 0.192% | 0.8631% | 1.81% | 1.794% | -1.015% | -0.6402% | 1.07% | 1.364% | 1.059% | 1.134% | -0.3538% | 0.5052% | 1.029% | -5.673% | -2.466% | -0.5865% | 0.4873% | -1.481% | -1.911% | -0.02274% | 0.4408% | 0.6036% |  |  | -6.297% | -0.5935% | -0.3922% |  | -2.125% | -0.8187% | -1.827% | -0.7568% | -1.615% | -2.137% | -0.6772% | -0.7833% | -0.1021% | -0.9514% | -0.1552% | -1.845% | -0.1443% | 2.105% | 2.617% | 1.559% | 2.811% | 1.897% | -0.9742% | -1.38% | -2.34% | -1.709% | -2.127% | -1.204% | -1.856% | -1.016% | -2.213% | -1.729% | 1.054% | -1.537% | 1.256% | -0.04627% | 0.9824% |  | 0.3025% | 0.6303% | -1.042% | -1.991% | -1.708% |  |  | 2.687% | 1.916% | 3.453% | -1.708% | 0.9757%
2025-06-23 | 2.687% | 1.378% | 1.965% | 1.454% | 0.9739% | 1.538% | 1.402% | 1.454% | -6.758% | 1.4% | 2.278% | 2.82% | 2.288% | 1.34% | 0.9434% | 0.9017% | 0.6619% | 4.071% | 0.6082% | 0.4542% | 1.048% | 1.34% | 0.6756% | 1.896% | 1.782% | 0.8873% | 1.927% | 0.8392% | 1.738% | 1.126% | 2.776% | -6.399% | 2.332% | 2.512% | 1.173% | -0.2558% | 1.83% | 3.321% | 2.299% | 1.955% | 0.3387% | 3.206% | 4.165% | 3.696% | 1.694% | 2.111% | -8.477% | -0.005317% | 1.089% | -8.819% | 1.089% | 1.444% | 1.015% | 1.145% | -0.4793% | 1.942% | 1.896% | 1.121% | 0.7743% | 2.35% | 1.767% | 0.5824% | 1.486% | 3.553% | 1.272% | 1.763% | 0.4735% | -0.09434% | 1.757% | 1.559% | 1.694% | 0.8288% | 0.1928% | 0.1928% | 0.08852% | 1.803% | -0.09683% | 2.476% | 1.444% | 3.159% | 2.236% | 0.7036% | 1.548% | 3.112% | 1.194% | 1.454% | 1.642% | 1.006% | -0.3181% | -1.402% | 0.07851% | -2.125% | -0.4328% | -0.12% | -0.7456% | -0.1096% | -22.33% | 2.716% | -0.3285% | 0.08852% | 1.131% | -0.12% | -0.8498% | -1.309% | 0.08852% | -0.8498% | 0.08852% | 0.5266% | -0.8498% | -1.858% | 0.589% | 1.32% | -0.8382% | -1.672% | -0.8498% | 0.5056% | -9.941% | 1.015% | -1.858% | 1.705% | -0.3285% | -3.656% | -5.833% | -0.8498% | 0.8183% | 0.9226% | -1.986% | 0.516% | 0.08852% | -3.062% | -0.9701% | -1.904% | 0.5216% | -2.186% | -0.7208% | 0.3207% | -15.35% | 0.1552% | -0.9124% | -2.622% | 0.05002% | -1.798% | 0.3387% | 0.281% | -1.309% | 0.4735% | 0.6098% | -0.3664% | 2.341% | 2.071% | 0.8584% | 1.256% | 0.1812% | 0.3387% | 1.548% | 0.3179% | 0.6202% | -0.6413% | 1.152% | 0.07655% | 1.179% | -2.897% | -7.266% | -7.378% | -1.68% | 0.6185% | -0.883% | -6.966% | -0.883% | -2.297% | 0.3756% | -1.953% | -0.6487% | -0.7986% | 0.8697% | 0.6038% | -0.7775% | -0.4296% | -0.4987% | 0.2769% | -0.7208% | -2.429% | 0.3823% | 0.2136% | -0.2828% | 0.5417% | -1.71% | 0.3047% | -6.872% | -1.694% | 0.182% | -1.326% | -0.7775% | -0.7037% | 0.8674% | -1.832% | -1.305% | -1.832% |  |  | -6.993% | -9.93% | -1.901% |  | 1.35% | -1.632% | -6.031% | -1.861% | 0.04681% | 0.9017% | 1.861% | 1.767% | -1.892% | 1.559% | 1.923% | -1.892% | 0.08852% | 1.942% | 3.47% | 2.099% | 1.517% | 3.146% | -0.7826% | 0.6687% | 3.341% | 2.044% | 1.195% | 2.475% | 3.361% | 3.226% | 2.934% | 1.256% | 1.832% | -1.486% | 0.5662% | -1.94% | -1.406% |  | 2.508% | -1.101% | 3.039% | -2.732% | -2.451% |  |  | 9.72% | 3.626% | 2.816% | -2.884% | -0.6081%
2025-06-24 | -0.9319% | 1.518% | 2.061% | 0.635% | 0.5312% | 1.492% | 1.446% | 1.939% | 1.269% | 1.917% | 3.213% | 2.986% | -2.398% | 4.721% | 1.727% | 1.666% | 0.8398% | 0.6122% | 0.8112% | 0.7902% | 1.826% | 2.296% | -0.4839% | 2.234% | 2.428% | 1.532% | -1.359% | 0.6569% | 1.756% | -1.918% | -1.884% | -2.181% | 0.1274% | 2.812% | -0.5708% | 0.1375% | -2.671% | -2.004% | -0.1234% | 0.8322% | -0.8742% | -1.223% | 0.5667% | -0.131% | 1.249% | 1.689% | -1.373% | -0.3281% | -0.01962% | -1.352% | 1.007% | 0.9004% | 2.416% | 1.061% | -0.4979% | 1.385% | 1.23% | 1.409% | -0.02394% | 1.351% | 1.105% | 1.919% | 0.8398% | 9.117% | 1.721% | 0.8112% | 1.651% | -1.555% | 0.7184% | 0.5364% | 0.635% | -0.1006% | 2.478% | 0.2634% | 0.5558% | -1.568% | 1.109% | 0.7867% | -0.009614% | 1.259% | 1.81% | 2.129% | 0.6881% | 1.674% | 0.8322% | 1.227% | 0.9914% | 0.8549% | -1.276% | -1.883% | -1.534% | -1.912% | 2.243% | -1.36% | -0.003716% | -0.6011% | -2.323% | 2.22% | -0.2295% | 1.234% | 3.32% | 0.3772% | 1.067% | -0.6466% | 1.216% | -1.602% | 3.583% | -49.43% | 2.015% | 0.785% | 1.304% | 0.4612% | 0.4479% | 1.183% | 2.235% | 1.879% | -2.01% | 0.185% | 0.3064% | 1.204% | 2.584% | -3.765% | -5.919% | 1.462% | -0.7149% | -0.3071% | -0.5481% | -1.989% | 0.1378% | -0.7587% | -1.289% | -2.647% | -0.8969% | -0.6322% | 2.134% | -2.525% | 0.7461% | 1.638% | 0.6647% | 0.0283% | -1.282% | -1.842% | -0.2599% | 0.8882% | -2.664% | -0.8409% | -2.027% | 0.02141% | -1.016% | -1.31% | 0.8462% | -0.3888% | -0.3003% | -0.4722% | -2.247% | -2.088% | -2.732% | -1.155% | 1.786% | -0.05451% | 0.8258% | -1.665% | -1.417% | -1.335% | -0.8718% | 0.5348% | -0.8522% | -0.6468% | -1.213% | -2.315% | 0.6747% | -1.519% | -1.554% | 0.9104% | 0.9213% | 0.398% | 0.5974% | -1.243% | -0.7559% | 2.408% | -1.654% | -0.9331% | -1.758% | 4.555% | 1.312% | 0.5463% | 0.984% | -0.5991% | -1.792% | -0.1743% | 1.111% | 0.4057% | -1.98% | -0.1312% | 0.6204% | -1.742% | 1.536% | -1.059% |  |  | -7.49% | -2.029% | -1.826% |  | -0.9451% | -1.633% | -1.124% | -1.14% | 0.5288% | 0.6881% | 1.31% | 1.325% | 1.151% | -2.239% | 0.4985% | 1.242% | 0.4614% | 0.9535% | 3.735% | -0.1638% | -0.1336% | 1.686% | -0.2484% | -1.604% | 0.7594% | 0.9333% | -0.000864% | -0.3369% | 1.597% | 0.4892% | 0.4277% | -0.4823% | -2.062% | -2.184% | -2.259% | 0.2342% | 0.5545% |  | 3.219% | -1.177% | 5.674% | -1.447% | -2.18% |  |  | 10.11% | 1.337% | 0.9314% | -2.196% | -1.067%
2025-06-25 | -0.5187% | -0.3409% | 2.177% | 2.085% | 1.131% | 1.584% | 1.915% | 0.2589% | 1.034% | 1.256% | 1.099% | 0.9061% | -2.6% | 0.04313% | 1.469% | 1.361% | 0.9369% | 0.49% | 0.2707% | 0.7259% | 1.8% | 1.838% | -0.5259% | 1.933% | 2.141% | 0.8966% | -2.482% | 0.3308% | 0.8171% | -2.662% | -2.368% | -2.916% | 1.505% | -0.1899% | -0.0108% | 0.7089% | 0.8984% | -1.267% | 0.3976% | 2.07% | -0.319% | -1.221% | 0.6672% | -0.1649% | 1.445% | 1.553% | 0.3916% | 0.2049% | 0.3168% | -2.842% | 1.183% | 1.014% | 0.6595% | 1.221% | -1.301% | 0.4883% | 0.276% | 0.1433% | 0.6458% | 0.3102% | 1.731% | 0.6125% | 1.222% | 8.233% | 1.658% | 0.7899% | 2.013% | -1.002% | 1.13% | 0.7289% | 1.13% | 0.1433% | 1.638% | 1.145% | 1.913% | -0.1897% | 2.05% | 1.284% | 0.2204% | 2.063% | 1.784% | 0.2435% | 0.6133% | 1.869% | 0.4438% | 0.9369% | 0.7982% | 0.5902% | -1.544% | -2.345% | -1.111% | -2.098% | 2.486% | -0.5193% | 0.4952% | 0.1202% | 0.4207% | 2.216% | 0.9677% | 1.538% | 1.792% | 0.3899% | 1.33% | 0.2589% | 1.721% | -0.5964% | 2.07% | -2.664% | 0.8676% | 0.5568% | 1.096% | 1.032% | -0.2719% | 0.4198% | 2.031% | -2.361% | -2.361% | -0.1555% | 0.4609% | 1.445% | 1.638% | -3.731% | -6.299% | 1.445% | -0.5887% | 0.4815% | -0.5887% | -0.3498% | -3.169% | -0.8198% | -0.2769% | -1.18% | -0.7748% | 1.144% | 0.7844% | -1.151% | -0.006895% | 1.655% | 0.1763% | -1.976% | -1.721% | -2.432% | 0.4207% | -0.348% | -2.569% | -0.9384% | -1.313% | 0.6736% | -0.2271% | 0.6264% | -0.348% | 0.02772% | 1.81% | 0.09707% | -1.744% | -1.929% | -1.929% | 0.08166% | -0.5889% | -2.467% | -1.992% | -2.233% | -2.47% | -3.094% | -0.1015% | -1.453% | -2.498% | -0.8426% | -1.462% | -1.738% | -1.431% | -1.774% | -2.027% | -0.3985% | -1.764% | -1.672% | -0.737% | -1.072% | -2.221% | 0.1124% | -2.23% | -2.789% | -0.08069% | 1.906% | -0.9708% | -1.722% | -0.2264% | -0.4733% | -0.9521% | -2.489% | -0.3084% | -2.459% | -1.462% | -1.501% | 0.8605% | -1.197% | 0.1701% | 0.5254% |  |  | -6.136% | -2.514% | -0.9837% |  | -0.3218% | -1.983% | -0.7736% | -2.06% | 0.413% | 0.8676% | 1.784% | 1.923% | -0.5964% | -2.03% | 1.515% | -0.6041% | 1.529% | 3.885% | 6.318% | 3.462% | 3.938% | 1.767% | -1.045% | -2.01% | 1.071% | 0.2007% | -1.422% | -1.386% | 1.67% | -0.8175% | 0.04998% | -1.964% | -2.172% | -1.946% | -2.412% | -2.409% | 0.1202% |  | 4.173% | -1.995% | 2.966% | -1.747% | -1.645% |  |  | 8.465% | 1.17% | 3.494% | -1.493% | 1.55%
2025-06-26 | 0.3563% | 1.002% | 2.968% | 2.714% | 1.314% | 2.115% | 1.515% | 1.922% | 1.064% | 1.403% | 2.768% | 2.084% | -0.8379% | 1.66% | 0.5846% | 0.4308% | -0.2074% | -0.6687% | -0.8077% | -0.4954% | 0.723% | 0.9229% | -1.532% | 0.5965% | 0.6331% | -0.5451% | -2.795% | -1.297% | -0.6405% | -1.297% | -2.718% | -1.939% | 0.66% | 2.753% | -0.7533% | -0.2326% | -0.03822% | -2.23% | -0.6918% | 1.092% | -1.176% | -2.099% | -0.5226% | -1.345% | 0.5769% | 1.115% | 0.4201% | -0.6149% | 0.8792% | -2.472% | 1.523% | 1.292% | 0.5897% | 1.034% | -2.149% | 0.5487% | -0.2578% | 1.238% | -0.3193% | 0.7401% | 0.7307% | 1.642% | 0.5307% | 8.819% | 1.158% | 0.1646% | 1.471% | -0.9212% | 0.7845% | 0.2386% | 0.9998% | 0.1924% | 0.1309% | 0.03866% | -0.4423% | -2.035% | 0.494% | 0.03866% | -0.7687% | 0.3208% | 0.7076% | 1.138% | 0.04635% | 1.1% | -0.2458% | 0.5% | 0.6615% | 0.6999% | -1.553% | -2.122% | -0.9071% | -1.943% | 1.976% | 0.9921% | -0.2441% | -0.784% | -0.9916% | 1.546% | -0.3919% | 0.5615% | 0.8152% | -0.8379% | 0.1694% | -1.069% | -0.6063% | -6.082% | 2.039% | -1.407% | 1.023% | -0.5448% | -0.4031% | 0.5195% | -0.1279% | 0.2958% | 1.346% | -2.268% | -1.421% | -2.185% | -1.283% | 0.7383% | 1.984% | -4.249% | -7.502% | 0.3155% | 0.6538% | 0.3163% | -0.8455% | -0.9378% | -2.192% | -1.016% | -1.241% | -1.226% | -0.8929% | 0.8544% | -0.2906% | -1.432% | 0.3626% | 0.5779% | -0.2649% | -0.03053% | -1.532% | -1.979% | 0.5999% | 1.18% | -2.214% | -0.8787% | -1.53% | 0.2085% | -1.737% | -0.3677% | 0.1079% | -1.192% | 0.8494% | -0.8225% | -2.46% | -1.73% | -2.591% | -0.8071% | 0.2812% | -1.157% | -1.08% | -1.577% | -1.772% | -0.8662% | -0.5275% | -1.379% | -1.593% | 0.3019% | -0.4653% | 1.152% | 0.2563% | -0.6096% | -1.737% | 0.1145% | -1.779% | -1.157% | -1.103% | 0.3901% | -1.08% | 1.168% | -0.6208% | -1.744% | -2.504% | 2.354% | 0.3554% | -0.8316% | 0.331% | 0.3384% | -0.01242% | -1.583% | 0.4523% | -0.04539% | 0.009045% | 0.2734% | 0.3123% | -0.6208% | -0.1543% | 1.175% |  |  | -5.809% | -1.243% | -1.171% |  | 1.221% | -1.13% | -0.7071% | -1.461% | 0.03098% | -0.3688% | 2.345% | 1.73% | 0.03866% | -0.8148% | 0.8767% | 1.869% | 1.376% | 3.672% | 5.817% | 4.217% | 4.522% | 2.838% | -1.324% | 0.6762% | 1.241% | 0.9246% | 0.1433% | 0.03689% | 1.204% | 0.9028% | 2.326% | 1.136% | -1.008% | -0.1913% | -1.598% | -0.9415% | -1.22% |  | 4.65% | -1.566% | 4.831% | -2.017% | -1.702% |  |  | 8.201% | 2.854% | 3.912% | -2.236% | 2.654%
2025-06-27 | 3.087% | 3.303% | 3.148% | 4.102% | 4.015% | 3.798% | 2.42% | 3.85% | 0.02928% | 0.6867% | 3.157% | 3.902% | -0.7782% | 0.2328% | 2.854% | 3.244% | 2.368% | 2.238% | 0.1426% | 0.3426% | 1.207% | 1.571% | 0.6466% | 0.2475% | 1.439% | 1.263% | -2.266% | 1.919% | 1.519% | -2.156% | -2.495% | -1.602% | 0.2879% | 0.7641% | -0.9429% | -1.24% | -0.1801% | -2.052% | -0.4142% | 1.649% | -1.134% | -1.784% | -0.2755% | -1.16% | 1.094% | 1.467% | -3.026% | 0.2273% | 1.519% | -2.825% | 1.51% | 1.675% | 0.2475% | 1.218% | -3.026% | 0.2552% | 1.103% | 2.195% | 0.07027% | 0.5942% | 1.189% | 1.54% | 0.5133% | 6.551% | 0.7347% | 1.279% | 1.759% | 0.1266% | -0.1021% | 0.0799% | 0.7127% | 1.562% | 1.042% | 0.808% | 0.5249% | -0.8312% | 0.1473% | 1.484% | 1.233% | 1.039% | 0.8513% | 0.3399% | 1.397% | 1.692% | 1.354% | 0.444% | 0.444% | 0.02789% | 0.09723% | -0.9342% | -0.445% | -1.906% | 1.155% | 1.033% | 1.442% | 1.501% | -33.72% | 1.64% | 1.441% | 1.224% | 0.7647% | 1.683% | 2.386% | -2.252% | 0.5634% | 2.178% | 1.303% | -2.61% | 1.571% | 1.434% | 1.847% | 0.7187% | 0.6096% | 1.765% | -0.1281% | -2.659% | -2.897% | -1.717% | -1.224% | 1.9% | 2.958% | -4.753% | -5.423% | 0.06256% | 0.886% | -1.532% | 0.02789% | -1.099% | -2.372% | -2.226% | -2.53% | -1.514% | -1.282% | 0.3841% | -0.4511% | -1.924% | -0.8153% | -1.277% | -1.835% | -2.245% | -1.386% | -2.298% | -2.182% | -1.538% | -1.957% | -1.498% | -1.957% | -2.169% | -1.466% | -2.338% | -1.89% | -2.65% | -1.155% | -2.503% | -1.957% | -2.477% | -0.7089% | -1.142% | 0.01617% | -1.869% | -1.582% | -0.8166% | -2.369% | -2.221% | -0.1484% | -1.022% | -0.9744% | -2.798% | -0.6501% | -1.334% | -1.19% | -2.697% | -1.567% | -0.4751% | -2.276% | -1.597% | -0.6413% | -1.72% | -2.478% | -0.0452% | -1.924% | -2.276% | -1.465% | 2.319% | -0.7344% | -1.239% | -0.4583% | -0.4078% | 0.8125% | -2.086% | -0.7553% | -0.4309% | -1.72% | -0.2118% | -0.8429% | -2.421% | 0.579% | -1.457% |  |  | -99.99% | -1.919% | -1.739% |  | 1.092% | 0.4526% | 1.51% | -2.2% | 1.51% | 0.574% | 1.215% | 1.831% | 0.09723% | -1.896% | -0.2148% | 0.2359% | 1.873% | 4.061% | 6.14% | 5.715% | 5.342% | 1.744% | -1.293% | 0.497% | 3.89% | 2.189% | 0.9747% | 1.447% | 4.473% | 2.815% | 1.727% | 0.08568% | -1.897% | -0.8809% | -1.007% | -1.167% | -1.657% |  | 6.218% | -1.566% | 0.357% | -1.981% | -1.852% |  |  | 8.447% | 3.619% | 4.784% | 0.7914% | 1.238%
2025-06-28 | 0.862% | 2.794% | 0.09213% | 0.3629% | 2.669% | 2.477% | 3.164% | 3.164% | 1.887% | 2.397% | 0.894% | 3.925% | -2.168% | -0.2383% | 2.404% | 1.446% | 1.821% | 1.665% | 1.17% | 1.487% | -0.9493% | -0.04326% | -1.339% | 1.264% | -0.5415% | 0.7947% | -2.599% | -1.031% | -0.1243% | -1.578% | -0.8463% | -2.688% | -1.399% | -0.1618% | 1.144% | -2.32% | 1.144% | 0.6024% | -9.291% | 1.488% | 1.644% | 1.29% | 1.144% | 0.5608% | 0.1025% | -0.3557% | -0.9838% | 0.7899% | -0.3424% | -2.732% | 1.144% | 1.519% | 1.2% | 1.709% | -1.657% | 1.838% | 2.162% | -9.166% | -0.3279% | 1.014% | 3.279% | -1.855% | 2.644% | 4.833% | 1.948% | 0.09293% | 1.535% | 0.2275% | 1.394% | 0.3629% | 0.7066% | 2.175% | 0.9565% | -0.4702% | -0.6982% | 0.0794% | 0.9681% | 0.9982% | 1.363% | 1.996% | -0.2515% | 1.144% | 1.977% | 0.6962% | 2.081% | 0.6233% | -0.4182% | 1.883% | 1.061% | -0.314% | -0.3224% | -2.08% | 0.1025% | -11.06% | 1.903% | 1.508% | -100% | 1.238% | -0.2307% | -0.6265% | 0.4566% | -0.8972% | -0.08492% | -1.033% | -0.8556% | 0.7066% | 0.3201% | -2.199% | -2.116% | 2.292% | -0.7915% | -2.022% | -2.068% | -0.8093% | 0.6962% | -0.4286% | -1.278% | -2.429% | -0.9574% | -0.6265% | 0.7274% | -7.521% | -6.965% | -0.439% | -2.001% | -1.966% | -0.439% | -1.48% | 0.9033% | 0.0146% | -7.992% | 0.6697% | 2.092% | 2.818% | 3.69% | -0.8794% | 3.573% | 3.087% | 2.647% | -8.76% | 0.8908% | -1.301% | 2.06% | 3.256% | -0.8452% | 1.16% | 0.3941% | 2.613% | 0.5063% | 1.65% | 1.593% | -0.2515% | -0.5593% | -1.199% | -1.512% | -1.064% | 0.7691% | 2.842% | 1.946% | -0.9402% | 1.385% | -2.257% | -1.648% | -2.21% | 1.198% | -0.5143% | -0.6979% | -2.154% | -1.593% | -2.931% | 0.02165% | -1.98% | -1.452% | -9.685% | 0.008917% | 1.029% | 2.694% | 1.619% | 0.3085% | 0.6924% | -1.609% | -1.115% | -1.676% | 2.125% | -0.7239% | 1.263% | -1.111% | 0.1025% | -2.638% | -9.338% | -0.4241% | 1.861% | 1.029% | 2.325% | 0.6818% | -0.4662% | 0.5449% | 0.007747% |  |  | -100% | -0.4905% | -1.476% |  | -1.737% | 1.134% | -0.439% | -0.1162% | -10.67% | 2.185% | 0.6337% | 1.446% | -1.397% | -0.3557% | -1.241% | -1.168% | -1.642% | 5.81% | 5.97% | 4.725% | 4.746% | 2.857% | -0.7989% | -1.484% | 0.6174% | -0.2631% | -2.474% | -2.368% | 2.127% | -0.5512% | -1.115% | -0.1983% | 0.5843% | 1.535% | -1.803% | -1.321% | -1.257% |  | 5.857% | -1.114% | 0.2962% | -2.839% | -1.479% |  |  | 4.717% | 4.165% | 4.194% | -1.943% | 0.4115%
2025-06-29 | -0.4523% | 1.619% | 1.819% | 1.465% | 1.183% | 1.229% | 1.701% | 2.056% | 1.148% | 1.602% | 1.111% | -0.803% | -0.8975% | 3.988% | 1.465% | 0.5436% | 0.6381% | 0.52% | 0.8562% | 1.183% | 0.2837% | 1.819% | -0.9974% | 1.741% | -1.761% | 1.292% | -1.652% | 0.5856% | 1.426% | -0.8634% | -0.04439% | -3.698% | -0.7% | 1.076% | 0.2837% | 1.082% | 1.111% | -2.079% | -0.3069% | 1.583% | -1.252% | -1.476% | -0.07064% | -3.236% | 0.7562% | 1.111% | -1.761% | -0.07064% | 0.01441% | -2.344% | 0.4018% | 0.8743% | 2.161% | 0.9006% | -0.2669% | 0.2181% | 0.9216% | 0.01205% | 0.7956% | -1.997% | 1.111% | 2.559% | 2.174% | 3.874% | 0.6381% | 0.2019% | 1.183% | -2.524% | -0.1888% | 0.1656% | 0.6381% | -1.016% | -0.8975% | 0.04748% | 1.321% | 0.06061% | 1.531% | 0.2837% | -0.1888% | 1.401% | 0.8743% | 1.583% | -0.07064% | 0.6381% | -1.016% | 0.1656% | -0.7794% | -0.425% | -0.803% | -1.464% | -0.3031% | -1.761% | 1.347% | -1.819% | -0.4644% | -0.3069% | -100% | 0.04748% | 0.6381% | -0.8975% | -1.606% | 0.9924% | -1.252% | 0.6381% | 1.321% | -0.6612% | 3.21% | 0.5122% | -0.425% | 0.4806% | 0.42% | 0.42% | -1.903% | -2.596% | 1.583% | -1.157% | -0.2686% | -2.249% | -0.1494% | 0.7562% | -1.405% | -5.609% | -7.289% | 0.8743% | -2.102% | 0.5856% | -1.689% | -0.8148% | -2.092% | 0.3441% | -1.575% | -0.05973% | 0.5945% | -1.295% | -0.8648% | -0.7215% | -1.549% | -0.4238% | -1.233% | 1.701% | 0.2129% | -1.325% | -0.07064% | 2.721% | -1.831% | 0.9107% | 0.1774% | 1.54% | 0.42% | 2.95% | 1.848% | 2.174% | -0.1284% | -0.1888% | 0.6735% | -0.6849% | 1.111% | 2.906% | 1.304% | -1.085% | 0.242% | -2.28% | -0.7137% | -2.094% | 1.091% | -0.3399% | -1.324% | -4.855% | -0.2014% | -2.381% | -0.9134% | -0.6955% | -0.289% | -5.959% | -1.277% | -0.3686% | 1.065% | -1.563% | -1.669% | 0.9455% | 0.6459% | -1.138% | -1.563% | 0.004102% | -1.56% | 1.091% | -0.08765% | -0.7184% | -0.8904% | -0.534% | -1.922% | -0.3447% | 0.6707% | -0.2492% | -0.3686% | -0.9659% | -1.229% | -1.683% |  |  | -100% | -0.4238% | -0.2346% |  | -0.1369% | 0.2837% | -0.1061% | -0.8148% | -0.673% | -0.3423% | -1.252% | 0.2483% | -0.8148% | -0.01158% | 0.6381% | -1.701% | 0.9111% | 5.1% | 6.238% | 4.373% | 3.644% | 5.588% | -2.155% | -1.362% | -1.913% | 0.5856% | -1.761% | -1.87% | 1.829% | 1.837% | 0.2706% | -1.577% | -1.857% | -1.472% | -0.8771% | -0.6193% | -0.3272% |  | 4.549% | -0.08026% | 1.047% | -1.481% | -1.612% |  |  | 3.874% | 5.168% | 2.106% | -0.8771% | -0.6658%
2025-06-30 | 2.255% | 1.286% | 1.482% | 0.8825% | 0.7326% | 1.032% | 1.482% | 1.782% | 0.8765% | 1.308% | 3.581% | 2.831% | 2.082% | 3.676% | 1.032% | 0.8825% | 0.4328% | -0.1668% | 1.009% | 0.5942% | 1.032% | 1.332% | 0.8709% | 1.665% | 1.424% | 0.4558% | 1.701% | 0.5993% | 0.9991% | 1.399% | 1.132% | 0.3328% | 2.103% | 3.363% | -0.7664% | -0.3772% | 0.8825% | -0.4666% | -2.265% | 0.7326% | 0.8825% | -1.666% | 2.981% | 1.332% | 2.531% | 0.8825% | -5.632% | 1.302% | -4.88% | -5.167% | -0.4666% | 1.632% | 0.06636% | 1.799% | 0.04073% | 1.665% | 1.932% | 1.932% | 0.7326% | 2.065% | 0.4328% | 2.836% | 0.8825% | 4.387% | 0.5942% | 0.1791% | 0.7326% | 1.563% | -0.7664% | -0.4666% | 1.032% | 0.5827% | 2.381% | 1.782% | 2.305% | 0.06636% | 1.532% | 0.2829% | 1.137% | 1.148% | 0.133% | 0.8825% | -0.6165% | 0.2829% | 1.032% | -1.816% | 2.082% | -1.816% | -1.666% | -0.1668% | -1.973% | 0.04073% | -0.01692% | -4.964% | 0.7326% | -0.7664% | -92.88% | 1.332% | 2.381% | 0.7326% | -1.396% | 2.636% | -1.381% | -0.01692% | 0.5993% | -2.865% | 1.705% | -1.047% | 0.5827% | 0.7326% | 0.5942% | 2.808% | 0.7326% | 0.9991% | 0.7326% | 0.8825% | 0.6941% | -2.465% | 0.5993% | 0.8825% | -1.876% | -5.663% | -3.132% | 0.133% | 0.2829% | 0.4661% | 1.032% | 2.531% | -3.931% | 2.731% | 2.255% | 3.085% | 2.255% | 0.07847% | 1.038% | 0.8977% | -0.5017% | 2.017% | 1.164% | 2.232% | -0.5681% | -1.066% | 2.381% | -1.896% | 2.232% | -1.592% | -0.3017% | 1.272% | 2.255% | 1.563% | 2.241% | 1.662% | 1.425% | 1.827% | 0.2379% | 2.531% | 0.4328% | 2.681% | 0.2096% | 1.529% | -0.6831% | -1.61% | 1.608% | -2.031% | -1.492% | -1.616% | 2.18% | -5.534% | -1.306% | -0.888% | 1.586% | -1.179% | -0.4136% | -2.78% | -0.4136% | -1.064% | -0.8516% | -0.7303% | -2.435% | -1.306% | 1.318% | -1.492% | -2.435% | -2.067% | -0.5017% | -0.8179% | 0.713% | 1.004% | -6.127% | -1.901% | -0.4271% | -2.216% | -0.5484% | -1.155% | -0.7% | -0.1845% | -1.034% | 0.05803% |  |  | -100% | -2.523% | -2.974% |  | -0.4207% | 2.232% | -2.086% | -1.966% | 2.681% | -0.01692% | 0.133% | -1.351% | 0.4328% | -1.591% | -0.3167% | -0.9163% | 1.132% | 3.131% | 5.211% | 2.702% | 3.299% | 3.885% | -2.974% | -0.693% | 1.308% | 1.399% | 1.286% | -0.236% | 2.603% | 2.255% | 1.132% | 0.5993% | -0.6417% | -2.396% | -0.01971% | -0.2789% | -1.034% |  | 5.807% | -1.162% | 0.3567% | -1.028% | -1.419% |  |  | 6.896% | 6.331% | 4.888% | -1.108% | -0.2738%
2025-07-01 | 1.892% | 3.728% | 3.968% | 3.442% | 3.416% | 3.33% | 3.855% | 4.155% | -9.772% | -2.208% | 6.2% | 5.506% | -0.91% | 6.502% | 3.705% | 3.742% | 2.711% | 2.317% | 3.728% | 3.555% | 3.855% | 4.493% | 1.702% | 5.423% | 4.836% | 4.109% | 3.486% | 3.872% | 4.956% | 0.4699% | 2.588% | 2.054% | 1.911% | 3.307% | 2.129% | -1.129% | 0.5533% | -2.242% | -0.1971% | 0.7034% | -1.323% | -0.7599% | 0.8159% | 0.7784% | 1.529% | -1.004% | -0.7743% | 1.154% | 1.124% | -1.074% | 1.754% | 2.767% | -1.114% | -0.614% | -1.121% | -0.614% | -9.752% | 1.116% | -1.948% | -1.615% | -0.9475% | -1.129% | 0.1781% | 4.533% | 1.494% | 1.131% | 1.131% | -1.467% | -0.1596% | 0.5533% | 0.6471% | -1.923% | -0.7411% | 1.548% | -0.1137% | -1.948% | -1.615% | 0.1781% | 0.2531% | -1.813% | -0.7599% | -1.66% | 1.285% | -0.04703% | -1.529% | -1.848% | -1.717% | -0.1408% | -0.3847% | -1.323% | -1.668% | -2.662% | 0.5533% | -1.886% | 0.1197% | -0.1783% | -11.83% | -2.261% | 1.116% | 1.81% | -0.1971% | 0.9285% | -0.00951% | 1.435% | 1.854% | -1.848% | 0.2198% | 0.2451% | -1.698% | 0.7534% | 0.4552% | 0.663% | -1.615% | -1.114% | -0.3847% | -1.698% | -2.47% | -2.115% | 0.5366% | -0.08455% | 1.041% | -7.217% | -4.199% | 0.1218% | 0.4407% | -1.781% | -1.698% | 0.4782% | -2.031% | 0.3865% | -0.9475% | 1.702% | -1.813% | -1.766% | 0.1781% | -1.573% | -1.398% | -0.5225% | 0.8174% | 1.116% | 2.395% | 1.944% | -0.2909% | -0.4626% | -1.886% | 0.7842% | 2.317% | -11.79% | 2.343% | 2.17% | 0.0915% | -0.7599% | 2.488% | -0.7599% | 0.3657% | 1.435% | -1.698% | 1.06% | 0.3678% | 1.316% | -0.4965% | -1.416% | 1.848% | -10.45% | -2.014% | 0.7063% | 1.582% | -10.78% | 1.089% | -0.678% | -0.3137% | 0.1599% | -0.2941% | -0.5505% | -1.677% | -6.614% | -0.5808% | -0.6757% | -0.05802% | -1.529% | -0.2422% | -2.52% | -0.4965% | -0.004053% | 1.439% | -1.677% | -0.7326% | -2.008% | 0.3602% | -13.31% | 0.3678% | 1.886% | -0.01164% | -0.3911% | -2.516% | -0.2014% | -0.8465% | -1.264% |  |  | -100% | 0.3097% | -1.71% |  | -2.253% | 0.1781% | -1.135% | 0.5533% | 0.5533% | -1.098% | -9.014% | 1.191% | -1.923% | 0.1406% | -1.079% | 1.397% | -1.615% | 2.971% | 5.876% | 1.165% | 2.062% | 4.7% | -0.4965% | -1.054% | 0.5653% | -0.3639% | -1.571% | -0.7743% | 1.664% | -0.5146% | -0.3472% | -2.298% | -0.1722% | -0.4001% | 2.747% | 0.8152% | 0.5828% |  | 4.063% | -1.95% | -1.317% | -1.621% | -0.9506% |  |  | 7.192% | 5.595% | 4.208% | -0.4252% | 1.133%
2025-07-02 | 0.8183% | 2.761% | 2.554% | 2.671% | 1.466% | 1.619% | 2.437% | 2.32% | -2.895% | 1.595% | 4.776% | 3.841% | -2.123% | 4.861% | 3.139% | 2.788% | 3.022% | 3.022% | 3.841% | 3.841% | 4.308% | 3.958% | 1.142% | 4.672% | 4.057% | 3.409% | 2.545% | 2.801% | 3.009% | -1.564% | -0.4211% | 3.529% | -0.221% | 2.752% | 2.554% | 2.891% | 3.607% | 1.736% | -1.071% | 1.853% | -1.071% | -1.889% | -0.1352% | -0.01828% | 0.5664% | 1.034% | 0.6024% | 0.3325% | 0.2483% | -1.548% | -0.486% | 1.151% | 2.697% | 0.6184% | -1.341% | 2.281% | -0.629% | -7.619% | -0.629% | 0.2026% | 0.4495% | 0.6971% | -6.333% | 4.14% | 0.7103% | 1.466% | 1.682% | -2.204% | 1.151% | 1.619% | 1.502% | -0.7199% | -1.889% | -0.8368% | -0.3171% | -1.564% | -2.916% | -0.3691% | 1.151% | -1.88% | -2.24% | 0.9172% | 1.151% | 0.9172% | -1.655% | -0.603% | -1.655% | -0.01828% | -1.889% | -1.246% | -1.099% | -2.744% | -5.047% | -0.3691% | -0.4211% | 1.151% | -7.853% | -0.2522% | -1.071% | -0.2522% | -0.3691% | 0.8003% | -1.538% | -0.1352% | 0.09866% | -9.022% | 0.5144% | -0.8698% | 2.32% | 1.658% | 2.006% | 0.9262% | 1.658% | 1.762% | 2.788% | -1.422% | -1.079% | -2.084% | 0.5144% | 1.268% | 2.671% | -5.93% | -3.435% | 1.385% | 1.97% | -1.357% | -0.7199% | -1.422% | 0.2026% | -2.396% | -2.528% | 2.222% | -0.2611% | 1.8% | -1.529% | -2.075% | -1.42% | 0.2172% | 1.483% | 0.2156% | 3.085% | 1.25% | -0.7199% | -0.3691% | -1.188% | 2.329% | -0.486% | 1.162% | 1.898% | 2.869% | 2.006% | 0.6833% | 0.9302% | -0.1352% | -0.9538% | -1.538% | -1.188% | 2.087% | 0.6448% | 0.6448% | 0.8156% | -0.6561% | -0.1305% | -1.813% | -0.1305% | -1.11% | 0.05348% | 2.077% | -1.721% | 0.5928% | 1.842% | 0.1386% | 1.446% | 0.7063% | -5.282% | -1.366% | 1.354% | -1.721% | -0.8664% | 0.6448% | -0.9836% | -0.6561% | 0.07976% | -0.3155% | 2.401% | 2.182% | -0.9967% | 0.7063% | -1.564% | -0.547% | -0.7744% | -1.862% | -10.47% | -1.721% | -1.721% | -4.559% | -0.3723% | -1.484% |  |  | -50.63% | -0.1081% | 0.2669% |  | -0.01588% | -1.071% | -0.486% | -1.655% | -0.1352% | -1.538% | -0.7199% | 1.619% | -0.8368% | -0.1352% | -0.486% | 1.268% | 0.6184% | 0.2026% | 4.447% | 6.405% | 3.096% | 3.944% | 0.01969% | -1.698% | -0.8743% | -0.1092% | -1.772% | -1.017% | 1.259% | -1.88% | -0.005285% | -1.876% | -0.6561% | -1.445% | -1.869% | 0.1031% | -0.2146% |  | 6.137% | 0.1595% | -0.2748% | 0.1031% | -1.02% |  |  | 4.531% | 5.339% | 3.237% | -1.869% | -0.1972%
2025-07-03 | 0.7874% | 3.025% | 3.074% | 2.757% | 2.539% | 2.547% | 0.755% | 0.2281% | -2.466% | 2.897% | 1.387% | 0.6496% | -1.458% | 2.326% | 2.863% | 2.547% | 2.02% | 1.914% | 2.441% | 2.441% | 3.074% | 3.074% | 0.3983% | 3.612% | 3.317% | 2.344% | 1.663% | 1.926% | 2.207% | -2.571% | -2.009% | -1.54% | -0.2278% | 2.869% | 0.8604% | 0.1696% | -2.091% | -2.196% | -1.669% | 1.598% | -1.353% | -1.616% | -0.9313% | -0.4043% | 0.2281% | 0.8604% | 1.079% | 0.5442% | -0.03753% | -1.758% | 0.2281% | 1.493% | 3.612% | 1.551% | -2.326% | 1.27% | -0.416% | 0.01727% | 2.301% | 3.612% | 1.914% | -0.01873% | 0.5442% | 5.972% | 0.3983% | 1.566% | 1.858% | -1.937% | 0.5442% | 1.493% | 1.177% | -1.353% | 2.231% | 0.2281% | -0.3223% | 0.7082% | 1.27% | 0.01727% | 0.5442% | 1.663% | 2.336% | -0.6151% | 1.387% | 0.1227% | -1.985% | -0.7205% | -2.301% | -0.4043% | -1.669% | -2.091% | -1.758% | -1.742% | 1.598% | -1.458% | 1.832% | 1.282% | -1.669% | 0.4388% | 0.8604% | 0.01727% | 1.282% | 0.8604% | -0.1935% | -0.2989% | -0.04128% | 0.2281% | 1.551% | -2.579% | 2.02% | 2.301% | 1.955% | -0.38% | -2.196% | -1.165% | -0.4043% | -2.091% | -1.902% | -2.196% | 2.394% | 2.02% | 2.968% | -4.913% | -2.852% | 0.8604% | 1.598% | -1.259% | -1.669% | -0.6151% | -0.6783% | 0.3053% | -0.4773% | 0.4178% | 1.196% | -1.468% | -1.511% | -0.3597% | -2.2% | 1.146% | -0.2399% | 0.3334% | -1.839% | -0.4189% | 1.029% | 0.3983% | -2.449% | 1.04% | 1.303% | -5.607% | -0.5551% | 0.5929% | 0.301% | 0.4388% | 0.4271% | 0.8604% | 0.2281% | -0.6151% | -0.2989% | -1.037% | 0.5143% | -1.085% | -0.9898% | -0.445% | 0.0524% | -11.03% | 0.5261% | -1.255% | -14.94% | -14.92% | -1.618% | -0.8458% | 1.098% | -1.05% | -0.9898% | -1.869% | -2.127% | -1.618% | -2.044% | -2.044% | -2.032% | -1.511% | -0.6254% | -2.032% | -2.316% | 1.201% | -1.806% | -2.127% | -0.3342% | -1.255% | 1.303% | -2.003% | -0.6582% | -0.445% | -0.445% | -1.191% | -0.3384% | 0.7275% | 1.431% | 0.8341% |  |  | -5.217% | 1.56% | 0.3505% |  | -0.4626% | -1.564% | -1.88% | -1.88% | -0.2989% | 1.282% | 0.755% | 0.4388% | 1.598% | -1.458% | 1.598% | 0.3334% | -1.728% | 1.832% | 4.721% | 3.965% | 3.061% | 4.091% | -1.464% | 0.3314% | 3.2% | -0.135% | 0.3983% | 0.8847% | 1.379% | -0.2827% | -0.2286% | 1.645% | -1.5% | -0.5161% | -1.5% | -1.569% | -1.767% |  | 3.702% | -1.594% | -0.3209% | -1.674% | -1.5% |  |  | 2.914% | 5.414% | 1.777% | -1.937% | -1.768%
2025-07-04 | 1.865% | 2.612% | 1.331% | 2.719% | 1.865% | 1.91% | 2.372% | 2.141% | -1.056% | 0.05412% | 0.8685% | 1.215% | 1.25% | 1.079% | -0.5196% | 0.1744% | 1.678% | 2.951% | 1.652% | 1.331% | 2.025% | 1.1% | 3.04% | 4.056% | 3.146% | 4.428% | 3.68% | 1.794% | 4.015% | -0.4374% | 2% | 2.411% | 0.7046% | 1.643% | -0.6469% | -1.393% | -7.344% | 0.7528% | -1.549% | 2.28% | 0.2901% | 1.331% | -1.399% | -0.9939% | 0.1976% | 1.389% | 1.94% | 0.961% | 1.065% | -0.3901% | 2.407% | 2.847% | 2.102% | 2.75% | -0.3132% | 1.794% | -1.702% | -0.6353% | 3.573% | 2.308% | 1.91% | -0.287% | -0.9823% | 5.597% | 1.555% | 1.032% | 2.079% | -1.328% | -0.6006% | 0.3364% | 0.8916% | -1.11% | 1.401% | 0.3479% | -0.4065% | -2.422% | 0.1076% | -0.1726% | -1.04% | 0.1032% | 1.273% | -0.404% | 0.4636% | -1.017% | -2.544% | -0.9939% | -2.313% | 0.3479% | -0.9823% | -1.214% | 0.9425% | -2.62% | 1.204% | -1.214% | -0.7767% | -0.6584% | -1.908% | 2.002% | 0.4405% | 0.7528% | 2.083% | 0.1629% | 1.065% | -0.6816% | -1.507% | -1.561% | 0.4983% | -2.044% | -0.3461% | -1.496% | -2.278% | 1.022% | 0.9713% | 1.259% | 1.389% | -2.255% | -2.56% | -2.011% | -0.1597% | -1.526% | -0.3114% | -9.157% | -5.558% | -2.66% | -2.104% | -0.6944% | -6.419% | -1.561% | -2.813% | -3.399% | -5.652% | -1.456% | -0.3025% | 0.7002% | -0.2171% | -0.4979% | -2.701% | 0.8628% | 0.05412% | 1.296% | -0.7403% | -1.84% | 1.528% | 0.6905% | -2.081% | -0.3132% | -1.329% | 0.2585% | -1.797% | -0.04625% | 0.7973% | -0.03379% | -1.065% | 0.3479% | -1.121% | -2.081% | -1.04% | -2.023% | -0.4421% | -0.6761% | -0.06511% | -0.1613% | 0.59% | -1.781% | 4.854% | -0.6508% | -1.144% | 0.1637% | 0.7395% | 0.3039% | 0.5734% | -0.1903% | -0.2731% | 3.224% | -2.769% | -1.261% | -1.518% | -0.4421% | -2.831% | -1.904% | 0.6468% | -0.793% | -0.3667% | -2.627% | 0.8736% | 0.5484% | 0.7643% | -0.2914% | -0.04431% | -1.513% | -1.495% | -1.612% | -1.963% | -1.144% | -2.162% | -1.495% | 0.8682% | -1.542% |  |  | -8.28% | -1.187% | -1.501% |  | -1.412% | -2.255% | -1.792% | -1.098% | -0.9823% | -1.561% | -2.023% | 0.267% | -0.7741% | -0.404% | -0.08006% | 2.326% | -1.085% | -1.702% | 5.256% | 3.873% | 5.532% | 7.275% | -0.3177% | -1.587% | 1.309% | 0.3749% | -1.659% | -0.1637% | 2.408% | -1.178% | 0.004765% | -0.7767% | -1.249% | -0.7262% | 1.271% | 0.4086% | 1.079% |  | 3.242% | 1.229% | -1.352% | -1.325% | 0.07088% |  |  | 3.402% | 6.259% | 5.081% | -1.249% | 1.158%
2025-07-05 | -0.8131% | 0.9635% | 0.6509% | 0.2398% | 0.1529% | -0.04048% | 0.2492% | 0.6696% | -7.052% | 0.4457% | 1.641% | 1.389% | -1.993% | 3.268% | 0.3519% | 0.3239% | -2.18% | -2.171% | -1.9% | -1.675% | 0.01558% | 0.9312% | -1.322% | 1.277% | -0.5198% | -0.7441% | -0.8389% | -0.1516% | -0.07681% | -3.457% | -0.7163% | -0.02698% | -2.454% | 0.9601% | -3.516% | -4.257% | -4.703% | -4.422% | -5.151% | -5.45% | -4.142% | -5.45% | -4.534% | -3.32% | -2.713% | -1.377% | -1.434% | -2.787% | -0.9086% | -2.218% | -0.7599% | -0.09653% | 1.867% | -0.9654% | -2.288% | 1.974% | -7.651% | 0.6602% | -0.8159% | 0.38% | -1.358% | 0.7251% | -0.4609% | 3.223% | 0.9894% | 1.421% | 1.334% | 0.8169% | -2.273% | -1.526% | -1.993% | -2.554% | -1.993% | 1.837% | -0.5917% | -0.9239% | 1.484% | 1.837% | 1.931% | 2.111% | 0.7163% | 2.865% | 1.183% | 1.183% | 0.05295% | 1.632% | 0.3332% | 0.436% | -2.18% | -2.554% | 2.275% | -3.323% | 4.126% | 2.856% | 2.232% | 3.921% | -0.7786% | 5.472% | 3.687% | 4.201% | 5.846% | 4.098% | 5.519% | 4.126% | 2.772% | 2.772% | 5.72% | 4.781% | 2.949% | 3.984% | 3.482% | 2.947% | 3.561% | 3.478% | 4.622% | -0.6851% | -0.3515% | -0.002066% | 4.208% | 4.566% | 4.042% | -2.909% | 0.762% | 1.912% | 2.725% | 5.222% | -4.609% | -5.73% | -5.674% | -5.741% | -5.306% | -5.229% | -4.013% | -4.804% | -4.492% | -3.009% | -4.317% | -1.901% | -3.94% | -4.422% | -4.754% | -3.495% | -3.357% | -5.048% | -5.543% | -3.926% | -3.983% | -5.11% | -4.616% | -4.271% | -5.048% | -3.488% | -3.449% | -3.581% | -4.422% | -3.339% | -4.796% | -4.086% | 0.2356% | -1.777% | -1.528% | -2.297% | -2.15% | -1.646% | 0.02559% | -2.576% | -0.218% | -0.8059% | -0.1235% | -2.495% | -2.576% | -1.851% | -1.226% | -0.2452% | -3.998% | -3.998% | -2.202% | -2.391% | -2.15% | 0.8214% | -1.265% | -1.562% | -1.394% | 3.039% | -2.259% | -1.898% | -0.989% | -2.395% | -7.203% | -8.853% | 0.4718% | 3.184% | 0.6324% | -1.257% | 3.08% | -1.257% | 3.909% | 3.051% |  |  | -6.692% | 0.1227% | -1.638% |  | -1.19% | -1.619% | -1.246% | 0.9125% | 2.015% | 3.005% | 2.613% | 6.201% | 4.145% | 0.3986% | 3.678% | 5.023% | -1.588% | 5.903% | 6.798% | 7.133% | 7.002% | 6.664% | 2.614% | 5.098% | 6.724% | 7.896% | 7.397% | 5.612% | 7.72% | 7.932% | 7.024% | 7.364% | 2.583% | 4.12% | 1.207% | 2.824% | 2.826% |  | 5.946% | 1.45% | 1.52% | 2.731% | 3.387% |  |  | 4.682% | 4.005% | 5.421% | -1.924% | -2.214%
2025-07-06 | -2.168% | -0.07614% | 0.1253% | 0.03982% | -0.9545% | -1.104% | -0.2916% | -0.01364% | -1.242% | -0.6568% | 0.3926% | 1.173% | 0.1788% | 1.903% | -0.7407% | -1.286% | -1.04% | -1.297% | -1.033% | -1.024% | -0.5161% | -0.6231% | -2.198% | -0.1182% | -0.04654% | -0.9249% | -1.626% | -1.214% | -0.5458% | -1.525% | -1.591% | -0.6694% | -1.031% | 0.003246% | -1.949% | -2.701% | -1.019% | -2.494% | -2.815% | -2.334% | -2.173% | -1.532% | -1.746% | -0.6765% | -1.211% | -2.761% | -2.198% | -1.104% | -1.878% | -1.776% | -1.104% | -1.927% | 0.5756% | -2.418% | -2.198% | -0.1847% | 0.5851% | 0.7134% | -0.6124% | 0.5756% | -1.927% | 0.7949% | -1.425% | -0.8491% | 1.868% | 1.602% | 2.401% | 0.1114% | -1.393% | 0.7455% | 1.547% | 0.2536% | 1.355% | 1.665% | 2.714% | 0.8037% | 3.265% | 1.472% | -0.7727% | 0.5949% | -1.532% | 2.317% | -0.5482% | -2.184% | -0.9973% | -0.3558% | 0.4782% | -0.313% | 0.4995% | -0.5803% | 0.4003% | 1.019% | 2.959% | 0.8203% | 0.6136% | 0.8631% | -2.772% | 3.13% | 2.381% | 0.3926% | -0.4627% | -0.3558% | 1.034% | 2.403% | 2.191% | -2.601% | 1.973% | 2.715% | 1.569% | 2.125% | 1.414% | 2.006% | 2.6% | 2.324% | 2.135% | -1.318% | -2.108% | -2.019% | 2.296% | 1.462% | 1.633% | -3.473% | -1.477% | -0.9759% | 0.3499% | 0.8322% | -1.746% | -1.104% | -1.373% | -0.869% | -2.198% | 0.8614% | 0.07189% | 2.393% | 1.409% | -1.516% | -2.085% | 2.207% | 1.611% | 1.676% | 0.3581% | -0.4413% | 2.638% | 1.848% | 0.3071% | 0.664% | -0.1419% | 1.588% | -2.395% | 0.5653% | 1.848% | 1.996% | 2.676% | 2.531% | 2.232% | 1.825% | 2.349% | 0.2323% | -0.0236% | -1.97% | -1.761% | 0.01965% | -1.867% | -0.9055% | 0.5555% | -2.113% | 2.182% | -1.098% | -2.716% | -1.905% | -2.528% | -1.282% | -0.8958% | -1.023% | -1.098% | 1.533% | -0.3047% | -1.062% | -1.867% | 0.1278% | 0.71% | -2.732% | -1.098% | 1.52% | 0.3108% | -1.098% | -0.9916% | -0.431% | -0.6386% | 1.009% | 0.6684% | 1.317% | -7.982% | 0.01965% | 1.858% | 0.2359% | -0.3999% | -0.6183% |  |  | -7.064% | -2.522% | -0.943% |  | 0.8774% | -1.371% | -1.211% | -1.97% | -1.414% | 0.8951% | -0.7513% | 0.3926% | 0.9272% | -1.318% | 0.2643% | 0.6065% | -1.259% | 4.444% | 7.256% | 7.639% | 6.936% | 6.668% | -1.825% | -0.148% | 3.233% | -0.1182% | 1.72% | 0.2199% | 1.611% | 0.7627% | 2.372% | 1.022% | -0.07739% | -1.798% | 1.032% | -1.429% | -2.309% |  | 1.039% | 0.3242% | -0.3015% | -1.429% | -2.639% |  |  | 2.969% | 4.14% | 3.357% | -0.07739% | -1.651%
2025-07-07
2025-07-08
2025-07-09
2025-07-10
2025-07-11
2025-07-12
2025-07-13
2025-07-14
2025-07-15
2025-07-16
2025-07-17
2025-07-18
2025-07-19
2025-07-20
2025-07-21
2025-07-22
2025-07-23
2025-07-24
2025-07-25
2025-07-26
2025-07-27
2025-07-28
2025-07-29
2025-07-30
2025-07-31
2025-08-01
2025-08-02
Formulas:
Date = [Date, row above]+1