## Dashboard
Performance Summary of JPPL 50 MW Agra as on date and YTD
Month | 2025-06-01
Date | 2025-06-30
Operation Year | FY26
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 265.7258 | 165.3055 | -37.79%
| E_Grid MTD(MWh) | 7971.775 | 8219.9827 | 3.114%
| E_Grid YTD (MWh) | 28155.8545 | 26543.4184 | -5.727%
2 | CUF Daily(%) | 16.59% | 10.32% | -37.79%
| CUF MTD(%) | 16.59% | 17.1% | 3.114%
| CUF YTD(%) | 19.31% | 18.21% | -5.727%
3 | PR_Daily (%) | 76.01% | 81.73% | 7.522%
| PR_MTD (%) | 76.01% | 76.96% | 1.245%
| PR_YTD (%) | 75.94% | 75.87% | -0.09865%
4 | POA Daily (KWh/m2) | 5.2367 | 3.03 | -42.14%
| POA MTD(KWh/m2) | 157.1 | 160 | 1.846%
| POA YTD(KWh/m2) | 555.4 | 524.1102 | -5.634%
5 | PA Daily | 99.5% | 99.32% | -0.1859%
| PA MTD | 99.5% | 99.09% | -0.4134%
| PA YTD | 99.5% | 98.7% | -0.8016%
6 | GA Daily | 99.5% | 100% | 0.5025%
| GA MTD | 99.5% | 100% | 0.5025%
| GA YTD | 99.5% | 100% | 0.5025%

## Annual_KPI
Till Date | 2025-06-30 | 2025-06-01
JPPL 50 MW Performance Summary-YTD
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2026 | 91 | 555.4 | 524.1102 | 28155.8545 | 26543.4184 | 75.94% | 75.87% | 19.31% | 18.21% | 99.5% | 100% | 99.5% | 98.7% | 0 | 0
JPPL 50 MW Performance Summary-Monthwise
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-04-01 | 30 | 206.6 | 181.3903 | 10495.2627 | 9324.465 | 76.1% | 77.01% | 21.84% | 19.4% | 99.5% | 100% | 99.5% | 99.69% | 0 | 0
2025-05-01 | 31 | 191.7 | 182.72 | 9688.8168 | 8998.9708 | 75.71% | 73.78% | 19.51% | 18.12% | 99.5% | 100% | 99.5% | 97.38% | 0 | 0
2025-06-01 | 30 | 157.1 | 160 | 7971.775 | 8219.9827 | 76.01% | 76.96% | 16.59% | 17.1% | 99.5% | 100% | 99.5% | 99.09% | 0 | 0
2025-07-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2025-08-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2025-09-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2025-10-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2025-11-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2025-12-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2026-01-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2026-02-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0
2026-03-01 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 99.5% |  | 99.5% |  | 0 | 0

## Monthly_KPI
Till Date | 2025-06-30
JPPL 50 MW Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-06-01 | 30 | 157.1 | 160 | 7971.775 | 8219.9827 | 76.01% | 76.96% | 16.59% | 17.1% | 99.5% | 100% | 99.5% | 99.09% | 0 | 0
Start Date | 2025-06-24
End Date | 2025-06-30
JPPL50 MW Performance Summary
Year | Days | Estimated POA(KWh/m2) | Measured POA (KWh/m2) | Budgeted Energy (MWh) | Measured Energy (MWh) | Targt PR (%) | Measured PR(%) | Target DC CUF (%) | Measured DC CUF (%) | Target GA (%) | Measured GA (%) | Target PA (%) | Measured PA (%) | WPR_Eac | WPR_Edc
2025-06-01 | 7 | 36.6567 | 36.13 | 1860.0808 | 1869.9691 | 76.01% | 77.53% | 16.59% | 16.67% | 99.5% | 100% | 99.5% | 99.51% | 0 | 0
Formulas:
Days = [Days, row below]-6

## Grass_Ct
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | Blk1 | Blk2 | Blk3 | Blk4 | Blk5 | Blk6 | Blk7 | Blk8 | Total No.Table GC done | Mrthod of Cutting | Remarks for the day
1 | 2023-10-01 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
2 | 2023-10-02 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
3 | 2023-10-03 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
4 | 2023-10-04 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
5 | 2023-10-05 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
6 | 2023-10-06 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
7 | 2023-10-07 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
8 | 2023-10-08 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
9 | 2023-10-09 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
10 | 2023-10-10 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
11 | 2023-10-11 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
12 | 2023-10-12 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
13 | 2023-10-13 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
14 | 2023-10-14 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
15 | 2023-10-15 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
16 | 2023-10-16 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
17 | 2023-10-17 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
18 | 2023-10-18 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
19 | 2023-10-19 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
20 | 2023-10-20 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
21 | 2023-10-21 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
22 | 2023-10-22 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
23 | 2023-10-23 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
24 | 2023-10-24 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
25 | 2023-10-25 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
26 | 2023-10-26 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
27 | 2023-10-27 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
28 | 2023-10-28 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
29 | 2023-10-29 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
30 | 2023-10-30 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
31 | 2023-10-31 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 | [10 empty] | 0
32 | 2023-11-01 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
33 | 2023-11-02 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
34 | 2023-11-03 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
35 | 2023-11-04 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
36 | 2023-11-05 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
37 | 2023-11-06 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
38 | 2023-11-07 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
39 | 2023-11-08 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
40 | 2023-11-09 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
41 | 2023-11-10 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
42 | 2023-11-11 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
43 | 2023-11-12 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
44 | 2023-11-13 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
45 | 2023-11-14 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
46 | 2023-11-15 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
47 | 2023-11-16 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
48 | 2023-11-17 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
49 | 2023-11-18 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
50 | 2023-11-19 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
51 | 2023-11-20 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
52 | 2023-11-21 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
53 | 2023-11-22 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
54 | 2023-11-23 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
55 | 2023-11-24 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
56 | 2023-11-25 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
57 | 2023-11-26 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
58 | 2023-11-27 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
59 | 2023-11-28 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
60 | 2023-11-29 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
61 | 2023-11-30 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 | [10 empty] | 0
62 | 2023-12-01 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
63 | 2023-12-02 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
64 | 2023-12-03 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
65 | 2023-12-04 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
66 | 2023-12-05 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
67 | 2023-12-06 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
68 | 2023-12-07 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
69 | 2023-12-08 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
70 | 2023-12-09 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
71 | 2023-12-10 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
72 | 2023-12-11 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
73 | 2023-12-12 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
74 | 2023-12-13 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
75 | 2023-12-14 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
76 | 2023-12-15 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
77 | 2023-12-16 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
78 | 2023-12-17 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
79 | 2023-12-18 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
80 | 2023-12-19 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
81 | 2023-12-20 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
82 | 2023-12-21 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
83 | 2023-12-22 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
84 | 2023-12-23 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
85 | 2023-12-24 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
86 | 2023-12-25 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
87 | 2023-12-26 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
88 | 2023-12-27 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
89 | 2023-12-28 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
90 | 2023-12-29 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
91 | 2023-12-30 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
92 | 2023-12-31 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 | [10 empty] | 0
93 | 2024-01-01 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
94 | 2024-01-02 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
95 | 2024-01-03 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
96 | 2024-01-04 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
97 | 2024-01-05 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
98 | 2024-01-06 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
99 | 2024-01-07 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
100 | 2024-01-08 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
101 | 2024-01-09 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
102 | 2024-01-10 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
103 | 2024-01-11 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
104 | 2024-01-12 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
105 | 2024-01-13 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
106 | 2024-01-14 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
107 | 2024-01-15 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
108 | 2024-01-16 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
109 | 2024-01-17 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
110 | 2024-01-18 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
111 | 2024-01-19 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
112 | 2024-01-20 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
113 | 2024-01-21 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
114 | 2024-01-22 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
115 | 2024-01-23 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
116 | 2024-01-24 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
117 | 2024-01-25 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
118 | 2024-01-26 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
119 | 2024-01-27 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
120 | 2024-01-28 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
120 | 2024-01-29 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
122 | 2024-01-30 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
123 | 2024-01-31 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 | [10 empty] | 0
124 | 2024-02-01 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
125 | 2024-02-02 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
126 | 2024-02-03 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-04 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-05 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-06 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-07 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-08 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-09 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-10 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-11 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-12 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-13 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-14 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
127 | 2024-02-15 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
139 | 2024-02-16 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
140 | 2024-02-17 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
141 | 2024-02-18 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
142 | 2024-02-19 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
143 | 2024-02-20 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
144 | 2024-02-21 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
145 | 2024-02-22 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
146 | 2024-02-23 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
147 | 2024-02-24 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
148 | 2024-02-25 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
149 | 2024-02-26 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
150 | 2024-02-27 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
151 | 2024-02-28 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
152 | 2024-02-29 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 29 | [10 empty] | 0
153 | 2024-03-01 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
154 | 2024-03-02 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
155 | 2024-03-03 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
156 | 2024-03-04 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
157 | 2024-03-05 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
158 | 2024-03-06 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
159 | 2024-03-07 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0 |  | Grass cutting in Block 8 by Rotavator
160 | 2024-03-08 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
161 | 2024-03-09 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
162 | 2024-03-10 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
163 | 2024-03-11 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
164 | 2024-03-12 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
165 | 2024-03-13 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
166 | 2024-03-14 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
167 | 2024-03-15 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
168 | 2024-03-16 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
169 | 2024-03-17 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
170 | 2024-03-18 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
171 | 2024-03-19 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
172 | 2024-03-20 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
173 | 2024-03-21 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
174 | 2024-03-22 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
175 | 2024-03-23 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
176 | 2024-03-24 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
177 | 2024-03-25 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
177 | 2024-03-26 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
179 | 2024-03-27 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
180 | 2024-03-28 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
181 | 2024-03-29 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
182 | 2024-03-30 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
183 | 2024-03-31 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 | [10 empty] | 0
184 | 2024-04-01 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
185 | 2024-04-02 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
186 | 2024-04-03 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
187 | 2024-04-04 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
188 | 2024-04-05 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
189 | 2024-04-06 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
190 | 2024-04-07 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
191 | 2024-04-08 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
192 | 2024-04-09 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
193 | 2024-04-10 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
194 | 2024-04-11 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
195 | 2024-04-12 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
196 | 2024-04-13 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
197 | 2024-04-14 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
198 | 2024-04-15 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
199 | 2024-04-16 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
200 | 2024-04-17 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
201 | 2024-04-18 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
202 | 2024-04-19 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
203 | 2024-04-20 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
204 | 2024-04-21 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
205 | 2024-04-22 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
206 | 2024-04-23 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
207 | 2024-04-24 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
208 | 2024-04-25 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
209 | 2024-04-26 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
210 | 2024-04-27 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
211 | 2024-04-28 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
212 | 2024-04-29 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
213 | 2024-04-30 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 | [10 empty] | 0
214 | 2024-05-01 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
215 | 2024-05-02 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
216 | 2024-05-03 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
217 | 2024-05-04 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
218 | 2024-05-05 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
219 | 2024-05-06 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
220 | 2024-05-07 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
221 | 2024-05-08 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
222 | 2024-05-09 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
223 | 2024-05-10 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
224 | 2024-05-11 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
225 | 2024-05-12 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
226 | 2024-05-13 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
227 | 2024-05-14 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
228 | 2024-05-15 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
229 | 2024-05-16 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
230 | 2024-05-17 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 130
231 | 2024-05-18 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
232 | 2024-05-19 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
233 | 2024-05-20 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
234 | 2024-05-21 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
235 | 2024-05-22 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
236 | 2024-05-23 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
237 | 2024-05-24 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
238 | 2024-05-25 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
239 | 2024-05-26 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
240 | 2024-05-27 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
241 | 2024-05-28 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
242 | 2024-05-29 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
243 | 2024-05-30 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
244 | 2024-05-31 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 | [10 empty] | 0
245 | 2024-06-01 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
246 | 2024-06-02 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
247 | 2024-06-03 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
248 | 2024-06-04 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
249 | 2024-06-05 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
250 | 2024-06-06 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
251 | 2024-06-07 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
252 | 2024-06-08 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
253 | 2024-06-09 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
254 | 2024-06-10 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
255 | 2024-06-11 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
256 | 2024-06-12 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
257 | 2024-06-13 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
258 | 2024-06-14 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
259 | 2024-06-15 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
260 | 2024-06-16 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
261 | 2024-06-17 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
262 | 2024-06-18 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
263 | 2024-06-19 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
264 | 2024-06-20 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
265 | 2024-06-21 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
266 | 2024-06-22 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
267 | 2024-06-23 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
268 | 2024-06-24 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
269 | 2024-06-25 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
270 | 2024-06-26 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
271 | 2024-06-27 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
272 | 2024-06-28 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
273 | 2024-06-29 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
274 | 2024-06-30 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 | [10 empty] | 0
275 | 2024-07-01 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
276 | 2024-07-02 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
277 | 2024-07-03 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
278 | 2024-07-04 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
279 | 2024-07-05 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
280 | 2024-07-06 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0 |  | It was raining so grass could not be harvested
281 | 2024-07-07 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0 |  | It was raining so grass could not be harvested
282 | 2024-07-08 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0 |  | It was raining so grass could not be harvested
283 | 2024-07-09 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
284 | 2024-07-10 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
285 | 2024-07-11 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
286 | 2024-07-12 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
287 | 2024-07-13 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
288 | 2024-07-14 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
289 | 2024-07-15 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
290 | 2024-07-16 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
291 | 2024-07-17 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
292 | 2024-07-18 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
293 | 2024-07-19 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
294 | 2024-07-20 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
295 | 2024-07-21 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
296 | 2024-07-22 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
297 | 2024-07-23 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
298 | 2024-07-24 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
299 | 2024-07-25 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
300 | 2024-07-26 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
301 | 2024-07-27 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
302 | 2024-07-28 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
303 | 2024-07-29 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
304 | 2024-07-30 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
305 | 2024-07-31 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 | [10 empty] | 0
306 | 2024-08-01 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
307 | 2024-08-02 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
308 | 2024-08-03 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
309 | 2024-08-04 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
310 | 2024-08-05 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
311 | 2024-08-06 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
312 | 2024-08-07 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
313 | 2024-08-08 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
314 | 2024-08-09 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
315 | 2024-08-10 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
316 | 2024-08-11 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
317 | 2024-08-12 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
318 | 2024-08-13 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
319 | 2024-08-14 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
320 | 2024-08-15 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
321 | 2024-08-16 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
322 | 2024-08-17 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
323 | 2024-08-18 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
324 | 2024-08-19 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
325 | 2024-08-20 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
326 | 2024-08-21 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
327 | 2024-08-22 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
328 | 2024-08-23 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
329 | 2024-08-24 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
330 | 2024-08-25 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
331 | 2024-08-26 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
332 | 2024-08-27 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
333 | 2024-08-28 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
334 | 2024-08-29 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
335 | 2024-08-30 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
336 | 2024-08-31 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 | [10 empty] | 0
337 | 2024-09-01 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
338 | 2024-09-02 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
339 | 2024-09-03 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
340 | 2024-09-04 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
341 | 2024-09-05 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
342 | 2024-09-06 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
343 | 2024-09-07 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
344 | 2024-09-08 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
345 | 2024-09-09 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
346 | 2024-09-10 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
347 | 2024-09-11 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
348 | 2024-09-12 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
349 | 2024-09-13 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
350 | 2024-09-14 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
351 | 2024-09-15 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
352 | 2024-09-16 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
353 | 2024-09-17 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
354 | 2024-09-18 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
355 | 2024-09-19 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
356 | 2024-09-20 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
357 | 2024-09-21 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
358 | 2024-09-22 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
359 | 2024-09-23 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
360 | 2024-09-24 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
361 | 2024-09-25 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
362 | 2024-09-26 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
363 | 2024-09-27 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
364 | 2024-09-28 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
365 | 2024-09-29 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
366 | 2024-09-30 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 | [10 empty] | 0
367 | 2024-10-01 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
368 | 2024-10-02 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
369 | 2024-10-03 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
370 | 2024-10-04 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
371 | 2024-10-05 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
372 | 2024-10-06 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
373 | 2024-10-07 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
374 | 2024-10-08 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
375 | 2024-10-09 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
376 | 2024-10-10 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
377 | 2024-10-11 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
378 | 2024-10-12 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
379 | 2024-10-13 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
380 | 2024-10-14 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
381 | 2024-10-15 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
382 | 2024-10-16 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
383 | 2024-10-17 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
384 | 2024-10-18 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
385 | 2024-10-19 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
386 | 2024-10-20 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
387 | 2024-10-21 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
388 | 2024-10-22 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
389 | 2024-10-23 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
390 | 2024-10-24 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
391 | 2024-10-25 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
392 | 2024-10-26 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
393 | 2024-10-27 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
394 | 2024-10-28 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
395 | 2024-10-29 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
396 | 2024-10-30 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
397 | 2024-10-31 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 | [10 empty] | 0
398 | 2024-11-01 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
399 | 2024-11-02 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
400 | 2024-11-03 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
401 | 2024-11-04 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
402 | 2024-11-05 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
403 | 2024-11-06 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
404 | 2024-11-07 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
405 | 2024-11-08 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
406 | 2024-11-09 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
407 | 2024-11-10 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
408 | 2024-11-11 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
409 | 2024-11-12 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
410 | 2024-11-13 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
411 | 2024-11-14 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
412 | 2024-11-15 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
413 | 2024-11-16 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
414 | 2024-11-17 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
415 | 2024-11-18 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
416 | 2024-11-19 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
417 | 2024-11-20 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
418 | 2024-11-21 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
419 | 2024-11-22 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
420 | 2024-11-23 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
421 | 2024-11-24 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
422 | 2024-11-25 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
423 | 2024-11-26 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
424 | 2024-11-27 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
425 | 2024-11-28 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
426 | 2024-11-29 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
427 | 2024-11-30 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 | [10 empty] | 0
428 | 2024-12-01 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
429 | 2024-12-02 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
430 | 2024-12-03 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
431 | 2024-12-04 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
432 | 2024-12-05 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
433 | 2024-12-06 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
434 | 2024-12-07 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
435 | 2024-12-08 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
436 | 2024-12-09 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
437 | 2024-12-10 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
438 | 2024-12-11 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
439 | 2024-12-12 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
440 | 2024-12-13 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
441 | 2024-12-14 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
442 | 2024-12-15 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
443 | 2024-12-16 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
444 | 2024-12-17 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
445 | 2024-12-18 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
446 | 2024-12-19 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
447 | 2024-12-20 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
448 | 2024-12-21 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
449 | 2024-12-22 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
450 | 2024-12-23 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
451 | 2024-12-24 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
452 | 2024-12-25 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
453 | 2024-12-26 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
454 | 2024-12-27 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
455 | 2024-12-28 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
456 | 2024-12-29 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
457 | 2024-12-30 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
458 | 2024-12-31 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 | [10 empty] | 0
459 | 2025-01-01 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
460 | 2025-01-02 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
461 | 2025-01-03 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
462 | 2025-01-04 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
463 | 2025-01-05 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
464 | 2025-01-06 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
465 | 2025-01-07 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
466 | 2025-01-08 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
467 | 2025-01-09 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
468 | 2025-01-10 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
469 | 2025-01-11 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
470 | 2025-01-12 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
471 | 2025-01-13 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
472 | 2025-01-14 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
473 | 2025-01-15 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
474 | 2025-01-16 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
475 | 2025-01-17 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
476 | 2025-01-18 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
477 | 2025-01-19 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
478 | 2025-01-20 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting has been completed in the entire ICR area.
479 | 2025-01-21 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
480 | 2025-01-22 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
481 | 2025-01-23 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting happened near MCR area.
482 | 2025-01-24 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0 |  | The grass cutting happened near MCR area.
483 | 2025-01-25 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
484 | 2025-01-26 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
485 | 2025-01-27 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
486 | 2025-01-28 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
487 | 2025-01-29 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
488 | 2025-01-30 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
489 | 2025-01-31 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 | [10 empty] | 0
490 | 2025-02-01 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
491 | 2025-02-02 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
492 | 2025-02-03 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
493 | 2025-02-04 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
494 | 2025-02-05 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
495 | 2025-02-06 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
496 | 2025-02-07 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
497 | 2025-02-08 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
498 | 2025-02-09 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
499 | 2025-02-10 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
500 | 2025-02-11 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
501 | 2025-02-12 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
502 | 2025-02-13 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
503 | 2025-02-14 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
504 | 2025-02-15 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
505 | 2025-02-16 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
506 | 2025-02-17 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
507 | 2025-02-18 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
508 | 2025-02-19 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
509 | 2025-02-20 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
510 | 2025-02-21 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
511 | 2025-02-22 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
512 | 2025-02-23 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
513 | 2025-02-24 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
514 | 2025-02-25 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
515 | 2025-02-26 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
516 | 2025-02-27 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
517 | 2025-02-28 | 2025 | 2025 | Year_2 | Year_2 | Feb-25 | 28 | [10 empty] | 0
518 | 2025-03-01 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
519 | 2025-03-02 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
520 | 2025-03-03 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
521 | 2025-03-04 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
522 | 2025-03-05 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
523 | 2025-03-06 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
524 | 2025-03-07 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
525 | 2025-03-08 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
527 | 2025-03-09 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
528 | 2025-03-10 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
529 | 2025-03-11 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
530 | 2025-03-12 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
531 | 2025-03-13 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
532 | 2025-03-14 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
533 | 2025-03-15 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
534 | 2025-03-16 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
535 | 2025-03-17 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
536 | 2025-03-18 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
537 | 2025-03-19 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
538 | 2025-03-20 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
539 | 2025-03-21 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
540 | 2025-03-22 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
541 | 2025-03-23 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
542 | 2025-03-24 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
543 | 2025-03-25 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
544 | 2025-03-26 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
545 | 2025-03-27 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
546 | 2025-03-28 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
547 | 2025-03-29 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
548 | 2025-03-30 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
549 | 2025-03-31 | 2025 | 2025 | Year_2 | Year_2 | Mar-25 | 31 | [10 empty] | 0
550 | 2025-04-01 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 | [10 empty] | 0
551 | 2025-04-02 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk5: 90 | 90 | Tractor Based Rotavetor
552 | 2025-04-03 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk5: 118 | 118 | Tractor Based Rotavetor
553 | 2025-04-04 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk5: 112 | 112 | Tractor Based Rotavetor
554 | 2025-04-05 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | [8 empty] | 0 | Tractor Based Rotavetor
555 | 2025-04-06 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 120 | 120 | Tractor Based Rotavetor
556 | 2025-04-07 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 50 | 50 | Tractor Based Rotavetor
557 | 2025-04-08 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 20 | 20 | Tractor Based Rotavetor
558 | 2025-04-09 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | [8 empty] | 0 | Tractor Based Rotavetor
559 | 2025-04-10 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 24 | 24 | Tractor Based Rotavetor
560 | 2025-04-11 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Honda Machine | Blk5: 50; Blk6: 49 | 99 | Honda Machine
561 | 2025-04-12 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Honda Machine | Blk5: 45; Blk6: 50 | 95 | Honda Machine
562 | 2025-04-13 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Honda Machine | [8 empty] | 0 | Honda Machine
563 | 2025-04-14 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Honda Machine | Blk5: 65 | 65 | Honda Machine
564 | 2025-04-15 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk6: 82 | 82 | Tractor Based Rotavetor
565 | 2025-04-16 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 60 | 60 | Tractor Based Rotavetor
566 | 2025-04-17 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 130 | 130 | Tractor Based Rotavetor
567 | 2025-04-18 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 40; Blk2: 80; Blk3: 80 | 200 | Tractor Based Rotavetor
568 | 2025-04-19 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 95; Blk2: 95; Blk3: 130 | 320 | Tractor Based Rotavetor
569 | 2025-04-21 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk1: 30; Blk2: 35; Blk3: 25 | 90 | Tractor Based Rotavetor
570 | 2025-04-22 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk2: 40; Blk3: 40 | 80 | Tractor Based Rotavetor
571 | 2025-04-23 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk2: 40 | 40 | Tractor Based Rotavetor
572 | 2025-04-24 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk4: 140 | 140 | Tractor Based Rotavetor
573 | 2025-04-25 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk7: 80 | 80 | Tractor Based Rotavetor
574 | 2025-04-26 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk7: 120 | 120 | Tractor Based Rotavetor
575 | 2025-04-27 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk7: 80 | 80 | Tractor Based Rotavetor
576 | 2025-04-28 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Tractor based Rotavetor | Blk7: 70 | 70 | Tractor Based Rotavetor
577 | 2025-04-29 | 2026 | 2025 | Year_2 | Year_2 | Apr-25 | 30 |  | Honda Machine | Blk1: 40; Blk2: 40 | 80 | Honda Machine
578 | 2025-04-30 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 80 | 80
579 | 2025-05-01 | 2026 | 2025 |  |  | May-25 | 31 |  |  | Blk8: 40 | 40
580 | 2025-05-02 | 2026 | 2025 |  |  | May-25 | 31 | [10 empty] | 0
581 | 2025-05-03 | 2026 | 2025 |  |  | May-25 | 31 |  |  | Blk8: 100 | 100 | Tractor Based Rotavetor & Honda Machine
582 | 2025-05-04 | 2026 | 2025 |  |  | May-25 | 31 |  | Honda Machine | Blk8: 90 | 90 | Honda Machine
583 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
584 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
585 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
586 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
587 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
588 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
589 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
590 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
591 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
592 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
593 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
594 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
595 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
596 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
597 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
598 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
599 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
600 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
601 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
602 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
603 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
604 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
605 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
606 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
607 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
608 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
609 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
610 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
611 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
612 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
613 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
614 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
615 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
616 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
617 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
618 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
619 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
620 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
621 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
622 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
623 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
624 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
625 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
626 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
627 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
628 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
629 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
630 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
631 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
632 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
633 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
634 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
635 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
636 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
637 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
638 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
639 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
640 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
641 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
642 |  | 1900 | 1900 |  |  | Jan-00 | 31 | [10 empty] | 0
Formulas:
Days = DAY(EOMONTH(GC[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Mod_CL
Sr. No. | Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Cycle Number | Resources | Blk1 | Blk2 | Blk3 | Blk4 | Blk5 | Blk6 | Blk7 | Blk8 | Total NO. Module cleaned | Morning Start Time | Morning End Time | Evening Start Time | Evening End time | Brush/MOP Replcemnet | Water Test Report | Remarks for the day
1 | 2023-10-01 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
2 | 2023-10-02 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
3 | 2023-10-03 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
4 | 2023-10-04 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
5 | 2023-10-05 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
6 | 2023-10-06 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
7 | 2023-10-07 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
8 | 2023-10-08 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
9 | 2023-10-09 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
10 | 2023-10-10 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
11 | 2023-10-11 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
12 | 2023-10-12 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
13 | 2023-10-13 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
14 | 2023-10-14 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
15 | 2023-10-15 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
16 | 2023-10-16 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
17 | 2023-10-17 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
18 | 2023-10-18 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
19 | 2023-10-19 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
20 | 2023-10-20 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
21 | 2023-10-21 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
22 | 2023-10-22 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
23 | 2023-10-23 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
24 | 2023-10-24 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
25 | 2023-10-25 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
26 | 2023-10-26 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
27 | 2023-10-27 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
28 | 2023-10-28 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
29 | 2023-10-29 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
30 | 2023-10-30 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
31 | 2023-10-31 | 2024 | 2023 | Year_2 | Year_2 | Oct-23 | 31 |  |  | Blk8: 6000 | 6000
32 | 2023-11-01 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
33 | 2023-11-02 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
34 | 2023-11-03 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
35 | 2023-11-04 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
36 | 2023-11-05 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
37 | 2023-11-06 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
38 | 2023-11-07 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
39 | 2023-11-08 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
40 | 2023-11-09 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
41 | 2023-11-10 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
42 | 2023-11-11 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
43 | 2023-11-12 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
44 | 2023-11-13 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
45 | 2023-11-14 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
46 | 2023-11-15 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
47 | 2023-11-16 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
48 | 2023-11-17 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
49 | 2023-11-18 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
50 | 2023-11-19 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
51 | 2023-11-20 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
52 | 2023-11-21 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
53 | 2023-11-22 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
54 | 2023-11-23 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
55 | 2023-11-24 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
56 | 2023-11-25 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
57 | 2023-11-26 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
58 | 2023-11-27 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
59 | 2023-11-28 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
60 | 2023-11-29 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
61 | 2023-11-30 | 2024 | 2023 | Year_2 | Year_2 | Nov-23 | 30 |  |  | Blk8: 6000 | 6000
62 | 2023-12-01 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
63 | 2023-12-02 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
64 | 2023-12-03 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
65 | 2023-12-04 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
66 | 2023-12-05 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
67 | 2023-12-06 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
68 | 2023-12-07 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
69 | 2023-12-08 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
70 | 2023-12-09 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
71 | 2023-12-10 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
72 | 2023-12-11 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
73 | 2023-12-12 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
74 | 2023-12-13 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
75 | 2023-12-14 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
76 | 2023-12-15 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
77 | 2023-12-16 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
78 | 2023-12-17 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
79 | 2023-12-18 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
80 | 2023-12-19 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
81 | 2023-12-20 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
82 | 2023-12-21 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
83 | 2023-12-22 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
84 | 2023-12-23 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
85 | 2023-12-24 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
86 | 2023-12-25 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
87 | 2023-12-26 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
88 | 2023-12-27 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
89 | 2023-12-28 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
90 | 2023-12-29 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
91 | 2023-12-30 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
92 | 2023-12-31 | 2024 | 2023 | Year_2 | Year_2 | Dec-23 | 31 |  |  | Blk8: 6000 | 6000
93 | 2024-01-01 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
94 | 2024-01-02 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
95 | 2024-01-03 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
96 | 2024-01-04 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
97 | 2024-01-05 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
98 | 2024-01-06 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
99 | 2024-01-07 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
100 | 2024-01-08 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
101 | 2024-01-09 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
102 | 2024-01-10 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
103 | 2024-01-11 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
104 | 2024-01-12 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
105 | 2024-01-13 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
106 | 2024-01-14 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
107 | 2024-01-15 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
108 | 2024-01-16 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
109 | 2024-01-17 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
110 | 2024-01-18 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
111 | 2024-01-19 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
112 | 2024-01-20 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
113 | 2024-01-21 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
114 | 2024-01-22 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
115 | 2024-01-23 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
116 | 2024-01-24 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
117 | 2024-01-25 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
118 | 2024-01-26 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
119 | 2024-01-27 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
120 | 2024-01-28 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
120 | 2024-01-29 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
122 | 2024-01-30 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
123 | 2024-01-31 | 2024 | 2024 | Year_2 | Year_2 | Jan-24 | 31 |  |  | Blk8: 6000 | 6000
124 | 2024-02-01 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000
125 | 2024-02-02 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000
126 | 2024-02-03 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000
127 | 2024-02-04 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000
127 | 2024-02-05 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-06 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-07 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-08 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-09 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-10 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-11 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP |  | Cleaning Stop due to Fanbalt Broken
127 | 2024-02-12 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-13 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
127 | 2024-02-14 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning not done due to marriage in vendor's family
127 | 2024-02-15 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning not done due to marriage in vendor's family
139 | 2024-02-16 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP |  | Cleaning stop due to Tractor pulli Broken
140 | 2024-02-17 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning Stop due to Tractor under breakdown
141 | 2024-02-18 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning Stop due to Tractor under breakdown
142 | 2024-02-19 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 4:00 | 9:00 | MOP
143 | 2024-02-20 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 |  |  | 5:00 | 11:00 | MOP
144 | 2024-02-21 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
145 | 2024-02-22 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
146 | 2024-02-23 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
147 | 2024-02-24 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
148 | 2024-02-25 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
149 | 2024-02-26 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
150 | 2024-02-27 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
151 | 2024-02-28 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
152 | 2024-02-29 | 2024 | 2024 | Year_2 | Year_2 | Feb-24 | 28 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
153 | 2024-03-01 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
154 | 2024-03-02 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
155 | 2024-03-03 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
156 | 2024-03-04 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
157 | 2024-03-05 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
158 | 2024-03-06 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
159 | 2024-03-07 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
160 | 2024-03-08 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Module cleaning stopped by vendor due to festival yesterday.
161 | 2024-03-09 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | Venders absent
162 | 2024-03-10 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | Venders absent
163 | 2024-03-11 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | Venders absent
164 | 2024-03-12 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | Venders absent
165 | 2024-03-13 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | Venders absent
166 | 2024-03-14 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
167 | 2024-03-15 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
168 | 2024-03-16 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
169 | 2024-03-17 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
170 | 2024-03-18 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
171 | 2024-03-19 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
172 | 2024-03-20 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
173 | 2024-03-21 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
174 | 2024-03-22 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
175 | 2024-03-23 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
176 | 2024-03-24 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning Stop due to Festival
177 | 2024-03-25 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning Stop due to Festival
177 | 2024-03-26 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
179 | 2024-03-27 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | Cleaning happed only evening due to tractor breadown on 26 March night.
180 | 2024-03-28 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
181 | 2024-03-29 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
182 | 2024-03-30 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
183 | 2024-03-31 | 2024 | 2024 | Year_2 | Year_2 | Mar-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
184 | 2024-04-01 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
185 | 2024-04-02 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
186 | 2024-04-03 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
187 | 2024-04-04 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
188 | 2024-04-05 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
189 | 2024-04-06 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
190 | 2024-04-07 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
191 | 2024-04-08 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
192 | 2024-04-09 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
193 | 2024-04-10 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
194 | 2024-04-11 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
195 | 2024-04-12 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
196 | 2024-04-13 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
197 | 2024-04-14 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
198 | 2024-04-15 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
199 | 2024-04-16 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
200 | 2024-04-17 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
201 | 2024-04-18 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
202 | 2024-04-19 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
203 | 2024-04-20 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
204 | 2024-04-21 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
205 | 2024-04-22 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
206 | 2024-04-23 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
207 | 2024-04-24 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
208 | 2024-04-25 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
209 | 2024-04-26 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
210 | 2024-04-27 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
211 | 2024-04-28 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
212 | 2024-04-29 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
213 | 2024-04-30 | 2024 | 2024 | Year_2 | Year_2 | Apr-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
214 | 2024-05-01 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
215 | 2024-05-02 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
216 | 2024-05-03 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
217 | 2024-05-04 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
218 | 2024-05-05 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
219 | 2024-05-06 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
220 | 2024-05-07 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
221 | 2024-05-08 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
222 | 2024-05-09 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
223 | 2024-05-10 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 14950 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
224 | 2024-05-11 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
225 | 2024-05-12 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
226 | 2024-05-13 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
227 | 2024-05-14 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
228 | 2024-05-15 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
229 | 2024-05-16 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
230 | 2024-05-17 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
231 | 2024-05-18 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
232 | 2024-05-19 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
233 | 2024-05-20 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
234 | 2024-05-21 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
235 | 2024-05-22 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
236 | 2024-05-23 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
237 | 2024-05-24 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
238 | 2024-05-25 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
239 | 2024-05-26 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
240 | 2024-05-27 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
241 | 2024-05-28 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
242 | 2024-05-29 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
243 | 2024-05-30 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
244 | 2024-05-31 | 2024 | 2024 | Year_2 | Year_2 | May-24 | 31 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
245 | 2024-06-01 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
246 | 2024-06-02 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
247 | 2024-06-03 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
248 | 2024-06-04 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 | 16:30 | 23:00 | MOP
249 | 2024-06-05 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | 5:30 | 9:30 |  |  | MOP |  | One tractor breakdown
250 | 2024-06-06 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
251 | 2024-06-07 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
252 | 2024-06-08 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
253 | 2024-06-09 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
254 | 2024-06-10 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
255 | 2024-06-11 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
256 | 2024-06-12 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP |  | One tractor breakdown
257 | 2024-06-13 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
258 | 2024-06-14 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
259 | 2024-06-15 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
260 | 2024-06-16 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
261 | 2024-06-17 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
262 | 2024-06-18 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
263 | 2024-06-19 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
264 | 2024-06-20 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
265 | 2024-06-21 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
266 | 2024-06-22 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
267 | 2024-06-23 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
268 | 2024-06-24 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
269 | 2024-06-25 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
270 | 2024-06-26 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning was stopped at the site yesterday because module cleaning was done by rain.
271 | 2024-06-27 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
272 | 2024-06-28 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
273 | 2024-06-29 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning was stopped at the site yesterday because module cleaning was done by rain.
274 | 2024-06-30 | 2024 | 2024 | Year_2 | Year_2 | Jun-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
275 | 2024-07-01 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
276 | 2024-07-02 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
277 | 2024-07-03 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
278 | 2024-07-04 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning was stopped at the site yesterday due to heavy rain
279 | 2024-07-05 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 13.40mm Rain fall at Site
280 | 2024-07-06 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 53.40mm Rain fall at Site
281 | 2024-07-07 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 180.20mm Rain fall at Site
282 | 2024-07-08 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
283 | 2024-07-09 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
284 | 2024-07-10 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
285 | 2024-07-11 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 111.20mm Rain fall at Site
286 | 2024-07-12 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
287 | 2024-07-13 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 36.0mm rainfall at site
288 | 2024-07-14 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
289 | 2024-07-15 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Rain at Site
290 | 2024-07-16 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 10250 |  |  | 16:30 | 23:00 | MOP
291 | 2024-07-17 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
292 | 2024-07-18 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
293 | 2024-07-19 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 15.2mm rainfall at site
294 | 2024-07-20 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
295 | 2024-07-21 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
296 | 2024-07-22 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
297 | 2024-07-23 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 3.20mm rainfall at site
298 | 2024-07-24 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | light Rain at Site
299 | 2024-07-25 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
300 | 2024-07-26 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 2.2mm rainfall at site
301 | 2024-07-27 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 22.2mm rainfall at site
302 | 2024-07-28 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
303 | 2024-07-29 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
304 | 2024-07-30 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
305 | 2024-07-31 | 2024 | 2024 | Year_2 | Year_2 | Jul-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 7.80mm rainfall at site
306 | 2024-08-01 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | light Rain at Site
307 | 2024-08-02 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
308 | 2024-08-03 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
309 | 2024-08-04 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 12.2 mm rainfall at Site
310 | 2024-08-05 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 9.20mm rainfall at site
311 | 2024-08-06 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
312 | 2024-08-07 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 6.60mm rainfall at site
313 | 2024-08-08 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 27.60mm rainfall at site
314 | 2024-08-09 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 6.8mm rainfall at site
315 | 2024-08-10 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 4.5mm rainfall at site
316 | 2024-08-11 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 12.6mm rainfall at site
317 | 2024-08-12 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 38.2mm rainfall at site
318 | 2024-08-13 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 6.8mm rainfall at site
319 | 2024-08-14 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 13.6mm rainfall at site
320 | 2024-08-15 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 8.2mm rainfall at site
321 | 2024-08-16 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000
322 | 2024-08-17 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.8 mm rainfall at site
323 | 2024-08-18 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.9 mm rainfall at site
324 | 2024-08-19 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 15.8mm rainfall at site
325 | 2024-08-20 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.6mm rainfall at site
326 | 2024-08-21 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
327 | 2024-08-22 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000
328 | 2024-08-23 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 14.6mm rainfall at site
329 | 2024-08-24 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000
330 | 2024-08-25 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 7mm rainfall at site
331 | 2024-08-26 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.2mm rainfall at site
332 | 2024-08-27 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 4.2mm rainfall at site
333 | 2024-08-28 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 8.0mm rainfall at site
334 | 2024-08-29 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 0.2mm rainfall at site
335 | 2024-08-30 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | 8.4mm rainfall at site
336 | 2024-08-31 | 2024 | 2024 | Year_2 | Year_2 | Aug-24 | 31 |  |  | Blk8: 6000 | 6000
337 | 2024-09-01 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
338 | 2024-09-02 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:30 | 23:00 | MOP
339 | 2024-09-03 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | 23.20mm rainfall at site
340 | 2024-09-04 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | 42.40mm rainfall at site
341 | 2024-09-05 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | 2.6mm rainfall at site
342 | 2024-09-06 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000 | [6 empty] | 144.4mm rainfall at site
343 | 2024-09-07 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
344 | 2024-09-08 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
345 | 2024-09-09 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
346 | 2024-09-10 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
347 | 2024-09-11 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
348 | 2024-09-12 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
349 | 2024-09-13 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
350 | 2024-09-14 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
351 | 2024-09-15 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
352 | 2024-09-16 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
353 | 2024-09-17 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
354 | 2024-09-18 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
355 | 2024-09-19 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
356 | 2024-09-20 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
357 | 2024-09-21 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
358 | 2024-09-22 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
359 | 2024-09-23 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
360 | 2024-09-24 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
361 | 2024-09-25 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
362 | 2024-09-26 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
363 | 2024-09-27 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
364 | 2024-09-28 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
365 | 2024-09-29 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
366 | 2024-09-30 | 2024 | 2024 | Year_2 | Year_2 | Sep-24 | 30 |  |  | Blk8: 6000 | 6000
367 | 2024-10-01 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
368 | 2024-10-02 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
369 | 2024-10-03 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
370 | 2024-10-04 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
371 | 2024-10-05 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
372 | 2024-10-06 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
373 | 2024-10-07 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
374 | 2024-10-08 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
375 | 2024-10-09 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
376 | 2024-10-10 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
377 | 2024-10-11 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
378 | 2024-10-12 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
379 | 2024-10-13 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
380 | 2024-10-14 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
381 | 2024-10-15 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
382 | 2024-10-16 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
383 | 2024-10-17 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
384 | 2024-10-18 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
385 | 2024-10-19 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
386 | 2024-10-20 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
387 | 2024-10-21 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
388 | 2024-10-22 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
389 | 2024-10-23 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
390 | 2024-10-24 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
391 | 2024-10-25 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
392 | 2024-10-26 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
393 | 2024-10-27 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
394 | 2024-10-28 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
395 | 2024-10-29 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
396 | 2024-10-30 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
397 | 2024-10-31 | 2024 | 2024 | Year_2 | Year_2 | Oct-24 | 31 |  |  | Blk8: 6000 | 6000
398 | 2024-11-01 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
399 | 2024-11-02 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
400 | 2024-11-03 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
401 | 2024-11-04 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
402 | 2024-11-05 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
403 | 2024-11-06 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
404 | 2024-11-07 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
405 | 2024-11-08 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
406 | 2024-11-09 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
407 | 2024-11-10 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
408 | 2024-11-11 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP |  | Tractor breakdown
409 | 2024-11-12 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
410 | 2024-11-13 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
411 | 2024-11-14 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
412 | 2024-11-15 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
413 | 2024-11-16 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP |  | one tractor breakdown
414 | 2024-11-17 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP |  | one tractor breakdown
415 | 2024-11-18 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP |  | one tractor breakdown
416 | 2024-11-19 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP |  | one tractor breakdown
417 | 2024-11-20 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
418 | 2024-11-21 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
419 | 2024-11-22 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 |  |  | 16:00 | 19:00 | MOP
420 | 2024-11-23 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
421 | 2024-11-24 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
422 | 2024-11-25 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
423 | 2024-11-26 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
424 | 2024-11-27 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
425 | 2024-11-28 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
426 | 2024-11-29 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
427 | 2024-11-30 | 2024 | 2024 | Year_2 | Year_2 | Nov-24 | 30 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
428 | 2024-12-01 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
429 | 2024-12-02 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
430 | 2024-12-03 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
431 | 2024-12-04 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
432 | 2024-12-05 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
433 | 2024-12-06 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
434 | 2024-12-07 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
435 | 2024-12-08 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
436 | 2024-12-09 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
437 | 2024-12-10 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
438 | 2024-12-11 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
439 | 2024-12-12 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
440 | 2024-12-13 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
441 | 2024-12-14 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
442 | 2024-12-15 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
443 | 2024-12-16 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
444 | 2024-12-17 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
445 | 2024-12-18 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
446 | 2024-12-19 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
447 | 2024-12-20 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
448 | 2024-12-21 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
449 | 2024-12-22 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
450 | 2024-12-23 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
451 | 2024-12-24 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
452 | 2024-12-25 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
453 | 2024-12-26 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
454 | 2024-12-27 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
455 | 2024-12-28 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
456 | 2024-12-29 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
457 | 2024-12-30 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
458 | 2024-12-31 | 2024 | 2024 | Year_2 | Year_2 | Dec-24 | 31 |  |  | Blk8: 6000 | 17250 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
459 | 2025-01-01 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Yesterday module cleaning stopped because the vendor did not come due to the New Year.
460 | 2025-01-02 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
461 | 2025-01-03 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 14250 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
462 | 2025-01-04 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
463 | 2025-01-05 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
464 | 2025-01-06 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
465 | 2025-01-07 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
466 | 2025-01-08 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
467 | 2025-01-09 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
468 | 2025-01-10 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
469 | 2025-01-11 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
470 | 2025-01-12 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
471 | 2025-01-13 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
472 | 2025-01-14 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
473 | 2025-01-15 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
474 | 2025-01-16 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
475 | 2025-01-17 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
476 | 2025-01-18 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
477 | 2025-01-19 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
478 | 2025-01-20 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
479 | 2025-01-21 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
480 | 2025-01-22 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
481 | 2025-01-23 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning stopped that day due to bad weather.
482 | 2025-01-24 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
483 | 2025-01-25 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
484 | 2025-01-26 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
485 | 2025-01-27 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
486 | 2025-01-28 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
487 | 2025-01-29 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
488 | 2025-01-30 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
489 | 2025-01-31 | 2024 | 2025 | Year_2 | Year_2 | Jan-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
490 | 2025-02-01 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
491 | 2025-02-02 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
492 | 2025-02-03 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
493 | 2025-02-04 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
494 | 2025-02-05 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
495 | 2025-02-06 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
496 | 2025-02-07 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
497 | 2025-02-08 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
498 | 2025-02-09 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning stopped that day due to vendor home family function.
499 | 2025-02-10 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
500 | 2025-02-11 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | [6 empty] | Cleaning stopped that day due to vendor home family function.
501 | 2025-02-12 | 2024 | 2025 | Year_2 | Year_2 | Feb-25 | 28 |  |  | Blk8: 6000 | 6000
502 | 2025-02-13 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
503 | 2025-02-14 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
504 | 2025-02-15 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
505 | 2025-02-16 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
506 | 2025-02-17 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
507 | 2025-02-18 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
508 | 2025-02-19 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
509 | 2025-02-20 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
510 | 2025-02-21 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
511 | 2025-02-22 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
512 | 2025-02-23 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
513 | 2025-02-24 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
514 | 2025-02-25 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
515 | 2025-02-26 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
516 | 2025-02-27 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
517 | 2025-02-28 | 2025 | 2025 |  |  | Feb-25 | 28 |  |  | Blk8: 6000 | 6000
518 | 2025-03-01 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
519 | 2025-03-02 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
520 | 2025-03-03 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
521 | 2025-03-04 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
522 | 2025-03-05 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
523 | 2025-03-06 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
524 | 2025-03-07 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | [6 empty] | Function at vendor's home
525 | 2025-03-08 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
526 | 2025-03-09 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
527 | 2025-03-10 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
528 | 2025-03-11 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
529 | 2025-03-12 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
530 | 2025-03-13 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
531 | 2025-03-14 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
532 | 2025-03-15 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
533 | 2025-03-16 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
534 | 2025-03-17 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
535 | 2025-03-18 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
536 | 2025-03-19 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
537 | 2025-03-20 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
538 | 2025-03-21 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
539 | 2025-03-22 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
540 | 2025-03-23 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
541 | 2025-03-24 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
542 | 2025-03-25 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000 | 7:00 | 10:00 | 16:00 | 19:00 | MOP
543 | 2025-03-26 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
544 | 2025-03-27 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
545 | 2025-03-28 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
546 | 2025-03-29 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
547 | 2025-03-30 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
548 | 2025-03-31 | 2025 | 2025 |  |  | Mar-25 | 31 |  |  | Blk8: 6000 | 6000
549 | 2025-04-01 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
550 | 2025-04-02 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
551 | 2025-04-03 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
552 | 2025-04-04 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
553 | 2025-04-05 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
554 | 2025-04-06 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
555 | 2025-04-07 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
556 | 2025-04-08 | 2026 | 2025 |  |  | Apr-25 | 30 |  |  | Blk8: 6000 | 6000
557 | 2025-04-09 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk8: 6000 | 6000
558 | 2025-04-10 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk4: 4200; Blk6: 6600; Blk7: 6000; Blk8: 6000 | 22800 | 9:00 | 12:00 | 14:00 | 18:00
559 | 2025-04-11 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7200 | 7450 | 7800 | 7250 |  | 7200 |  | 6000 | 42900 | 9:00 | 12:00 | 14:00 | 18:00
560 | 2025-04-12 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 6500 | 7550 | 7100 | 7300 | 6900 |  |  | 6000 | 41350 | 9:00 | 12:00 | 14:00 | 18:00
561 | 2025-04-13 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7100 | 7200 | 6000 |  | 7500 | 7700 | 7800 | 6000 | 49300 | 9:00 | 12:00 | 14:00 | 18:00
562 | 2025-04-14 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 | 7800 |  |  | 9000 | 6500 | 7250 | 5500 | 43650 | 9:00 | 12:00 | 14:00 | 18:00
563 | 2025-04-15 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 | 7450 | 5600 | 7250 | 6300 | 5000 | 0 | 4100 | 43300 | 9:00 | 12:00 | 14:00 | 18:00
564 | 2025-04-16 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 | 6750 | 7800 | 6500 | 7600 |  |  | 7600 | 49200 | 9:00 | 12:00 | 14:00 | 18:00
565 | 2025-04-17 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning |  | 7600 | 7600 | 6300 | 6300 |  |  | 7000 | 34800 | 9:00 | 12:00 | 14:00 | 18:00
566 | 2025-04-18 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7800 | 7600 | 7500 | 6500 | 7100 |  |  | 6000 | 42500 | 9:00 | 12:00 | 14:00 | 18:00
567 | 2025-04-19 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 8580 | 8640 | 10080 |  | 8880 | 9240 | 8700 | 6000 | 45100 | 9:00 | 12:00 | 14:00 | 18:00
568 | 2025-04-20 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 |  | 9360 |  | 9180 | 9360 | 9360 | 6000 | 38650 | 9:00 | 12:00 | 14:00 | 18:00
569 | 2025-04-21 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 5760 | 9360 | 10080 |  | 9360 | 9120 | 9000 | 6000 | 46300 | 9:00 | 12:00 | 14:00 | 18:00
570 | 2025-04-22 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7600 | 6000 | 7600 | 7250 | 7200 | 7600 |  | 6000 | 49250 | 9:00 | 12:00 | 14:00 | 18:00
571 | 2025-04-23 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 6200 | 6000 | 6000 | 8640 | 7500 | 7920 | 7000 | 0 | 49260 | 9:00 | 12:00 | 14:00 | 18:00
572 | 2025-04-24 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7200 | 6000 | 5500 | 9900 | 7200 | 8640 |  | 0 | 44440 | 9:00 | 12:00 | 14:00 | 18:00
573 | 2025-04-25 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7200 | 6000 | 6800 | 7500 | 7400 | 6200 | 6800 | 0 | 47900 | 9:00 | 12:00 | 14:00 | 18:00
574 | 2025-04-26 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 6200 | 6800 | 5750 | 6200 | 6900 | 6200 | 5100 | 0 | 43150 | 9:00 | 12:00 | 14:00 | 18:00
575 | 2025-04-27 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | 7200 | 7200 | 6000 | 7400 | 7200 | 6600 | 7200 | 0 | 48800 | 9:00 | 12:00 | 14:00 | 18:00
576 | 2025-04-28 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk2: 0; Blk3: 0 | 0 | 9:00 | 12:00 | 14:00 | 18:00
577 | 2025-04-29 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk2: 3600; Blk3: 4800; Blk8: 6000 | 14400
578 | 2025-04-30 | 2026 | 2025 |  |  | Apr-25 | 30 |  | Robot Cleaning | Blk2: 3250; Blk6: 7200; Blk8: 110 | 10560 | 9:00 | 12:00 | 14:00 | 18:00
579 | 2025-05-01 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | 7200 |  |  | 3600 | 7200 | 2500 | 6600 |  | 27100 | 9:00 | 12:00 | 14:00 | 18:00
580 | 2025-05-02 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7500; Blk4: 5450; Blk5: 6250; Blk6: 6600 | 25800 | [6 empty] | RO
581 | 2025-05-03 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7050; Blk4: 6600; Blk5: 7150; Blk7: 5500 | 26300
582 | 2025-05-04 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (1 to 11),Robot2 (73 to 79),Robot 3(80 to 86) & Robot 4 (87 to 92)
583 | 2025-05-05 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (12 to 18),Robot2 (70 to 73),Robot 3(93 to 98) & Robot 4 (99 to104)
584 | 2025-05-06 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (19 to 33),Robot2 (81 to 86),Robot 3(105 to 112) & Robot 4 (113 to126)
585 | 2025-05-07 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (22 to 33),Robot2 (34 to 40),Robot 3(80 to 92) & Robot 4 (127 to144)
586 | 2025-05-08 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (40 to 55),Robot2 (73 to 77),Robot 3(93 to 98) & Robot 4 (137 to 166)
587 | 2025-05-09 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (132 to 152),Robot2 (56 to 64),Robot 3(68 to 72) & Robot 4 (99 to 104)
588 | 2025-05-10 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (57 to 63),Robot2 (64 to 67),Robot 3(95 to 111) & Robot 4 (172 to 185)
589 | 2025-05-11 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (50 to 56),Robot2 (68to 74),Robot 3(123 to 131) & Robot 4 (110 to 116)
590 | 2025-05-12 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (26 to 49),Robot2 (2 to 17),Robot 3(103 to 110) & Robot 4 (64 to 69)
591 | 2025-05-13 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (44 to 59),Robot2 (17 to 34),Robot 3(67 to 70) & Robot 4 (97 to 102)
592 | 2025-05-14 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (40 to 55),Robot2 (76 to 79),Robot 3(87 to 91) & Robot 4 (104 to 113)
593 | 2025-05-15 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (62 to 65),Robot2 (81 to 84),Robot 3(87 to 90) & Robot 4 (98 to 102)
594 | 2025-05-16 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0 | [6 empty] | 4 Robot Running (Robot1 (01 to 08),Robot2 (158 to165),Robot 3(148 to 157) & Robot 4 (104 to 110)
595 | 2025-05-17 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 5500; Blk4: 3250; Blk6: 4000; Blk8: 2250 | 15000 | 9:00 | 12:00 | 14:00 | 18:00
596 | 2025-05-18 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7750; Blk4: 7250; Blk6: 7450; Blk8: 3750 | 26200 | 9:00 | 12:00 | 14:00 | 18:00
597 | 2025-05-19 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7450; Blk4: 7550; Blk6: 7250; Blk8: 5250 | 27500 | 9:00 | 12:00 | 14:00 | 18:00
598 | 2025-05-20 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 7650; Blk4: 1400; Blk5: 5400; Blk8: 5100 | 19550 | 9:00 | 12:00 | 14:00 | 18:00
599 | 2025-05-21 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning |  | 7400 | 7700 |  | 5400 | 1700 | 7750 |  | 29950 | 9:00 | 12:00 | 14:00 | 18:00
600 | 2025-05-22 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 4600; Blk3: 5950; Blk5: 7000; Blk7: 5100 | 22650 | 9:00 | 12:00 | 14:00 | 18:00
601 | 2025-05-23 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk5: 3900; Blk7: 3250; Blk8: 3500 | 10650 | 9:00 | 12:00 | 14:00 | 18:00
602 | 2025-05-24 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk4: 3000; Blk5: 3650; Blk8: 3400 | 10050 | 9:00 | 12:00 | 14:00 | 18:00
603 | 2025-05-25 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk1: 7600; Blk4: 7600; Blk8: 7550 | 22750 | 9:00 | 12:00 | 14:00 | 18:00
604 | 2025-05-26 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0
605 | 2025-05-27 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0
606 | 2025-05-28 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 7000; Blk3: 3500; Blk5: 5250; Blk7: 4000 | 19750 | 9:00 | 12:00 | 14:00 | 18:00
607 | 2025-05-29 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | [8 empty] | 0
608 | 2025-05-30 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 4400; Blk6: 6900 | 11300 | 9:00 | 12:00 | 14:00 | 18:00
609 | 2025-05-31 | 2026 | 2025 |  |  | May-25 | 31 |  | Robot Cleaning | Blk2: 7000; Blk3: 7250; Blk6: 7000; Blk7: 8250 | 29500 | 9:00 | 12:00 | 14:00 | 18:00
610 | 2025-06-01 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 8250; Blk3: 7250; Blk6: 5400; Blk7: 6600 | 27500 | 9:00 | 12:00 | 14:00 | 18:00
611 | 2025-06-02 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 6000 |  | 6400 | 2400 |  | 6050 | 1100 | 4500 | 26450 | 9:00 | 12:00 | 14:00 | 18:00
612 | 2025-06-03 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk1: 6600; Blk4: 7800; Blk5: 7250; Blk8: 5500 | 27150 | 9:00 | 12:00 | 14:00 | 18:00
613 | 2025-06-04 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk1: 7500; Blk4: 7500; Blk5: 7800; Blk8: 6600 | 29400 | 9:00 | 12:00 | 14:00 | 18:00
614 | 2025-06-05 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 4500 | 7250 | 7200 | 1850 |  | 7800 | 7750 |  | 36350 | 9:00 | 12:00 | 14:00 | 18:00
615 | 2025-06-06 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | [8 empty] | 0
616 | 2025-06-07 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 7800; Blk3: 7200; Blk6: 6500; Blk7: 7200 | 28700 | 9:00 | 12:00 | 14:00 | 18:00
617 | 2025-06-08 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 1300 | 2650 |  |  |  | 6100 | 1100 | 4900 | 16050 | 9:00 | 12:00 | 14:00 | 18:00
618 | 2025-06-09 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 7300 |  | 4800 | 3250 | 8600 |  |  | 5000 | 28950 | 9:00 | 12:00 | 14:00 | 18:00
619 | 2025-06-10 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk1: 5800; Blk4: 7300; Blk5: 8000; Blk8: 6750 | 27850 | 9:00 | 12:00 | 14:00 | 18:00
620 | 2025-06-11 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 5700 | 2000 | 4050 | 7200 | 3900 |  |  |  | 22850 | 9:00 | 12:00 | 14:00 | 18:00
621 | 2025-06-12 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning |  | 7200 | 7700 | 1800 |  | 5450 | 7000 |  | 29150 | 9:00 | 12:00 | 14:00 | 18:00
622 | 2025-06-13 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 7500; Blk3: 7600; Blk6: 7700; Blk7: 7250 | 30050 | 9:00 | 12:00 | 14:00 | 18:00
623 | 2025-06-14 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 4000 | 3000 |  | 7500 |  | 7700 | 2300 | 6300 | 30800 | 9:00 | 12:00 | 14:00 | 18:00
624 | 2025-06-15 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk1: 8000; Blk4: 9700; Blk5: 7750; Blk8: 6000 | 31450 | 9:00 | 12:00 | 14:00 | 18:00
625 | 2025-06-16 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 8000 |  |  | 3150 | 6050 | 4500 |  | 6500 | 28200 | 9:00 | 12:00 | 14:00 | 18:00
626 | 2025-06-17 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 7500; Blk5: 6800; Blk6: 7550; Blk7: 7100 | 28950 | 9:00 | 12:00 | 14:00 | 18:00
627 | 2025-06-18 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | Blk2: 7500; Blk3: 7400; Blk6: 7600; Blk7: 7150 | 29650 | 9:00 | 12:00 | 14:00 | 18:00
628 | 2025-06-19 | 2026 | 2025 |  |  | Jun-25 | 30 |  | Robot Cleaning | 2500 | 4500 |  |  | 6600 | 1100 | 6500 |  | 21200 | 9:00 | 12:00 | 14:00 | 18:00
Formulas:
Days = DAY(EOMONTH(MC[[#This Row],[Month Year]],0))
Date = [Date, row above]+1

## Raw_Data
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261 | 262 | 263 | 264 | 265 | 266 | 267 | 268 | 269 | 270 | 271 | 272 | 273 | 274 | 275 | 276 | 277 | 278 | 279 | 280 | 281 | 282 | 283 | 284 | 285 | 286 | 287 | 288 | 289 | 290 | 291 | 292 | 293 | 294 | 295 | 296 | 297 | 298 | 299 | 300 | 301 | 302
Date | Finacial Year | Calendor Year | Contrcatual Year | Operating Year | Month Year | Days | Plant DC Capcity (MW) | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | BLK1_INV1 | BLK1_INV2 | BLK1_INV3 | BLK1_INV4 | BLK1_INV5 | BLK1_INV6 | BLK1_INV7 | BLK1_INV8 | BLK1_INV9 | BLK1_INV10 | BLK1_INV11 | BLK1_INV12 | BLK1_INV13 | BLK1_INV14 | BLK1_INV15 | BLK1_INV16 | BLK1_INV17 | BLK1_INV18 | BLK1_INV19 | BLK1_INV20 | BLK1_INV21 | BLK1_INV22 | BLK1_INV23 | BLK1_INV24 | BLK1_INV25 | BLK1_INV26 | BLK1_INV27 | BLK1_INV28 | BLK1_INV29 | BLK1_INV30 | BLK1_INV31 | BLK1_INV32 | BLK2_INV1 | BLK2_INV2 | BLK2_INV3 | BLK2_INV4 | BLK2_INV5 | BLK2_INV6 | BLK2_INV7 | BLK2_INV8 | BLK2_INV9 | BLK2_INV10 | BLK2_INV11 | BLK2_INV12 | BLK2_INV13 | BLK2_INV14 | BLK2_INV15 | BLK2_INV16 | BLK2_INV17 | BLK2_INV18 | BLK2_INV19 | BLK2_INV20 | BLK2_INV21 | BLK2_INV22 | BLK2_INV23 | BLK2_INV24 | BLK2_INV25 | BLK2_INV26 | BLK2_INV27 | BLK2_INV28 | BLK2_INV29 | BLK2_INV30 | BLK2_INV31 | BLK2_INV32 | BLK3_INV1 | BLK3_INV2 | BLK3_INV3 | BLK3_INV4 | BLK3_INV5 | BLK3_INV6 | BLK3_INV7 | BLK3_INV8 | BLK3_INV9 | BLK3_INV10 | BLK3_INV11 | BLK3_INV12 | BLK3_INV13 | BLK3_INV14 | BLK3_INV15 | BLK3_INV16 | BLK3_INV17 | BLK3_INV18 | BLK3_INV19 | BLK3_INV20 | BLK3_INV21 | BLK3_INV22 | BLK3_INV23 | BLK3_INV24 | BLK3_INV25 | BLK3_INV26 | BLK3_INV27 | BLK3_INV28 | BLK3_INV29 | BLK3_INV30 | BLK3_INV31 | BLK4_INV1 | BLK4_INV2 | BLK4_INV3 | BLK4_INV4 | BLK4_INV5 | BLK4_INV6 | BLK4_INV7 | BLK4_INV8 | BLK4_INV9 | BLK4_INV10 | BLK4_INV11 | BLK4_INV12 | BLK4_INV13 | BLK4_INV14 | BLK4_INV15 | BLK4_INV16 | BLK4_INV17 | BLK4_INV18 | BLK4_INV19 | BLK4_INV20 | BLK4_INV21 | BLK4_INV22 | BLK4_INV23 | BLK4_INV24 | BLK4_INV25 | BLK4_INV26 | BLK4_INV27 | BLK4_INV28 | BLK4_INV29 | BLK4_INV30 | BLK4_INV31 | BLK5_INV1 | BLK5_INV2 | BLK5_INV3 | BLK5_INV4 | BLK5_INV5 | BLK5_INV6 | BLK5_INV7 | BLK5_INV8 | BLK5_INV9 | BLK5_INV10 | BLK5_INV11 | BLK5_INV12 | BLK5_INV13 | BLK5_INV14 | BLK5_INV15 | BLK5_INV16 | BLK5_INV17 | BLK5_INV18 | BLK5_INV19 | BLK5_INV20 | BLK5_INV21 | BLK5_INV22 | BLK5_INV23 | BLK5_INV24 | BLK5_INV25 | BLK5_INV26 | BLK5_INV27 | BLK5_INV28 | BLK5_INV29 | BLK5_INV30 | BLK5_INV31 | BLK5_INV32 | BLK6_INV1 | BLK6_INV2 | BLK6_INV3 | BLK6_INV4 | BLK6_INV5 | BLK6_INV6 | BLK6_INV7 | BLK6_INV8 | BLK6_INV9 | BLK6_INV10 | BLK6_INV11 | BLK6_INV12 | BLK6_INV13 | BLK6_INV14 | BLK6_INV15 | BLK6_INV16 | BLK6_INV17 | BLK6_INV18 | BLK6_INV19 | BLK6_INV20 | BLK6_INV21 | BLK6_INV22 | BLK6_INV23 | BLK6_INV24 | BLK6_INV25 | BLK6_INV26 | BLK6_INV27 | BLK6_INV28 | BLK6_INV29 | BLK6_INV30 | BLK6_INV31 | BLK6_INV32 | BLK7_INV1 | BLK7_INV2 | BLK7_INV3 | BLK7_INV4 | BLK7_INV5 | BLK7_INV6 | BLK7_INV7 | BLK7_INV8 | BLK7_INV9 | BLK7_INV10 | BLK7_INV11 | BLK7_INV12 | BLK7_INV13 | BLK7_INV14 | BLK7_INV15 | BLK7_INV16 | BLK7_INV17 | BLK7_INV18 | BLK7_INV19 | BLK7_INV20 | BLK7_INV21 | BLK7_INV22 | BLK7_INV23 | BLK7_INV24 | BLK7_INV25 | BLK7_INV26 | BLK7_INV27 | BLK7_INV28 | BLK7_INV29 | BLK7_INV30 | BLK7_INV31 | BLK7_INV32 | BLK8_INV1 | BLK8_INV2 | BLK8_INV3 | BLK8_INV4 | BLK8_INV5 | BLK8_INV6 | BLK8_INV7 | BLK8_INV8 | BLK8_INV9 | BLK8_INV10 | BLK8_INV11 | BLK8_INV12 | BLK8_INV13 | BLK8_INV14 | BLK8_INV15 | BLK8_INV16 | BLK8_INV17 | BLK8_INV18 | BLK8_INV19 | BLK8_INV20 | BLK8_INV21 | BLK8_INV22 | BLK8_INV23 | BLK8_INV24 | BLK8_INV25 | BLK8_INV26 | BLK8_INV27 | BLK8_INV28 | AT (°C) 14 Hours | MT (°C) Gen. Hours | WS_Avg (m/s) (24 Hours) | WS_Max (m/s) | Rain (mm) | GHI | POA | GHI_Lost | POA_Lost | 33kV_IC1_ExPort | 33kV_IC1_Import | 33kV_IC2_ExPort | 33kV_IC2_Import | 33kV_IC3_ExPort | 33kV_IC3_Import | 33kV_IC4_ExPort | 33kV_IC4_Import |  | I31kV_PQM_Im | 33kV_IC1_ExPort(KWh) | 33kV_IC1_Import(KWh) | 33kV_IC2_ExPort(KWh) | 33kV_IC2_Import(KWh) | 33kV_IC3_ExPort(KWh) | 33kV_IC3_Import(KWh) | 33kV_IC4_ExPort(kWh) | 33kV_IC4_Import(KWh) | 132kV_PQM_Ex(KWh) | 132kV_PQM_Im(KWh) | 33kV_Net_Ex (kWh) | 132kV_Net_Ex (kWh) | Operating Hours | GHI (KWh/m2)2 | POA(KWh/m2)2 | Amm_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | Inv_Exp(KWh) | WPR_Eac | WPR_Edc | WPR
2025-03-29 | 2025 | 2025 |  |  | Mar-25 | 31 | 66750 | 7:00 | 19:00 | [266 empty] | 54996.705 | 306246841.6003 | 81683.2331 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  |  | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-03-30 | 2025 | 2025 |  |  | Mar-25 | 31 | 66750 | 7:00 | 19:00 | [266 empty] | 55011.744 | 306590465.4889 | 81745.1624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.039 | 343623.8886 | 61.9293 | -15.039 | 343561.9593 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-03-31 | 2025 | 2025 |  |  | Mar-25 | 31 | 66750 | 7:00 | 19:00 | 1590.1 | 1625.2 | 1522.4 | 1520.1 | 1598.4 | 1485.5 | 1544.3 | 1555.5 | 1580.5 | 1513.2 | 1550.6 | 1573 | 1569.8 | 1408.7 | 1504.6 | 1484.1 | 1452.9 | 1468 | 1589.1 | 1590.5 | 1596.5 | 1494.7 | 1541.1 | 1529.8 | 1509.6 | 1605.5 | 1593.4 | 1625.1 | 1594.9 | 1646.2 | 1616.2 | 1543.3 | 1387.5 | 1817.1 | 1398.5 | 1593.3 | 1512.2 | 1457.7 | 1508.8 | 1471.4 | 1478.6 | 1456.7 | 1512.4 | 1529.3 | 1535.4 | 1547.8 | 1567.5 | 1472.3 | 1542.2 | 1494.4 | 1431.4 | 1453.4 | 1610.5 | 1732.5 | 1563.5 | 1613.1 | 1633.3 | 1544.4 | 1634.4 | 1601.2 | 1478.6 | 1625 | 1455 | 1300.5 | 1644.7 | 1649.7 | 1648.2 | 1654.1 | 1502.1 | 1508.6 | 1506.5 | 1492.4 | 1471.1 | 1522.5 | 1602.1 | 1694.3 | 1724.1 | 1445.1 | 1482.4 | 1604.5 | 1541.1 | 1529.1 | 1512.1 | 1523.2 | 1542.2 | 1492.5 | 1529.5 | 1451.4 | 1470.1 | 1472.5 | 1548.5 | 1574.5 | 1540.3 | 1462.6 | 1631.5 | 1470.1 | 1492 | 1511.1 | 1515.1 | 1505.1 | 1538.2 | 1498.1 | 1522.1 | 1474.1 | 1679.1 | 1565.1 | 1740.2 | 1676.5 | 1471.4 | 1613.2 | 1559.1 | 1572.4 | 1620.1 | 1710.4 | 1510.4 | 1484.3 | 1660.1 | 1624.2 | 1628.1 | 1543.3 | 1506.1 | 1645.2 | 1616.2 | 1546.4 | 1456.7 | 1621.1 | 0 | 1403.4 | 1717.1 | 1629 | 1560.1 | 1589.2 | 1582.2 | 1356.6 | 1602 | 1575.4 | 1561.2 | 1548.5 | 1623.5 | 1304.5 | 1635.6 | 1562.3 | 1544.4 | 1524 | 1317 | 1563.3 | 1427.7 | 1449.8 | 1605.7 | 1550.5 | 1650.6 | 1502.2 | 1561.5 | 1507.5 | 1489.4 | 1448.5 | 1461.4 | 1440.4 | 1320 | 1285 | 1540 | 1371 | 1305 | 1408 | 1512 | 1406 | 1360 | 1421 | 1462 | 1375 | 1422 | 1430 | 1597 | 1512 | 1626 | 1413 | 1433 | 1280 | 1732 | 1526 | 1495 | 1584 | 1525 | 1568 | 1524 | 1576 | 1508 | 1524 | 1510 | 1437 | 1419 | 1450 | 1436 | 1429 | 1549 | 1397 | 1292 | 1565 |  |  | 1262 | 1064 | 1532 |  | 1659 | 1454 | 1514 | 1472 | 1495 | 1511 | 1521 | 1531 | 1533 | 1537 | 1550 | 1546 | 1521 | 1729 | 1306 | 1295 | 1033 | 908 | 1084 | 1279 | 1486 | 1676 | 1472 | 1533 | 1555 | 1551 | 1593 | 1618 | 1178 | 1422 | 1293 | 1409 | 1141 |  | 1843 | 1480 | 564 | 1371 | 1421 |  |  | 1266 | 1268 | 1417 | 1250 | 1154 | 30.32 | 40.28 | 1.71 | 6.3 |  | 0 | 7.31 |  |  | 80931088.744 | 281250.305 | 54078351.551 | 61052.203 | 81718077.5 | 185254.507 | 59077703.113 | 55026.783 | 306934089.3774 | 81807.0917 | 80931088.744 | 281250.305 | 54078351.551 | 61052.203 | 81718077.5 | 185254.507 | 59077703.113 | 15.039 | 343623.8886 | 61.9293 | 275277648.854 | 343561.9593 | 12 | 0 | 7.31 | 30.32 | 40.28 | 1.71 | 6.3 | 364093.2
2025-04-01 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1577 | 1616 | 1507 | 1509 | 1568 | 1462 | 1505 | 1498 | 1469 | 1476 | 1539 | 1533 | 1529 | 1371 | 1508 | 1488 | 1398 | 1410 | 1535 | 1600 | 1519 | 1458 | 1565 | 1487 | 1592 | 1580 | 1565 | 1592 | 1557 | 1609 | 1590 | 1504 | 1400 | 1797 | 1399 | 1602 | 1507 | 1442 | 1467 | 1420 | 1465 | 1435 | 1473 | 1487 | 1492 | 1503 | 1621 | 1432 | 1510 | 1470 | 1398 | 1420 | 1560 | 1698 | 1488 | 1598 | 1560 | 1490 | 1590 | 1590 | 1348 | 1610 | 1390 | 1290 | 1350 | 1611 | 1616 | 1423 | 1484 | 1489 | 1263 | 1353 | 1448 | 1511 | 1467 | 1657 | 1680 | 1402 | 1439 | 1565 | 1498 | 1485 | 1468 | 1478 | 1498 | 1457 | 1487 | 1411 | 1410 | 1434 | 1510 | 1510 | 1502 | 1390 | 1610 | 1425 | 1446 | 1469 | 1470 | 1363 | 1496 | 1451 | 1474 | 1427 | 1641 | 1321 | 1692 | 1630 | 1427 | 1631 | 1516 | 1594 | 1637 | 1672 | 1453 | 1495 | 1626 | 1546 | 1594 | 1476 | 1503 | 1591 | 1536 | 1414 | 1496 | 1590 | 0 | 1377 | 1680 | 1678 | 1531 | 1554 | 1533 | 1190 | 1591 | 1481 | 1564 | 1514 | 1580 | 1367 | 1406 | 1483 | 1488 | 1506 | 1285 | 1676 | 1474 | 1340 | 1556 | 1563 | 1603 | 1461 | 1611 | 1509 | 1427 | 1410 | 1410 | 1403 | 1291 | 1257 | 1498 | 1334 | 1271 | 1370 | 1490 | 1390 | 1337 | 1580 | 1430 | 1336 | 1386 | 1391 | 1556 | 1471 | 1591 | 1470 | 1453 | 1311 | 1720 | 1521 | 1502 | 1547 | 1481 | 1526 | 1548 | 1544 | 1544 | 1548 | 1469 | 1396 | 1372 | 1404 | 1390 | 1381 | 1505 | 1354 | 1255 | 1525 |  |  | 1299 | 1048 | 1492 |  | 1618 | 1390 | 1468 | 1417 | 1461 | 1462 | 1476 | 1488 | 1488 | 1496 | 1506 | 1501 | 1478 | 1691 | 1338 | 1257 | 1080 | 930 | 998 | 1181 | 1368 | 1550 | 1350 | 1406 | 1490 | 1520 | 1480 | 1491 | 1111 | 1313 | 1188 | 1298 | 1052 |  | 1760 | 1470 | 590 | 1380 | 1298 |  |  | 1385 | 1184 | 1410 | 1230 | 1150 | 25.08 | 40.95 | 1.76 | 5.3 |  | 0 | 7.18 |  |  | 81024220.217 | 281265.893 | 54170029.175 | 61064.408 | 81809917.614 | 185282.999 | 59149543.494 | 55041.822 | 307277713.266 | 81869.021 | 93131.473 | 15.588 | 91677.624 | 12.205 | 91840.114 | 28.492 | 71840.381 | 15.039 | 343623.8886 | 61.9293 | 348418.268 | 343561.9593 | 12 | 0 | 7.18 | 25.08 | 40.95 | 1.76 | 5.3 | 354559
2025-04-02 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1496 | 1535 | 1432 | 1434 | 1510 | 1388 | 1470 | 1398 | 1390 | 1404 | 1498 | 1454 | 1451 | 1304 | 1370 | 1415 | 1352 | 1360 | 1511 | 1547 | 1439 | 1384 | 1583 | 1480 | 1562 | 1558 | 1551 | 1580 | 1546 | 1599 | 1526 | 1490 | 1330 | 1703 | 1370 | 1522 | 1467 | 1380 | 1409 | 1449 | 1402 | 1381 | 1414 | 1427 | 1418 | 1439 | 1538 | 1358 | 1480 | 1410 | 1370 | 1378 | 1507 | 1561 | 1480 | 1490 | 1510 | 1404 | 1568 | 1520 | 1413 | 1563 | 1340 | 1300 | 1410 | 1573 | 1581 | 1410 | 1436 | 1444 | 1278 | 1319 | 1390 | 1464 | 1498 | 1571 | 1594 | 1333 | 1364 | 1499 | 1418 | 1406 | 1390 | 1402 | 1423 | 1389 | 1438 | 1361 | 1420 | 1394 | 1490 | 1490 | 1456 | 1300 | 1582 | 1351 | 1371 | 1399 | 1393 | 1340 | 1417 | 1374 | 1397 | 1355 | 1583 | 1290 | 1623 | 1547 | 1351 | 1581 | 1472 | 1511 | 1562 | 1586 | 1381 | 1416 | 1544 | 1519 | 1543 | 1432 | 1468 | 1549 | 1507 | 1387 | 1456 | 1577 | 0 | 1341 | 1646 | 1631 | 1498 | 1510 | 1488 | 1178 | 1507 | 1490 | 1482 | 1387 | 1495 | 1292 | 1398 | 1411 | 1413 | 1426 | 1278 | 1586 | 1396 | 1274 | 1492 | 1487 | 1529 | 1414 | 1531 | 1422 | 1391 | 1369 | 1387 | 1333 | 1290 | 1292 | 1445 | 1282 | 1360 | 1378 | 1478 | 1398 | 1335 | 1501 | 1398 | 1378 | 1390 | 1321 | 1477 | 1397 | 1508 | 1392 | 1373 | 1242 | 1630 | 1441 | 1419 | 1464 | 1505 | 1445 | 1467 | 1510 | 1460 | 1467 | 1393 | 1410 | 1296 | 1320 | 1313 | 1305 | 1425 | 1282 | 1188 | 1446 |  |  | 1265 | 990 | 1410 |  | 1534 | 1310 | 1390 | 1339 | 1387 | 1387 | 1401 | 1412 | 1411 | 1422 | 1470 | 1490 | 1460 | 1710 | 1272 | 1186 | `1031 | 910 | 992 | 1173 | 1363 | 1546 | 1344 | 1400 | 1510 | 1498 | 1472 | 1489 | 1123 | 1303 | 1177 | 1289 | 1043 |  | 1175 | 1450 | 690 | 1310 | 1290 |  |  | 1368 | 1012 | 1390 | 1190 | 1158 | 26.5 | 39.7 | 1.9 | 5.9 |  | 0 | 6.87 |  |  | 81114928.986 | 281280.784 | 54257592.783 | 61077.806 | 81897649.596 | 185319.828 | 59218660.672 | 55054.694 | 307612421.636 | 81927.037 | 90708.769 | 14.891 | 87563.608 | 13.398 | 87731.982 | 36.829 | 69117.178 | 12.872 | 334708.37 | 58.016 | 335043.547 | 334650.354 | 12 | 0 | 6.87 | 26.5 | 39.7 | 1.9 | 5.9 | 341179
2025-04-03 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1342 | 1375 | 1283 | 1281 | 1292 | 1245 | 1134 | 1189 | 1199 | 1258 | 1313 | 1304 | 1299 | 1163 | 1230 | 1265 | 1211 | 1229 | 1379 | 1401 | 1308 | 1283 | 1422 | 1304 | 1409 | 1404 | 1397 | 1423 | 1405 | 1447 | 1387 | 1391 | 1197 | 1534 | 1194 | 1444 | 1226 | 1243 | 1283 | 1315 | 1263 | 1248 | 1296 | 1302 | 1295 | 1321 | 1398 | 1221 | 1203 | 1218 | 1166 | 1155 | 1331 | 1406 | 1187 | 1362 | 1231 | 1264 | 1411 | 1355 | 1272 | 1406 | 1300 | 1280 | 1156 | 1405 | 1439 | 1253 | 1289 | 1294 | 1078 | 1191 | 1257 | 1315 | 1285 | 1450 | 1467 | 1202 | 1249 | 1382 | 1301 | 1305 | 1298 | 1309 | 1303 | 1268 | 1315 | 1247 | 1154 | 1274 | 1324 | 690 | 1331 | 1125 | 1393 | 1248 | 1258 | 1284 | 1251 | 1184 | 1318 | 1285 | 1306 | 1273 | 1448 | 1152 | 1497 | 1365 | 1244 | 1448 | 1363 | 1358 | 1409 | 1422 | 1262 | 1272 | 1388 | 1373 | 1420 | 1286 | 1321 | 1395 | 1356 | 1254 | 1327 | 1431 | 521 | 775 | 1490 | 1460 | 1322 | 1326 | 1306 | 975 | 1346 | 1178 | 1325 | 1240 | 1338 | 1175 | 1196 | 1296 | 1265 | 1274 | 1108 | 1449 | 1293 | 1181 | 1372 | 1384 | 1412 | 1291 | 1375 | 1291 | 1265 | 1251 | 1261 | 1202 | 1151 | 1157 | 1293 | 1145 | 1076 | 1165 | 1144 | 966 | 1197 | 1343 | 1215 | 1137 | 1184 | 1185 | 1323 | 1248 | 1345 | 1242 | 1228 | 1109 | 1456 | 1286 | 1267 | 1313 | 1249 | 1290 | 1310 | 1308 | 1303 | 1308 | 1246 | 1184 | 1164 | 1194 | 1178 | 1173 | 1284 | 1153 | 1070 | 1302 |  |  | 1146 | 895 | 1273 |  | 1389 | 1124 | 1250 | 1203 | 1252 | 1249 | 1259 | 1269 | 1269 | 1278 | 1279 | 1277 | 1271 | 1444 | 1143 | 1062 | 919 | 762 | 894 | 1057 | 1225 | 1391 | 1207 | 1256 | 1400 | 1385 | 1338 | 1346 | 1041 | 1174 | 1058 | 1162 | 939 |  | 1265 | 1180 | 700 | 1087 | 1186 |  |  | 1012 | 815 | 1049 | 1180 | 1110 | 25.78 | 32 | 2.63 | 5.3 |  | 0 |  |  |  | 81196825.693 | 281293.339 | 54337502.169 | 61098.808 | 81976932.974 | 185359.42 | 59281082.425 | 55074.059 | 307915539.166 | 81986.655 | 81896.707 | 12.555 | 79909.386 | 21.002 | 79283.378 | 39.592 | 62421.753 | 19.365 | 303117.53 | 59.618 | 161772.536 | 303057.912 | 12 | 0 | 0 | 25.78 | 32 | 2.63 | 5.3 | 305040
2025-04-04 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1401 | 1428 | 1331 | 1332 | 1354 | 1301 | 1170 | 1235 | 1243 | 1311 | 1368 | 1770 | 1355 | 1216 | 1282 | 1320 | 1250 | 1273 | 1420 | 1445 | 1349 | 1296 | 1476 | 1345 | 1450 | 1445 | 1435 | 1472 | 1440 | 1489 | 1460 | 1389 | 1241 | 1624 | 1226 | 1393 | 1267 | 1272 | 1302 | 1378 | 1289 | 1273 | 1311 | 1318 | 1424 | 1349 | 1441 | 1256 | 1264 | 1286 | 1232 | 1195 | 1373 | 1478 | 1241 | 1438 | 1263 | 1306 | 1442 | 1384 | 1290 | 1449 | 1350 | 1380 | 1192 | 1446 | 1474 | 1311 | 1322 | 1329 | 1123 | 1222 | 1314 | 1351 | 1357 | 1517 | 1532 | 1277 | 1314 |  | 1348 | 1353 | 1336 | 1345 | 1327 | 1321 | 1348 | 1276 | 1214 | 1303 | 1376 | 1303 | 1367 | 1152 | 1410 | 1304 | 1314 | 1359 | 1290 | 1264 | 1379 | 1331 | 1348 | 1303 | 1504 | 1209 | 1528 | 1443 | 1307 | 1488 | 1413 | 1465 | 1518 | 1533 | 1337 | 1379 | 1505 | 1405 | 1472 | 1329 | 1363 | 1439 | 1405 | 1291 | 1366 | 1478 | 1237 | 1243 | 1525 | 1503 | 1363 | 1400 | 1374 | 1017 | 1402 | 1212 | 1365 | 1236 | 1406 | 1207 | 1253 | 1337 | 1318 | 1335 | 1140 | 1489 | 1301 | 1217 | 1408 | 1424 | 1449 | 1322 | 1432 | 1363 | 1294 | 1280 | 1278 | 1287 | 1183 | 1196 | 1340 | 1202 | 1134 | 1218 | 1205 | 1017 | 1227 | 1419 | 1273 | 1190 | 1237 | 1242 | 1393 | 1319 | 1405 | 1273 | 1255 | 1132 | 1493 | 1317 | 1299 | 1373 | 1298 | 1352 | 1340 | 1359 | 1337 | 1346 | 1311 | 1239 | 1231 | 1271 | 1226 | 1226 | 1327 | 1199 | 1117 | 1353 |  |  | 1032 | 923 | 1323 |  | 1458 | 1164 | 1316 | 1270 | 1310 | 1312 | 1326 | 1335 | 1336 | 1342 | 1350 | 1370 | 1359 | 1543 | 1231 | 1148 | 1020 | 798 | 979 | 1148 | 1337 | 1483 | 1310 | 1374 | 1510 | 1470 | 1447 | 1446 | 1095 | 1240 | 1114 | 1230 | 1000 |  | 1175 | 1250 | 677 | 990 | 1243 |  |  | 1143 | 910 | 1120 | 1272 | 1090 | 35.1 | 50.1 | 1.5 | 4.3 |  | 0 | 6.1 |  |  | 81281718.732 | 281316.668 | 54421147.914 | 61118.521 | 82060118.024 | 185405.861 | 59347306.787 | 55089.676 | 308233092.831 | 82048.512 | 84893.039 | 23.329 | 83645.745 | 19.713 | 83185.05 | 46.441 | 66224.362 | 15.617 | 317553.665 | 61.857 | 168495.742 | 317491.808 | 12 | 0 | 6.1 | 35.1 | 50.1 | 1.5 | 4.3 | 318035
2025-04-05 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1504.6 | 1533.2 | 1434.3 | 1430 | 1445 | 1391.2 | 1356.7 | 1317.3 | 1381.6 | 1387.3 | 1455.5 | 1454.2 | 1440.4 | 1292.1 | 1355.1 | 1394 | 1331.7 | 1348.9 | 1501.1 | 1530.4 | 1546.5 | 1371.2 | 1560.1 | 1454.4 | 1534.3 | 1532.5 | 1531.3 | 1556.2 | 1527.9 | 1570.5 | 1505.5 | 1470.6 | 1313.6 | 1720.1 | 1297.8 | 1377.2 | 1345.7 | 1374.3 | 1377.6 | 1415.6 | 1362.5 | 1347.5 | 1385 | 1394.4 | 1407.1 | 1428.5 | 1531 | 1333.2 | 1335.4 | 1362.9 | 1293.4 | 1251.3 | 1435.5 | 1343.4 | 1343.5 | 1484.5 | 1393 | 1358.5 | 1493.6 | 1333.7 | 1336.2 | 1499.5 | 1330 | 1395 | 1228.2 | 1532.6 | 1556.8 | 1350.6 | 1398.8 | 1407.9 | 1155.1 | 1292.6 | 1352.3 | 1432.4 | 1406.4 | 1606.7 | 1626.1 | 1350.6 | 1390.2 | 1511.4 | 1330 | 1433.2 | 1416.4 | 1424.6 | 1408.1 | 1373.2 | 1428.1 | 1353.6 | 1261.8 | 1373.2 | 1445.8 | 1376.7 | 1448.3 | 1178.7 | 1335.9 | 1379.4 | 1391.1 | 1416.3 | 1364.5 | 1307.3 | 1407.6 | 1412.5 | 1353.5 | 1383.5 | 1585.5 | 1249.3 | 1625.4 | 1526.1 | 1387.9 | 1584.4 | 1465.9 | 1561.4 | 1594.4 | 1626 | 1388.8 | 1473.8 | 1592.9 | 1492.1 | 1537.2 | 1431.1 | 1447.2 | 1531.9 | 1473.6 | 1370.8 | 1451.2 | 1552.8 | 1306.1 | 1312.9 | 1614.4 | 1593.2 | 1447.4 | 1484.4 | 1451.1 | 1099.1 | 1502.4 | 1283.3 | 1499.9 | 1288.7 | 1498.1 | 1287.1 | 1328.6 | 1418.7 | 1403.1 | 1421.5 | 1217 | 1590.5 | 1425.6 | 1295.5 | 1495.1 | 1511.4 | 1542.1 | 1403.5 | 1418.5 | 1401 | 1470.4 | 1351.9 | 1352.2 | 1358.2 | 1260.1 | 1267.4 | 1420.8 | 1278.4 | 1204.2 | 1290.1 | 1275.9 | 1071.1 | 1297 | 1495.6 | 1347.2 | 1256.5 | 1304.3 | 1310.9 | 1471.5 | 1394.5 | 1532.6 | 1363.3 | 1339.4 | 1214.8 | 1587.4 | 1414.3 | 1383.9 | 1456.3 | 1382.3 | 1489.4 | 1433.9 | 1459 | 1438.5 | 1348.5 | 1388.4 | 1313.8 | 1306.3 | 1356.6 | 1317.1 | 1306.6 | 1420.1 | 1307.2 | 1211.5 | 1468.8 |  |  | 1255 | 961.6 | 1405.3 |  | 1536.5 | 1228.2 | 1427.6 | 1380.2 | 1379.5 | 1421.6 | 1440.7 | 1446.3 | 1448.2 | 1447.2 | 1467.8 | 1470.2 | 1421.8 | 1651.1 | 1307.4 | 1216.5 | 1054.2 | 886.9 | 976.1 | 1125.9 | 1296.6 | 1452.6 | 1280.3 | 1343.2 | 1345.4 | 1350.3 | 1382 | 1407 | 1368.9 | 1237.2 | 1020.7 | 1222.8 | 1112 |  | 1357.6 | 1431.1 | 664.3 | 1326.3 | 1213.4 |  |  | 1352.3 | 1156.6 | 1200 | 1239.6 | 1315.3 | 37.8 | 58.63 | 1.48 | 7.5 |  | 0 | 5.9 |  |  | 81371402.865 | 281330.577 | 54509149.521 | 61128.592 | 82148517.468 | 185452.895 | 59414773.455 | 55101.734 | 308566273.151 | 82104.15 | 89684.133 | 13.909 | 88001.607 | 10.071 | 88399.444 | 47.034 | 67466.668 | 12.058 | 333180.32 | 55.638 | 177661.76 | 333124.682 | 12 | 0 | 5.9 | 37.8 | 58.63 | 1.48 | 7.5 | 336772.2
2025-04-06 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1483.7 | 1507.4 | 1390.6 | 1398.6 | 1408.1 | 1355.9 | 1384.8 | 1284.1 | 1385.7 | 1350.6 | 1418.7 | 1416.1 | 1404.9 | 1259.1 | 1321.8 | 1359.1 | 1288 | 1315.5 | 1451.8 | 1491 | 1390.3 | 1335.5 | 1520.9 | 1442 | 1495.9 | 1491.9 | 1482.8 | 1512.8 | 1484.6 | 1525.3 | 1420.3 | 1423.9 | 1281.8 | 1680.4 | 1266 | 1439.6 | 1311.6 | 1314.3 | 1342.3 | 1379.1 | 1330.4 | 1315.1 | 1351.1 | 1360.9 | 1367.2 | 1392.8 | 1401.6 | 1297.1 | 1335.7 | 1369.1 | 1287.3 | 1247.5 | 1430.7 | 1539 | 1396 | 1484 | 1406.3 | 1355.5 | 1490.3 | 1428 | 1401 | 1494.7 | 1330 | 1240 | 1290 | 1492.7 | 1521 | 1380.5 | 1361.5 | 1371.4 | 1186 | 1254.6 | 1292 | 1384.8 | 1390.5 | 1568.8 | 1584.7 | 1318.2 | 1354.2 | 1466.8 | 1392.7 | 1396.5 | 1379.4 | 1386.8 | 1371.7 | 1320 | 1391.2 | 1320.6 | 1190 | 1336.6 | 1400 | 1327.1 | 1411.7 | 1132 | 1311.5 | 1343.4 | 1354.1 | 1356.8 | 1329.4 | 1291.2 | 1422.7 | 1375.3 | 1392.6 | 1344.3 | 1547.1 | 1184.1 | 1579.4 | 1489.2 | 1350.9 | 1536 | 1419.3 | 1522.7 | 1545.1 | 1587.3 | 1335.4 | 1343.4 | 1555.8 | 1448.9 | 1404.1 | 1378.2 | 1408.2 | 1480.4 | 1421 | 1334 | 1402 | 1474 | 1280.9 | 1285.1 | 1631.8 | 1558.2 | 1414.7 | 1491.6 | 1419.5 | 1075 | 1459.2 | 1255.6 | 1412.5 | 1258.4 | 1461.4 | 1256.3 | 1298.5 | 1388.3 | 1368.9 | 1388.3 | 1187 | 1553.6 | 1393.8 | 1263.7 | 1460.7 | 1476.7 | 1505.2 | 1371.8 | 1481.4 | 1357.2 | 1339.9 | 1323.9 | 1325.2 | 1330.4 | 1231 | 1240.3 | 1425 | 1281 | 1226.7 | 1352 | 1257.6 | 1044.9 | 1265.9 | 1460.2 | 1317 | 1229.5 | 1274.1 | 1297.8 | 1433.1 | 1365.5 | 1544.3 | 1365.1 | 1357.1 | 1225.7 | 1500 | 1416.6 | 1394.3 | 1448.1 | 1403 | 1471.9 | 1439.5 | 1455 | 1444.6 | 1444.5 | 1393.3 | 1327.1 | 1359.2 | 1359.1 | 1314.7 | 1345.6 | 1408.7 | 1267.8 | 1163.3 | 1428 |  |  | 1244.9 | 955.3 | 1397 |  | 1559.7 | 1228 | 1408.2 | 1357.1 | 1340.5 | 1405.4 | 1413.7 | 1419.4 | 1422.7 | 1443.7 | 1435 | 1430.4 | 1382.3 | 1613.2 | 1272.7 | 1185.7 | 1040 | 855 | 988.1 | 1154 | 1354.8 | 1534.6 | 1334.7 | 1407 | 1405 | 1402 | 1416.5 | 1470.3 | 1098.5 | 1277.1 | 1167.1 | 1276.3 | 1026.3 |  | 1176.1 | 1407.9 | 758.9 | 1223.4 | 1213.7 |  |  | 1391.4 | 1280.4 | 1195 | 1190.5 | 1310 | 39.3 | 47.4 | 1.2 | 5.33 |  | 0 | 6.92 |  |  | 81459682.41 | 281344.869 | 54594618.216 | 61137.77 | 82235619.976 | 185501.963 | 59483445.32 | 55113.894 | 308895385.727 | 82159.511 | 88279.545 | 14.292 | 85468.695 | 9.178 | 87102.508 | 49.068 | 68671.865 | 12.16 | 329112.576 | 55.361 | 173724.77 | 329057.215 | 12 | 0 | 6.92 | 39.3 | 47.4 | 1.2 | 5.33 | 331522.2
2025-04-07 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1422 | 1445 | 1333 | 1339 | 1390 | 1300 | 1328 | 1280 | 1328 | 1340 | 1358 | 1356 | 1344 | 1204 | 1262 | 1299 | 1290 | 1256 | 1400 | 1422 | 1328 | 1276 | 1452 | 1420 | 1427 | 1421 | 1414 | 1440 | 1411 | 1444 | 1478 | 1390 | 1226 | 1612 | 1280 | 1410 | 1296 | 1259 | 1286 | 1322 | 1276 | 1262 | 1294 | 1303 | 1310 | 1334 | 1429 | 1297 | 1310 | 1314 | 1260 | 1230 | 1398 | 1476 | 1388 | 1426 | 1424 | 1301 | 1427 | 1394 | 1301 | 1435 | 1340 | 1310 | 1440 | 1430 | 1456 | 1299 | 1302 | 1315 | 1328 | 1210 | 1250 | 1332 | 1350 | 1502 | 1519 | 1320 | 1300 | 1406 | 1334 | 1338 | 1322 | 1330 | 1315 | 1297 | 1333 | 1317 | 1296 | 1281 | 1342 | 1376 | 1353 | 1191 | 1410 | 1289 | 1300 | 1299 | 1276 | 1260 | 1364 | 1319 | 1336 | 1293 | 1487 | 1200 | 1514 | 1425 | 1295 | 1473 | 1390 | 1460 | 1472 | 1519 | 1269 | 1374 | 1488 | 1420 | 1406 | 1331 | 1353 | 1420 | 1390 | 1282 | 1354 | 1478 | 1260 | 1280 | 1513 | 1491 | 1396 | 1392 | 1398 | 1100 | 1404 | 1299 | 1391 | 1260 | 1394 | 1280 | 1290 | 1388 | 1307 | 1399 | 1189 | 1484 | 1331 | 1211 | 1400 | 1415 | 1439 | 1316 | 1421 | 1312 | 1286 | 1271 | 1310 | 1274 | 1287 | 1303 | 1433 | 1269 | 1280 | 1372 | 1311 | 1099 | 1242 | 1430 | 1307 | 1299 | 1298 | 1296 | 1427 | 1341 | 1528 | 1337 | 1314 | 1230 | 1543 | 1364 | 1355 | 1403 | 1395 | 1430 | 1409 | 1475 | 1393 | 1402 | 1369 | 1306 | 1304 | 1304 | 1258 | 1291 | 1353 | 1211 | 1116 | 1354 |  |  | 1220 | 939 | 1360 |  | 1488 | 1230 | 1350 | 1301 | 1275 | 1339 | 1357 | 1357 | 1365 | 1378 | 1384 | 1372 | 1320 | 1552 | 1224 | 1135 | 1020 | 910 | 972 | 1145 | 1336 | 1510 | 1314 | 1386 | 1410 | 1378 | 1387 | 1459 | 1200 | 1256 | 1155 | 1268 | 1150 |  | 1700 | 1410 | 600 | 1210 | 1245 |  |  | 1178 | 1300 | 1300 | 1130 | 1098 | 41.9 | 51.1 | 1.1 | 3.13 |  | 0 | 6.5257 |  |  | 81544202.804 | 281359.701 | 54676516.993 | 61149.622 | 82320465.624 | 185544.891 | 59549914.342 | 55125.834 | 309212772.728 | 82213.909 | 84520.394 | 14.832 | 81898.777 | 11.852 | 84845.648 | 42.928 | 66469.022 | 11.94 | 317387.001 | 54.398 | 166392.487 | 317332.603 | 12 | 0 | 6.5257 | 41.9 | 51.1 | 1.1 | 3.13 | 324271
2025-04-08 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1318.6 | 1341.3 | 1243.2 | 1247 | 1320.2 | 1214.4 | 1280.2 | 1243.7 | 1300.1 | 1272.5 | 1269.5 | 1258.1 | 1280 | 1177.2 | 1212.7 | 1230 | 1240 | 1245 | 1380 | 1324 | 1335.1 | 1240.1 | 1340.2 | 1430 | 1324.4 | 1313.7 | 1380 | 1388 | 1382.3 | 1395.6 | 1390.6 | 1325.8 | 1190 | 1600.1 | 1248.6 | 1391.3 | 1275.2 | 1230.4 | 1280.2 | 1237.1 | 1290 | 1250 | 1240 | 1219.6 | 1228.8 | 1245.6 | 1341.3 | 1287.8 | 1301.9 | 1300.9 | 1278.2 | 1272.1 | 1390.9 | 1396.9 | 1345.9 | 1420.1 | 1420.7 | 1290.3 | 1448.3 | 1377.7 | 1249.4 | 1420 | 1308 | 1215.9 | 1333.8 | 1331.1 | 1352.3 | 1270.2 | 1280.4 | 1312.7 | 1239.3 | 1219.4 | 1243.7 | 1246.1 | 1333.5 | 1408.1 | 1423.7 | 1235.4 | 1292.2 | 1401.8 | 1250.3 | 1254.3 | 1238.3 | 1245.2 | 1239.6 | 1277.3 | 1243.8 | 1280.5 | 1290.2 | 1280.5 | 1336.9 | 1350.1 | 1265.5 | 1232.5 | 1360.4 | 1280.9 | 1290.7 | 1288.9 | 1240.4 | 1255.4 | 1253.8 | 1232 | 1248.8 | 1280.1 | 1395.2 | 1230.9 | 1413.9 | 1420.8 | 1289.4 | 1430.5 | 1370.5 | 1369 | 1396.3 | 1427.1 | 1250.6 | 1301.5 | 1405.5 | 1401.3 | 1399.4 | 1254.3 | 1268.5 | 1390.1 | 1368.2 | 1290.5 | 1268.5 | 1463.7 | 1247.1 | 1252.4 | 1419 | 1399.3 | 1372.1 | 1390.7 | 1376 | 1090 | 1398.1 | 1290.3 | 1366 | 1300.5 | 1310.7 | 1227.4 | 1265.5 | 1352 | 1324.9 | 1388.5 | 1190 | 1395.2 | 1299.5 | 1190.8 | 1390.3 | 1428.4 | 1399 | 1331 | 1426.6 | 1264 | 1299.3 | 1289.5 | 1295.9 | 1292.9 | 1276 | 1244.6 | 1477.1 | 1266.3 | 1328.3 | 1397 | 1423.5 | 1230.5 | 1277.5 | 1380.6 | 1249.5 | 1300.4 | 1299.9 | 1290.3 | 1410.4 | 1364.3 | 1454 | 1278.8 | 1281.5 | 1250.5 | 1475.3 | 1305.3 | 1366.5 | 1400.8 | 1388.2 | 1420 | 1388 | 1405.5 | 1339.6 | 1329.6 | 1310.6 | 1343.2 | 1288.1 | 1322.6 | 1250 | 1280 | 1270.9 | 1235.8 | 1052.1 | 1272.5 |  |  | 1204.6 | 930.1 | 1270.3 |  | 1452.5 | 1212.5 | 1261.4 | 1287.9 | 1272.6 | 1280.9 | 1287.5 | 1295.7 | 1297 | 1317.5 | 1290.5 | 1282.4 | 1324.1 | 1454.9 | 1144.9 | 1120.5 | 916.4 | 760.2 | 970.5 | 1177.5 | 1352.4 | 1415.5 | 1300 | 1296 | 1295.8 | 1280.2 | 1380.8 | 1471.4 | 1190.3 | 1250.5 | 1187 | 1250.8 | 1092.1 |  | 1708.5 | 1400.2 | 550.8 | 1210.9 | 1212.7 |  |  | 1162.8 | 1288.5 | 1315.2 | 1140.2 | 1115.2 | 43.9 | 51.1 | 1.1 | 3.13 |  | 0 | 6.0578 |  |  | 81623456.674 | 281374.677 | 54753444.461 | 61162.416 | 82400731.86 | 185586.944 | 59612531.256 | 55139.475 | 309511535.47 | 82271.483 | 79253.87 | 14.976 | 76927.468 | 12.794 | 80266.236 | 42.053 | 62616.914 | 13.641 | 298762.742 | 57.574 | 156153.568 | 298705.168 | 12 | 0 | 6.0578 | 43.9 | 51.1 | 1.1 | 3.13 | 315636
2025-04-09 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1233 | 1254 | 1180 | 1165 | 1222 | 1133 | 1158 | 1172 | 1199 | 1188 | 1189 | 1184 | 1173 | 1040 | 1098 | 1130 | 1120 | 1130 | 1219 | 1232 | 1150 | 1130 | 1248 | 1250 | 1231 | 1222 | 1290 | 1250 | 1255 | 1250 | 1300 | 1242 | 1073 | 351 | 1114 | 1208 | 1150 | 1102 | 1124 | 1155 | 1160 | 1160 | 1132 | 1141 | 1146 | 1164 | 1252 | 1136 | 1188 | 1178 | 1150 | 1171 | 1336 | 1329 | 1250 | 1278 | 1280 | 1171 | 1281 | 1270 | 1149 | 1291 | 1220 | 1080 | 1246 | 1244 | 1264 | 1190 | 1148 | 1143 | 1158 | 1132 | 1140 | 1166 | 1277 | 1316 | 1330 | 1154 | 1138 | 1250 | 1168 | 1172 | 1156 | 1164 | 1148 | 1155 | 1162 | 1143 | 1129 | 1140 | 1180 | 1310 | 1182 | 1160 | 1398 | 1125 | 1135 | 1162 | 1160 | 1150 | 1195 | 1153 | 1170 | 1131 | 1304 | 1140 | 1325 | 1302 | 1180 | 1290 | 1222 | 1281 | 1325 | 1334 | 1140 | 1205 | 1310 | 1319 | 1262 | 1178 | 1187 | 1298 | 1240 | 1123 | 1186 | 1498 | 1167 | 1140 | 1321 | 1303 | 1240 | 1218 | 1230 | 1000 | 1225 | 1245 | 1199 | 1200 | 1215 | 1150 | 1199 | 1240 | 1138 | 1230 | 1100 | 1298 | 1134 | 1057 | 1260 | 1239 | 1253 | 1147 | 1290 | 1141 | 1120 | 1108 | 1198 | 1140 | 1098 | 1162 | 1293 | 1146 | 1230 | 1280 | 1270 | 1160 | 1129 | 1297 | 1179 | 1200 | 1162 | 1166 | 1280 | 1207 | 1359 | 1195 | 1200 | 1176 | 1386 | 1218 | 1226 | 1259 | 1290 | 1300 | 1256 | 1327 | 1252 | 1243 | 1232 | 1240 | 1153 | 1156 | 1130 | 1139 | 1220 | 1150 | 1009 | 1233 |  |  | 1198 | 898 | 1280 |  | 1250 | 1278 | 1182 | 1172 | 1149 | 1209 | 1214 | 1233 | 1230 | 1244 | 1213 | 1201 | 1230 | 1365 | 1072 | 1110 | 860 | 810 | 910 | 1011 | 1213 | 1372 | 1198 | 1244 | 1298 | 1278 | 1287 | 1300 | 1099 | 1219 | 1099 | 1124 | 1010 |  | 1498 | 1398 | 450 | 1198 | 1123 |  |  | 1098 | 1298 | 1199 | 1110 | 1110 | 39.9 | 50.1 | 1.1 | 3.4 |  | 0 | 5.6268 |  |  | 81698640.225 | 281383.068 | 54825971.097 | 61171.181 | 82476110.299 | 185620.066 | 59671741.712 | 55149.599 | 309793554.329 | 82309.564 | 75183.551 | 8.391 | 72526.636 | 8.765 | 75378.439 | 33.122 | 59210.456 | 10.124 | 282018.859 | 38.081 | 147693.031 | 281980.778 | 12 | 0 | 5.6268 | 39.9 | 50.1 | 1.1 | 3.4 | 289705
2025-04-10 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 971 | 984 | 912 | 911 | 965 | 892 | 901 | 932 | 990 | 940 | 926 | 922 | 910 | 818 | 854 | 882 | 940 | 940 | 952 | 963 | 896 | 920 | 981 | 960 | 963 | 954 | 999 | 950 | 935 | 954 | 990 | 1000 | 835 | 1105 | 888 | 940 | 898 | 857 | 874 | 890 | 899 | 899 | 888 | 883 | 893 | 908 | 978 | 884 | 898 | 976 | 925 | 864 | 990 | 980 | 950 | 997 | 988 | 860 | 999 | 990 | 943 | 1010 | 910 | 898 | 968 | 964 | 980 | 950 | 884 | 885 | 898 | 881 | 862 | 902 | 1010 | 1020 | 1030 | 893 | 899 | 968 | 904 | 906 |  | 900 | 889 | 899 | 907 | 895 | 883 | 898 | 917 | 992 | 918 | 892 | 978 | 868 | 876 | 897 | 896 | 949 | 926 | 895 | 908 | 950 | 1008 | 909 | 1021 | 1005 | 914 | 1000 | 947 | 989 | 1032 | 1031 | 883 | 933 | 1012 | 961 | 972 | 938 | 960 | 978 | 943 | 894 | 919 | 1010 | 826 | 833 | 1022 | 1010 | 920 | 949 | 927 | 805 | 958 | 913 | 916 | 809 | 949 | 929 | 946 | 915 | 850 | 960 | 931 | 928 | 840 | 784 | 904 | 921 | 928 | 847 | 1010 | 845 | 831 | 822 | 910 | 922 | 862 | 916 | 1009 | 893 | 933 | 968 | 1002 | 945 | 883 | 1007 | 932 | 961 | 919 | 913 | 1015 | 954 | 1053 | 924 | 928 | 931 | 1068 | 942 | 945 | 970 | 952 | 1009 | 971 | 1031 | 969 | 965 | 957 | 920 | 899 | 994 | 851 | 886 | 946 | 853 | 796 | 964 |  |  | 840 | 646 | 940 |  | 1012 | 929 | 912 | 897 | 890 | 932 | 945 | 947 | 948 | 958 | 970 | 950 | 954 | 1101 | 834 | 767 | 620 | 610 | 653 | 760 | 895 | 1014 | 943 | 929 | 978 | 998 | 967 | 949 | 913 | 932 | 846 | 934 | 773 |  | 1175 | 950 | 426 | 862 | 815 |  |  | 898 | 978 | 1010 | 898 | 810 | 34.9 | 49 | 3 | 5 |  | 0 | 4.36 |  |  | 81756527.707 | 281390.022 | 54882722.441 | 61177.887 | 82534835.19 | 185649.094 | 59717471.191 | 55158.877 | 310012420.729 | 82339.924 | 57887.482 | 6.954 | 56751.344 | 6.706 | 58724.891 | 29.028 | 45729.479 | 9.278 | 218866.4 | 30.36 | 114625.166 | 218836.04 | 12 | 0 | 4.36 | 34.9 | 49 | 3 | 5 | 223694
2025-04-11 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1107 | 1131 | 1048 | 1046 | 1110 | 1025 | 1029 | 1010 | 1041 | 1024 | 1059 | 1057 | 1043 | 938 | 1012 | 1049 | 963 | 996 | 1092 | 1126 | 1059 | 1022 | 1171 | 1093 | 1113 | 1110 | 1097 | 1120 | 1091 | 1121 | 1200 | 1098 | 961 | 1283 | 908 | 1079 | 986 | 987 | 1033 | 1057 | 989 | 989 | 1029 | 1044 | 1025 | 1049 | 1122 | 1040 | 1035 | 1060 | 1004 | 1050 | 1201 | 1188 | 1087 | 1154 | 1143 | 1040 | 1149 | 1106 | 1034 | 1163 | 1210 | 1098 | 1128 | 1120 | 1150 | 1099 | 1027 | 1031 | 1069 | 1059 | 1046 | 1049 | 1170 | 1170 | 1184 | 1017 | 1007 | 1122 | 1040 | 1040 | 1038 | 1039 | 1026 | 1036 | 1084 | 1074 | 1044 | 1041 | 1067 | 1078 | 1082 | 1024 | 1200 | 1002 | 1032 | 1063 | 1038 | 1041 | 1079 | 1035 | 1066 | 1036 | 1198 | 1044 | 1186 | 1175 | 1068 | 1187 | 1146 | 1140 | 1201 | 1189 | 1048 | 1074 | 1172 | 1114 | 1175 | 1064 | 1094 | 1133 | 1114 | 1030 | 1081 | 1478 | 950 | 968 | 1165 | 1154 | 1059 | 1083 | 1051 | 898 | 1104 | 1098 | 1051 | 978 | 1059 | 1004 | 988 | 1046 | 1024 | 1094 | 999 | 1168 | 1006 | 942 | 1093 | 1113 | 1126 | 1026 | 1119 | 1024 | 1001 | 988 | 1050 | 1178 | 966 | 1025 | 1130 | 1001 | 1039 | 1088 | 1125 | 1055 | 983 | 1137 | 1040 | 999 | 1025 | 1019 | 1140 | 1068 | 1201 | 1044 | 1043 | 931 | 1199 | 1059 | 1068 | 1096 | 1076 | 1159 | 1100 | 1172 | 1089 | 1104 | 1069 | 1034 | 1021 | 1016 | 977 | 1005 | 1064 | 962 | 900 | 1086 |  |  | 944 | 738 | 1059 |  | 1165 | 1132 | 1051 | 1020 | 1045 | 1058 | 1065 | 1072 | 1069 | 1083 | 1086 | 1080 | 1149 | 1235 | 975 | 894 | 790 | 640 | 781 | 913 | 999 | 1200 | 1018 | 1100 | 1098 | 1097 | 1186 | 1141 | 975 | 994 | 900 | 997 | 960 |  | 1250 | 1068 | 398 | 985 | 918 |  |  | 1000 | 1000 | 1088 | 945 | 913 | 36.6 | 55.86 | 2.52 | 13.1 |  | 0 | 4.88 |  |  | 81824612.484 | 281411.612 | 54949789.39 | 61214.424 | 82601901.2 | 185683.778 | 59770602.626 | 55201.359 | 310267495.625 | 82401.977 | 68084.777 | 21.59 | 67066.949 | 36.537 | 67066.01 | 34.684 | 53131.435 | 42.482 | 255074.896 | 62.053 | 135093.599 | 255012.843 | 12 | 0 | 4.88 | 36.6 | 55.86 | 2.52 | 13.1 | 257651
2025-04-12 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1392 | 1415 | 1315 | 1313 | 1396 | 1287 | 1302 | 1199 | 1310 | 1288 | 1332 | 1330 | 1311 | 1180 | 1282 | 1324 | 1249 | 1276 | 1409 | 1442 | 1345 | 1293 | 1481 | 1303 | 1448 | 1440 | 1433 | 1457 | 1386 | 1425 | 1350 | 1378 | 1215 | 1600 | 1148 | 1364 | 1263 | 1294 | 1315 | 1346 | 1296 | 1283 | 1310 | 1327 | 1323 | 1325 | 1442 | 1332 | 1230 | 1260 | 1210 | 1198 | 1388 | 1330 | 1202 | 1275 | 1255 | 1133 | 1286 | 1232 | 1178 | 1283 | 1226 | 1110 | 1455 | 1446 | 1484 | 1318 | 1327 | 1334 | 1358 | 1333 | 1268 | 1357 | 1396 | 1480 | 1496 | 1286 | 1271 | 1422 | 1315 | 1316 | 1314 | 1316 | 1325 | 1284 | 1365 | 1352 | 1326 | 1320 | 1378 | 1240 | 1377 | 1313 | 1330 | 1310 | 1319 | 1357 | 1349 | 1265 | 1394 | 1348 | 1370 | 1321 | 1518 | 1220 | 1501 | 1505 | 1370 | 1506 | 1425 | 1441 | 1505 | 1517 | 1327 | 1360 | 1494 | 1404 | 1455 | 1341 | 1375 | 1432 | 1394 | 1297 | 1365 | 1498 | 1229 | 1261 | 1478 | 1470 | 1398 | 1378 | 1335 | 1131 | 1432 | 1299 | 1365 | 1270 | 1341 | 1331 | 1271 | 1318 | 1310 | 1440 | 1254 | 1486 | 1282 | 1202 | 1390 | 1411 | 1432 | 1306 | 1424 | 1344 | 1272 | 1254 | 1190 | 1245 | 1213 | 1288 | 1419 | 1257 | 1285 | 1373 | 1340 | 1267 | 1242 | 1429 | 1307 | 1203 | 1285 | 1277 | 1426 | 1341 | 1520 | 1330 | 1339 | 1206 | 1531 | 1361 | 1374 | 1404 | 1367 | 1452 | 1399 | 1481 | 1401 | 1403 | 1344 | 1318 | 1287 | 1283 | 1200 | 1262 | 1333 | 1206 | 1129 | 1357 |  |  | 1197 | 926 | 1327 |  | 1466 | 1210 | 1324 | 1289 | 1303 | 1331 | 1339 | 1346 | 1342 | 1362 | 1365 | 1361 | 1361 | 1553 | 1225 | 1138 | 910 | 810 | 977 | 1143 | 1327 | 1510 | 1282 | 1386 | 1298 | 1310 | 1445 | 1432 | 1178 | 1248 | 1136 | 1251 | 1178 |  | 1478 | 1263 | 578 | 1163 | 1153 |  |  | 1078 | 1178 | 1299 | 1270 | 1078 | 29.88 | 43.21 | 1.3 | 6.1 |  | 0 | 6.15 |  |  | 81907526.273 | 281425.064 | 55034099.627 | 61224.371 | 82686891.459 | 185720.486 | 59836769.598 | 55214.015 | 310585448.108 | 82457.052 | 82913.789 | 13.452 | 84310.237 | 9.947 | 84990.259 | 36.708 | 66166.972 | 12.656 | 317952.483 | 55.075 | 167200.627 | 317897.408 | 12 | 0 | 6.15 | 29.88 | 43.21 | 1.3 | 6.1 | 321089
2025-04-13 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1443 | 1470 | 1366 | 1365 | 1450 | 1339 | 1367 | 1257 | 1372 | 1348 | 1426 | 1416 | 1391 | 1259 | 1335 | 1374 | 1312 | 1329 | 1487 | 1496 | 1394 | 1339 | 1532 | 1445 | 1504 | 1493 | 1486 | 1516 | 1473 | 1510 | 1310 | 1334 | 1276 | 1687 | 1200 | 1433 | 1316 | 1339 | 1358 | 1394 | 1342 | 1331 | 1354 | 1369 | 1383 | 1405 | 1508 | 1384 | 1308 | 1340 | 1266 | 1331 | 1518 | 1502 | 1388 | 1478 | 1445 | 1305 | 1491 | 1433 | 1332 | 1477 | 1278 | 1080 | 1515 | 1506 | 1525 | 1340 | 1380 | 1387 | 1396 | 1345 | 1277 | 1408 | 1417 | 1548 | 1570 | 1370 | 1363 | 1486 | 1403 | 1402 | 1397 | 1399 | 1385 | 1326 | 1407 | 1391 | 1365 | 1358 | 1418 | 1278 | 1427 | 1363 | 1310 | 1365 | 1361 | 1386 | 1393 | 1278 | 1445 | 1391 | 1413 | 1364 | 1564 | 1198 | 1568 | 1563 | 1425 | 1551 | 1444 | 1512 | 1558 | 1582 | 1357 | 1423 | 1550 | 1449 | 1479 | 1390 | 1419 | 1491 | 1416 | 1340 | 1412 | 1464 | 1290 | 1319 | 1546 | 1539 | 1463 | 1446 | 1402 | 1195 | 1532 | 1480 | 1477 | 1454 | 1407 | 1399 | 1332 | 1390 | 1379 | 1550 | 1321 | 1573 | 1393 | 1262 | 1453 | 1478 | 1495 | 1364 | 1485 | 1357 | 1326 | 1312 | 1178 | 1326 | 1265 | 1341 | 1518 | 1317 | 1378 | 1452 | 1354 | 1231 | 1307 | 1512 | 1386 | 1284 | 1372 | 1364 | 1508 | 1431 | 1578 | 1382 | 1399 | 1254 | 1604 | 1418 | 1437 | 1471 | 1442 | 1505 | 1453 | 1544 | 1454 | 1458 | 1432 | 1389 | 1327 | 1322 | 1165 | 1301 | 1384 | 1241 | 1164 | 1401 |  |  | 1203 | 955 | 1364 |  | 1503 | 1210 | 1370 | 1348 | 1335 | 1390 | 1401 | 1411 | 1406 | 1426 | 1408 | 1417 | 1365 | 1601 | 1273 | 1182 | 898 | 878 | 1007 | 1184 | 1373 | 1578 | 1365 | 1452 | 1278 | 1363 | 1482 | 1486 | 1117 | 1295 | 1179 | 1299 | 1198 |  | 1520 | 1365 | 644 | 1183 | 1195 |  |  | 1163 | 1191 | 1298 | 1263 | 1191 | 31.82 | 40.8 | 3.02 | 7.1 |  | 0 | 6.14 |  |  | 81995608.799 | 281439.981 | 55121205.499 | 61234.011 | 82776560.366 | 185766.511 | 59905210.194 | 55227.06 | 310918312.508 | 82518.014 | 88082.526 | 14.917 | 87105.872 | 9.64 | 89668.907 | 46.025 | 68440.596 | 13.045 | 332864.4 | 60.962 | 175163.841 | 332803.438 | 12 | 0 | 6.14 | 31.82 | 40.8 | 3.02 | 7.1 | 335292
2025-04-14 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1457 | 1485 | 1383 | 1384 | 1471 | 1363 | 1382 | 1266 | 1395 | 1362 | 1427 | 1413 | 1392 | 1266 | 1323 | 1363 | 1295 | 1314 | 1471 | 1480 | 1380 | 1326 | 1521 | 1432 | 1489 | 1477 | 1472 | 1503 | 1460 | 1495 | 1363 | 1322 | 1300 | 1681 | 1208 | 1455 | 1304 | 1321 | 1347 | 1379 | 1324 | 1311 | 1336 | 1351 | 1355 | 1388 | 1491 | 1378 | 1306 | 1336 | 1263 | 1328 | 1503 | 1483 | 1374 | 1465 | 1450 | 1285 | 1471 | 1413 | 1314 | 1477 | 1263 | 1098 | 1499 | 1488 | 1509 | 1330 | 1365 | 1371 | 1381 | 1331 | 1270 | 1392 | 1398 | 1557 | 1588 | 1371 | 1355 | 1468 | 1406 | 1401 | 1383 | 1383 | 1369 | 1307 | 1391 | 1377 | 1350 | 1345 | 1399 | 1298 | 1412 | 1349 | 1298 | 1348 | 1344 | 1373 | 1376 | 1266 | 1424 | 1373 | 1396 | 1348 | 1541 | 1182 | 1572 | 1545 | 1406 | 1534 | 1402 | 1496 | 1547 | 1563 | 1342 | 1406 | 1533 | 1433 | 1456 | 1377 | 1403 | 1478 | 1398 | 1324 | 1394 | 1478 | 1276 | 1297 | 1521 | 1514 | 1438 | 1450 | 1423 | 1207 | 1544 | 1486 | 1480 | 1439 | 1398 | 1402 | 1353 | 1398 | 1391 | 1546 | 1328 | 1565 | 1356 | 1251 | 1446 | 1470 | 1480 | 1353 | 1495 | 1345 | 1319 | 1307 | 1190 | 1325 | 1281 | 1356 | 1534 | 1330 | 1307 | 1453 | 1357 | 1191 | 1312 | 1512 | 1376 | 1269 | 1361 | 1349 | 1379 | 1417 | 1548 | 1357 | 1378 | 1233 | 1578 | 1394 | 1415 | 1446 | 1424 | 1480 | 1428 | 1531 | 1433 | 1433 | 1412 | 1273 | 1324 | 1306 | 1166 | 1330 | 1395 | 1255 | 1168 | 1419 |  |  | 1188 | 943 | 1357 |  | 1484 | 1173 | 1353 | 1339 | 1334 | 1382 | 1399 | 1406 | 1403 | 1420 | 1404 | 1399 | 1358 | 1587 | 1257 | 1164 | 963 | 810 | 993 | 1174 | 1379 | 1562 | 1386 | 1448 | 1298 | 1378 | 1490 | 1469 | 1109 | 1291 | 1169 | 1300 | 1178 |  | 1498 | 1382 | 633 | 1197 | 1176 |  |  | 1110 | 1263 | 1278 | 1210 | 1163 | 32.37 | 45.01 | 1.79 | 6.1 |  | 0 | 6.51 |  |  | 82083194.141 | 281455.645 | 55207413.543 | 61246.338 | 82865707.869 | 185809.522 | 59973320.461 | 55239.414 | 311248951.343 | 82573.423 | 87585.342 | 15.664 | 86208.044 | 12.327 | 89147.503 | 43.011 | 68110.267 | 12.354 | 330638.835 | 55.409 | 173765.395 | 330583.426 | 12 | 0 | 6.51 | 32.37 | 45.01 | 1.79 | 6.1 | 333086
2025-04-15 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1424 | 1452 | 1351 | 1355 | 1432 | 1328 | 1333 | 1228 | 1351 | 1319 | 1378 | 1365 | 1343 | 1222 | 1274 | 1315 | 1276 | 1273 | 1433 | 1422 | 1325 | 1272 | 1460 | 1364 | 1435 | 1419 | 1415 | 1447 | 1410 | 1444 | 1378 | 1307 | 1269 | 1631 | 1194 | 1425 | 1295 | 1301 | 1312 | 1349 | 1308 | 1290 | 1301 | 1315 | 1322 | 1345 | 1444 | 1333 | 1288 | 1318 | 1246 | 1311 | 1484 | 1465 | 1357 | 1449 | 1431 | 1267 | 1471 | 1414 | 1312 | 1467 | 1278 | 1461 | 1451 | 1457 | 1289 | 1318 | 1326 | 1335 | 1290 | 1229 | 1346 | 1377 | 1525 | 1545 | 1323 | 1424 | 1360 | 1356 | 1337 | 1337 | 1325 | 1272 | 1345 | 1333 | 1304 | 1301 | 1351 | 1412 | 1365 | 1303 | 1410 | 1363 | 1278 | 1302 | 1311 | 1332 | 1337 | 1234 | 1379 | 1333 | 1356 | 1334 | 1495 | 1151 | 1520 | 1496 | 1360 | 1484 | 1364 | 1465 | 1512 | 1514 | 1304 | 1359 | 1485 | 1340 | 1413 | 1345 | 1376 | 1437 | 1362 | 1281 | 1348 | 1463 | 1259 | 1279 | 1502 | 1497 | 1429 | 1435 | 1394 | 1190 | 1519 | 1470 | 1471 | 1445 | 1351 | 1358 | 1330 | 1361 | 1349 | 1499 | 1286 | 1510 | 1315 | 1214 | 1401 | 1428 | 1435 | 1316 | 1458 | 1314 | 1292 | 1278 | 1163 | 1280 | 1242 | 1316 | 1496 | 1299 | 1421 | 1434 | 1317 | 1289 | 1269 | 1462 | 1328 | 1218 | 1314 | 1299 | 1292 | 1364 | 1499 | 1313 | 1332 | 1194 | 1524 | 1348 | 1368 | 1394 | 1394 | 1432 | 1380 | 1487 | 1386 | 1386 | 1356 | 1250 | 1306 | 1259 | 1150 | 1292 | 1349 | 1224 | 1144 | 1376 |  |  | 1157 | 926 | 1317 |  | 1436 | 1214 | 1307 | 1292 | 1294 | 1336 | 1353 | 1359 | 1356 | 1371 | 1380 | 1384 | 1333 | 1568 | 1217 | 1125 | 925 | 863 | 881 | 1178 | 1363 | 1510 | 1310 | 1410 | 1263 | 1298 | 1445 | 1478 | 1111 | 1270 | 1163 | 1278 | 1110 |  | 1478 | 1351 | 614 | 1180 | 1168 |  |  | 1135 | 1256 | 1270 | 1225 | 1135 | 32.7 | 43.6 | 1.6 | 6.5 |  | 0 | 6.23 |  |  | 82168621 | 281469 | 55291405 | 61256 | 82952664 | 185854 | 60036190 | 55251 | 311567840.3 | 82626.6 | 85426.859 | 13.355 | 83991.457 | 9.662 | 86956.131 | 44.478 | 62869.539 | 11.586 | 318888.957 | 53.177 | 169395.299 | 318835.78 | 12 | 0 | 6.23 | 32.7 | 43.6 | 1.6 | 6.5 | 326506
2025-04-16 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1403 | 1428 | 1328 | 1330 | 1407 | 1310 | 1313 | 1209 | 1330 | 1298 | 1360 | 1346 | 1322 | 1202 | 1275 | 1314 | 1266 | 1274 | 1431 | 1434 | 1331 | 1280 | 1465 | 1380 | 1432 | 1413 | 1413 | 1430 | 1380 | 1409 | 1363 | 1253 | 1250 | 1608 | 1211 | 1402 | 1307 | 1288 | 1309 | 1342 | 1294 | 1279 | 1290 | 1304 | 1308 | 1355 | 1444 | 1315 | 1283 | 1313 | 1247 | 1312 | 1495 | 1480 | 1355 | 1437 | 1411 | 1252 | 1480 | 1415 | 1301 | 1450 | 1263 | 1425 | 1462 | 1453 | 1476 | 1268 | 1323 | 1333 | 1342 | 1277 | 1196 | 1331 | 1355 | 1512 | 1525 | 1301 | 1288 | 1396 | 1338 | 1335 | 1314 | 1316 | 1309 | 1255 | 1341 | 1330 | 1314 | 1307 | 1369 | 1290 | 1351 | 1298 | 1263 | 1282 | 1290 | 1302 | 1315 | 1202 | 1360 | 1314 | 1337 | 1315 | 1478 | 1124 | 1497 | 1472 | 1340 | 1496 | 1353 | 1444 | 1474 | 1490 | 1272 | 1339 | 1464 | 1338 | 1411 | 1341 | 1380 | 1427 | 1352 | 1303 | 1371 | 1425 | 1255 | 1295 | 1510 | 1509 | 1428 | 1425 | 1371 | 1168 | 1491 | 1442 | 1440 | 1415 | 1309 | 1332 | 1308 | 1362 | 1323 | 1471 | 1262 | 1481 | 1331 | 1238 | 1429 | 1470 | 1466 | 1335 | 1443 | 1327 | 1304 | 1296 | 1098 | 1259 | 1225 | 1298 | 1478 | 1284 | 1400 | 1431 | 1299 | 1269 | 1252 | 1439 | 1306 | 1199 | 1291 | 1277 | 1270 | 1338 | 1476 | 1294 | 1311 | 1176 | 1500 | 1328 | 1348 | 1376 | 1411 | 1411 | 1361 | 1466 | 1362 | 1364 | 1334 | 1188 | 1287 | 1244 | 1111 | 1272 | 1327 | 1203 | 1124 | 1350 |  |  | 1180 | 919 | 1296 |  | 1494 | 1220 | 1287 | 1275 | 1261 | 1317 | 1332 | 1337 | 1334 | 1350 | 1360 | 1363 | 1300 | 1546 | 1199 | 1105 | 910 | 825 | 943 | 1117 | 1316 | 1531 | 1339 | 1399 | 1278 | 1300 | 1418 | 1366 | 1094 | 1241 | 1113 | 1237 | 996 |  | 1175 | 1345 | 604 | 1261 | 1214 |  |  | 1098 | 1234 | 1301 | 1270 | 1117 | 34.09 | 46.02 | 1.33 | 6.1 |  | 0 | 6.27 |  |  | 82253458.237 | 281482.329 | 55374252.019 | 61264.956 | 83038923.775 | 185897.441 | 60101967.276 | 55263.176 | 311887179.23 | 82681.229 | 84837.237 | 13.329 | 82847.019 | 8.956 | 86259.775 | 43.441 | 65777.276 | 12.176 | 319338.93 | 54.629 | 167661.971 | 319284.301 | 12 | 0 | 6.27 | 34.09 | 46.02 | 1.33 | 6.1 | 323020
2025-04-17 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1355 | 1375 | 1281 | 1281 | 1360 | 1265 | 1275 | 1248 | 1295 | 1286 | 1306 | 1318 | 1296 | 1152 | 1240 | 1272 | 1217 | 1235 | 1379 | 1389 | 1297 | 1252 | 1423 | 1341 | 1381 | 1389 | 1379 | 1411 | 1370 | 1395 | 1310 | 1253 | 1203 | 1546 | 1189 | 1350 | 1285 | 1244 | 1275 | 1300 | 1246 | 1233 | 1257 | 1277 | 1267 | 1310 | 1389 | 1288 | 1219 | 1300 | 1208 | 1369 | 1450 | 1400 | 1314 | 1309 | 1400 | 1334 | 1400 | 1400 | 1324 | 1400 | 1461 | 1406 | 1398 | 1422 | 1400 | 1269 | 1295 | 1305 | 1211 | 1200 | 1300 | 1270 | 1460 | 1468 | 1500 | 1266 | 1360 | 1301 | 1308 | 1299 | 1303 | 1260 | 1180 | 1318 | 1303 | 1284 | 1248 | 1248 | 1331 | 1226 | 1334 | 1272 | 1298 | 1261 | 1264 | 1225 | 1266 | 1119 | 1307 | 1266 | 1294 | 1290 | 1452 | 1045 | 1499 | 1413 | 1289 | 1461 | 1306 | 1387 | 1391 | 1431 | 1192 | 1288 | 1409 | 1300 | 1359 | 1292 | 1326 | 1373 | 1280 | 1258 | 1331 | 1426 | 1213 | 1245 | 1451 | 1450 | 1376 | 1375 | 1318 | 1122 | 1436 | 1383 | 1387 | 1364 | 1293 | 1321 | 1262 | 1338 | 1288 | 1442 | 1240 | 1457 | 1306 | 1201 | 1394 | 1427 | 1427 | 1307 | 1451 | 1309 | 1286 | 1269 | 1026 | 1232 | 1178 | 1243 | 1423 | 1228 | 1337 | 1374 | 1239 | 1216 | 1201 | 1378 | 1254 | 1153 | 1240 | 1216 | 1284 | 1424 | 1245 | 1264 | 1132 | 1439 | 1500 | 1297 | 1323 | 1361 | 1400 | 1408 | 1316 | 1400 | 1284 | 1300 | 1284 | 1149 | 1236 | 1205 | 1079 | 1225 | 1274 | 1152 | 1069 | 1297 |  |  | 1132 | 882 | 1246 |  | 1363 | 1173 | 1241 | 1232 | 1183 | 1267 | 1281 | 1283 | 1281 | 1299 | 1308 | 1311 | 1215 | 1483 | 1152 | 1062 | 926 | 855 | 906 | 1082 | 1296 | 1480 | 1312 | 1364 | 1226 | 1280 | 1327 | 1331 | 1066 | 1228 | 1082 | 1218 | 984 |  | 1175 | 1318 | 585 | 1285 | 1178 |  |  | 1185 | 1251 | 1299 | 1251 | 1074 | 35.7 | 46 | 0.6 | 6.78 |  | 0 | 6.11 |  |  | 82335200 | 281497 | 55454144 | 61275 | 83122389 | 185944 | 60165461 | 55276 | 312195388.5 | 82741.8 | 81741.763 | 14.671 | 79891.981 | 10.044 | 83465.225 | 46.559 | 63493.724 | 12.824 | 308209.27 | 60.571 | 161609.029 | 308148.699 | 12 | 0 | 6.11 | 35.7 | 46 | 0.6 | 6.78 | 314197
2025-04-18 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1328 | 1353 | 1259 | 1355 | 1356 | 1247 | 1235 | 1251 | 1266 | 1254 | 1260 | 1276 | 1256 | 1105 | 1190 | 1224 | 1175 | 1184 | 1319 | 1330 | 1349 | 1204 | 1370 | 1379 | 1325 | 1333 | 1325 | 1359 | 1317 | 1347 | 1326 | 1225 | 1176 | 1505 | 1154 | 1324 | 1240 | 1202 | 1236 | 1262 | 1202 | 1201 | 1223 | 1243 | 1220 | 1261 | 1340 | 1242 | 1241 | 1271 | 1195 | 1257 | 1430 | 1417 | 1335 | 1384 | 1390 | 1273 | 1405 | 1363 | 1247 | 1402 | 1363 | 1463 | 1364 | 1357 | 1378 | 1195 | 1237 | 1244 | 1255 | 1204 | 1124 | 1259 | 1294 | 1436 | 1445 | 1242 | 1230 | 1347 | 1261 | 1271 | 1270 | 1263 | 1212 | 1179 | 1264 | 1251 | 1229 | 1222 | 1295 | 1210 | 1284 | 1223 | 1226 | 1224 | 1235 | 1235 | 1254 | 1148 | 1297 | 1260 | 1284 | 1266 | 1430 | 1062 | 1477 | 1393 | 1271 | 1402 | 1284 | 1331 | 1365 | 1403 | 1203 | 1248 | 1380 | 1280 | 1337 | 1237 | 1274 | 1368 | 1297 | 1261 | 1279 | 1468 | 1167 | 1198 | 1397 | 1399 | 1329 | 1343 | 1297 | 1113 | 1421 | 1357 | 1373 | 1327 | 1284 | 1281 | 1240 | 1284 | 1266 | 1405 | 1206 | 1368 | 1256 | 1156 | 1343 | 1374 | 1375 | 1258 | 1400 | 1260 | 1239 | 1224 | 1068 | 1204 | 1198 | 1199 | 1369 | 1187 | 1292 | 1323 | 1263 | 1210 | 1155 | 1326 | 1207 | 1107 | 1190 | 1179 | 1170 | 1234 | 1371 | 1199 | 1216 | 1090 | 1385 | 1228 | 1247 | 1276 | 1315 | 1312 | 1258 | 1360 | 1267 | 1269 | 1235 | 1102 | 1180 | 1146 | 1021 | 1168 | 1218 | 1107 | 1033 | 1241 |  |  | 1233 | 875 | 1184 |  | 1297 | 1118 | 1186 | 1176 | 1170 | 1212 | 1227 | 1234 | 1229 | 1244 | 1253 | 1258 | 1217 | 1424 | 1103 | 1014 | 963 | 896 | 998 | 1056 | 1240 | 1417 | 1249 | 1302 | 1263 | 1298 | 1319 | 1270 | 1012 | 1176 | 1032 | 1178 | 948 |  | 1175 | 1263 | 551 | 1173 | 1127 |  |  | 1098 | 1235 | 1264 | 1200 | 1063 | 35.61 | 47.4 | 1.3 | 5.1 |  | 0 | 5.95 |  |  | 82415821.321 | 281510.713 | 55532508.045 | 61284.336 | 83203137.502 | 185982.206 | 60226428.183 | 55288.399 | 312495765.901 | 82799.368 | 80621.321 | 13.713 | 78364.045 | 9.336 | 80748.502 | 38.206 | 60967.183 | 12.399 | 300377.401 | 57.568 | 158962.317 | 300319.833 | 12 | 0 | 5.95 | 35.61 | 47.4 | 1.3 | 5.1 | 305558
2025-04-19 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1318 | 1344 | 1246 | 1236 | 1328 | 1232 | 1209 | 1219 | 1244 | 1234 | 1237 | 1246 | 1226 | 1079 | 1188 | 1224 | 1175 | 1190 | 1128 | 1322 | 1250 | 1197 | 1375 | 1280 | 1303 | 1307 | 1298 | 1331 | 1283 | 1315 | 1363 | 1193 | 1162 | 1476 | 1131 | 1313 | 1212 | 1173 | 1205 | 1230 | 1170 | 1168 | 1190 | 1210 | 1185 | 1259 | 1325 | 1212 | 1189 | 1217 | 1160 | 1220 | 1392 | 1379 | 1316 | 1314 | 1363 | 1221 | 1367 | 1328 | 1188 | 1349 | 1400 | 1461 | 13143 | 1337 | 1356 | 1163 | 1227 | 1234 | 1245 | 1202 | 1082 | 1218 | 1256 | 1398 | 1407 | 1208 | 1192 | 1331 | 1228 | 1237 | 1209 | 1211 | 1178 | 1182 | 1264 | 1252 | 1225 | 1220 | 1271 | 1256 | 1277 | 1247 | 1268 | 1201 | 1200 | 1225 | 1222 | 1135 | 1271 | 1228 | 1252 | 1231 | 1398 | 1054 | 1446 | 1373 | 1254 | 1371 | 1278 | 1330 | 1382 | 1379 | 1201 | 1252 | 1367 | 1312 | 1319 | 1225 | 1246 | 1338 | 1280 | 1232 | 1293 | 1498 | 1167 | 1197 | 1400 | 1388 | 1325 | 1331 | 1284 | 1103 | 1399 | 1324 | 1338 | 1267 | 1283 | 1272 | 1230 | 1270 | 1255 | 1397 | 1197 | 1353 | 1229 | 1133 | 1310 | 1344 | 1341 | 1230 | 1368 | 1226 | 1206 | 1193 | 1100 | 1169 | 1106 | 1172 | 1338 | 1160 | 1257 | 1292 | 1166 | 1143 | 1126 | 1294 | 1179 | 1080 | 1162 | 1161 | 1142 | 1203 | 1413 | 1227 | 1221 | 1101 | 1369 | 1242 | 1204 | 1237 | 1282 | 1357 | 1287 | 1377 | 1283 | 1301 | 1202 | 1076 | 1156 | 1126 | 1011 | 1142 | 1195 | 1083 | 1014 | 1214 |  |  | 1098 | 858 | 1162 |  | 1297 | 1091 | 1186 | 1184 | 1162 | 1230 | 1227 | 1246 | 1233 | 1263 | 1221 | 1232 | 1207 | 1389 | 1080 | 1063 | 998 | 898 | 889 | 1040 | 1238 | 1390 | 1228 | 1277 | 1268 | 1310 | 1309 | 1251 | 1001 | 1156 | 1014 | 1157 | 929 |  | 1175 | 1241 | 604 | 1156 | 1108 |  |  | 1110 | 1278 | 1263 | 1210 | 1063 | 35.4 | 46.4 | 1.2 | 5.3 |  | 0 | 5.87 |  |  | 82494845 | 281530 | 55609764 | 61302 | 83282860 | 186033 | 60286490 | 55303 | 312791511.1 | 82871.8 | 79023.679 | 19.287 | 77255.955 | 17.664 | 79722.498 | 50.794 | 60061.817 | 14.601 | 295745.199 | 72.432 | 156242.683 | 295672.767 | 12 | 0 | 5.87 | 35.4 | 46.4 | 1.2 | 5.3 | 312642
2025-04-20 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1466 | 1477 | 1357 | 1354 | 1446 | 1337 | 1345 | 1357 | 1374 | 1381 | 1364 | 1378 | 1363 | 1213 | 1306 | 1342 | 1280 | 1309 | 1474 | 1466 | 1374 | 1303 | 1488 | 1404 | 1468 | 1447 | 1441 | 1457 | 1390 | 1423 | 1402 | 1294 | 1261 | 1602 | 1230 | 1426 | 1317 | 1277 | 1310 | 1336 | 1271 | 1273 | 1294 | 1316 | 1286 | 1374 | 1440 | 1315 | 1319 | 1352 | 1273 | 1339 | 1519 | 1506 | 1435 | 1467 | 1503 | 1334 | 1488 | 1443 | 1288 | 1460 | 1463 | 1498 | 1459 | 1454 | 1069 | 1194 | 1318 | 1334 | 1355 | 1250 | 1385 | 1356 | 1556 | 1537 | 1553 | 1338 | 1329 | 1412 | 1354 | 1373 | 1365 | 1370 | 1280 | 1213 | 1385 | 1371 | 1333 | 1295 | 1365 | 1298 | 1398 | 1388 | 1302 | 1299 | 1320 | 1282 | 1322 | 1168 | 1371 | 1329 | 1358 | 1336 | 1508 | 1071 | 1568 | 1480 | 1363 | 1486 | 1329 | 1435 | 1450 | 1515 | 1253 | 1357 | 1486 | 1483 | 1391 | 1334 | 1351 | 1436 | 1334 | 1335 | 1354 | 1563 | 1275 | 1299 | 1515 | 1512 | 1443 | 1445 | 1390 | 1194 | 1522 | 1436 | 1455 | 1374 | 1405 | 1391 | 1335 | 1389 | 1376 | 1523 | 1317 | 1486 | 1376 | 1270 | 1450 | 1475 | 1485 | 1358 | 1485 | 1336 | 1314 | 1313 | 1278 | 1296 | 1213 | 1279 | 1451 | 1260 | 1366 | 1402 | 1266 | 1256 | 1255 | 1437 | 1319 | 1221 | 1300 | 1295 | 1277 | 1358 | 1545 | 1348 | 1355 | 1218 | 1503 | 1370 | 1307 | 1370 | 1396 | 1477 | 1412 | 1500 | 1417 | 1429 | 1362 | 1222 | 1266 | 1224 | 1139 | 1307 | 1354 | 1233 | 1117 | 1368 |  |  | 1197 | 932 | 1280 |  | 1388 | 1189 | 1327 | 1304 | 1267 | 1350 | 1361 | 1350 | 1362 | 1383 | 1263 | 1210 | 1244 | 1534 | 1171 | 1077 | 1010 | 963 | 965 | 1134 | 1355 | 1509 | 1330 | 1383 | 1310 | 1398 | 1362 | 1349 | 1086 | 1256 | 1101 | 1256 | 1007 |  | 1175 | 1348 | 660 | 1249 | 1199 |  |  | 1202 | 1212 | 1280 | 1298 | 1096 | 35.9 | 47.6 | 1.6 | 5.1 |  | 0 | 6.7 |  |  | 82581398.495 | 281543.717 | 55693455.236 | 61311.454 | 83370328.118 | 186091.183 | 60351293.025 | 55314.633 | 313113666.068 | 82927.647 | 86553.495 | 13.717 | 83691.236 | 9.454 | 87468.118 | 58.183 | 64803.025 | 11.633 | 322154.968 | 55.847 | 170221.56 | 322099.121 | 12 | 0 | 6.7 | 35.9 | 47.6 | 1.6 | 5.1 | 327345
2025-04-21 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1450 | 1498 | 1344 | 1338 | 1447 | 1326 | 1369 | 1367 | 1393 | 1398 | 1360 | 1376 | 1359 | 1219 | 1302 | 1337 | 1266 | 1297 | 1464 | 1458 | 1361 | 1295 | 1475 | 1400 | 1460 | 1438 | 1431 | 1461 | 1431 | 1460 | 1450 | 1450 | 1400 | 1650 | 1400 | 1441 | 1302 | 1263 | 1292 | 1320 | 1300 | 1405 | 1276 | 1297 | 1287 | 1376 | 1445 | 1400 | 1409 | 1410 | 1300 | 1289 | 1466 | 1452 | 1450 | 1391 | 1452 | 1271 | 1413 | 1374 | 1224 | 1388 | 1490 | 1510 | 1454 | 1448 | 1467 | 1205 | 1327 | 1351 | 1361 | 1259 | 1390 | 1362 | 1557 | 1535 | 1549 | 1329 | 1318 | 1404 | 1344 | 1363 | 1349 | 1355 | 1282 | 1214 | 1395 | 1391 | 1344 | 1301 | 1368 | 1397 | 1385 | 1384 | 1310 | 1291 | 1302 | 1278 | 1304 | 1150 | 1355 | 1312 | 1342 | 1320 | 1490 | 1098 | 1555 | 1470 | 1346 | 1475 | 1324 | 1426 | 1448 | 1500 | 1250 | 1342 | 1468 | 1463 | 1384 | 1317 | 1334 | 1422 | 1329 | 1318 | 1337 | 1426 | 1257 | 1280 | 1495 | 1489 | 1422 | 1428 | 1384 | 1200 | 1529 | 1436 | 1468 | 1386 | 1378 | 1373 | 1332 | 1379 | 1350 | 1502 | 1295 | 1516 | 1355 | 1252 | 1449 | 1456 | 1477 | 1362 | 1465 | 1360 | 1337 | 1320 | 1325 | 1282 | 1246 | 1314 | 1503 | 1303 | 1443 | 1445 | 1317 | 1270 | 1263 | 1447 | 1322 | 1218 | 1302 | 1292 | 1281 | 1356 | 1528 | 1333 | 1341 | 1203 | 1486 | 1355 | 1292 | 1358 | 1428 | 1462 | 1396 | 1502 | 1401 | 1412 | 1354 | 1218 | 1250 | 1213 | 1132 | 1300 | 1339 | 1203 | 1121 | 1357 |  |  | 1181 | 921 | 1272 |  | 1394 | 1242 | 1311 | 1290 | 1259 | 1334 | 1343 | 1339 | 1343 | 1368 | 1369 | 1356 | 1235 | 1542 | 1156 | 1061 | 1062 | 998 | 952 | 1116 | 1337 | 1489 | 1317 | 1369 | 1362 | 1400 | 1398 | 1380 | 1090 | 1300 | 1150 | 1303 | 1100 |  | 1250 | 1360 | 668 | 1298 | 1283 |  |  | 1210 | 1412 | 1300 | 1310 | 1117 | 37.4 | 47.37 | 2.08 | 5.4 |  | 0 | 6.75 |  |  | 82666836.801 | 281560.312 | 55776650.679 | 61327.538 | 83457790.293 | 186135.647 | 60416203.414 | 55328.08 | 313434297.117 | 82986.708 | 85438.306 | 16.595 | 83195.443 | 16.084 | 87462.175 | 44.464 | 64910.389 | 13.447 | 320631.049 | 59.061 | 168601.07 | 320571.988 | 12 | 0 | 6.75 | 37.4 | 47.37 | 2.08 | 5.4 | 328589
2025-04-22 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1563 | 1564 | 1437 | 1432 | 1551 | 1422 | 1464 | 1462 | 1483 | 1494 | 1492 | 1488 | 1466 | 1316 | 1397 | 1423 | 1308 | 1339 | 1506 | 1502 | 1405 | 1357 | 1539 | 1455 | 1507 | 1484 | 1478 | 1509 | 1504 | 1528 | 1498 | 1398 | 1324 | 1681 | 1347 | 1551 | 1387 | 1352 | 1403 | 1433 | 1340 | 1347 | 1387 | 1409 | 1412 | 1470 | 1577 | 1427 | 1382 | 1421 | 1335 | 1409 | 1603 | 1586 | 1479 | 1525 | 1575 | 1376 | 1529 | 1484 | 1325 | 1428 | 1510 | 1580 | 1580 | 1571 | 1590 | 1261 | 1413 | 1422 | 1464 | 1326 | 1479 | 1434 | 1638 | 1611 | 1635 | 1406 | 1398 | 1467 | 1427 | 1448 | 1424 | 1414 | 1423 | 1339 | 1488 | 1475 | 1448 | 1379 | 1478 | 1400 | 1483 | 1475 | 1378 | 1353 | 1386 | 1339 | 1379 | 1419 | 1431 | 1398 | 1429 | 1406 | 1565 | 1424 | 1638 | 1566 | 1436 | 1561 | 1384 | 1506 | 1522 | 1594 | 1310 | 1423 | 1552 | 1593 | 1446 | 1443 | 1476 | 1520 | 1408 | 1447 | 1438 | 1463 | 1354 | 1390 | 1614 | 1622 | 1549 | 1561 | 1510 | 1296 | 1652 | 1548 | 1486 | 1492 | 1470 | 1462 | 1448 | 1479 | 1399 | 1605 | 1391 | 1625 | 1600 | 1341 | 1543 | 1556 | 1576 | 1451 | 1557 | 1447 | 1426 | 1407 | 1363 | 1304 | 1343 | 1408 | 1618 | 1401 | 1554 | 1559 | 1412 | 1346 | 1347 | 1538 | 1405 | 1297 | 1386 | 1373 | 1357 | 1444 | 1628 | 1429 | 1428 | 1281 | 1585 | 1442 | 1378 | 1442 | 1547 | 1556 | 1479 | 1606 | 1493 | 1505 | 1441 | 1296 | 1332 | 1286 | 1198 | 1385 | 1428 | 1262 | 1181 | 1452 |  |  | 1266 | 982 | 1354 |  | 1561 | 1363 | 1396 | 1370 | 1323 | 1418 | 1431 | 1410 | 1432 | 1451 | 1461 | 1450 | 1572 | 1627 | 1232 | 1133 | 1100 | 1010 | 1019 | 1189 | 1427 | 1582 | 1399 | 1452 | 1410 | 1462 | 1421 | 1414 | 1141 | 1319 | 1156 | 1318 | 1052 |  | 1175 | 1414 | 700 | 1313 | 1257 |  |  | 1278 | 1400 | 1335 | 1320 | 1149 | 37.9 | 46.08 | 1.93 | 5.1 |  | 0 | 7.08 |  |  | 82757675.466 | 281573.49 | 55865708.265 | 61336.975 | 83551224.232 | 186178.147 | 60485503.243 | 55339.845 | 313776481.848 | 83040.583 | 90838.665 | 13.178 | 89057.586 | 9.437 | 93433.939 | 42.5 | 69299.829 | 11.765 | 342184.731 | 53.875 | 179873.636 | 342130.856 | 12 | 0 | 7.08 | 37.9 | 46.08 | 1.93 | 5.1 | 347261
2025-04-23 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1634 | 1639 | 1516 | 1505 | 1633 | 1507 | 1518 | 1519 | 1486 | 1560 | 1548 | 1539 | 1517 | 1362 | 1440 | 1467 | 1357 | 1368 | 1535 | 1529 | 1433 | 1385 | 1574 | 1482 | 1534 | 1512 | 1507 | 1504 | 1529 | 1557 | 1560 | 1425 | 1383 | 1730 | 1424 | 1614 | 1481 | 1434 | 1460 | 1494 | 1424 | 1423 | 1443 | 1463 | 1458 | 1524 | 1623 | 1483 | 1435 | 1476 | 1387 | 1461 | 1664 | 1646 | 1574 | 1612 | 1652 | 1426 | 1601 | 1540 | 1431 | 808 | 1570 | 1560 | 1623 | 1616 | 1634 | 1278 | 1448 | 1440 | 1524 | 1354 | 1526 | 1468 | 1662 | 1637 | 1668 | 1434 | 1434 | 1498 | 1474 | 1484 | 1476 | 1482 | 1462 | 1518 | 1548 | 1536 | 1506 | 1420 | 1518 | 852 | 1526 | 1522 | 1392 | 1380 | 1445 | 1374 | 1467 | 1475 | 1474 | 1478 | 1511 | 1491 | 1614 | 1520 | 1670 | 1602 | 1478 | 1644 | 1440 | 1540 | 1554 | 1631 | 1336 | 1451 | 1586 | 1656 | 1488 | 1495 | 1533 | 1558 | 1441 | 1517 | 1528 | 1489 | 1402 | 1439 | 1671 | 1678 | 1600 | 1605 | 1543 | 1329 | 1682 | 1585 | 1621 | 1524 | 1501 | 1501 | 1483 | 1526 | 1424 | 1651 | 1393 | 1673 | 1561 | 1408 | 1614 | 1641 | 1640 | 1516 | 1615 | 1508 | 1487 | 1467 | 1430 | 1400 | 1395 | 1455 | 1671 | 1438 | 1592 | 1600 | 1445 | 1376 | 1415 | 1571 | 1486 | 1358 | 1457 | 1440 | 1388 | 1511 | 1673 | 1459 | 1467 | 1314 | 1627 | 1461 | 1416 | 1477 | 1643 | 1682 | 1526 | 1668 | 1536 | 1547 | 1509 | 1340 | 1424 | 1389 | 1234 | 1445 | 1481 | 1301 | 1210 | 1489 |  |  | 1303 | 1009 | 1400 |  | 1606 | 1405 | 1308 | 1339 | 1506 | 1502 | 1405 | 1358 | 1540 | 1416 | 1432 | 1461 | 1461 | 1450 | 1627 | 1233 | 1134 | 1111 | 1011 | 1189 | 1337 | 1478 | 1378 | 1410 | 1428 | 1463 | 1232 | 1310 | 1067 | 1232 | 1081 | 1234 | 998 |  | 1175 | 1445 | 699 | 1343 | 1284 |  |  | 1210 | 1310 | 1380 | 1298 | 1175 | 38 | 46.1 | 2 | 5.3 |  | 0 | 7.22 |  |  | 82851348.837 | 281586.673 | 55957678.329 | 61345.996 | 83647713.106 | 186202.292 | 60554920.387 | 55352.806 | 314127642.011 | 83095.409 | 93673.371 | 13.183 | 91970.064 | 9.021 | 96488.874 | 24.145 | 69417.144 | 12.961 | 351160.163 | 54.826 | 185621.231 | 351105.337 | 12 | 0 | 7.22 | 38 | 46.1 | 2 | 5.3 | 355743
2025-04-24 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1619 | 1624 | 1501 | 1492 | 1608 | 1487 | 1482 | 1482 | 1453 | 1527 | 1514 | 1502 | 1484 | 1328 | 1433 | 1477 | 1432 | 1435 | 1605 | 1575 | 1490 | 1438 | 1641 | 1538 | 1575 | 1545 | 1533 | 1506 | 1552 | 1579 | 1580 | 1445 | 1374 | 1712 | 1418 | 1616 | 1470 | 1408 | 1427 | 1459 | 1399 | 1394 | 1415 | 1429 | 1448 | 1515 | 1604 | 1455 | 1224 | 1256 | 1187 | 1252 | 1426 | 1414 | 1346 | 1381 | 1402 | 1220 | 1411 | 1370 | 1226 | 1112 | 1595 | 1563 | 1594 | 1587 | 1603 | 1251 | 1418 | 1419 | 1491 | 1311 | 1512 | 1436 | 1648 | 1622 | 1653 | 1414 | 1421 | 1452 | 1470 | 1476 | 1471 | 1487 | 1452 | 1509 | 1518 | 1505 | 1476 | 1377 | 1474 | 755 | 1508 | 1515 | 1395 | 1325 | 1422 | 1321 | 1461 | 1486 | 1463 | 1475 | 1505 | 1482 | 1589 | 1493 | 1638 | 1611 | 1498 | 1578 | 1394 | 1501 | 1509 | 1623 | 1306 | 1430 | 1580 | 1613 | 1440 | 1456 | 1497 | 1515 | 1390 | 1478 | 1492 | 1492 | 1377 | 1406 | 1631 | 1639 | 1567 | 1571 | 1525 | 1322 | 1680 | 1568 | 1612 | 1515 | 1513 | 1500 | 1465 | 1501 | 1436 | 1658 | 1386 | 1671 | 1483 | 1376 | 1587 | 1654 | 1608 | 1491 | 1631 | 1486 | 1447 | 1472 | 1389 | 1404 | 1366 | 1424 | 1636 | 1408 | 1557 | 1567 | 1413 | 1343 | 1388 | 1534 | 1452 | 1334 | 1432 | 1418 | 1354 | 1480 | 1671 | 1462 | 1482 | 1324 | 1671 | 1488 | 1449 | 1491 | 1606 | 1650 | 1527 | 1644 | 1543 | 1551 | 1489 | 1342 | 1413 | 1379 | 1229 | 1423 | 1472 | 1274 | 1184 | 1479 |  |  | 1279 | 992 | 1369 |  | 1573 | 1371 | 1448 | 1342 | 1334 | 1416 | 1459 | 1401 | 1453 | 1452 | 1468 | 1453 | 1574 | 1625 | 1430 | 1139 | 1139 | 1114 | 1008 | 1175 | 1405 | 1564 | 1377 | 1435 | 1434 | 1467 | 1538 | 1392 | 1127 | 1302 | 1141 | 1304 | 1441 |  | 1175 | 1449 | 621 | 1315 | 1263 |  |  | 1278 | 1353 | 1260 | 1152 | 1182 | 36.5 | 45.1 | 2.47 | 8.3 |  | 0 | 7.18 |  |  | 82942719.164 | 281600.438 | 56048174.186 | 61355.935 | 83743255.547 | 186244.522 | 60624877.611 | 55365.967 | 314474585.976 | 83153.541 | 91370.327 | 13.765 | 90495.857 | 9.939 | 95542.441 | 42.23 | 69957.224 | 13.161 | 346943.965 | 58.132 | 181842.48 | 346885.833 | 12 | 0 | 7.18 | 36.5 | 45.1 | 2.47 | 8.3 | 351420
2025-04-25 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1522 | 1531 | 1418 | 1410 | 1520 | 1408 | 1398 | 1398 | 1371 | 1443 | 1433 | 1420 | 1399 | 1254 | 1354 | 1398 | 1178 | 1179 | 1330 | 1312 | 1226 | 1191 | 1354 | 1282 | 1325 | 1308 | 1302 | 1282 | 1293 | 1319 | 1584 | 1208 | 1287 | 1621 | 1343 | 1420 | 1391 | 1331 | 1352 | 1379 | 1343 | 1333 | 1361 | 1371 | 1395 | 1438 | 1534 | 1398 | 1347 | 1397 | 1321 | 1390 | 1578 | 1563 | 1475 | 1519 | 1535 | 1333 | 1553 | 1508 | 1340 | 1115 | 1592 | 1573 | 1508 | 1500 | 1517 | 1183 | 1348 | 1342 | 1413 | 1260 | 1443 | 1364 | 1573 | 1549 | 1579 | 1356 | 1361 | 1391 | 1402 | 1404 | 1401 | 1415 | 1400 | 1433 | 1451 | 1438 | 1409 | 1292 | 1312 | 1000 | 1533 | 1443 | 1396 | 1355 | 1365 | 1408 | 1377 | 1401 | 1437 | 1390 | 1417 | 1394 | 1540 | 1404 | 1541 | 1520 | 1417 | 1504 | 1508 | 1453 | 1469 | 1559 | 1408 | 1383 | 1517 | 1539 | 1512 | 1392 | 1422 | 1428 | 1513 | 1401 | 1405 | 1489 | 1319 | 1347 | 1563 | 1570 | 1508 | 1517 | 1472 | 1262 | 1597 | 1490 | 1531 | 1437 | 1439 | 1420 | 1408 | 1415 | 1358 | 1561 | 1306 | 1574 | 1435 | 1296 | 1494 | 1510 | 1512 | 1403 | 1535 | 1400 | 1382 | 1374 | 1392 | 1335 | 1280 | 1339 | 1533 | 1324 | 1459 | 1468 | 1408 | 1267 | 1307 | 1446 | 1370 | 1258 | 1353 | 1339 | 1280 | 1393 | 1610 | 1402 | 1410 | 1266 | 1595 | 1424 | 1380 | 1420 | 1506 | 1568 | 1466 | 1570 | 1476 | 1482 | 1408 | 1310 | 1335 | 1303 | 1203 | 1343 | 1429 | 1257 | 1170 | 1410 |  |  | 1231 | 934 | 1290 |  | 1488 | 1296 | 1379 | 1327 | 1382 | 1378 | 1390 | 1395 | 1398 | 1394 | 1389 | 1440 | 1493 | 1550 | 1364 | 1163 | 1132 | 1107 | 929 | 1084 | 1297 | 1441 | 1270 | 1319 | 1421 | 1455 | 1416 | 1285 | 1035 | 1199 | 1049 | 1202 | 956 |  | 1175 | 1433 | 581 | 1237 | 1188 |  |  | 1271 | 1347 | 1188 | 1152 | 1039 | 37.08 | 47.02 | 1.4 | 6.5 |  | 0 | 7.1 |  |  | 83028954.272 | 281612.677 | 56135133.047 | 61364.572 | 83833891.496 | 186312.499 | 60691066.882 | 55377.348 | 314804205.234 | 83205.261 | 86235.108 | 12.239 | 86958.861 | 8.637 | 90635.949 | 67.977 | 66189.271 | 11.381 | 329619.258 | 51.72 | 173173.093 | 329567.538 | 12 | 0 | 7.1 | 37.08 | 47.02 | 1.4 | 6.5 | 335649
2025-04-26 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1168 | 1144 | 1091 | 1079 | 1169 | 1088 | 1086 | 1088 | 1071 | 1133 | 1116 | 1104 | 1086 | 1060 | 1039 | 1071 | 1038 | 1036 | 1174 | 1155 | 1079 | 1053 | 1195 | 1133 | 1166 | 1155 | 1151 | 1162 | 1158 | 1180 | 1076 | 1089 | 1081 | 1243 | 1037 | 1091 | 1087 | 1044 | 1057 | 1077 | 1044 | 1029 | 1049 | 1056 | 1070 | 1092 | 1173 | 1071 | 1071 | 1099 | 1047 | 1088 | 1240 | 1226 | 1168 | 1203 | 1228 | 1095 | 1227 | 1191 | 1080 | 1206 | 1083 | 1204 | 1175 | 1170 | 1184 | 974 | 1055 | 1030 | 1084 | 1042 | 1102 | 1062 | 1211 | 1198 | 1214 | 1048 | 1056 | 1104 | 1074 | 1077 | 1077 | 1085 | 1068 | 1083 | 1103 | 1090 | 1088 | 1082 | 1116 | 1131 | 1103 | 1097 | 1134 | 1052 | 1053 | 1069 | 1046 | 1064 | 1092 | 1058 | 1078 | 1068 | 1196 | 1100 | 1189 | 1170 | 1077 | 1197 | 1187 | 1136 | 1160 | 1200 | 1068 | 1074 | 1169 | 1216 | 1209 | 1082 | 1101 | 1127 | 1183 | 1090 | 1105 | 1196 | 1017 | 1037 | 1199 | 1199 | 1153 | 1156 | 1131 | 966 | 1223 | 1142 | 1170 | 1101 | 1102 | 1093 | 1077 | 1088 | 1033 | 1193 | 1002 | 1198 | 1073 | 998 | 1161 | 1174 | 1177 | 1084 | 1174 | 1084 | 1067 | 1055 | 1054 | 1022 | 1083 | 1039 | 1195 | 1027 | 1125 | 1141 | 1110 | 985 | 1016 | 1122 | 1060 | 977 | 1053 | 1034 | 1001 | 1078 | 1241 | 1079 | 1088 | 1089 | 1233 | 1102 | 1067 | 1106 | 1163 | 1208 | 1133 | 1216 | 1139 | 1140 | 1097 | 1101 | 1019 | 1011 | 1113 | 1025 | 1082 | 1130 | 1060 | 1083 |  |  | 1050 | 768 | 1013 |  | 1137 | 1011 | 1054 | 1020 | 1053 | 1065 | 1056 | 1073 | 1084 | 1105 | 1086 | 1114 | 1166 | 1219 | 1035 | 1113 | 1050 | 1060 | 914 | 1008 | 1029 | 1153 | 1026 | 1055 | 1021 | 1089 | 1130 | 1038 | 835 | 957 | 842 | 959 | 758 |  | 1175 | 1163 | 588 | 1200 | 1050 |  |  | 1011 | 1100 | 1080 | 1157 | 981 | 36.9 | 43.37 | 1.8 | 9.9 |  | 0 | 5.34 |  |  | 83099811.757 | 281622.638 | 56203507.306 | 61372.195 | 83904016.468 | 186328.13 | 60742671.538 | 55387.237 | 315064821.334 | 83247.126 | 70857.485 | 9.961 | 68374.259 | 7.623 | 70124.972 | 15.631 | 51604.656 | 9.889 | 260616.1 | 41.865 | 139214.16 | 260574.235 | 12 | 0 | 5.34 | 36.9 | 43.37 | 1.8 | 9.9 | 266123
2025-04-27 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1233 | 1194 | 1147 | 1136 | 1228 | 1137 | 1142 | 1133 | 1126 | 1192 | 1170 | 1150 | 1136 | 1125 | 1192 | 1170 | 1082 | 1094 | 1226 | 1150 | 1146 | 1262 | 1187 | 1232 | 1225 | 1232 | 1214 | 1262 | 1234 | 1206 | 1235 | 1213 | 975 | 1048 | 930 | 1069 | 1069 | 1027 | 1054 | 1074 | 1022 | 1011 | 1045 | 1050 | 1053 | 1078 | 1172 | 1071 | 1068 | 1068 | 1093 | 1041 | 1080 | 1236 | 1225 | 1162 | 1180 | 1228 | 1094 | 1213 | 1178 | 1070 | 1192 | 1213 | 1205 | 1199 | 1219 | 1088 | 1096 | 1055 | 1127 | 1129 | 1143 | 1100 | 1273 | 1254 | 1276 | 1102 | 1099 | 1158 | 1128 | 1134 | 1119 | 1086 | 1112 | 1134 | 1151 | 1139 | 1136 | 1130 | 1159 | 1241 | 1145 | 1160 | 1206 | 1086 | 1091 | 1121 | 1111 | 1111 | 1141 | 1122 | 1137 | 1113 | 1273 | 1133 | 1276 | 1220 | 1127 | 1221 | 1205 | 1170 | 1227 | 1248 | 1131 | 1111 | 1209 | 1225 | 1224 | 1106 | 1124 | 1149 | 1196 | 1115 | 1133 | 1187 | 1056 | 1073 | 1249 | 1246 | 1196 | 1201 | 1169 | 1005 | 1257 | 1192 | 1218 | 1160 | 1162 | 1151 | 1115 | 1153 | 1086 | 1258 | 1052 | 1262 | 1125 | 1043 | 1204 | 1224 | 1226 | 1123 | 1214 | 1121 | 1104 | 1092 | 1057 | 1081 | 1026 | 1078 | 1237 | 1065 | 1170 | 1182 | 1160 | 1021 | 1060 | 1165 | 1125 | 1026 | 1113 | 1086 | 1032 | 1125 | 1177 | 1277 | 1113 | 1008 | 1275 | 1139 | 1100 | 1140 | 1208 | 1252 | 1167 | 1255 | 1175 | 1170 | 1138 | 1028 | 1031 | 1011 | 1103 | 1133 | 1095 | 982 | 956 | 1106 |  |  | 997 | 765 | 1027 |  | 1171 | 1018 | 1076 | 1042 | 1078 | 1091 | 1086 | 1100 | 1112 | 1126 | 1136 | 1134 | 1183 | 1206 | 1255 | 1069 | 903 | 1052 | 760 | 912 | 1050 | 1151 | 1050 | 1061 | 1133 | 1092 | 1140 | 1083 | 950 | 1103 | 930 | 1010 | 965 |  | 1172 | 1170 | 931 | 1204 | 1032 |  |  | 1056 | 1032 | 1078 | 1153 | 1103 | 38 | 45.8 | 1.9 | 6.1 |  | 0 | 5.5 |  |  | 83171848.185 | 281686.886 | 56274614.128 | 61382.252 | 83976924.049 | 186398.997 | 60795693.149 | 55399.988 | 315333493.718 | 83305.997 | 72036.428 | 64.248 | 71106.822 | 10.057 | 72907.581 | 70.867 | 53021.611 | 12.751 | 268672.384 | 58.871 | 143068.945 | 268613.513 | 12 | 0 | 5.5 | 38 | 45.8 | 1.9 | 6.1 | 274076
2025-04-28 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1375.6 | 1331.9 |  | 1267.5 | 1366.8 | 1266.4 | 1274 | 1261.9 | 1255.4 | 1325.2 | 1314 | 1280.1 | 1260.3 | 1179.1 | 1207.8 | 1246.7 | 1208.7 | 1222.7 | 1364 | 1373.6 | 1286.6 | 1292.1 | 1403.3 | 1340.3 | 1382.2 | 1364.7 | 1361.8 | 1400.7 | 1344.6 | 1378.4 | 1239.3 | 1259.8 | 1154.4 | 1456.1 | 1099.5 | 1263.6 | 1258.1 | 1200.2 | 1264.1 | 1277.8 | 1210.7 | 1222.4 | 1262.5 | 1254.9 | 1249.1 | 1273.8 | 1386.9 | 1270.6 | 1258.1 | 1287.1 | 1222.1 | 1269.6 | 1401.5 | 1440.5 | 1367.4 | 1385.9 | 1442.9 | 1295.4 | 1421.2 | 1377.5 | 1261.4 | 1398 | 1265.7 | 1132.1 | 1370.1 | 1363.1 | 1386.9 | 1216.6 | 1251 | 1201.1 | 1267.4 | 1266.5 | 1284.2 | 1267.1 | 1471.6 | 1450.4 | 1459.5 | 1253.7 | 1242.1 | 1337.1 | 1270.1 | 1279.5 | 1265.2 | 1225.3 | 1252.5 | 1270.1 | 1289.3 | 1275.4 | 1272.8 | 1268 | 1323.4 | 1375 | 1296 | 1291.7 | 1328.4 | 1217.8 | 1235.5 | 1266.1 | 1255.9 | 1258.6 | 1291.2 | 1267.7 | 1287.9 | 1260.9 | 1405.5 | 1282.3 | 1385.6 | 1409.7 | 1286.1 | 1403.7 | 1373.7 | 1374.1 | 1421.3 | 1443.1 | 1284.1 | 1293.4 | 1405.1 | 1406.2 | 1401.9 | 1248.1 | 1281.5 | 1326.1 | 1364.2 | 1264.9 | 1282.2 | 1386.5 | 1179.3 | 1202.7 | 1400 | 1399.8 | 1343.1 | 1350.2 | 1306.9 | 1138 | 1440 | 1371.1 | 1387.3 | 1311.5 | 1306.5 | 1288.3 | 1247.4 | 1292.3 | 1223.2 | 1411.5 | 1183.6 | 1417.6 | 1264.1 | 1171.9 | 1353.6 | 1372.9 | 1378.7 | 1267 | 1369.3 | 1307 | 1246.5 | 1230.7 | 1235.5 | 1213.2 | 1147.1 | 1203.1 | 1378.6 | 1189.4 | 1309.9 | 1317.6 | 1279 | 1135.2 | 1187.9 | 1295.1 | 1251.3 | 1141.7 | 1242.5 | 1210.6 | 1149.4 | 1252.3 | 1430.2 | 1248.4 | 1255.6 | 1129.8 | 1427.7 | 1274.2 | 1230.7 | 1271.1 | 1351.6 | 1397.8 | 1309.4 | 1405.5 | 1317 | 1319.4 | 1268.8 | 1145.4 | 1160.7 | 1133.9 | 817 | 1180.2 | 1273.8 | 1122.8 | 1086.4 | 1302.2 |  |  | 1085.6 | 848.4 | 1175.3 |  | 1327.6 | 1157.3 | 1219.3 | 1188.2 | 1224.8 | 1233.6 | 1232.3 | 1244.3 | 1258.9 | 1291.9 | 1291.5 | 1297.9 | 1374.4 | 1438.4 | 1214.6 | 1021.2 | 930.5 | 574.8 | 862.5 | 1005.9 | 1163 | 1308.6 | 1171.9 | 1214.6 | 1224.5 | 1276 | 1307.2 | 1192.9 | 969.7 | 1106.5 | 977.5 | 1112.9 | 1065 |  | 1670.5 | 1313 | 512.6 | 1245 | 1200 |  |  | 1202.9 | 1173.9 | 738.9 | 1112 | 1012 | 38.9724 | 45.8338 | 2.2649 | 5.9 |  | 0 | 6.2 |  |  | 83254910.28 | 281723.886 | 56355236.306 | 61393.252 | 84058696.005 | 186454.997 | 60856040.738 | 55412 | 315638896.479 | 83366.997 | 83062.095 | 37 | 80622.178 | 11 | 81771.956 | 56 | 60347.589 | 12.012 | 305402.761 | 61 | 163636.273 | 305341.761 | 12 | 0 | 6.2 | 38.9724 | 45.8338 | 2.2649 | 5.9 | 306127.9
2025-04-29 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1407 | 1364 | 1308 | 1299 | 1396 | 1295 | 1302 | 1289 | 1283 | 1353 | 1343 | 1311 | 1290 | 1208 | 1234 | 1278 | 1238 | 1306 | 1394 | 1408 | 1318 | 1321 | 1439 | 1369 | 1414 | 1398 | 1394 | 1432 | 1371 | 1411 | 1264 | 1289 | 1177 | 1560 | 1117 | 1288 | 1290 | 1258 | 1293 | 1308 | 1254 | 1251 | 1291 | 1282 | 1301 | 1320 | 1437 | 1300 | 1289 | 1318 | 1255 | 1302 | 1445 | 1490 | 1397 | 1418 | 1475 | 1325 | 1458 | 1409 | 1294 | 1428 | 1299 | 1154 | 1404 | 1396 | 1421 | 1325 | 1281 | 1283 | 1299 | 1298 | 1311 | 1302 | 1504 | 1483 | 1495 | 1299 | 1279 | 1390 | 1331 | 1327 | 1298 | 1307 | 1302 | 1313 | 1322 | 1307 | 1302 | 1299 | 1354 | 1363 | 1329 | 1325 | 1399 | 1239 | 1270 | 1298 | 1290 | 1293 | 1324 | 1301 | 1326 | 1300 | 1447 | 1320 | 1601 | 1444 | 1320 | 1448 | 1410 | 1411 | 1485 | 1479 | 1314 | 1328 | 1440 | 1441 | 1437 | 1284 | 1319 | 1356 | 1401 | 1298 | 1316 | 1425 | 1210 | 1223 | 1428 | 1429 | 1373 | 1379 | 1327 | 1163 | 1471 | 1399 | 1477 | 1337 | 1338 | 1314 | 1267 | 1316 | 1149 | 1447 | 1214 | 1454 | 1290 | 1200 | 1386 | 1406 | 1414 | 1301 | 1486 | 1304 | 1280 | 1262 | 1280 | 1251 | 1173 | 1228 | 1410 | 1215 | 1339 | 1344 | 1293 | 1163 | 1208 | 1319 | 1277 | 1161 | 1262 | 1230 | 1168 | 1277 | 1465 | 1276 | 1286 | 1153 | 1462 | 1304 | 1259 | 1291 | 1383 | 1431 | 1339 | 1439 | 1347 | 1351 | 1292 | 1164 | 1191 | 1154 | 940 | 1209 | 1309 | 1169 | 1113 | 1336 |  |  | 1254 | 872 | 1182 |  | 1330 | 1255 | 1249 | 1214 | 1255 | 1264 | 1266 | 1278 | 1296 | 1326 | 1321 | 1331 | 1405 | 1472 | 1246 | 1040 | 951 | 688 | 894 | 1057 | 1334 | 1368 | 1323 | 1335 | 1230 | 1450 | 1381 | 1264 | 1022 | 1224 | 1031 | 1194 | 1031 |  | 1665 | 1195 | 520 | 1110 | 1142 |  |  | 1097 | 1225 | 798 | 1178 | 1099 | 40 | 46 | 2.1 | 5.1 |  | 0 | 6.38 |  |  | 83340164.309 | 281785 | 56438227.545 | 61405 | 84142145.623 | 186495 | 60919090.96 | 55425 | 315953204.4097 | 83421 | 85254.029 | 61.114 | 82991.239 | 11.748 | 83449.618 | 40.003 | 63050.222 | 13 | 314307.9307 | 54.003 | 168172.406 | 314253.9277 | 12 | 0 | 6.38 | 40 | 46 | 2.1 | 5.1 | 316090
2025-04-30 | 2026 | 2025 |  |  | Apr-25 | 30 | 66750 | 7:00 | 19:00 | 1370.1 | 1329.7 | 1272 | 1262.9 | 1358.6 | 1260.8 | 1269.7 | 1256.5 | 1248.5 | 1318.5 | 1307.4 | 1276 | 1257.2 | 1174.6 | 1202 | 1245.6 | 1206.7 | 1273.1 | 1358.5 | 1372.7 | 1285.1 | 1286.5 | 1401 | 1437.3 | 1377.9 | 1359.5 | 1356.9 | 1396 | 1373.5 | 1376.2 | 1236.2 | 1321.7 | 1147.6 | 1524.4 | 1195.9 | 1253.7 | 1258.2 | 1233 | 1259.4 | 1275.4 | 1240.3 | 1227 | 1258.2 | 1248.8 | 1277.8 | 1306.8 | 1409.5 | 1266.1 | 1255.5 | 1283.7 | 1223.3 | 1276.8 | 1430.6 | 1472.1 | 1362.2 | 1168.5 | 1438.9 | 1289.9 | 1420.2 | 1430.4 | 1263.4 | 1393.4 | 1262.7 | 1126.5 | 1367.2 | 1359.2 | 1383.6 | 1270.4 | 1247.3 | 1249.6 | 1265.3 | 1263.7 | 1275.4 | 1266.9 | 1462.6 | 1441.3 | 1454.4 | 1267.1 | 1246.1 | 1350.9 | 1300.6 | 1295.4 | 1261.9 | 1271.6 | 1276.6 | 1302.5 | 1233.8 | 1278 | 1268.7 | 1263 | 1317.4 | 1342.6 | 1294 | 1289.4 | 1377.2 | 1205.9 | 1235.9 | 1264.7 | 1254 | 1257.2 | 1287.4 | 1264.1 | 1289.1 | 1262.8 | 1406.4 | 1281.9 | 1557.6 | 1405.2 | 1282.3 | 1407.4 | 1371.8 | 1371.3 | 1441.7 | 1438.3 | 1279.3 | 1290.8 | 1401.1 | 1403.5 | 1398 | 1249.3 | 1282.8 | 1322.6 | 1365 | 1262.9 | 1280.2 | 1385.9 | 1183.5 | 1195.2 | 1391.4 | 1394.1 | 1341.2 | 1346.8 | 1293.7 | 1133.4 | 1434.5 | 1363.4 | 1382 | 1301.8 | 1305.5 | 1283 | 1236.9 | 1285.4 | 1121.4 | 1411.4 | 1184.3 | 1372.9 | 1262.1 | 1170.8 | 1351.4 | 1372.4 | 1378.7 | 1269.9 | 1449.2 | 1270.6 | 1250.9 | 1230.9 | 1239.5 | 1221.7 | 1144 | 1197.3 | 1374.1 | 1186.7 | 1306.7 | 1310.3 | 1243.5 | 997.1 | 1200.4 | 1334.4 | 1252.2 | 1129.5 | 1237.7 | 1194.8 | 1173.4 | 1243.2 | 1427.4 | 1245.6 | 1256.1 | 1126.4 | 1445.2 | 1274.1 | 1244 | 1261.1 | 1350.8 | 1396.6 | 1307.9 | 1404.2 | 1313.1 | 1317 | 1256.5 | 1131.1 | 1157.1 | 1122.2 | 1101.1 | 1175.6 | 1272.5 | 1233.1 | 1082.5 | 1298.2 |  |  | 1087.1 | 847.8 | 1208.7 |  | 1321.5 | 1149.9 | 1215 | 1181.6 | 1220.6 | 1231.8 | 1232.5 | 1244.2 | 1261.8 | 1292.3 | 1285 | 1295 | 1365.3 | 1431.5 | 1213.7 | 1014.9 | 926 | 717.9 | 850.9 | 1006.8 | 1277.5 | 1392.3 | 1296.6 | 1308.2 | 1315.5 | 1365.5 | 1390.3 | 1312.7 | 976.6 | 1203 | 980.5 | 1152.8 | 1005.7 |  | 1645 | 1282.1 | 521.5 | 1192.2 | 1128 |  |  | 1190.8 | 1166.4 | 794.5 | 1121.6 | 1055.5 | 35.51 | 43.47 | 2.54 | 6.7 |  | 0 | 6.29 |  |  | 83423432.755 | 281823.456 | 56518786.828 | 61413.795 | 84223652.282 | 186538.509 | 60981207.812 | 55435.396 | 316260211.859 | 83464.615 | 83268.446 | 38.456 | 80559.283 | 8.795 | 81506.659 | 43.509 | 62116.852 | 10.396 | 307007.4493 | 43.615 | 163780.478 | 306963.8343 | 12 | 0 | 6.29 | 35.51 | 43.47 | 2.54 | 6.7 | 308834.9
2025-05-01 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 7:00 | 19:00 | 1312.3 | 1273.4 | 1219.5 | 1212.5 | 1304.8 | 1208.9 | 1214.3 | 1201.7 | 1215.7 | 1263 | 1251.2 | 1221.8 | 1201.9 | 1124.6 | 1183.3 | 1231.8 | 1181.6 | 1238.4 | 1305.5 | 1314.2 | 1241.1 | 1251.2 | 1375.2 | 1381.6 | 1319.7 | 1301.1 | 1300.8 | 1340.8 | 1326.2 | 1317.6 | 1312.2 | 1288.2 | 1119.2 | 1462.8 | 1145.2 | 1201 | 1203.7 | 1178.1 | 1205.3 | 1219.7 | 1184.7 | 1172.4 | 1204.6 | 1195.6 | 1223.5 | 1255.4 | 1349.6 | 1211.8 | 1213.2 | 1233.5 | 1176.1 | 1231.4 | 1380.8 | 1413.8 | 1307.8 | 1324.4 | 1375.3 | 1233.9 | 1386.7 | 1379.8 | 1206.9 | 1333.7 | 1201.6 | 1071.2 | 1364.9 | 1304.8 | 1323 | 1225.9 | 1193.3 | 1194.8 | 1210.8 | 1208.6 | 1220.3 | 1211.2 | 1398.2 | 1378 | 1389.4 | 1210 | 1190 | 1289.5 | 1243.2 | 1238.4 | 1206.8 | 1215.9 | 1221.6 | 1250.9 | 1184.8 | 1226.2 | 1211.6 | 1210.1 | 1262 | 1292.3 | 1236.7 | 1233 | 1313.5 | 1171.5 | 1180.2 | 1209.1 | 1198.3 | 1202.5 | 1231.2 | 1208.8 | 1233.6 | 1208.2 | 1344.6 | 1220.9 | 1490.8 | 1343 | 1226.5 | 1345.8 | 1312.3 | 1320.5 | 1388.2 | 1380.2 | 1222.8 | 1239.8 | 1345 | 1341.3 | 1334.2 | 1215.9 | 1249.2 | 1334.7 | 1316.7 | 1207.8 | 1224.5 | 1312.5 | 1159.3 | 1161.3 | 1330.4 | 1333.3 | 1275 | 1319.5 | 1268.4 | 1085.1 | 1375.1 | 1306.1 | 1326.1 | 1247 | 1251.9 | 1243.2 | 1185.4 | 1258.8 | 1077.4 | 1345.4 | 1136.4 | 1342.8 | 1223.8 | 1124.1 | 1292.6 | 1316 | 1319.7 | 1213.6 | 1386.9 | 1215.3 | 1195.7 | 1178.3 | 1181.3 | 1189.6 | 1119.4 | 1145.7 | 1317.8 | 1136.5 | 1249.2 | 1255 | 1282.6 | 1100.7 | 1173.7 | 1311.6 | 1221 | 1081.8 | 1193.7 | 1144.2 | 1233.4 | 1208.4 | 1367.2 | 1194.3 | 1249.5 | 1111.5 | 1415.5 | 1251.3 | 1230.2 | 1212 | 1294.6 | 1339.3 | 1251.8 | 1344.3 | 1264.4 | 1260.6 | 1201.5 | 1118.6 | 1151.3 | 1114.2 | 1063.2 | 1149.3 | 1227.5 | 1209.9 | 1036.9 | 1265.6 |  |  | 1042 | 813.4 | 1158.6 |  | 1268.2 | 1120.2 | 1167.2 | 1138.7 | 1175.2 | 1179 | 1181.3 | 1190.6 | 1209.3 | 1237.2 | 1228.2 | 1245.6 | 1306.2 | 1369.4 | 1163.3 | 971 | 886.5 | 707.1 | 899.1 | 1017.6 | 1254.2 | 1357.1 | 1263 | 1273.4 | 1277.6 | 1323.1 | 1356.2 | 1273.2 | 958.4 | 1180 | 960.6 | 1128.9 | 984.4 |  | 1578.1 | 1229.2 | 501.1 | 1143.4 | 1100.8 |  |  | 1139.3 | 1117.4 | 797.8 | 1080 | 1000.1 | 34.64 | 42.7 | 3.78 | 7.5 |  | 0 | 6.3 |  |  | 83503615.233 | 281835.466 | 56596133.071 | 61424 | 84302475.451 | 186580 | 61041530.906 | 55471.573 | 316556555.744 | 83487.6 | 80182.478 | 12.01 | 77346.243 | 10.205 | 78823.169 | 41.491 | 60323.094 | 36.177 | 296343.885 | 22.985 | 157506.506 | 296320.9 | 12 | 0 | 6.3 | 34.64 | 42.7 | 3.78 | 7.5 | 298175.2
2025-05-02 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 7:00 | 19:00 | 931.2 | 903.1 | 871.3 | 863.9 | 932.6 | 866.2 | 858.4 | 859.9 | 858.4 | 904.8 | 880.7 | 873 | 859.6 | 810.1 | 830.1 | 864.1 | 823.6 | 859 | 932.3 | 928.7 | 866.7 | 873.6 | 957.6 | 979.4 | 931.5 | 922.8 | 917.2 | 950.4 | 958 | 942.1 | 938.6 | 941.3 | 796.7 | 1105.3 | 832.4 | 859.7 | 857.5 | 837.6 | 845.6 | 850.7 | 840.1 | 822.2 | 843.6 | 836.8 | 854.1 | 887.4 | 934.1 | 846.8 | 856.7 | 877.3 | 833.9 | 854.3 | 952.1 | 975.8 | 926.8 | 942.8 | 971.1 | 859.2 | 969.6 | 985.1 | 858.5 | 970.4 | 853.5 | 879.4 | 932.7 | 917.8 | 933.3 | 899.7 | 845.2 | 842.2 | 854.9 | 853.4 | 863.3 | 855.4 | 970.7 | 556.1 | 988.2 | 836.9 | 827.3 | 915.9 | 857.9 | 855.8 | 849.7 | 857.1 | 850.1 | 861.4 | 873 | 861.5 | 854.8 | 850.3 | 887.9 | 924 | 874.2 | 871.9 | 930.6 | 836.2 | 825.7 | 868 | 839.1 | 848.4 | 871.1 | 843.6 | 869.9 | 853.6 | 955 | 863.4 | 1054.7 | 942.8 | 860.7 | 953.2 | 933.3 | 918.2 | 971.2 | 962.9 | 853 | 861 | 940.8 | 960.6 | 953.4 | 853.4 | 875.7 | 948 | 937.3 | 854.4 | 868 | 931.4 | 828.7 | 823.2 | 940.7 | 941.5 | 892.2 | 907.4 | 894.6 | 764.3 | 963.3 | 916.8 | 923.9 | 877.8 | 880.2 | 875.1 | 837.6 | 915.7 | 764.7 | 958 | 800.6 | 932.5 | 855 | 793.3 | 915.7 | 933.3 | 936.2 | 859.4 | 986.2 | 858.2 | 840.7 | 829.9 | 830.3 | 828.6 | 850.2 | 819.2 | 947 | 812.5 | 913.3 | 918.4 | 926.2 | 792.1 | 809.4 | 922.6 | 843.6 | 805.8 | 852.8 | 818.9 | 915.2 | 855.7 | 962 | 842 | 852.2 | 810.2 | 973.1 | 871.4 | 905.9 | 910.2 | 955.4 | 943.6 | 885.1 | 950.1 | 887.4 | 892.2 | 854.9 | 842.1 | 813.4 | 822.2 | 814.9 | 811.9 | 854.6 | 835.9 | 723 | 873.3 |  |  | 756.4 | 592.7 | 855 |  | 918.5 | 798.1 | 849.3 | 822.4 | 843.1 | 840.1 | 844.5 | 850.2 | 850.6 | 869.3 | 853.6 | 870.7 | 923.3 | 977.9 | 826.8 | 720.5 | 650.1 | 578.8 | 652.7 | 739.2 | 853.6 | 929.2 | 899.4 | 903.6 | 900.1 | 896.6 | 922 | 903.3 | 697.9 | 833 | 697 | 813.6 | 709.8 |  | 1101 | 870.2 | 347.6 | 802.5 | 775.1 |  |  | 822.7 | 853.1 | 565.1 | 767.8 | 725.4 | 26.59 | 33.02 | 3.03 | 7.7 |  | 0 | 4.16 |  |  | 83560630.704 | 281851.284 | 56650810.423 | 61437 | 84358523.571 | 186623 | 61084340.104 | 55483 | 316766786.327 | 83569.12 | 57015.471 | 15.818 | 54677.352 | 13 | 56048.12 | 43 | 42809.198 | 11.427 | 210230.583 | 81.52 | 111664.005 | 210149.063 | 12 | 0 | 4.16 | 26.59 | 33.02 | 3.03 | 7.7 | 211112
2025-05-03 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 7:00 | 19:00 | 1289.3 | 1249.1 | 1206.8 | 1201.5 | 1293.8 | 1199.4 | 1192.9 | 1196.8 | 1192 | 1253.4 | 1220.5 | 1214.9 | 1198.1 | 1129.2 | 1169 | 1198.8 | 1146.1 | 1194.5 | 1293.9 | 1289.1 | 1205.7 | 1209.7 | 1328.7 | 1356.4 | 1300.9 | 1283.5 | 1278.5 | 1325.8 | 1332.1 | 1319 | 1329.5 | 1320.7 | 1118.1 | 1541.2 | 1143.8 | 1212.9 | 1189.9 | 1167.9 | 1184.2 | 1197.9 | 1178 | 1158.2 | 1182 | 1175 | 1189.5 | 1202.2 | 1295.5 | 1184.4 | 1194.1 | 1191.6 | 1153.2 | 1196.7 | 1345.9 | 1351 | 1289.6 | 1309.6 | 1347.4 | 1206.4 | 1344.4 | 1361.1 | 1196.4 | 1350.5 | 1198.2 | 1193.1 | 1296.1 | 1276.2 | 1299.1 | 1230 | 1186.8 | 1177.7 | 1189.8 | 1189 | 1214.3 | 1194.2 | 1355.2 | 1345.4 | 1348.4 | 1170.3 | 1157.7 | 1269.3 | 1196.5 | 1195.7 | 1186.8 | 1196.7 | 1189.1 | 1197.4 | 1211.9 | 1196.7 | 1170.1 | 1183.2 | 1237.3 | 1286 | 1218.2 | 1214.1 | 1293.8 | 1142.4 | 1156.7 | 1199.4 | 1177.7 | 1188 | 1219.6 | 1182.4 | 1210.1 | 1189.9 | 1349.5 | 1199 | 1439 | 1322.9 | 1201.3 | 1320.5 | 1292.2 | 1279.3 | 1348.1 | 1341.1 | 1191.3 | 1200.8 | 1313.5 | 1329.2 | 1321.1 | 1186.1 | 1213.3 | 1313.3 | 1294.3 | 1189 | 1205.2 | 1332.5 | 1120.1 | 1138.5 | 1322 | 1319.3 | 1220 | 1266 | 1225.6 | 1069.4 | 1342.2 | 1283.7 | 1294.9 | 1228.1 | 1218.7 | 1208.8 | 1270.4 | 1266.2 | 1144.8 | 1324.4 | 1101.6 | 1337.3 | 1187 | 1101.5 | 1272.2 | 1297 | 1299.8 | 1192.7 | 1365.3 | 1229.3 | 1173.1 | 1159 | 1149.1 | 1155.4 | 1184 | 1146.8 | 1313.8 | 1142.7 | 1292.4 | 1273.5 | 1309.5 | 1114.1 | 1128.1 | 1290.4 | 1171 | 1125.9 | 1230 | 1147.2 | 1280.9 | 1199.6 | 1335.9 | 1173.5 | 1176.2 | 1112.6 | 1349.6 | 1177.8 | 1261.8 | 1278.6 | 1307.8 | 1303.5 | 1230.9 | 1325.6 | 1233.6 | 1214 | 1194.6 | 1174.7 | 1130 | 1123.8 | 1070.4 | 1127.1 | 1186.5 | 1159.8 | 1003.5 | 1207.9 |  |  | 1043.7 | 816.6 | 1173 |  | 1277.9 | 1096.1 | 1180.7 | 1151.8 | 1175.6 | 1182.4 | 1183.7 | 1192.1 | 1201.5 | 1216.8 | 1142.5 | 1211 | 1290.5 | 1361.9 | 1140.9 | 1007.7 | 905.2 | 800.1 | 873 | 1035.9 | 1200.2 | 1334.2 | 1251.6 | 1252.2 | 1204.6 | 1301.6 | 1330.7 | 1188 | 1012] | 1169.2 | 1018.8 | 1113 | 991 |  | 1356 | 1167.5 | 508 | 1089.3 | 1059.2 |  |  | 1206.8 | 1243.5 | 784.2 | 1015.6 | 931 | 27 | 31 | 3.1 | 5.9 |  | 0 | 5.85 |  |  | 83639719.132 | 281866.63 | 56726946.982 | 61457.096 | 84436429.55 | 186658.586 | 61144398.403 | 55497.082 | 317059642.463 | 83628.29 | 79088.428 | 15.346 | 76136.559 | 20.096 | 77905.979 | 35.586 | 60058.299 | 14.082 | 292856.136 | 59.17 | 155189.545 | 292796.966 | 12 | 0 | 5.85 | 27 | 31 | 3.1 | 5.9 | 293330
2025-05-04 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:29 | 6:20 | 1414 | 1371 | 1323 | 1318 | 1423 | 1316 | 1307 | 1328 | 1372 | 1383 | 1338 | 1345 | 1325 | 1244 | 1318 | 1312 | 1255 | 1310 | 1417 | 1417 | 1322 | 1326 | 1451 | 1484 | 1428 | 1409 | 1403 | 1453 | 1462 | 1442 | 1410 | 1444 | 1222 | 1617 | 1251 | 1328 | 1306 | 1292 | 1305 | 1321 | 1297 | 1282 | 1301 | 1294 | 1313 | 1332 | 1430 | 1303 | 1353 | 1331 | 1274 | 1328 | 1513 | 1498 | 1412 | 1436 | 1479 | 1321 | 1473 | 1494 | 1324 | 1483 | 1307 | 1304 | 1414 | 1395 | 1418 | 1310 | 1292 | 1286 | 1302 | 1299 | 1339 | 1308 | 1475 | 1398 | 1468 | 1276 | 1273 | 1376 | 1310 | 1313 | 1309 | 1320 | 1312 | 1326 | 1342 | 1325 | 1244 | 1290 | 1345 | 1378 | 1293 | 1341 | 1412 | 1269 | 1278 | 1328 | 1300 | 1317 | 1355 | 1312 | 1341 | 1316 | 1488 | 1328 | 1564 | 1444 | 1322 | 1455 | 1432 | 1387 | 1452 | 1463 | 1303 | 1298 | 1432 | 1453 | 1469 | 1306 | 1328 | 1423 | 1418 | 1300 | 1337 | 1433 | 1221 | 1245 | 1443 | 1443 | 1284 | 1389 | 1341 | 1168 | 1471 | 1404 | 1417 | 1382 | 1333 | 1322 | 1326 | 1378 | 1198 | 1450 | 1213 | 1464 | 1299 | 1207 | 1390 | 1414 | 1426 | 1306 | 1493 | 1308 | 1286 | 1267 | 1414 | 1234 | 1300 | 1253 | 1445 | 1247 | 1422 | 1408 | 1433 | 1217 | 1235 | 1409 | 1484 | 1233 | 1310 | 1251 | 1396 | 1312 | 1476 | 1291 | 1301 | 1222 | 1483 | 1322 | 1387 | 1407 | 1477 | 1446 | 1352 | 1459 | 1397 | 1364 | 1311 | 1294 | 1237 | 1237 | 1244 | 1317 | 1267 | 1278 | 1100 | 1276 |  |  | 1100 | 998 | 1396 |  | 1259 | 1313 | 1279 | 1312 | 1309 | 1316 | 1318 | 1328 | 1339 | 1252 | 1328 | 1411 | 1485 | 1378 | 1106 | 999 | 876 | 798 | 929 | 1114 | 1323 | 1434 | 1342 | 1342 | 1219 | 1310 | 1403 | 1393 | 1109 | 1285 | 1113 | 1207 | 1074 |  | 1410 | 1333 | 598 | 1246 | 1195 |  |  | 1339 | 1383 | 860 | 1126 | 1010 | 33.65 | 43.22 | 1.9 | 7.5 |  | 0 | 6.49 |  |  | 83726824.722 | 281882.851 | 56809802.29 | 61467.68 | 84521862.024 | 186707.953 | 61210236.424 | 55510.862 | 317380486.88 | 83692.452 | 87105.59 | 16.221 | 82855.308 | 10.584 | 85432.474 | 49.367 | 65838.021 | 13.78 | 320844.417 | 64.162 | 169934.093 | 320780.255 | 12 | 0 | 6.49 | 33.65 | 43.22 | 1.9 | 7.5 | 322757
2025-05-05 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:32 | 18:17 | 927.5 | 900.4 | 867.5 | 865.8 | 933.3 | 861.3 | 868.1 | 864.7 | 893.3 | 901.5 | 877.5 | 875.4 | 862.5 | 811.6 | 856.7 | 854.1 | 822.7 | 856.2 | 925 | 925.5 | 861.6 | 857.7 | 944.4 | 962.7 | 929.6 | 912.4 | 907.1 | 942.3 | 942.5 | 935.4 | 929.5 | 934.9 | 805.9 | 1065.4 | 841.4 | 938.1 | 861.6 | 853.1 | 864.9 | 874.9 | 859.6 | 846.8 | 863.1 | 855.8 | 871.8 | 878.3 | 946.8 | 865.7 | 899.4 | 884.6 | 842 | 871.8 | 994.1 | 984.5 | 931.7 | 942.5 | 984 | 868.7 | 968.1 | 978.7 | 873.6 | 976.5 | 870 | 847 | 931.4 | 918.7 | 934.7 | 905 | 855.6 | 779 | 861.2 | 860 | 877.9 | 861.5 | 965.7 | 1001.5 | 960 | 834.2 | 832.7 | 922.6 | 867.9 | 865.1 | 861.8 | 864.7 | 864.7 | 871.3 | 880.1 | 868.5 | 874.1 | 855.7 | 888.1 | 934.6 | 870.2 | 879 | 932.5 | 821.7 | 835.9 | 866.3 | 857.2 | 853.5 | 885.5 | 860.4 | 880 | 862.8 | 979.2 | 867.2 | 1019 | 954.6 | 872 | 962.1 | 938.8 | 892.7 | 955.7 | 962.7 | 858.7 | 863.7 | 946.7 | 956.3 | 960.4 | 859.3 | 875.6 | 938.8 | 934.6 | 856.3 | 872 | 940.1 | 834.3 | 835.1 | 941.9 | 945.2 | 901.7 | 908.1 | 905.2 | 768.3 | 962.4 | 926.3 | 931.2 | 879.7 | 876 | 858.2 | 832.5 | 903.3 | 769.1 | 947.7 | 783.9 | 924.6 | 846.4 | 785.7 | 906.4 | 923.7 | 930.3 | 853.5 | 945.6 | 861.8 | 850.5 | 831.1 | 827.7 | 810.9 | 850.9 | 817.6 | 959.3 | 830.1 | 951.6 | 922.6 | 953.3 | 791.8 | 806 | 919.7 | 839.3 | 804.3 | 826.6 | 816.5 | 909.2 | 853.8 | 977.1 | 845.9 | 949.1 | 796.3 | 974 | 864.5 | 905.7 | 917.4 | 975.6 | 952.9 | 890.1 | 972.6 | 884 | 892 | 858.8 | 792.6 | 797.5 | 780.6 | 773.3 | 807.5 | 852.7 | 818.4 | 710.3 | 859.8 |  |  | 782.6 | 541.4 | 827 |  | 917.1 | 765.1 | 854.3 | 827.3 | 854.2 | 860.3 | 862.9 | 866 | 868.7 | 876.1 | 809.1 | 865 | 926 | 940.2 | 807 | 718.3 | 644.6 | 568.5 | 623.4 | 749.5 | 893 | 957.9 | 881.2 | 888.7 | 810.5 | 931.4 | 913.5 | 913.6 | 727.1 | 857.6 | 736 | 814.6 | 719.9 |  | 1139.9 | 868.9 | 397.2 | 813.4 | 780.9 |  |  | 870.2 | 900.7 | 568 | 748.4 | 741.8 | 27.91 | 34.01 | 2.69 | 9.1 |  | 0 | 4.14 |  |  | 83784058.891 | 281898.851 | 56864716.575 | 61479.68 | 84577882.491 | 186757.953 | 61253729.251 | 55528.862 | 317591883.672 | 83756.214 | 57234.169 | 16 | 54914.285 | 12 | 56020.467 | 50 | 43492.827 | 18 | 211396.792 | 63.762 | 112120.454 | 211333.03 | 12 | 0 | 4.14 | 27.91 | 34.01 | 2.69 | 9.1 | 212087.7
2025-05-06 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:09 | 18:24 | 1403.8 | 1413.5 | 1314.9 | 1308.9 | 1410.1 | 1303.3 | 1310.6 | 1311.6 | 1353.5 | 1366.1 | 1332.4 | 1325.1 | 1304.5 | 1228.6 | 1307.5 | 1301.2 | 1245.2 | 1296.6 | 1404.3 | 1402.9 | 1308.5 | 1313.6 | 1436.6 | 1472.5 | 1414.1 | 1396.7 | 1389 | 1443.5 | 1454.8 | 1436.5 | 1441.5 | 1444.8 | 1194.9 | 1567 | 1227 | 1395.6 | 1263.4 | 1244 | 1259.7 | 1274.3 | 1252.8 | 1234.1 | 1255.7 | 1249.6 | 1265.9 | 1281.6 | 1375.4 | 1255.4 | 1315.2 | 1293.1 | 1271.4 | 1271.1 | 1450.2 | 1438.1 | 1367.7 | 1386.7 | 1441.3 | 1281.4 | 1425.5 | 1444.7 | 1272.1 | 1440.2 | 1267.6 | 1257.9 | 1413.7 | 1402.1 | 1417.7 | 1425.8 | 1296.2 | 1301.1 | 1302.6 | 1300.7 | 1325.2 | 1301.2 | 1466.2 | 1471.5 | 1466.8 | 1273 | 1266.2 | 1372.6 | 1308.7 | 1310.1 | 1303.2 | 1314.7 | 1304.8 | 1314.8 | 1326.9 | 1306.7 | 1303.7 | 1293.1 | 1353.9 | 1361.2 | 1338.1 | 1328.8 | 1440.5 | 1302.3 | 1300.4 | 1311.9 | 1293.1 | 1300 | 1336.8 | 1298.7 | 1325.5 | 1300.7 | 1471.5 | 1312.1 | 1549.1 | 1447 | 1316.4 | 1449 | 1413.9 | 1390.2 | 1451.9 | 1462.6 | 1304.1 | 1279.5 | 1434.5 | 1450.8 | 1447.2 | 1297.4 | 1322.4 | 1418.2 | 1413.1 | 1301.5 | 1315.9 | 1430.4 | 1293.6 | 1304.5 | 1439 | 1438.6 | 1378.9 | 1382.6 | 1371.2 | 1162.9 | 1467.7 | 1403.3 | 1416.6 | 1389.7 | 1382.2 | 1308.4 | 1273.9 | 1380.2 | 1251.2 | 1440.9 | 1203 | 1455.7 | 1289.4 | 1201.9 | 1385.2 | 1409.6 | 1418.3 | 1302.6 | 1487.8 | 1302.6 | 1283.3 | 1264.8 | 1265.8 | 1278.5 | 1297.5 | 1245.9 | 1447.9 | 1248.1 | 1430.6 | 1407 | 1446.5 | 1221.8 | 1240.3 | 1407.2 | 1286.3 | 1236 | 1275.7 | 1250.8 | 1410.3 | 1312.7 | 1474 | 1289.1 | 1300 | 1240 | 1482.5 | 1347.2 | 1158.1 | 1417.2 | 1455.7 | 1425 | 1373.1 | 1458.3 | 1355.8 | 1364.2 | 1315.5 | 1208 | 1247.6 | 1245.6 | 1187.9 | 1242.6 | 1240.2 | 1201.3 | 1096.7 | 1308.8 |  |  | 1003.4 | 873 | 1292.1 |  | 1388.3 | 1193.3 | 1262.9 | 1265.2 | 1289.4 | 1296.9 | 1297.1 | 1304.3 | 1307.7 | 1322.8 | 1256.6 | 1324.7 | 1469.7 | 1490.2 | 1224.9 | 1125.6 | 1010.6 | 863 | 956 | 1142.8 | 1360.1 | 1464.9 | 1381.8 | 1375 | 1345.5 | 1379.2 | 1398.4 | 1436 | 1153.8 | 1297.7 | 1165.3 | 1243.2 | 1020.2 |  | 1693.2 | 1313.9 | 541.4 | 1226.2 | 1187.7 |  |  | 1308.4 | 1371.1 | 878 | 1167.9 | 980.5 | 30.59 | 43.32 | 1.89 | 5.1 |  | 0 | 6.31 |  |  | 83869638.121 | 281921.136 | 56947478.718 | 61523.885 | 84663181.628 | 186809.826 | 61320152.131 | 55583.377 | 317911517.35 | 83859.522 | 85579.23 | 22.285 | 82762.143 | 44.205 | 85299.137 | 51.873 | 66422.88 | 54.515 | 319633.678 | 103.308 | 168274.883 | 319530.37 | 12.25 | 0 | 6.31 | 30.59 | 43.32 | 1.89 | 5.1 | 321279.5
2025-05-07 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:56 | 18:30 | 885.8 | 892.1 | 827.8 | 823.8 | 893.8 | 825.8 | 830.3 | 830.1 | 853.1 | 859.5 | 841.9 | 838.3 | 826 | 774.2 | 826.5 | 820 | 789.5 | 823.8 | 887.6 | 889.3 | 831.4 | 828.9 | 903.4 | 926.9 | 898.9 | 887 | 878.9 | 910.3 | 917 | 906.8 | 915.2 | 911.1 | 783.6 | 1023.8 | 803.4 | 911.6 | 824.3 | 811.5 | 823.4 | 831.1 | 821.8 | 815.1 | 821.1 | 818.2 | 828.3 | 837.8 | 894.5 | 821 | 855.9 | 841 | 827.1 | 829.8 | 945 | 939.6 | 893.5 | 904.3 | 8938.5 | 834.2 | 928.3 | 938 | 829.6 | 935.9 | 823.9 | 802 | 899.7 | 893.5 | 902.7 | 907.1 | 822.4 | 826.2 | 828.1 | 825.1 | 846.8 | 831.8 | 936.3 | 906.7 | 935.2 | 814.4 | 810.6 | 873.7 | 832.3 | 833.7 | 828.4 | 836.8 | 828.3 | 834.5 | 840.6 | 829.4 | 826 | 819.5 | 859 | 886.2 | 848.2 | 846 | 927.8 | 808.3 | 813 | 841 | 830.9 | 834.7 | 855.8 | 830.4 | 847 | 832.2 | 944.2 | 834.5 | 976.5 | 926.8 | 841.1 | 923.6 | 898.6 | 892.3 | 922.1 | 936.1 | 833.4 | 769.8 | 921.9 | 920.6 | 922.6 | 825.2 | 842.6 | 905.4 | 897.4 | 828.5 | 838.9 | 908.3 | 790.9 | 794.6 | 921.3 | 921 | 887.2 | 881.1 | 850.2 | 739.3 | 934.2 | 900.2 | 906.4 | 892.9 | 877.6 | 833.8 | 809.8 | 870.8 | 806.8 | 916.2 | 761.5 | 927 | 822 | 764.7 | 880.6 | 894.9 | 905.1 | 829.3 | 944.3 | 831.7 | 819.2 | 807.9 | 811.5 | 798.2 | 827 | 794.8 | 921 | 800.1 | 917.5 | 895.3 | 927.4 | 778.1 | 796.7 | 905.9 | 825.9 | 799.9 | 822.3 | 801.1 | 842.2 | 842.2 | 938.5 | 822.5 | 828.4 | 814 | 947.5 | 838.5 | 888.2 | 899 | 935.7 | 907 | 898.4 | 933.3 | 863.8 | 866.7 | 838 | 781 | 801.2 | 790.5 | 672.9 | 820.1 | 791.5 | 818.9 | 704.5 | 841.5 |  |  | 655.5 | 564.5 | 823.2 |  | 888.2 | 772.5 | 810.3 | 802.6 | 825.6 | 821.9 | 825.6 | 824.1 | 836.2 | 841 | 823.7 | 847.3 | 938.8 | 954.2 | 776.4 | 741.3 | 600.2 | 500 | 607.2 | 725.5 | 870.8 | 931.8 | 866.6 | 869.3 | 881.5 | 869.5 | 891 | 900 | 722 | 827.9 | 735.5 | 788.2 | 670.9 |  | 1075.5 | 835.5 | 376.2 | 779.5 | 750 |  |  | 832.7 | 873.8 | 562.1 | 744.1 | 610.1 | 26.11 | 40.91 | 2.1 | 4.9 |  | 0 | 5.46 |  |  | 83924495.221 | 281921.743 | 56999990.355 | 61559.483 | 84717738.397 | 186820.499 | 61362560.511 | 55627.81 | 318115576.327 | 83861.638 | 54857.1 | 0.607 | 52511.637 | 35.598 | 54556.769 | 10.673 | 42408.38 | 44.433 | 204058.977 | 2.116 | 107332.532 | 204056.861 | 12.5667 | 0 | 5.46 | 26.11 | 40.91 | 2.1 | 4.9 | 213164.2
2025-05-08 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:13 | 18:40 | 1281 | 1291 | 1205 | 1195 | 1300 | 1200 | 1210 | 1210 | 1254 | 1264 | 1226 | 1219 | 1202 | 1133 | 1205 | 1201 | 1148 | 1195 | 1302 | 1294 | 1207 | 1215 | 1329 | 1366 | 1307 | 1291 | 1288 | 1340 | 1349 | 1334 | 1310 | 1342 | 1147 | 934 | 1180 | 1340 | 1213 | 1190 | 1202 | 1208 | 1202 |  | 1205 | 1201 | 1215 | 1217 | 1310 | 1201 | 1240 | 1217 | 1200 | 1200 | 1370 | 1360 | 1299 | 1306 | 1367 | 1212 | 1351 | 1375 | 1212 | 1361 | 1276 | 1098 | 1382 | 1374 | 1383 | 1230 | 1280 | 1283 | 1291 | 1248 | 1335 | 1275 | 1433 | 1402 | 1436 | 1258 | 1259 | 1340 | 1304 | 1302 | 1288 | 1303 | 1296 | 1294 | 1300 | 1275 | 1266 | 1265 | 1301 | 1210 | 1312 | 1321 | 1398 | 1266 | 1263 | 1312 | 1285 | 1298 | 1330 | 1288 | 1315 | 1297 | 1447 | 1303 | 1513 | 1432 | 1308 | 1413 | 1404 | 1380 | 1422 | 1306 | 1188 | 1404 | 1420 | 1424 | 1286 | 1304 | 1377 | 1389 | 1296 | 1317 | 1298 | 1410 | 1062 | 1099 | 1270 | 1273 | 1135 | 1225 | 1175 | 1039 | 1316 | 1270 | 1271 | 1254 | 1237 | 1173 | 1123 | 1227 | 1120 | 1289 | 1078 | 1255 | 1155 | 1074 | 1225 | 1254 | 1255 | 1155 | 1322 | 1160 | 1145 | 1123 | 1110 | 1131 | 1096 | 1198 | 1152 | 1341 | 1155 | 1318 | 1301 | 1228 | 1025 | 1150 | 1062 | 1150 | 1062 | 1192 | 1301 | 1217 | 1360 | 1189 | 1199 | 1173 | 1369 | 1215 | 1284 | 1310 | 1343 | 1316 | 1299 | 1347 | 1251 | 1258 | 1215 | 1224 | 1269 | 1261 | 1248 | 1276 | 1234 | 1277 | 1098 | 1304 |  |  | 1140 | 879 | 1284 |  | 1373 | 1206 | 1282 | 1249 | 1280 | 1286 | 1284 | 1292 | 1297 | 1299 | 1308 | 1440 | 1463 | 1193 | 1143 | 1198 | 1010 | 810 | 944 | 1128 | 1348 | 1440 | 1374 | 1368 | 1310 | 1346 | 1385 | 1423 | 1151 | 1294 | 1159 | 1230 | 1048 |  | 1175 | 1310 | 587 | 810 | 1164 |  |  | 1278 | 1337 | 864 | 1161 | 990 | 31.23 | 40.22 | 2.05 | 7.9 |  | 0 | 6.54 |  |  | 84038086.452 | 281938.345 | 57081493.737 | 61571.092 | 84794945.871 | 186840 | 61428667.418 | 55643.599 | 318419804.813 | 83928.17 | 113591.231 | 16.602 | 81503.382 | 11.609 | 77207.474 | 19.501 | 66106.907 | 15.789 | 304228.486 | 66.532 | 195066.402 | 304161.954 | 12.45 | 0 | 6.54 | 31.23 | 40.22 | 2.05 | 7.9 | 302578
2025-05-09 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:15 | 18:24 | 1446 | 1459 | 1359 | 1353 | 1466 | 1363 | 1364 | 1366 | 1414 | 1430 | 1380 | 1376 | 1358 | 1282 | 1358 | 1354 | 1278 | 1310 | 1396 | 1408 | 1309 | 1316 | 1478 | 1478 | 1415 | 1410 | 1393 | 1452 | 1457 | 1439 | 1498 | 1468 | 1272 | 1637 | 1315 | 1482 | 1336 | 1315 | 1340 | 1354 | 1329 | 1314 | 1336 | 1332 | 1347 | 1355 | 1431 | 1343 | 1399 | 1373 | 1349 | 1343 | 1532 | 1520 | 1460 | 1473 | 1541 | 1363 | 1512 | 1533 | 1346 | 1523 | 1378 | 1363 | 1447 | 1432 | 1455 | 1219 | 1326 | 1328 | 1346 | 1349 | 1361 | 1308 | 1495 | 1455 | 1500 | 1308 | 1302 | 1367 | 1355 | 1352 | 1339 | 1347 | 1350 | 1351 | 1365 | 1344 | 1352 | 1340 | 1388 | 1310 | 1373 | 1365 | 1410 | 1290 | 1296 | 1344 | 1318 | 1331 | 1362 | 1320 | 1347 | 1329 | 1498 | 1233 | 1557 | 1478 | 1350 | 1446 | 1446 | 1405 | 1461 | 1492 | 1343 | 1203 | 1457 | 1478 | 1475 | 1319 | 1350 | 1395 | 1447 | 1336 | 1349 | 1463 | 1239 | 1271 | 1464 | 1469 | 1307 | 1419 | 1370 | 1201 | 1503 | 1450 | 1449 | 1431 | 1406 | 1334 | 1307 | 1400 | 1278 | 1463 | 1224 | 1427 | 1316 | 1225 | 1401 | 1426 | 1433 | 1321 | 1515 | 1322 | 1305 | 1288 | 1278 | 1255 | 1353 | 1301 | 1510 | 1305 | 1491 | 1467 | 1393 | 1163 | 1303 | 1206 | 1344 | 1314 | 1346 | 1317 | 1480 | 1387 | 1528 | 1339 | 1342 | 1321 | 1542 | 1368 | 1445 | 1472 | 1516 | 1482 | 1465 | 1520 | 1401 | 1409 | 1370 | 1377 | 1298 | 1286 | 1268 | 1307 | 1268 | 1312 | 1134 | 1364 |  |  | 1121 | 914 | 1338 |  | 1436 | 1271 | 1312 | 1286 | 1309 | 1315 | 1320 | 1322 | 1358 | 1363 | 1346 | 1349 | 1493 | 1519 | 1243 | 1199 | 1095 | 870 | 921 | 1096 | 1308 | 1397 | 1328 | 1320 | 1390 | 1410 | 1341 | 1375 | 1106 | 1251 | 1115 | 1188 | 1014 |  | 1175 | 1378 | 518 | 1228 | 1193 |  |  | 1310 | 1318 | 1382 | 898 | 1184 | 32.39 | 43.99 | 1.81 | 7.1 |  | 0 | 6.68 |  |  | 84093096.913 | 281952.252 | 57165631.997 | 61582.723 | 84882994.442 | 186889.538 | 61495600.917 | 55657.622 | 318747693.799 | 83981.736 | 55010.461 | 13.907 | 84138.26 | 11.631 | 88048.571 | 49.538 | 66933.499 | 14.023 | 327888.986 | 53.566 | 139123.183 | 327835.42 | 12.15 | 0 | 6.68 | 32.39 | 43.99 | 1.81 | 7.1 | 328786
2025-05-10 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:05 | 18:10 | 1244 | 1254.3 | 1165.3 | 1160.2 | 1256.7 | 1160.3 | 1168 | 1168.3 | 1205.5 | 1214.9 | 1188.9 | 1182.5 | 1164.5 | 1096.4 | 1132.6 | 1156.7 | 1106.2 | 1147.7 | 1238.9 | 1238.4 | 1159.3 | 1159.3 | 1271.1 | 1298.5 | 1254.6 | 1234.5 | 1126.4 | 1274 | 1282.3 | 1265.1 | 1165.3 | 1268.6 | 1087.3 | 1415.9 | 1124.9 | 1263 | 1151.4 | 1137.4 | 1155.6 | 1167.69 | 1147.9 | 1136.2 | 1105.1 | 1147 | 1160.3 | 1166.2 | 1257.8 | 1152.9 | 1203.5 | 1181.8 | 1161.3 | 1159.6 | 1322.3 | 1312.3 | 1251.7 | 1267.5 | 1320.6 | 1175.8 | 1298.7 | 1306.9 | 1167.8 | 1306.9 | 1162.3 | 1135.6 | 1256.3 | 1247.3 | 1260.1 | 1098.3 | 1142.6 | 1151.7 | 1161.1 | 1157.4 | 1177.9 | 1141.5 | 1300.3 | 1270.6 | 1302.9 | 1125.8 | 1123.6 | 1200 | 1165.9 | 1163.9 | 1152.3 | 1162.6 | 1161.6 | 1172.7 | 1155.6 | 1158.3 | 1148 | 1192.9 | 824.9 | 1182.1 | 1177.4125 | 1251 | 1321 | 1115.3 | 1124.7 | 1169.6 | 1150.2 | 1158.2 | 1186.3 | 1153.6 | 1174.7 | 1157.7 | 1314.9 | 1158.2 | 1376.2 | 1288.7 | 1171.4 | 1269.2 | 1257.1 | 1225.4 | 1278.2 | 1296.8 | 1165.9 | 1104.5 | 1269.3 | 1288.6 | 1285.6 | 1154.6 | 1177 | 1228.7 | 1259.4 | 1161.8 | 1171.6 | 1270.3 | 1069.6 | 1097 | 1268.2 | 1218.6 | 1123.9 | 1216.7 | 1168 | 1026.6 | 1289.9 | 1238.2 | 1244.4 | 1113.4 | 1209.9 | 1147.6 | 1117 | 1209.3 | 1103.1 | 1263.5 | 1055.1 | 1233.9 | 1136.2 | 1058.9 | 1223.96 | 1247 | 1251.2 | 1148 | 1319.4 | 1174 | 1147.8 | 1133.2 | 1118.9 | 1080.6 | 1138.5 | 1091.3 | 1268.4 | 1097.6 | 1252.7 | 1226.8 | 1168.3 | 968.2 | 1095.5 | 1000.2 | 1135.5 | 1109.6 | 1132.3 | 1110.7 | 1247.3 | 1165.4 | 1237.6 | 1124.6 | 1135.9 | 1113.6 | 1303 | 1152.4 | 1219.3 | 1248.1 | 1270.3 | 1241.8 | 1231.6 | 1275 | 1168.1. | 1189.5 | 1160.8 | 1166 | 1143.9 | 1122.8 | 1110.4 | 1167.4 | 1107.1 | 1165.4 | 981.4 | 1187.6 |  |  | 1005.6 | 799.5 | 1161.9 |  | 1251.2 | 1109.4 | 1165.2 | 1124.7 | 1159.6 | 1162.3 | 1180.1 | 1170 | 1181.4 | 1184.2 | 1166.9 | 1176.4 | 1298.7 | 1317 | 1079.4 | 1041.1 | 998 | 962 | 821 | 975.7 | 1168.2 | 1246.7 | 1180.3 | 1177.9 | 1306 | 1256.3 | 1200.1 | 1220.7 | 974.6 | 1112 | 988.4 | 1059.3 | 901 |  | 1175.1 | 1290 | 520 | 1198 | 1075.2 |  |  | 1280 | 1150.9 | 1204 | 766 | 1020.1 | 29.02 | 40.1 | 1.6 | 5.4 |  | 0 | 5.78 |  |  | 84170081.762 | 281964.316 | 57238934.706 | 61593.285 | 84958087.189 | 186920.646 | 61554663.804 | 55671.488 | 319031987.79 | 84029.622 | 76984.849 | 12.064 | 73302.709 | 10.562 | 75092.747 | 31.108 | 59062.887 | 13.866 | 284293.991 | 47.886 | 150264.932 | 284246.105 | 12.0833 | 0 | 5.78 | 29.02 | 40.1 | 1.6 | 5.4 | 283650.6625
2025-05-11 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:48 | 18:15 | 1468 | 1482 | 1375 | 1367 | 1475 | 1366 | 1372 | 1375 | 1420 | 1431 | 1398 | 1394 | 1373 | 1294 | 1376 | 1370 | 1312 | 1367 | 1475 | 1477 | 1380 | 1382 | 1513 | 1545 | 1489 | 1468 | 1461 | 1514 | 1525 | 1510 | 1440 | 1517 | 1272 | 1668 | 1313 | 1482 | 1363 | 1341 | 1356 | 1370 | 1352 | 1336 | 1292 | 1344 | 1362 | 1374 | 1481 | 1352 | 1416 | 1392 | 1368 | 1366 | 1555 | 1543 | 1468 | 1490 | 1550 | 1383 | 1539 | 1557 | 1373 | 1546 | 1310 | 1310 | 1482 | 1472 | 1491 | 1328 | 1360 | 1355 | 1366 | 1361 | 1384 | 1370 | 1545 | 1495 | 1538 | 1319 | 1313 | 1439 | 1365 | 1366 | 1356 | 1395 | 1363 | 1369 | 1384 | 1364 | 1364 | 1351 | 1417 | 1310 | 1391 | 1384 | 1478 | 1308 | 1319 | 1376 | 1355 | 1364 | 1399 | 1363 | 1384 | 1363 | 1560 | 1374 | 1638 | 1525 | 1386 | 1560 | 1491 | 1471 | 1537 | 1538 | 1371 | 1387 | 1514 | 1547 | 1534 | 1376 | 1396 | 1482 | 1497 | 1377 | 1385 | 1460 | 1264 | 1310 | 1503 | 1452 | 1333 | 1442 | 1375 | 1217 | 1533 | 1465 | 1478 | 1458 | 1439 | 1371 | 1319 | 1420 | 1313 | 1502 | 1266 | 1520 | 1351 | 1258 | 1474 | 1482 | 1496 | 1370 | 1576 | 1375 | 1357 | 1341 | 1310 | 1276 | 1358 | 1304 | 1512 | 1254 | 1487 | 1464 | 1504 | 1329 | 1298 | 1311 | 1350 | 1313 | 1340 | 1308 | 1478 | 1383 | 1476 | 1341 | 1357 | 1325 | 1512 | 1357 | 1471 | 1473 | 1515 | 1482 | 1469 | 1518 | 1410 | 1418 | 1374 | 1374 | 1356 | 1344 | 1227 | 1379 | 1307 | 1378 | 1156 | 1405 |  |  | 1177 | 926 | 1377 |  | 1488 | 1314 | 1378 | 1342 | 1373 | 1372 | 1392 | 1381 | 1393 | 1414 | 1382 | 1388 | 1546 | 1576 | 1281 | 1236 | 1278 | 1263 | 1105 | 1196 | 1429 | 1541 | 1465 | 1453 | 1410 | 1478 | 1475 | 1517 | 1220 | 1360 | 1234 | 1305 | 1107 |  | 1350 | 1398 | 587 | 1280 | 1281 |  |  | 1230 | 1319 | 1369 | 1436 | 1226 | 31.8 | 43.4 | 1.5 | 4.8 |  | 0 | 6.7 |  |  | 84260905.719 | 281980.514 | 57325630.313 | 61632.383 | 85046238.548 | 186946.059 | 61625296.528 | 55720.302 | 319368171.542 | 84092.853 | 90823.957 | 16.198 | 86695.607 | 39.098 | 88151.359 | 25.413 | 70632.724 | 48.814 | 336183.752 | 63.231 | 177464.268 | 336120.521 | 12.45 | 0 | 6.7 | 31.8 | 43.4 | 1.5 | 4.8 | 338732
2025-05-12 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:13 | 18:32 | 1500 | 1512 | 1401 | 1395 | 1502 | 1392 | 1401 | 1403 | 1446 | 1460 | 1427 | 1422 | 1401 | 1319 | 1392 | 1394 | 1336 | 1393 | 1508 | 1511 | 1401 | 1409 | 1539 | 1579 | 1522 | 1502 | 1496 | 1550 | 1565 | 1542 | 1425 | 1552 | 1305 | 1702 | 1347 | 1517 | 1391 | 1371 | 1388 | 1401 | 1380 | 1354 | 1323 | 1377 | 1391 | 1404 | 1511 | 1381 | 1444 | 1421 | 1394 | 1393 | 1585 | 1576 | 1500 | 1516 | 1579 | 1412 | 1568 | 1590 | 1401 | 1577 | 1391 | 1370 | 1518 | 1508 | 1526 | 1350 | 1385 | 1388 | 1397 | 1393 | 1415 | 1396 | 1590 | 1545 | 1583 | 1350 | 1342 | 1452 | 1397 | 1397 | 1387 | 1397 | 1386 | 1399 | 1413 | 1394 | 1393 | 1379 | 1447 | 1356 | 1423 | 1416 | 1543 | 1342 | 1351 | 1408 | 1388 | 1396 | 1436 | 1395 | 1424 | 1396 | 1599 | 1413 | 1674 | 1560 | 1417 | 1556 | 1528 | 1499 | 1541 | 1576 | 1404 | 1301 | 1548 | 1585 | 1574 | 1413 | 1430 | 1512 | 1534 | 1409 | 1419 | 1548 | 1346 | 1367 | 1563 | 1495 | 1364 | 1474 | 1408 | 1244 | 1570 | 1501 | 1512 | 1481 | 1474 | 1406 | 1350 | 1455 | 1345 | 1539 | 1367 | 1555 | 1387 | 1291 | 1511 | 1520 | 1533 | 1405 | 1615 | 1410 | 1389 | 1375 | 1328 | 1307 | 1393 | 1341 | 1552 | 1283 | 1525 | 1498 | 1539 | 1297 | 1323 | 1518 | 1375 | 1339 | 1352 | 1334 | 1504 | 1410 | 1517 | 1377 | 1389 | 1355 | 1524 | 1405 | 1486 | 1504 | 1551 | 1517 | 1507 | 1497 | 1447 | 1455 | 1400 | 1404 | 1392 | 1386 | 1362 | 1413 | 1340 | 1411 | 1185 | 1437 |  |  | 1205 | 980 | 1409 |  | 1520 | 1343 | 1414 | 1378 | 1406 | 1405 | 1423 | 1414 | 1424 | 1444 | 1415 | 1422 | 1582 | 1611 | 1305 | 1266 | 1095 | 919 | 1130 | 1185 | 1420 | 1519 | 1458 | 1460 | 1450 | 1478 | 1463 | 1511 | 1212 | 1357 | 1226 | 1290 | 1097 |  | 1520 | 1368 | 534 | 1280 | 1400 |  |  | 1470 | 1312 | 1335 | 1415 | 1422 | 35.13 | 43.88 | 1.88 | 7.3 |  | 0 | 6.85 |  |  | 84353521.617 | 281995.734 | 57414124.155 | 61641.407 | 85137234.455 | 186972.569 | 61697142.631 | 55734.393 | 319711873.326 | 84154.281 | 92615.898 | 15.22 | 88493.842 | 9.024 | 90995.907 | 26.51 | 71846.103 | 14.091 | 343701.784 | 61.428 | 181085.496 | 343640.356 | 12.3167 | 0 | 6.85 | 35.13 | 43.88 | 1.88 | 7.3 | 345699
2025-05-13 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 6:03 | 18:30 | 1250 | 1272 | 1181 | 1176 | 1270 | 1173 | 1178 | 1182 | 1221 | 1232 | 1168 | 1182 | 1156 | 1076 | 1132 | 1175 | 1088 | 1071 | 1161 | 1161 | 1075 | 1084 | 1188.9 | 1218 | 1171 | 1156 | 1153 | 1198 | 1209 | 1192 | 1198 | 1202 | 1126.7 | 1430 | 1131 | 1267 | 1166 | 1151 | 1168 | 1180 | 1163 | 1105 | 1135 | 1158 | 1168 | 1178 | 1267 | 1159 | 1213 | 1195 | 1171 | 1168 | 1331 | 1320 | 1260 | 1281 | 1330 | 1192 | 1317 | 1333 | 1180 | 1297 | 1158 | 1110 | 1273 | 1262 | 1277 | 1128.8 | 1159 | 1160 | 1169 | 1166 | 1186 | 1159 | 1322 | 1298 | 1325 | 1139 | 1131 | 1210 | 1171 | 1178 | 1161 | 1169 | 1165 | 1170 | 1183 | 1167 | 1167 | 1158 | 1212 | 1212 | 1175 | 1154 | 1303 | 1117 | 1127 | 1167 | 1148 | 1157 | 1188 | 1156 | 1175 | 1153 | 1310 | 1167 | 1371 | 1289 | 1172 | 1267 | 1258 | 1233 | 1273 | 1304 | 1163 | 1106 | 1276 | 1301 | 1291 | 1165 | 1185 | 1263 | 1267 | 1166 | 1174 | 1398 | 1130 | 1134 | 1302 | 1238 | 1159 | 1246 | 1164 | 1025 | 1298 | 1244 | 1254 | 1238 | 1214 | 1155 | 1117 | 1212 | 1124 | 1270 | 1080 | 1241 | 1147 | 1069 | 1249 | 1264 | 1265 | 1158 | 1327 | 1159 | 1144 | 1135 | 1198 | 1088 | 1170 | 1131 | 1308 | 1112 | 1291 | 1263 | 1301 | 1089 | 1110 | 1276 | 1157 | 1125 | 1131 | 1123 | 1273 | 1186 | 1272 | 1157 | 1166 | 1141 | 1282 | 1182 | 1250 | 1264 | 1308 | 1278 | 1268 | 1260 | 1214 | 1221 | 1173 | 1169 | 1144 | 1137 | 1119 | 1162 | 1131 | 1160 | 975 | 1183 |  |  | 1004 | 842 | 1155 |  | 1252 | 1114 | 1163 | 1126 | 1158 | 1159 | 1171 | 1164 | 1175 | 1187 | 1165 | 1173 | 1301 | 1332 | 1075 | 1037 | 908 | 750 | 894 | 1003 | 1205 | 1282 | 1234 | 1223 | 1208 | 1228 | 1243 | 1278 | 1032 | 1145 | 1037 | 1091 | 925 |  | 1375 | 1170 | 425.9 | 1070.4 | 1076 |  |  | 1098 | 1142 | 1103 | 1103 | 1032 | 34.36 | 42.16 | 1.65 | 11.7 |  | 0 | 5.73 |  |  | 84429612.061 | 282011.535 | 57488191.804 | 61677.352 | 85214024.795 | 187000.005 | 61757442.493 | 55778.947 | 319998971.929 | 84220.239 | 76090.444 | 15.801 | 74067.649 | 35.945 | 76790.34 | 27.436 | 60299.862 | 44.554 | 287098.603 | 65.958 | 150106.347 | 287032.645 | 12.45 | 0 | 5.73 | 34.36 | 42.16 | 1.65 | 11.7 | 286967.7
2025-05-14 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:30 | 18:25 | 1516 | 1529 | 1418 | 1410 | 1463 | 1406 | 1420 | 1424 | 1466 | 1477 | 1451 | 1444 | 1424 | 1339 | 1358 | 1408 | 1351 | 1408 | 1522 | 1529 | 1362 | 1423 | 1558 | 1598 | 1542 | 1522 | 1516 | 1471 | 1588 | 1563 | 1542 | 1577 | 1311 | 1719 | 1351 | 1521 | 1404 | 1384 | 1406 | 1421 | 1396 | 1331 | 1341 | 1395 | 1406 | 1418 | 1526 | 1399 | 1466 | 1441 | 1410 | 1408 | 1602 | 1591 | 1511 | 1535 | 1602 | 1433 | 1585 | 1605 | 1419 | 1591 | 1425 | 1309 | 1537 | 1527 | 1547 | 1313 | 1408 | 1403 | 1419 | 1414 | 1426 | 1407 | 1628 | 1572 | 1604 | 1365 | 1348 | 1453 | 1415 | 1410 | 1398 | 1406 | 1407 | 1412 | 1427 | 1408 | 1415 | 1400 | 1468 | 1422 | 1437 | 1429 | 1415 | [63 empty] | 1404 | 1352 | 1565 | 1351 | 1544 | 1510 | 1556 | 1300 | 1332 | 1532 | 1390 | 1354 | 1381 | 1347 | 1525 | 1426 | 1528 | 1386 | 1400 | 1362 | 1542 | 1416 | 1502 | 1515 | 1567 | 1533 | 1519 | 1508 | 1456 | 1468 | 1416 | 1416 | [32 empty] | 844 | 1003 | 1205 | 1282 | 1234 | 1223 | 1363 | 1310 | 1243 | 1278 | 1032 | 1145 | 1037 | 1091 | 925 | [13 empty] | 38.2 | 45.38 | 2.6 | 7.1 |  | 0 | 6.95 |  |  | 84523132.602 | 282028.228 | 57577637.485 | 61704.247 | 85306571.244 | 187045.615 | 61830305.101 | 55807.783 | 320347094.315 | 84286.91 | 93520.541 | 16.693 | 89445.681 | 26.895 | 92546.449 | 45.61 | 72862.608 | 28.836 | 348122.386 | 66.671 | 182922.634 | 348055.715 | 12.9167 | 0 | 6.95 | 38.2 | 45.38 | 2.6 | 7.1 | 201945
2025-05-15 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:40 | 18:34 | 1470 | 1483 | 1376 | 1367 | 1442.4 | 1368 | 1382 | 1385 | 1428 | 1438 | 1407 | 1400 | 1382 | 1301 | 1318 | 1366 | 1378 | 1364 | 1476 | 1480 | 1321 | 1381 | 1511 | 1551 | 1495 | 1510 | 1471 | 1525 | 1543 | 1518 | 1563 | 1530 | 1268 | 1669 | 1311 | 1494 | 1364 | 1343 | 1364 | 1379 | 1354 | 1289 | 1301 | 1352 | 1377 | 1374 | 1489 | 1364 | 1424 | 1398 | 1378 | 1374 | 1555 | 1543 | 1471 | 1488 | 1559 | 1389 | 1536 | 1556 | 1376 | 1545 | 1463 | 1298 | 1488 | 1478 | 1498 | 1273 | 1359 | 1367 | 1375 | 1372 | 1389 | 1363 | 1558 | 1523 | 1552 | 1346 | 1318 | 1401 | 1379 | 1380 | 1356 | 1362 | 1375 | 1369 | 1393 | 1374 | 1373 | 1359 | 1421 | 1298 | 1400 | 1390 | 1410 | 1343 | 1354 | 1357 | 1329 | 1291 | 1421 | 1375 | 1393 | 1344 | 1547 | 1184 | 1379 | 1489 | 1391 | 1536 | 1419 | 1523 | 1545 | 1587 | 1331 | 1343 | 1556 | 1449 | 1404 | 1378 | 1408 | 1480 | 1421 | 1334 | 1402 | 1474 | 1259 | 1285 | 1510 | 1498 | 1426 | 1428 | 1384 | 1263 | 1529 | 1436 | 1478 | 1400 | 1398 | 1383 | 1342 | 1389 | 1350 | 1510 | 1300 | 1516 | 1400 | 1268 | 1449 | 1456 | 1477 | 1362 | 1465 | 1360 | 1337 | 1320 | 1325 | 1282 | 1361 | 1311 | 1522 | 1312 | 1496 | 1464 | 1508 | 1260 | 1289 | 1485 | 1349 | 1312 | 1339 | 1306 | 1478 | 1379 | 1480 | 1343 | 1357 | 1320 | 1495 | 1372 | 1455 | 1470 | 1523 | 1489 | 1471 | 1462 | 1411 | 1422 | 1377 | 1371 | 1268 | 1213 | 1210 | 1310 | 1339 | 1210 | 1121 | 1357 |  |  | 1181 | 921 | 1272 |  | 1394 | 1242 | 1311 | 1290 | 1259 | 1334 | 1343 | 1339 | 1343 | 1368 | 1369 | 1356 | 1398 | 1542 | 1156 | 1061 | 1069 | 998 | 952 | 1116 | 1337 | 1489 | 1317 | 1369 | 1362 | 1400 | 1398 | 1380 | 1090 | 1300 | 1150 | 1303 | 1100 |  | 1250 | 1360 | 610 | 1298 | 1283 |  |  | 1210 | 1412 | 1300 | 1310 | 1117 | 38.52 | 46.82 | 2.05 | 5.8 |  | 0 | 6.81 |  |  | 84614020.421 | 282042.855 | 57664448.69 | 61713.367 | 85396598.142 | 187073.753 | 61901422.817 | 55823.055 | 320685759.859 | 84346.922 | 90887.819 | 14.627 | 86811.205 | 9.12 | 90026.898 | 28.138 | 71117.716 | 15.272 | 338665.544 | 60.012 | 177675.277 | 338605.532 | 12.9 | 0 | 6.81 | 38.52 | 46.82 | 2.05 | 5.8 | 334705.4
2025-05-16 | 2026 |  |  |  | May-25 | 31 | 66750 | 5:15 | 18:24 | 1262 | 1272 | 1181 | 1176 | 1250 | 1173 | 1179 | 1181 | 1221 | 1233 | 1208 | 1202 | 1186 | 1116 | 1167 | 1175 | 1167 | 1153 | 1249 | 1253 | 1209 | 1283 | 1318 | 1303 | 1312 | 1253 | 1253 | 1339 | 1313 | 1298 | 1292 | 1332 | 1130 | 1430 | 1203 | 1293 | 1167 | 1151 | 1168 | 1181 | 1163 | 1170 | 1158 | 1208 | 1168 | 1178 | 1267 | 1159 | 1213 | 1196 | 1171 | 1168 | 1331 | 1321 | 1260 | 1281 | 1330 | 1192 | 1303 | 1317 | 1334 | 1292 | 1227 | 1109 | 1273 | 1262 | 1277 | 1088 | 1193 | 1197 | 1192 | 1166 | 1186 | 1159 | 1322 | 1293 | 1325 | 1139 | 1181 | 1299 | 1201 | 1172 | 1161 | 1169 | 1165 | 1170 | 1183 | 1167 | 1167 | 1158 | 1212 | 1270 | 1190 | 1184 | 1200 | 1125 | 1135 | 1162 | 1160 | 1150 | 1195 | 1153 | 1170 | 1193 | 1304 | 1140 | 1325 | 1302 | 1180 | 1290 | 1282 | 1281 | 1325 | 1334 | 1140 | 1205 | 1310 | 1319 | 1262 | 1178 | 1187 | 1298 | 1240 | 1123 | 1186 | 1498 | 1167 | 1140 | 1321 | 1303 | 1240 | 1258 | 1230 | 1102 | 1225 | 1245 | 1240 | 1234 | 1215 | 1150 | 1199 | 1240 | 1138 | 1230 | 1100 | 1298 | 1134 | 1057 | 1260 | 1239 | 1253 | 1147 | 1290 | 1141 | 1180 | 1160 | 1198 | 1140 | 1171 | 1131 | 1308 | 1180 | 1291 | 1320 | 1301 | 1089 | 1160 | 1276 | 1157 | 1125 | 1132 | 1123 | 1273 | 1186 | 1272 | 1157 | 1166 | 1141 | 1282 | 1182 | 1250 | 1264 | 1308 | 1278 | 1268 | 1260 | 1214 | 1221 | 1173 | 1169 | 1153 | 1156 | 1130 | 1139 | 1220 | 1150 | 1009 | 1233 |  |  | 1198 | 898 | 1280 |  | 1250 | 1278 | 1182 | 1172 | 1149 | 1209 | 1214 | 1233 | 1230 | 1244 | 1213 | 1201 | 1230 | 1365 | 1072 | 1110 | 860 | 810 | 910 | 1011 | 1213 | 1372 | 1198 | 1244 | 1298 | 1278 | 1287 | 1300 | 1099 | 1219 | 1099 | 1100 | 970 |  | 1230 | 1200 | 450 | 1210 | 1123 |  |  | 1098 | 1298 | 1050 | 1100 | 930 | 37.78 | 42.3 | 2.3 | 11.3 |  | 0 | 5.56 |  |  | 84689361.033 | 282058.64 | 57735686.702 | 61735.503 | 85470963.71 | 187105.571 | 61960225.142 | 55851.671 | 320965372.624 | 84407.417 | 75340.612 | 15.785 | 71238.012 | 22.136 | 74365.568 | 31.818 | 58802.325 | 28.616 | 279612.765 | 60.495 | 146540.703 | 279552.27 | 13.15 | 0 | 5.56 | 37.78 | 42.3 | 2.3 | 11.3 | 292468
2025-05-17 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:27 | 18:25 | 1094 | 1105 | 1030 | 1026 | 1080 | 1024 | 1018 | 1021 | 1053 | 1060 | 1038 | 1036 | 1019 | 958 | 998 | 1009 | 993 | 1000 | 1076 | 1083 | 998 | 1016 | 1113 | 1142 | 1098 | 1082 | 1082 | 1123 | 1126 | 1115 | 1123 | 1121 | 998 | 1271 | 993 | 1123 | 994 | 1013 | 994 | 1004 | 1023 | 993 | 1001 | 1023 | 999 | 1016 | 1088 | 992 | 1039 | 1098 | 1008 | 1066 | 1150 | 1140 | 1093 | 1116 | 1144 | 1020 | 1122 | 1153 | 1005 | 1126 | 1030 | 998 | 1085 | 1076 | 1090 | 998 | 1098 | 1088 | 1098 | 1023 | 1008 | 998 | 1154 | 1190 | 1145 | 1034 | 1023 | 1098 | 1006 | 1013 | 1003 | 1006 | 1003 | 1014 | 1011 | 999 | 1023 | 1013 | 1089 | 1100 | 1019 | 1078 | 1100 | 1002 | 1032 | 1063 | 1038 | 1041 | 1079 | 1035 | 1066 | 1036 | 1198 | 1044 | 1186 | 1175 | 1068 | 1187 | 1146 | 1140 | 1201 | 1189 | 1048 | 1074 | 1172 | 1114 | 1175 | 1064 | 1094 | 1133 | 1114 | 1030 | 1081 | 1478 | 950 | 968 | 1165 | 1154 | 1059 | 1083 | 1051 | 898 | 1104 | 1098 | 1051 | 1083 | 1059 | 1004 | 988 | 1046 | 1024 | 1094 | 999 | 1168 | 1006 | 942 | 1093 | 1113 | 1126 | 1026 | 1119 | 1024 | 1001 | 988 | 1050 | 1178 | 994 | 958 | 1108 | 959 | 1103 | 1073 | 1112 | 928 | 950 | 1086 | 985 | 959 | 980 | 959 | 1081 | 1009 | 1085 | 985 | 990 | 967 | 1093 | 1003 | 1061 | 1074 | 1125 | 1096 | 1078 | 1070 | 1030 | 1040 | 1008 | 1003 | 1021 | 1016 | 977 | 1005 | 1064 | 961 | 900 | 1086 |  |  | 944 | 738 | 1059 |  | 1165 | 1132 | 1051 | 1020 | 1045 | 1058 | 1065 | 1072 | 1069 | 1083 | 1086 | 1080 | 1149 | 1235 | 975 | 894 | 790 | 640 | 783 | 913 | 999 | 1200 | 1018 | 1100 | 1098 | 1097 | 1186 | 1141 | 975 | 994 | 900 | 997 | 960 |  | 1250 | 1068 | 498 | 985 | 918 |  |  | 1000 | 1000 | 970 | 920 | 860 | 34.4 | 42 | 2.7 | 19.29 |  | 0 | 4.84 |  |  | 84756017.786 | 282077.977 | 57798684.403 | 61771.515 | 85536883.57 | 187144.417 | 62011259.85 | 55889.816 | 321211838.837 | 84479.581 | 66656.753 | 19.337 | 62997.701 | 36.012 | 65919.86 | 38.846 | 51034.708 | 38.145 | 246466.213 | 72.164 | 129599.105 | 246394.049 | 12.9667 | 0 | 4.84 | 34.4 | 42 | 2.7 | 19.29 | 254893
2025-05-18 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:14 | 18:23 | 1439 | 1449 | 1344 | 1339 | 1402 | 1340 | 1343 | 1346 | 1387 | 1395 | 1368 | 1363 | 1343 | 1262 | 1310 | 1328 | 1298 | 1327 | 1440 | 1441 | 1310 | 1341 | 1470 | 1507 | 1455 | 1435 | 1430 | 1485 | 1500 | 1480 | 1498 | 1490 | 1247 | 1630 | 1293 | 1455 | 1304 | 1307 | 1324 | 1336 | 1317 | 1298 | 1298 | 1330 | 1276 | 1388 | 1441 | 1317 | 1378 | 1355 | 1398 | 1330 | 1513 | 1502 | 1435 | 1462 | 1516 | 1351 | 1496 | 1458 | 1337 | 1507 | 1337 | 1298 | 1445 | 1435 | 1455 | 1227 | 1316 | 1321 | 1331 | 1326 | 1346 | 1295 | 1518 | 1483 | 1509 | 1300 | 1298 | 1403 | 1336 | 1337 | 1323 | 1329 | 1330 | 1334 | 1347 | 1328 | 1328 | 1314 | 1382 | 1398 | 1358 | 1348 | 1463 | 1328 | 1344 | 1373 | 1376 | 1310 | 1424 | 1373 | 1396 | 1348 | 1541 | 1310 | 1572 | 1545 | 1406 | 1534 | 1402 | 1496 | 1547 | 1563 | 1342 | 1406 | 1533 | 1433 | 1456 | 1377 | 1403 | 1478 | 1417 | 1324 | 1394 | 1482 | 1276 | 1297 | 1521 | 1514 | 1438 | 1450 | 1423 | 1207 | 1544 | 1486 | 1480 | 1439 | 1398 | 1402 | 1353 | 1398 | 1391 | 1546 | 1328 | 1565 | 1356 | 1251 | 1446 | 1470 | 1480 | 1353 | 1496 | 1345 | 1318 | 1307 | 1310 | 1325 | 1328 | 1278 | 1482 | 1282 | 1465 | 1412 | 1477 | 1244 | 1263 | 1455 | 1317 | 1285 | 1309 | 1278 | 1443 | 1360 | 1444 | 1315 | 1315 | 1287 | 1457 | 1338 | 1414 | 1442 | 1482 | 1442 | 1439 | 1426 | 1375 | 1389 | 1351 | 1350 | 1324 | 1306 | 1266 | 1330 | 1395 | 1232 | 1168 | 1419 |  |  | 1210 | 943 | 1357 |  | 1484 | 1378 | 1353 | 1339 | 1334 | 1382 | 1399 | 1406 | 1403 | 1420 | 1404 | 1399 | 1478 | 1587 | 1257 | 1164 | 963 | 810 | 998 | 1174 | 1379 | 1562 | 1386 | 1448 | 1363 | 1378 | 1490 | 1468 | 1264 | 1291 | 1169 | 1300 | 1198 |  | 1478 | 1383 | 633 | 1263 | 1278 |  |  | 1160 | 1263 | 1234 | 1198 | 1110 | 32.3 | 41.68 | 1.14 | 4.7 |  | 0 | 6.4 |  |  | 84844195.864 | 282091.684 | 57882888.841 | 61778.917 | 85624746.958 | 187158.05 | 62078515.979 | 55902.753 | 321539137.169 | 84534.381 | 88178.078 | 13.707 | 84204.438 | 7.402 | 87863.388 | 13.633 | 67256.129 | 12.937 | 327298.332 | 54.8 | 172361.407 | 327243.532 | 13.15 | 0 | 6.4 | 32.3 | 41.68 | 1.14 | 4.7 | 332920
2025-05-19 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:14 | 18:27 | 1413 | 1425 | 1321 | 1315 | 1373 | 1317 | 1317 | 1320 | 1360 | 1372 | 1346 | 1341 | 1321 | 1242 | 1308 | 1317 | 1261 | 1311 | 1417 | 1418 | 1310 | 1326 | 1454 | 1490 | 1428 | 1410 | 1406 | 1459 | 1471 | 1452 | 1425 | 1464 | 1221 | 1597 | 1269 | 1447 | 1304 | 1280 | 1296 | 1309 | 1290 | 1259 | 1276 | 1246 | 1284 | 1311 | 1411 | 1290 | 1348 | 1326 | 1305 | 1302 | 1483 | 1472 | 1402 | 1432 | 1483 | 1328 | 1475 | 1437 | 1309 | 1476 | 1359 | 1258 | 1415 | 1403 | 1427 | 1285 | 1301 | 1292 | 1308 | 1306 | 1333 | 1288 | 1488 | 1456 | 1479 | 1271 | 1249 | 1391 | 1308 | 1307 | 1295 | 1302 | 1303 | 1306 | 1332 | 1301 | 1305 | 1288 | 1356 | 1400 | 1340 | 1331 | 1398 | 1273 | 1264 | 1326 | 1302 | 1316 | 1351 | 1309 | 1336 | 1276 | 1499 | 1329 | 1557 | 1465 | 1328 | 1469 | 1433 | 1406 | 1474 | 1474 | 1317 | 1322 | 1450 | 1481 | 1478 | 1316 | 1335 | 1417 | 1372 | 1321 | 1369 | 1432 | 1264 | 1264 | 1463 | 1458 | 1408 | 1418 | 1412 | 1195 | 1484 | 1380 | 1434 | 1420 | 1397 | 1324 | 1338 | 1371 | 1327 | 1437 | 1284 | 1399 | 1304 | 1211 | 1358 | 1424 | 1431 | 1311 | 1505 | 1318 | 1298 | 1286 | 1254 | 1232 | 1310 | 1270 | 1458 | 1264 | 1437 | 1411 | 1449 | 1220 | 1243 | 1428 | 1303 | 1259 | 1288 | 1253 | 1418 | 1328 | 1416 | 1292 | 1306 | 1273 | 1439 | 1325 | 1398 | 1412 | 1475 | 1414 | 1415 | 1398 | 1365 | 1365 | 1319 | 1312 | 1293 | 1224 | 1218 | 1313 | 1245 | 1311 | 1102 | 1336 |  |  | 1168 | 912 | 1309 |  | 1424 | 1258 | 1315 | 1280 | 1308 | 1310 | 1324 | 1278 | 1323 | 1283 | 1317 | 1325 | 1475 | 1504 | 1216 | 1177 | 910 | 798 | 936 | 1111 | 1314 | 1404 | 1343 | 1332 | 1378 | 1398 | 1358 | 1392 | 1136 | 1266 | 1136 | 1278 | 1210 |  | 1401 | 1402 | 610 | 1298 | 1237 |  |  | 1198 | 1278 | 1210 | 1178 | 1121 | 36.2 | 40 | 1.1 | 4.2 |  | 0 | 6.27 |  |  | 84931095.141 | 282106.839 | 57965993.75 | 61788.116 | 85711093.859 | 187189.533 | 62145633.467 | 55919.967 | 321862485.793 | 84589.752 | 86899.277 | 15.155 | 83104.909 | 9.199 | 86346.901 | 31.483 | 67117.488 | 17.214 | 323348.624 | 55.371 | 169979.832 | 323293.253 | 13.2167 | 0 | 6.27 | 36.2 | 40 | 1.1 | 4.2 | 324288
2025-05-20 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:14 | 18:26 | 1397 | 1409 | 1306 | 1301 | 1370 | 1301 | 1302 | 1305 | 1345 | 1356 | 1330 | 1325 | 1305 | 1228 | 1304 | 1298 | 1268 | 1303 | 1414 | 1416 | 1316 | 1317 | 1438 | 1482 | 1430 | 1411 | 1405 | 1460 | 1472 | 1452 | 1415 | 1461 | 1207 | 1583 | 1243 | 1455 | 1298 | 1267 | 1278 | 1293 | 1272 | 1270 | 1282 | 1268 | 1308 | 1308 | 1404 | 1275 | 1338 | 1314 | 1293 | 1309 | 1467 | 1463 | 1392 | 1415 | 1467 | 1313 | 1455 | 1433 | 1295 | 1465 | 1398 | 1260 | 1413 | 1391 | 1423 | 1263 | 1282 | 1278 | 1295 | 1292 | 1318 | 1285 | 1494 | 1457 | 1481 | 1263 | 1232 | 1351 | 1300 | 1298 | 1281 | 1288 | 1290 | 1292 | 1317 | 1310 | 1291 | 1281 | 1342 | 1363 | 1325 | 1318 | 1398 | 1262 | 1260 | 1316 | 1298 | 1306 | 1344 | 1301 | 1333 | 1311 | 1497 | 1321 | 1564 | 1450 | 1314 | 1436 | 1423 | 1385 | 1426 | 1456 | 1302 | 1310 | 1434 | 1468 | 1471 | 1303 | 1321 | 1401 | 1360 | 1308 | 1327 | 1470 | 1255 | 1263 | 1450 | 1446 | 1395 | 1404 | 1400 | 1197 | 1476 | 1365 | 1424 | 1405 | 1389 | 1316 | 1327 | 1359 | 1320 | 1427 | 1276 | 1353 | 1295 | 1203 | 1353 | 1411 | 1421 | 1302 | 1493 | 1315 | 1292 | 1275 | 1298 | 1227 | 1296 | 1254 | 1441 | 1246 | 1423 | 1393 | 1431 | 1202 | 1259 | 1447 | 1302 | 1245 | 1288 | 1233 | 1416 | 1312 | 1411 | 1280 | 1302 | 1266 | 1429 | 1311 | 1393 | 1395 | 1467 | 1405 | 1398 | 1383 | 1353 | 1353 | 1301 | 1294 | 1283 | 1236 | 1201 | 1307 | 1230 | 1313 | 1089 | 1329 |  |  | 1134 | 904 | 1292 |  | 1410 | 1249 | 1302 | 1272 | 1295 | 1297 | 1310 | 1300 | 1308 | 1329 | 1302 | 1311 | 1459 | 1476 | 1201 | 1167 | 910 | 810 | 957 | 1136 | 1378 | 1439 | 1377 | 1363 | 1398 | 1363 | 1386 | 1427 | 1202 | 1296 | 1161 | 1263 | 1223 |  | 1855 | 1361 | 598 | 1278 | 1223 |  |  | 1210 | 1356 | 1226 | 1164 | 1132 | 36.2 | 38.23 | 1.3 | 6.3 |  | 0 | 6.27 |  |  | 85017444.06 | 282131.806 | 58048179.351 | 61814.197 | 85796789.223 | 187222.612 | 62212722.54 | 55950.155 | 322183673.474 | 84680.598 | 86348.919 | 24.967 | 82185.601 | 26.081 | 85695.364 | 33.079 | 67089.073 | 30.188 | 321187.681 | 90.846 | 168483.472 | 321096.835 | 13.2 | 0 | 6.27 | 36.2 | 38.23 | 1.3 | 6.3 | 323147
2025-05-21 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:16 | 18:27 | 1279 | 1291 | 1197 | 1194 | 1252 | 1192 | 1220.3 | 1193 | 1232 | 1242 | 1217 | 1211 | 1196 | 1124 | 1193 | 1189 | 1174 | 1193 | 1293 | 1295 | 1205 | 1205 | 1319 | 1360 | 1310 | 1291 | 1288 | 1340 | 1355 | 1339 | 1325 | 1352 | 1128 | 1458 | 1176 | 1346 | 1208 | 1188 | 1203 | 1202 | 1201 | 1185 | 1212 | 1185 | 1214 | 1210 | 1310 | 1189 | 1223 | 1205 | 1196 | 1197 | 1372 | 1343 | 1275 | 1308 | 1341 | 1201 | 1340 | 1308 | 1209 | 1363 | 1325 | 1208 | 1290 | 1269 | 1300 | 1167 | 1171 | 1165 | 1183 | 1180 | 1216 | 1186 | 1374 | 1343 | 1364 | 1171 | 1169.4 | 1254 | 1208 | 1208 | 1196 | 1201 | 1205 | 1202 | 1203 | 1196 | 1179 | 1170 | 1226 | 1298 | 1226 | 1217 | 1310 | 1155 | 1163 | 1199 | 1184 | 1192 | 1225 | 1186 | 1215 | 1195 | 1361 | 1205 | 1428 | 1323 | 1198 | 1305 | 1296 | 1270 | 1315 | 1330 | 1188 | 1263 | 1311 | 1335 | 1337 | 1188 | 1207 | 1294.1 | 1309.1 | 1195 | 1210 | 1326 | 1192 | 1165 | 1323 | 1319 | 1273 | 1281 | 1277 | 1093 | 1344 | 1249 | 1300 | 1286 | 1266 | 1195 | 1210 | 1246 | 1206 | 1300 | 1209 | 1263 | 1179 | 1095 | 1258 | 1287 | 1295 | 1184 | 1355 | 1198 | 1181 | 1163 | 1165 | 1145 | 1181 | 1144 | 1311 | 1165 | 1298 | 1276 | 1308 | 1163 | 1170 | 1328 | 1192 | 1144 | 1184 | 1150 | 1309 | 1204 | 1330 | 1169 | 1186 | 1162 | 1304 | 1199 | 1268 | 1287 | 1284 | 1278 | 1275 | 1281 | 1236 | 1233 | 1203 | 1245 | 1188 | 1165 | 1119 | 1220 | 1152 | 1211 | 1000 | 1238 |  |  | 1046 | 824 | 1179 |  | 1291 | 1144 | 1205 | 1175 | 1211 | 1181 | 1219 | 1186 | 1208 | 1214 | 1203 | 1198 | 1378 | 1364 | 1098 | 1066 | 868 | 726 | 889.7 | 1047 | 1260 | 1328 | 1270 | 1263 | 1264 | 1298 | 1323 | 1298 | 1126 | 1180 | 1054 | 1163 | 1126 |  | 1698 | 1298 | 550 | 1210 | 1169 |  |  | 1110 | 1266 | 1240 | 1110 | 1051 | 35.5 | 28 | 1.1 | 4.3 |  | 0 | 5.79 |  |  | 85097003.114 | 282158.202 | 58123585.217 | 61835.796 | 85875128.954 | 187246.759 | 62274322.813 | 55975.842 | 322478484.407 | 84768.572 | 79559.054 | 26.396 | 75405.866 | 21.599 | 78339.731 | 24.147 | 61600.273 | 25.687 | 294810.933 | 87.974 | 154916.925 | 294722.959 | 13.1833 | 0 | 5.79 | 35.5 | 28 | 1.1 | 4.3 | 297837.6
2025-05-22 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:16 | 18:29 | 1401 | 1396 | 1300 | 1275 | 1384 | 1319 | 1294 | 1316 | 1362 | 1372 | 1334 | 1338 | 1321 | 1243 | 1311 | 1321 | 1260 | 1314 | 1423 | 1411 | 1292 | 1332 | 1461 | 1475 | 1443 | 1392 | 1420 | 1476 | 1479 | 1458 | 1443.5 | 1486 | 1208 | 1610 | 1297 | 1478 | 1239 | 1300 | 1319 | 1275 | 1316 | 1284 | 1300 | 1268 | 1300 | 1327 | 1433 | 1304 | 1366 | 1344 | 1276 | 1333 | 1514 | 1492 | 1409 | 1434 | 1480 | 1325 | 1479 | 1438 | 1325 | 1495 | 1412 | 1305 | 1421 | 1395 | 1433 | 1311 | 1311 | 1298 | 1318 | 1316 | 1338 | 1309 | 1500 | 1465 | 1493 | 1279 | 1293 | 1398 | 1319 | 1314 | 1304 | 1308 | 1313 | 1301 | 1328 | 1319 | 1315 | 1308 | 1359 | 1375 | 1348 | 1341 | 1423.6 | 1271 | 1264 | 1312 | 1292 | 1303 | 1342 | 1300 | 1330 | 1305 | 1432 | 1322 | 1559 | 1446 | 1312 | 1456 | 1423 | 1394 | 1472 | 1485 | 1302 | 1271 | 1432 | 1463 | 1462 | 1316 | 1329 | 1429 | 1427 | 1312 | 1328 | 1438 | 1241 | 1275 | 1462 | 1450 | 1405 | 1421 | 1368 | 1228 | 1513 | 1402 | 1450 | 1443 | 1425 | 1334 | 1342 | 1396 | 1346 | 1462 | 1302 | 1390 | 1313 | 1139 | 1395 | 1419 | 1422 | 1296 | 1492 | 1312 | 1290 | 1275 | 1325 | 1277 | 1311 | 1271 | 1455 | 1263 | 1443 | 1409 | 1454 | 1280 | 1295 | 1468 | 1320 | 1316 | 1332 | 1318 | 1450 | 1357 | 1474 | 1296 | 1308 | 1284 | 1446 | 1328 | 1399 | 1420 | 1431 | 1425 | 1417 | 1400 | 1368 | 1316 | 1319 | 1391 | 1294 | 1265 | 1217 | 1321 | 1256 | 1314 | 1105 | 1344 |  |  | 1190 | 849 | 1255 |  | 1418 | 1251 | 1321 | 1290 | 1317 | 1325 | 1333 | 1333 | 1336 | 1364 | 1322 | 1316 | 1473 | 1500 | 1212 | 1166 | 962 | 835 | 964 | 1053 | 1368 | 1461 | 1387 | 1369 | 1378 | 1450.2 | 1455 | 1441 | 1226 | 1271 | 1163 | 1322 | 1192 |  | 1721 | 1371.1 | 519 | 1275 | 1227 |  |  | 1127.6 | 1362.5 | 1348.6 | 1207.7 | 1097 | 33.8 | 43.42 | 3.64 | 8.3 |  | 6.88 | 6.41 |  |  | 85184158.709 | 282186.32 | 58207030.719 | 61858.545 | 85961987.153 | 187281.33 | 62341902.179 | 56009.599 | 322803070.42 | 84859.421 | 87155.595 | 28.118 | 83445.502 | 22.749 | 86858.199 | 34.571 | 67579.366 | 33.757 | 324586.013 | 90.849 | 170550.23 | 324495.164 | 13.2167 | 6.88 | 6.41 | 33.8 | 43.42 | 3.64 | 8.3 | 327534.8
2025-05-23 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:13 | 18:29 | 1402.2 | 1418.1 | 1319.9 | 1316.7 | 1391.6 | 1310.8 | 1294.8 | 1301 | 1352.3 | 1367.5 | 1324.6 | 1320.9 | 1308.7 | 1241.4 | 1309.5 | 1312.2 | 1261.1 | 1300.1 | 1411.7 | 1413.8 | 1318.2 | 1322.8 | 1456.9 | 1495 | 1430.4 | 1412.6 | 1410.5 | 1470.4 | 1476.87 | 1462.2 | 1449.6 | 1473.7 | 1240 | 1599.3 | 1283.4 | 1471.4 | 1314.7 | 1283.6 | 1303.6 | 1344.4 | 1302 | 1263.6 | 1309.8 | 1287.4 | 1311.7 | 1318.6 | 1428.6 | 1300.1 | 1368.5 | 1346.8 | 1274.9 | 1329.8 | 1522.8 | 1482.3 | 1394.7 | 1421.1 | 1459.9 | 1315.6 | 1468.5 | 1432.7 | 1332.1 | 1496.5 | 1328.3 | 1274.6 | 1441 | 1421.4 | 1450.4 | 1301.6 | 1316.1 | 1303.2 | 1259.7 | 1318.8 | 1323.5 | 1293.7 | 1482.8 | 1446.9 | 1477.9 | 1292.9 | 1278 | 1375.7 | 1311.9 | 1311 | 1299.1 | 1309.7 | 1304 | 1301.5 | 1317.9 | 1280.7 | 1320.3 | 1312.2 | 1377.4 | 1385.8 | 1336.5 | 1327.4 | 1485.5 | 1279.2 | 1269.5 | 1297.9 | 1276.1 | 1289.6 | 1330.2 | 1284.5 | 1318.1 | 1289.2 | 1422.4 | 1314.2 | 1542 | 1433.1 | 1302.8 | 1430.7 | 1417.7 | 1391.4 | 1456 | 1445.7 | 1288.8 | 1282.6 | 1420.2 | 1459.6 | 1458.3 | 1325 | 1331.8 | 1432.8 | 1443.1 | 1306.5 | 1321.4 | 1432.5 | 1265.4 | 1264.9 | 1458.2 | 1459.5 | 1432.3 | 1439.7 | 1432.5 | 1227.2 | 1508.6 | 1393.1 | 1435 | 1429.4 | 1410.1 | 1324.4 | 1382 | 1398.4 | 1330.5 | 1455.6 | 1286.4 | 1394.4 | 1318.7 | 1222.8 | 1409.9 | 1430 | 1414.9 | 1285.6 | 1479 | 1298.2 | 1272.9 | 1267.4 | 1268.5 | 1271.4 | 1298.8 | 1259.7 | 1445.3 | 1250.3 | 1429.4 | 1406.5 | 1438.3 | 1279.1 | 1285 | 1458.3 | 1306.8 | 1321 | 1322.1 | 1306.8 | 1439.8 | 1346.9 | 1465.8 | 1285.5 | 1294 | 1272.6 | 1432.3 | 1317.5 | 1385.8 | 1407.1 | 1417.5 | 1415.1 | 1405.7 | 1408.7 | 1354.9 | 1307.7 | 1317.1 | 1379.6 | 1286 | 1260.3 | 1217.7 | 1313.6 | 1254.9 | 1304.9 | 1094.5 | 1333 |  |  | 1174.4 | 902.9 | 1282.1 |  | 1393.3 | 1228 | 1322.9 | 1304.9 | 1310.1 | 1342.1 | 1332.4 | 1348.8 | 1340.7 | 1378.5 | 1320.8 | 1333.3 | 1488.7 | 1517.4 | 1198.7 | 1151.6 | 999.8 | 851.6 | 967 | 1100 | 1356.5 | 1440.2 | 1374.7 | 1369.8 | 1390.2 | 1450.1 | 1437.8 | 1465.6 | 1239 | 1273.7 | 1166.8 | 1257 | 1176.8 |  | 1751 | 1381.2 | 520.8 | 1293.9 | 1238.7 |  |  | 1301.9 | 1331.6 | 1351.4 | 1212.7 | 1095 | 34.93 | 46.23 | 3.32 | 7.1 |  | 6.9 | 6.38 |  |  | 85271343.807 | 282224.438 | 58289730.442 | 61891.294 | 86048437.603 | 187325.901 | 62409065.75 | 56053.356 | 323126301.235 | 84960.27 | 87185.098 | 38.118 | 82699.723 | 32.749 | 86450.45 | 44.571 | 67163.571 | 43.757 | 323230.815 | 100.849 | 169813.954 | 323129.966 | 13.2667 | 6.9 | 6.38 | 34.93 | 46.23 | 3.32 | 7.1 | 326090.97
2025-05-24 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:15 | 18:29 | 1259.4 | 1269.5 | 1180 | 1169.7 | 1227.7 | 1172.6 | 1146.2 | 1148.8 | 1187 | 1197.9 | 1177.5 | 1170.4 | 1151.3 | 1089 | 1155 | 1153.4 | 1128.5 | 1148.6 | 1250.8 | 1247.9 | 1158.2 | 1163.4 | 1278.3 | 1311.4 | 1280 | 1274.3 | 1261.4 | 1293.7 | 1311.1 | 1290.1 | 1295.5 | 1300.7 | 1104.5 | 1430.4 | 1141.9 | 1315.1 | 1145.2 | 1142.7 | 1160.8 | 1188.3 | 1158.3 | 1137.5 | 1163.7 | 1143.1 | 1164.4 | 1170.3 | 1267.4 | 1155.7 | 1213.9 | 1191.7 | 1129.4 | 1177.7 | 1347.1 | 1315.2 | 1254.5 | 1287.6 | 1307.7 | 1172.6 | 1304.5 | 1273.9 | 1183.5 | 1332.5 | 1174.2 | 1141.5 | 1281.8 | 1261.4 | 1290.2 | 1159.5 | 1162.5 | 1152.8 | 1168.6 | 1172.6 | 1183 | 1144.9 | 1333.9 | 1303.8 | 1325.4 | 1149.9 | 1135.3 | 1235.4 | 1163 | 1164.9 | 1158.2 | 1172.4 | 1155.3 | 1159 | 1168.8 | 1115.4 | 1171.9 | 1161.1 | 1217.6 | 1241.5 | 1144.1 | 1180.5 | 1330.5 | 1136.6 | 1127.8 | 1149.3 | 1136.3 | 1141.6 | 1176.5 | 1143.4 | 1172.6 | 1146.6 | 1266.5 | 1161.4 | 1383.1 | 1260.9 | 1148.1 | 1268.7 | 1252.1 | 1251.4 | 1318.6 | 1301.6 | 1135.7 | 1129.9 | 1276.1 | 1312.9 | 1296.1 | 1189 | 1203.7 | 1279.2 | 1217.4 | 1167.3 | 1165.1 | 1271.5 | 1194.5 | 1180.3 | 1339.4 | 1330 | 1283.2 | 1291.3 | 1281.7 | 1100.5 | 1357.5 | 1251.6 | 1293.2 | 1286.8 | 1274.4 | 1198.1 | 1269.9 | 1263.3 | 1196.5 | 1311.1 | 1159.2 | 1228.8 | 1188.7 | 1107.3 | 1238.1 | 1306.3 | 1307.4 | 1183.5 | 1334.7 | 1169.2 | 1144.5 | 1150.3 | 1157.2 | 1155.5 | 1158.3 | 1124.4 | 1295.4 | 1116.6 | 1272.5 | 1255.4 | 1273 | 1176.4 | 1135.8 | 1290.8 | 1164.7 | 1160.5 | 1171.9 | 1167.4 | 1274.4 | 1190.1 | 1268.6 | 1154.3 | 1167.1 | 1142.4 | 1279.2 | 1178.1 | 1241.5 | 1255.6 | 1127.9 | 762.5 | 1257.9 | 1264.9 | 1222.6 | 1176.1 | 1171.5 | 1232.9 | 1138.1 | 1078.4 | 1114.9 | 1158.4 | 1101.5 | 1150 | 962 | 1174.4 |  |  | 1039.3 | 812.6 | 1152.1 |  | 1236 | 1099.9 | 1171.6 | 1155.3 | 1156 | 1186 | 1171.3 | 1186.1 | 1175.8 | 1206.8 | 1164.5 | 1193.2 | 1318.8 | 1344.8 | 1061.7 | 1020.2 | 895.5 | 770 | 869.4 | 1005.8 | 1196.3 | 1281.7 | 1227.8 | 1224.6 | 1212.5 | 1311.5 | 1276.7 | 1272.8 | 1120.3 | 1151.8 | 1061.8 | 1127.5 | 1093.2 |  | 1550.5 | 1227.4 | 472 | 1141 | 1098.2 |  |  | 1161.4 | 1197.3 | 1187.1 | 1078.7 | 992.2 | 35.89 | 44.51 | 4.63 | 7.7 |  | 6.17 | 5.67 |  |  | 85348803.993 | 282272.556 | 58363669.317 | 61938.043 | 86125519.623 | 187381.472 | 62469113.062 | 56111.113 | 323414575.721 | 85081.119 | 77460.186 | 48.118 | 73938.875 | 46.749 | 77082.02 | 55.571 | 60047.312 | 57.757 | 288274.486 | 120.849 | 151304.194 | 288153.637 | 13.2333 | 6.17 | 5.67 | 35.89 | 44.51 | 4.63 | 7.7 | 290997.7
2025-05-25 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:45 | 18:31 | 1448 | 1462.1 | 1353.7 | 1350 | 1443.4 | 1344.4 | 1343.4 | 1345.2 | 1391.6 | 1399.1 | 1368.1 | 1359.4 | 1341.6 | 1264.3 | 1339 | 1336.9 | 1337.2 | 1329.1 | 1438.8 | 1442.6 | 1345 | 1344 | 1475.9 | 1516.9 | 1462.5 | 1450.6 | 1439.4 | 1491.2 | 1503.2 | 1485.5 | 1501.1 | 1496.2 | 1260.7 | 1637.4 | 1313 | 1501.1 | 1345.8 | 1310.8 | 1332.6 | 1356.7 | 1329.9 | 1314.7 | 1338.9 | 1312.8 | 1336.9 | 1346.9 | 1451.4 | 1325.3 | 1383.7 | 1360.6 | 1301.2 | 1254.1 | 1537.8 | 1510.4 | 1438.7 | 1522.1 | 1516.3 | 1349.5 | 1498.8 | 1458.4 | 1350 | 1520.1 | 1336.8 | 1302.3 | 1458.7 | 1446.5 | 1465.8 | 1359.8 | 1338.5 | 1329.6 | 1339.2 | 1337.5 | 1357.8 | 1342.6 | 1526.9 | 1492.4 | 1527.8 | 1342.9 | 1325.1 | 1461.2 | 1348.5 | 1351.3 | 1337.1 | 1354.9 | 1336.7 | 1339.1 | 1355.4 | 1342.9 | 1334.4 | 1324.7 | 1387.2 | 1474.3 | 1369.3 | 1359.9 | 1507.6 | 1323 | 1334.2 | 1326 | 1302 | 1316 | 1351 | 1309 | 1336 | 1326 | 1499 | 1329 | 1557 | 1465 | 1328 | 1469 | 1433 | 1406 | 1474 | 1474 | 1317 | 1322 | 1450 | 1481 | 1428 | 1316 | 1335 | 1477 | 1372 | 1321 | 1338 | 1525 | 1324 | 1331.9 | 1463 | 1458 | 1408 | 1418 | 1412 | 1195 | 1484 | 1400 | 1434 | 1350 | 1397 | 1324 | 1418 | 1421 | 1327 | 1437 | 1334 | 1409 | 1304 | 1211 | 1408 | 1424 | 1431 | 1311 | 1505 | 1318 | 1328 | 1332.9 | 1329.1 | 1332 | 1326.7 | 1289.9 | 1470.7 | 1298.2 | 1458.3 | 1489.1 | 1467.5 | 1379.1 | 1308.2 | 1485.5 | 1336.2 | 1333.6 | 1354.5 | 1350.9 | 1471.7 | 1374.9 | 1443 | 1315.8 | 1325.6 | 1304 | 1461.8 | 1344.6 | 1416.6 | 1448.1 | 1445 | 1444.1 | 1438.7 | 1451.4 | 1383.4 | 1335.4 | 1351.9 | 1405.4 | 1293 | 1324 | 1258 | 1313 | 1345 | 1271 | 1102 | 1336 |  |  | 1188 | 932 | 1319 |  | 1424 | 1278 | 1315 | 1280 | 1308 | 1310 | 1324 | 1333 | 1323 | 1335.3 | 1317 | 1325 | 1475 | 1504 | 1216 | 1177 | 1026 | 897.1 | 1016 | 1131 | 1354 | 1474 | 1423 | 1432.1 | 1353.5 | 1465.9 | 1478 | 1462 | 1296 | 1366 | 1256 | 1350 | 1273 |  | 1875 | 1421.8 | 537 | 1320 | 1287 |  |  | 1278 | 1401 | 1370 | 1266 | 1181 | 36.28 | 44.75 | 2.4 | 6.5 |  | 6.76 | 6.25 |  |  | 85437787.569 | 282335.674 | 58448978.722 | 61998.792 | 86213949.856 | 187445.043 | 62538374.165 | 56181.87 | 323746300.695 | 85241.968 | 88983.576 | 63.118 | 85309.405 | 60.749 | 88430.233 | 63.571 | 69261.103 | 70.757 | 331724.974 | 160.849 | 174169.114 | 331564.125 | 12.7667 | 6.76 | 6.25 | 36.28 | 44.75 | 2.4 | 6.5 | 333824.3
2025-05-26 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:14 | 18:31 | 1120.8 | 1087.1 | 1051.2 | 1046.4 | 1081.8 | 1042.9 | 1041.2 | 1043.8 | 1081.4 | 1088 | 1061.3 | 1056 | 1041.4 | 979.4 | 1037.6 | 1037.9 | 990.2 | 1030.2 | 1119.5 | 1121 | 1040.7 | 1043.8 | 1144.9 | 1176.4 | 1134.3 | 1125.7 | 1116.1 | 1155 | 1172.6 | 1151.8 | 1152.5 | 1162.8 | 968.8 | 1271.8 | 1009.5 | 1155.4 | 1041.7 | 1014.3 | 1030.4 | 1049.9 | 1025.7 | 1010.7 | 1033.9 | 1013.7 | 1032.2 | 1041.2 | 1122.8 | 1028.5 | 1066.6 | 1049.6 | 1014.1 | 1035.1 | 1186.5 | 1166.9 | 1112.7 | 1176.4 | 1176.3 | 1049.6 | 1163.8 | 1135 | 1044.8 | 1181.2 | 1035.9 | 1018 | 1121 | 1111 | 1126.6 | 1085.3 | 1028.8 | 1021.6 | 1030.8 | 1028.1 | 1051.2 | 1034.6 | 1170.7 | 1150.9 | 1173.5 | 1029.7 | 1017.4 | 1125 | 1036.6 | 1039.3 | 1028.3 | 1041.2 | 1026.8 | 1032.3 | 1044.9 | 1034.4 | 1027.8 | 1017 | 1066.2 | 1091.2 | 1055.4 | 1045.7 | 1156.2 | 1018 | 1013.7 | 1040.9 | 1025.4 | 1031.3 | 1058.1 | 1025.9 | 1044.6 | 1023.4 | 1170.1 | 1039.5 | 1226.2 | 1149.7 | 1041.9 | 1154.5 | 1120.3 | 1107.8 | 1170 | 1160.1 | 1033.7 | 1019.7 | 1145.9 | 1161.3 | 1154 | 1038.3 | 1054.7 | 1121.6 | 1090.7 | 1039.2 | 1045.4 | 1183 | 1009 | 1011.6 | 1166.8 | 1152.3 | 1110.8 | 1116.4 | 1113 | 952.5 | 1170.1 | 1088.4 | 1124.6 | 1118.5 | 1100.8 | 1039.3 | 1098.8 | 1101.5 | 1032.7 | 1133.36 | 1008.1 | 1097.9 | 1027.7 | 958.6 | 1066.5 | 1126.6 | 1130.3 | 1036 | 1184.9 | 1038.5 | 1022.8 | 1015.3 | 1025.5 | 1019.4 | 1018.1 | 988.5 | 1142.9 | 1011.9 | 1112.8 | 1121.2 | 1122.5 | 1034.7 | 1004.2 | 1151.6 | 1030.7 | 1031.1 | 1043.9 | 1028.6 | 1145.5 | 1064.7 | 1123.1 | 1004.6 | 1012.1 | 997.2 | 1121.2 | 1031.5 | 1080.6 | 1128.2 | 1110.3 | 1106.6 | 1101 | 1118.1 | 1059.8 | 1042.6 | 1037.6 | 1087.8 | 1014.2 | 1005.1 | 1012.1 | 1030 | 1026.4 | 1031.8 | 866.9 | 1054.4 |  |  | 935.5 | 729.4 | 1030.4 |  | 1113.5 | 999.4 | 1034.4 | 869.6 | 1027.7 | 1033.3 | 1039.6 | 1038.3 | 1041.5 | 1060.6 | 1035.1 | 1044.8 | 1164 | 1187.1 | 960.6 | 924.7 | 800.2 | 677 | 769.6 | 883.5 | 1025.9 | 1104.2 | 1050.4 | 1041.3 | 1019.4 | 1055.5 | 1098.2 | 1086.8 | 927.1 | 998.7 | 931.8 | 962.9 | 897 |  | 1450.1 | 1098.4 | 411.5 | 1007.7 | 975.9 |  |  | 1030.1 | 1075.5 | 1063.4 | 993.6 | 920.1 | 32.47 | 39.01 | 3.18 | 8.3 |  | 5.25 | 4.81 |  |  | 85506921.012 | 282398.792 | 58515310.988 | 62059.541 | 86282183.959 | 187508.614 | 62591209.703 | 56252.627 | 324002684.181 | 85402.817 | 69133.443 | 63.118 | 66332.266 | 60.749 | 68234.103 | 63.571 | 52835.538 | 70.757 | 256383.486 | 160.849 | 135341.842 | 256222.637 | 13.2833 | 5.25 | 4.81 | 32.47 | 39.01 | 3.18 | 8.3 | 258237.06
2025-05-27 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:10 | 18:31 | 1358.8 | 1320.4 | 1274 | 1270.6 | 1315.6 | 1266.5 | 1263 | 1270 | 1311.4 | 1321.7 | 1286.2 | 1280.9 | 1266.5 | 1190.4 | 1264 | 1261.4 | 1179.8 | 1154.3 | 1250.9 | 1253.7 | 1168.7 | 1171.8 | 1255.9 | 1316.7 | 1260.4 | 1276.1 | 1267.6 | 1311.2 | 1302 | 1318.8 | 1300.9 | 1310 | 1167.4 | 1529.4 | 1211.3 | 1398.5 | 1251.7 | 1217.1 | 1235.5 | 1261 | 1243 | 1216.3 | 1237.3 | 1211.8 | 1229.6 | 1234.6 | 1341.7 | 1228.3 | 1264.7 | 1265.5 | 1209.6 | 1228.5 | 1415.9 | 1389.8 | 1341.4 | 1427.3 | 1421.7 | 1267.1 | 1407.2 | 1372.4 | 1258.5 | 1422.6 | 1235.6 | 1201.5 | 1340.5 | 1331.7 | 1339.8 | 1314.6 | 1233.2 | 1227.9 | 1224 | 1217.1 | 1261.1 | 1236.4 | 1406.2 | 1384.1 | 1404 | 1233 | 1219.4 | 1330.1 | 1240.4 | 1244.7 | 1225.5 | 1247 | 1226.2 | 1225.1 | 1236.8 | 1228.1 | 1215.1 | 1207.1 | 1265.5 | 1332.5 | 1251.3 | 1248.6 | 1378.3 | 1228.3 | 1225.7 | 1254.7 | 1246.5 | 1246.5 | 1281.7 | 1250.8 | 1276.4 | 1249.4 | 1419.8 | 1257.8 | 1485.2 | 1385.5 | 1255.4 | 1363.7 | 1341.7 | 1323.3 | 1391.4 | 1393.4 | 1247.2 | 1212.6 | 1375.3 | 1375.5 | 1373.8 | 1242.1 | 1265.7 | 1357.5 | 1361.5 | 1254.7 | 1259.6 | 1408.6 | 1145.4 | 1139.9 | 1406 | 1390.7 | 1355.6 | 1359.1 | 1352.8 | 1159.1 | 1437.4 | 1329.7 | 1389.7 | 1377.5 | 1374.5 | 1293.2 | 1339.2 | 1340.7 | 1297.4 | 1405.1 | 1257.1 | 1322.1 | 1264.2 | 1178.9 | 1367.3 | 1380 | 1394.4 | 1273.5 | 1443 | 1272.9 | 1245.9 | 1237.1 | 1239.3 | 1169.5 | 1264.5 | 1255.1 | 1414.3 | 1222.4 | 1398.7 | 1355.7 | 1400.2 | 1260.1 | 1245.5 | 1422.2 | 1277.9 | 1270.7 | 1290 | 1265.7 | 1406.8 | 1311.2 | 1370.2 | 1247.3 | 1245.6 | 1234.4 | 1395.3 | 1277.6 | 1332.5 | 1359.1 | 1392.7 | 1380.3 | 1365.8 | 1352.6 | 1308.5 | 1267.8 | 1244.5 | 1332 | 1216.1 | 1205.1 | 1237.4 | 1240.5 | 1242.1 | 1250.7 | 1049.4 | 1277.7 |  |  | 1121 | 870.3 | 1238.7 |  | 1353 | 1218.1 | 1232.5 | 1223.5 | 1230 | 1232.2 | 1261 | 1247.1 | 1264.2 | 1274.7 | 1254.8 | 1262.6 | 1404.3 | 1429 | 1146 | 1116.8 | 960.4 | 811.1 | 955.1 | 1101.1 | 1293.1 | 1380.9 | 1324.4 | 1321.1 | 1313.5 | 1366 | 1376.1 | 1364.1 | 1190.1 | 1268.1 | 1212.1 | 1223.1 | 1141.1 |  | 1717.8 | 1301.4 | 501.4 | 1212 | 1178.3 |  |  | 1199.1 | 1313.1 | 1275.1 | 1194.1 | 1091.7 | 34.17 | 39.27 | 1.95 | 5.7 |  | 6.45 | 5.98 |  |  | 85588649.621 | 282458.91 | 58594183.415 | 62116.29 | 86365956.86 | 187568.185 | 62655291.274 | 56322.384 | 324310907.99 | 85561.666 | 81728.609 | 60.118 | 78872.427 | 56.749 | 83772.901 | 59.571 | 64081.571 | 69.757 | 308223.809 | 158.849 | 160484.169 | 308064.96 | 13.35 | 6.45 | 5.98 | 34.17 | 39.27 | 1.95 | 5.7 | 311840.2
2025-05-28 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:06 | 18:31 | 1052.8 | 1019.8 | 983.2 | 980.7 | 1016.2 | 978.1 | 981.6 | 981.9 | 1014 | 1017.8 | 1000.4 | 993.2 | 978.5 | 921.5 | 974.5 | 971.2 | 932 | 968.1 | 1046.9 | 1049.2 | 980.2 | 989.5 | 1073.5 | 1104.4 | 1066.9 | 1060.1 | 1052.3 | 1090 | 1103.5 | 1087.6 | 1006.1 | 1097.5 | 851.4 | 1055.6 | 954.8 | 1081.6 | 984.7 | 960.5 | 955.8 | 989.5 | 971.7 | 963.5 | 977.8 | 960.2 | 977.1 | 985.4 | 1060.4 | 979.2 | 1009.9 | 991.7 | 938.5 | 981.3 | 1122.7 | 1103.8 | 1050.5 | 1107.6 | 1109.3 | 986.7 | 1093.8 | 1061.7 | 989.5 | 1113.8 | 977.2 | 951.1 | 1054.4 | 1046.8 | 1061.5 | 1036.8 | 935.1 | 962.1 | 970.2 | 967.6 | 987 | 969 | 1104.8 | 1085.7 | 1105.1 | 971.2 | 955.9 | 1046.1 | 972.8 | 977.2 | 965.3 | 979.6 | 962.9 | 967.3 | 978.9 | 969 | 962.6 | 953.3 | 1001.8 | 1049.9 | 990.9 | 982.8 | 1089.7 | 958.1 | 961.9 | 978.7 | 974.7 | 971.2 | 998.2 | 974.8 | 995.7 | 978.7 | 1116.4 | 986.4 | 1163.4 | 1085.6 | 982.6 | 1083.7 | 1055.8 | 1044.8 | 1096.7 | 1094.9 | 975.8 | 928.8 | 1082.5 | 1091.8 | 1087.4 | 975.4 | 992.6 | 1044.5 | 1013.6 | 977.7 | 984.7 | 1111.6 | 551.7 | 586.4 | 703.7 | 692.8 | 615.2 | 666.6 | 655.8 | 559.8 | 684.9 | 639.8 | 662 | 656.2 | 646.2 | 614.2 | 647.2 | 643.8 | 622.3 | 674 | 603.3 | 639.8 | 617.5 | 580.7 | 678 | 682.9 | 687.2 | 630.5 | 715.8 | 631.8 | 622 | 618.3 | 624.5 | 620.4 | 451.5 | 436.9 | 503 | 436.9 | 508.9 | 482.7 | 516.2 | 444.5 | 445.7 | 506.2 | 457.3 | 452.7 | 462.9 | 455.9 | 501.6 | 471.9 | 472 | 447.8 | 450 | 443.5 | 502.8 | 457.3 | 478.5 | 487.4 | 506.7 | 492.9 | 486 | 483.6 | 468.6 | 454.7 | 437.6 | 477.2 | 935.2 | 915.3 | 881.2 | 956 | 952.9 | 956.1 | 802.2 | 974.6 |  |  | 852 | 643.4 | 946 |  | 1030.7 | 904.1 | 959 | 934.8 | 953.8 | 959.8 | 973.1 | 968.2 | 973.4 | 991.6 | 968.6 | 980 | 1092.7 | 1116.1 | 897 | 868.4 | 750.7 | 631.8 | 692.5 | 813.5 | 985.8 | 1047.1 | 993.9 | 976.5 | 985.5 | 1041.5 | 1044.4 | 1026.3 | 836.2 | 927.7 | 835.8 | 885.5 | 783.4 |  | 1180.5 | 942.8 | 391.3 | 873 | 845.7 |  |  | 962.9 | 978 | 875.9 | 841.5 | 741.5 | 36.79 | 48.09 | 1.97 | 4.9 |  | 6.79 | 6.28 |  |  | 85653541.874 | 282521.028 | 58656363.174 | 62174.039 | 86401496.786 | 187607.756 | 62704410.555 | 56393.141 | 324522533.773 | 85721.515 | 64892.253 | 62.118 | 62179.759 | 57.749 | 35539.926 | 39.571 | 49119.281 | 70.757 | 211625.783 | 159.849 | 126952.145 | 211465.934 | 13.4167 | 6.79 | 6.28 | 36.79 | 48.09 | 1.97 | 4.9 | 212537.6
2025-05-29 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:09 | 18:19 | 1087.9 | 1075.2 | 1015.7 | 1014.6 | 1048.6 | 1009.8 | 1010.7 | 1012.3 | 1045.3 | 1051.3 | 1029.8 | 1022.9 | 1007.6 | 944.7 | 1003.8 | 1000.8 | 1001.3 | 1000.2 | 1077.8 | 1082.1 | 1010.7 | 1007.8 | 1104.6 | 1134.4 | 1100.4 | 1089.8 | 1081 | 1124.3 | 1138.1 | 1135.2 | 1129.1 | 1131.8 | 940 | 1245.8 | 992.9 | 1126.6 | 1017.7 | 998.8 | 1002.5 | 1031.3 | 1012.4 | 1007.9 | 1021.4 | 1004.5 | 1010.5 | 1018 | 1095.4 | 1003.5 | 1045.1 | 1027.6 | 968.6 | 1012.4 | 1158.7 | 1139.9 | 1081.8 | 1126 | 1143.2 | 1017.4 | 1128.8 | 1094.4 | 1026.3 | 1152.5 | 1010.6 | 974.9 | 1097.1 | 1090.1 | 1105.1 | 1080.8 | 1004.7 | 1003.3 | 1010 | 1007.8 | 1027.5 | 1010 | 1166.5 | 1143.3 | 1163.1 | 1023.7 | 999.6 | 1090.9 | 1022.8 | 1022.7 | 1007.8 | 1019.9 | 1005.4 | 1010.7 | 1021.4 | 1012.3 | 1006.4 | 997.4 | 1047.7 | 1088.5 | 1031.4 | 1022.2 | 1137.6 | 998.2 | 1006.5 | 1019.1 | 1018.2 | 1012.5 | 1037.2 | 1016.2 | 1034 | 1017.7 | 1164.3 | 1018.4 | 1199.2 | 1131.3 | 1020.5 | 1126.5 | 1094.6 | 1091.1 | 1147 | 1140.3 | 1015.4 | 962.5 | 1128.3 | 1134.7 | 1130.2 | 1015.4 | 1029 | 1090.5 | 1055.1 | 1014.7 | 1021.2 | 1153.7 | 925.1 | 945.2 | 1059.4 | 1044.4 | 927.8 | 1009.3 | 999.1 | 854.7 | 1048.3 | 977.3 | 1014.2 | 1002.3 | 983.5 | 931.7 | 984.8 | 980.7 | 940.5 | 1017.8 | 901 | 959.1 | 926.4 | 862.6 | 1004.8 | 1011.4 | 1016.5 | 935.7 | 1069.4 | 942 | 931.7 | 922.9 | 935.5 | 931.4 | 110.4 | 108.1 | 123.3 | 106.7 | 123.7 | 121.8 | 123.5 | 115.7 | 107.8 | 121.9 | 105.8 | 113.9 | 111.2 | 114.9 | 122.6 | 115.8 | 120.9 | 108.2 | 105.8 | 107.4 | 124.9 | 106.4 | 117.8 | 123.8 | 110.4 | 119.5 | 116.7 | 118.1 | 113.6 | 112.1 | 113 | 116.9 | 994 | 967 | 921.8 | 1012.2 | 1004.6 | 1011.8 | 847.6 | 1030.6 |  |  | 916.6 | 686.4 | 1001 |  | 976 | 1009.8 | 1009.8 | 980.6 | 1007.3 | 1009.3 | 1027.7 | 1021.5 | 1025.4 | 1042.3 | 1017.6 | 1029.3 | 1148.3 | 1171.9 | 936.8 | 912.2 | 786.1 | 663.4 | 670.5 | 791.7 | 953.2 | 1022.7 | 961.3 | 943.1 | 964.5 | 991.5 | 1019.2 | 955.6 | 855.4 | 907 | 807.7 | 865.3 | 768.4 |  | 1300.2 | 1014.2 | 385.1 | 938.4 | 910.4 |  |  | 1033 | 1052.4 | 885 | 910.9 | 788 | 35.73 | 41.95 | 2.07 | 9.69 |  | 5.38 | 4.87 |  |  | 85720663.674 | 282584.146 | 58721000.481 | 62233.788 | 86435802.361 | 187649.327 | 62755226.617 | 56462.898 | 324739366.519 | 85883.364 | 67121.8 | 63.118 | 64637.307 | 59.749 | 34305.575 | 41.571 | 50816.062 | 69.757 | 216832.746 | 161.849 | 131636.24 | 216670.897 | 13.1667 | 5.38 | 4.87 | 35.73 | 41.95 | 2.07 | 9.69 | 218430.9
2025-05-30 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:12 | 18:13 | 1194.2 | 1189.9 | 1157.9 | 1113.5 | 1171.6 | 1111 | 1108.3 | 1111.7 | 1149 | 1159.6 | 1130.2 | 1124.7 | 1109.3 | 1041.8 | 1106.8 | 1101.8 | 1085.4 | 1100.2 | 1168.3 | 1190.8 | 1111.3 | 1110.7 | 1213.8 | 1246 | 1208.8 | 1199.1 | 1199.1 | 1230.5 | 1231.9 | 1253 | 1259.5 | 1238.1 | 1030.5 | 1360.7 | 1085.3 | 1231.9 | 1123.4 | 1095.4 | 1112.1 | 1129.8 | 1108.5 | 1096.9 | 1114.9 | 1094.4 | 1113 | 1111.4 | 1209.7 | 1140.6 | 1140.6 | 1121.2 | 1089.7 | 1104.7 | 1269.7 | 1249.8 | 1188.7 | 1255.2 | 1252.4 | 1118.3 | 1240.6 | 1208.6 | 1126.1 | 1268.8 | 1104.5 | 1075.2 | 1196.8 | 1189.7 | 1205.4 | 1176.6 | 1096.5 | 1094.1 | 1101.6 | 1098.1 | 1120 | 1101.1 | 1267.2 | 1241.2 | 1265.7 | 1114.2 | 1092.6 | 1182.6 | 1113.4 | 1114.5 | 1096.1 | 1111.4 | 1110.2 | 1104.8 | 1113.2 | 1102.5 | 1096.6 | 1085.7 | 1142.7 | 1185.5 | 1124.1 | 1115.5 | 1241.1 | 1087 | 1092.1 | 1112.3 | 1103.7 | 1104.4 | 1136.2 | 1107.4 | 1131 | 1110.5 | 1271.3 | 1118 | 1314.2 | 1232 | 1117.5 | 1229.7 | 1202.8 | 1188.5 | 1250.8 | 1243.9 | 1107.1 | 1081.6 | 1227.8 | 1246.4 | 1239.2 | 1116 | 1128.6 | 1243.5 | 1289.5 | 1113.2 | 1121.2 | 1266.7 | 1081.1 | 1078.4 | 1258.8 | 1243.6 | 1175.8 | 1203.8 | 1192.5 | 1022.5 | 1254.9 | 1164.1 | 1210.3 | 1173.3 | 1177.5 | 1116.6 | 1176.7 | 1172.2 | 1116.9 | 1213.6 | 1079.9 | 1167.9 | 1105.6 | 1030.3 | 1195.4 | 1208.8 | 1216.7 | 1118.5 | 1283.5 | 1127.6 | 1110.7 | 1097.2 | 1101.5 | 1087.9 | 1071.2 | 1079.6 | 1211.1 | 1064.5 | 1215.8 | 1201.2 | 1195.8 | 1121.5 | 1071.7 | 1203.4 | 1064.5 | 1111.5 | 1108.2 | 1121.5 | 1207.9 | 1169.1 | 1216.5 | 1063.8 | 1069.1 | 1075.5 | 1213.5 | 1078.8 | 1179.5 | 1201.2 | 1197.5 | 1121.7 | 1154.5 | 1220.5 | 1111.8 | 1119.7 | 1108.5 | 1159.4 | 1095.8 | 1079 | 1080.5 | 1111.9 | 1105.5 | 1114 | 931.4 | 1134 |  |  | 1008.2 | 792.1 | 1104.8 |  | 1203.1 | 1069.2 | 1112.5 | 1081.1 | 1107 | 1108.6 | 1127 | 1121.4 | 1124.1 | 1143.6 | 1117 | 1128.8 | 1256.4 | 1279.8 | 1025 | 996.6 | 860 | 724.1 | 845.3 | 981.7 | 1149 | 1243.1 | 1173.1 | 1247 | 1151.4 | 1174.9 | 1234.5 | 1251.5 | 1091.4 | 1134.6 | 1082.7 | 1087.8 | 1027.8 |  | 1475.5 | 1190.6 | 437.5 | 1078.3 | 1050.8 |  |  | 1081 | 1121.7 | 1101.3 | 1043.6 | 997 | 36.45 | 45.55 | 2.33 | 7.9 |  | 5.85 | 5.34 |  |  | 85794428.611 | 282650.264 | 58791589.399 | 62295.537 | 86508783.115 | 187691.898 | 62812737.713 | 56533.655 | 325014163.677 | 86045.213 | 73764.937 | 66.118 | 70588.918 | 61.749 | 72980.754 | 42.571 | 57511.096 | 70.757 | 274797.158 | 161.849 | 144225.988 | 274635.309 | 13.0167 | 5.85 | 5.34 | 36.45 | 45.55 | 2.33 | 7.9 | 277904.9
2025-05-31 | 2026 | 2025 |  |  | May-25 | 31 | 66750 | 5:13 | 18:24 | 1073.4 | 1003 | 1002 | 1000.6 | 1001 | 995.6 | 997.5 | 998.1 | 1031.4 | 1039.6 | 1014.1 | 1009.4 | 995.1 | 937 | 994.4 | 991.1 | 997 | 989.2 | 1068 | 1071.4 | 1008 | 1023.09 | 1098.8 | 1141 | 1099 | 1081.4 | 1071 | 1109.5 | 1129.5 | 1107.8 | 1121.8 | 1117.4 | 944.8 | 1234.4 | 988.6 | 1107.8 | 1006.4 | 980.7 | 995.9 | 1014.1 | 990.1 | 985.8 | 989.8 | 975.5 | 1010.2 | 989.2 | 1096.6 | 993.7 | 1039.9 | 1032.6 | 908.9 | 1010.6 | 1161.2 | 1144.4 | 1070.1 | 1128.3 | 1127.2 | 1003.1 | 1113 | 1009.4 | 1008.3 | 1135.5 | 1005.4 | 961.7 | 1084.1 | 1076.4 | 1092.9 | 1063.1 | 991.9 | 992.7 | 998.8 | 994.3 | 1017.1 | 995.9 | 1157.9 | 1134 | 1156.1 | 1015 | 994.1 | 1062.9 | 1010.3 | 1012.9 | 992.1 | 1008.1 | 1009.6 | 1014.7 | 1010.2 | 998.9 | 992.2 | 981.9 | 1033.4 | 1065.2 | 1018.3 | 1012 | 1123.7 | 985.8 | 992 | 1009.9 | 1001.8 | 1003.3 | 1032.2 | 1005 | 1028.2 | 1007.6 | 1158.2 | 1012.1 | 1119.5 | 1118.1 | 1013.2 | 1103.3 | 1087.1 | 1072.7 | 1114.9 | 1125.3 | 1004.2 | 997.5 | 1112.8 | 1123.3 | 1120.6 | 1006 | 1020.2 | 1113.2 | 1124.1 | 1006.2 | 1014.4 | 1144.9 | 998.9 | 987.1 | 1139.9 | 1120.6 | 1076 | 1084.2 | 1074.2 | 921.2 | 1059.4 | 1050.6 | 1090.4 | 1100.5 | 1060.5 | 1007.2 | 1059.6 | 1060.7 | 1007.3 | 1095.8 | 973.4 | 1035.3 | 1000.5 | 932.8 | 1081.3 | 1093.6 | 1102.5 | 1013 | 1164.3 | 1022.3 | 1006.1 | 994 | 1005.5 | 998 | 989.5 | 980.9 | 1121.2 | 972.6 | 1119.5 | 1125.5 | 1120.1 | 1035.5 | 981.5 | 1118.4 | 991.5 | 1031.5 | 1036.9 | 1034.8 | 1124.5 | 1031.8 | 1021.5 | 992.6 | 989.5 | 981.5 | 1129.6 | 987.5 | 1084.2 | 1116.2 | 1123.1 | 1029.5 | 1081.6 | 1013.8 | 1029.5 | 988.8 | 1026.4 | 1079.5 | 984.9 | 981.2 | 991.5 | 1002.4 | 998.6 | 1001.8 | 840.9 | 1021.7 |  |  | 906.5 | 710.5 | 991.9 |  | 1084.2 | 980.7 | 1011.3 | 980.2 | 1002.9 | 1007.3 | 1023.3 | 1018.9 | 1022.7 | 1033.6 | 1014 | 1024 | 1143 | 1163.8 | 924 | 899 | 774.3 | 656.1 | 769.2 | 879.3 | 1034.5 | 1109.7 | 1066.6 | 1122 | 1031.5 | 1061.4 | 1104.2 | 1112.6 | 950 | 1020.9 | 941.5 | 991 | 926 |  | 1330 | 1067.7 | 414.1 | 995.4 | 938.8 |  |  | 1024.6 | 1040.2 | 1053.7 | 946.8 | 901 | 33.5 | 42 | 3.1 | 8.3 |  | 5.3 | 4.85 |  |  | 85860885.701 | 282715.293 | 58855621.315 | 62358.83 | 86575069.974 | 187741 | 62864610.12 | 56612.761 | 325261923.023 | 86205.025 | 66457.09 | 65.029 | 64031.916 | 63.293 | 66286.859 | 49.102 | 51872.407 | 79.106 | 247759.346 | 159.812 | 130360.684 | 247599.534 | 13.1833 | 5.3 | 4.85 | 33.5 | 42 | 3.1 | 8.3 | 251303.79
2025-06-01 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:14 | 18:33 | 985.3 | 995.1 | 908.1 | 920.9 | 994.5 | 918.2 | 921.1 | 912.5 | 954.2 | 959.4 | 938.8 | 934.2 | 917.9 | 862.9 | 917.1 | 921.5 | 873.6 | 910 | 987.9 | 990.7 | 920.6 | 920.2 | 1007.6 | 1036 | 1006.9 | 997.3 | 988.7 | 1021.7 | 1040.6 | 1023.5 | 1031.7 | 1030.8 | 865.2 | 1139.4 | 902.2 | 1031.9 | 925.6 | 901 | 918.2 | 931.6 | 913.1 | 907.3 | 920.6 | 832.1 | 918 | 921.7 | 995.5 | 911.5 | 946.7 | 930.7 | 916.6 | 918.9 | 1050 | 1034.8 | 988.2 | 1040.1 | 1042.5 | 927.5 | 1028.5 | 1041.4 | 925.1 | 1046.4 | 918.8 | 892.2 | 987.9 | 980.6 | 996.5 | 971.1 | 905.9 | 901.1 | 909.8 | 905.8 | 927.6 | 911.9 | 1051 | 1030.4 | 1045.5 | 916.1 | 906 | 985.3 | 920 | 922.1 | 909.2 | 921.2 | 911.5 | 913.5 | 920 | 912.1 | 905.3 | 916.9 | 942.7 | 990.8 | 929.8 | 922.3 | 1023 | 900.1 | 903.5 | 915.8 | 909.4 | 908.5 | 933.4 | 908.6 | 927.8 | 910.6 | 1047.7 | 912.8 | 1090.1 | 1017.1 | 917.7 | 1014.6 | 981.8 | 983.2 | 1029 | 1024.6 | 911.3 | 915.5 | 1015 | 1017.6 | 1014.6 | 912.3 | 927 | 1019.1 | 1025.5 | 910.9 | 916.4 | 1021.5 | 901.4 | 909.9 | 1029.3 | 1018.7 | 907.2 | 989.5 | 985.7 | 843.6 | 1036 | 1041.4 | 1031.8 | 1038.5 | 973 | 926.5 | 1042 | 1036.6 | 921.2 | 1003.7 | 887.9 | 948.2 | 914 | 850.2 | 981.8 | 994.7 | 998.7 | 912.3 | 1040.7 | 915.7 | 921.6 | 911.6 | 909.6 | 917.5 | 887.5 | 891.2 | 1027.5 | 892.3 | 1031.3 | 1029.5 | 1025.6 | 919.5 | 889.5 | 1021.5 | 885.5 | 920.1 | 911.5 | 915.7 | 1030.6 | 915.4 | 1021.5 | 891.1 | 886.4 | 890.7 | 1024.4 | 888.1 | 957.6 | 1019.5 | 1028.3 | 916.4 | 966.3 | 1024.4 | 920.4 | 923.5 | 921.4 | 964.5 | 901.5 | 911.2 | 907.5 | 916.6 | 907.8 | 676.5 | 769.2 | 929 |  |  | 820.9 | 621.7 | 907.7 |  | 993.4 | 878 | 918 | 892.5 | 913.6 | 914.6 | 925.3 | 920.9 | 925.2 | 936.2 | 920.7 | 930.2 | 1037.4 | 1056.8 | 849.7 | 827.8 | 710.6 | 601.2 | 717.4 | 808.4 | 943.4 | 1017.8 | 983.7 | 962.4 | 935.5 | 989.7 | 1010.7 | 1116.3 | 860.9 | 929.5 | 869.2 | 926.7 | 868.5 |  | 1238.4 | 965.1 | 424.5 | 897.9 | 873.4 |  |  | 906.6 | 950.9 | 911.7 | 856.9 | 815.3 | 31.9 | 40.8 | 3.4 | 6.2 |  | 4.91 | 4.4 |  |  | 85922250.649 | 282756.322 | 58914133.54 | 62411.123 | 86636539.254 | 187780.102 | 62911708.9 | 56689.867 | 325491068.834 | 86361.837 | 61364.948 | 41.029 | 58512.225 | 52.293 | 61469.28 | 39.102 | 47098.78 | 77.106 | 229145.811 | 156.812 | 119783.851 | 228988.999 | 13.3167 | 4.91 | 4.4 | 31.9 | 40.8 | 3.4 | 6.2 | 229035.1
2025-06-02 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:15 | 17:56 | 1020.1 | 1026 | 984.9 | 1026 | 1098.5 | 1016.8 | 1014.6 | 932.7 | 1051.5 | 1057.3 | 1034.1 | 1030 | 1013.7 | 952.5 | 1012.5 | 1006.2 | 963.1 | 1004.7 | 1091.6 | 1092.3 | 1016.1 | 1016.4 | 1110.6 | 1144.6 | 1111.2 | 1100.8 | 1093.6 | 1130.8 | 1153.3 | 1130 | 1155.5 | 1145.5 | 1005.2 | 1154.5 | 1050.2 | 1182.9 | 1054 | 1024.5 | 1043 | 1056.2 | 1038.1 | 1030.5 | 1047.4 | 1041.2 | 1042.3 | 1049 | 1130.8 | 1035.8 | 1078.3 | 1058.6 | 1041.5 | 1044.4 | 1194.9 | 1177.3 | 1123.6 | 1199 | 1185 | 1054.3 | 1169.4 | 1185.9 | 1050.7 | 1193.2 | 1037.1 | 1021.1 | 1166.8 | 1161.2 | 1170 | 1141.6 | 1069.2 | 1067.6 | 1071.8 | 1066.7 | 1084 | 1066.3 | 1207.5 | 1187 | 1210.7 | 1066.2 | 1056.8 | 1141.7 | 1025.9 | 1076.3 | 1061.3 | 1077.6 | 1060.3 | 1062.6 | 1071.2 | 1060.6 | 1062.8 | 1052 | 1108 | 1168.09 | 1083.1 | 1075.4 | 1203 | 1055.7 | 1054.3 | 1078.3 | 1062.2 | 1070 | 1097.8 | 1065.4 | 1087.1 | 1064 | 1215.6 | 1077.7 | 1265 | 1188 | 1080.5 | 1183.4 | 1160.7 | 1140.5 | 1196.1 | 1196.7 | 1073.3 | 1027.4 | 1181.2 | 1199.9 | 1198.7 | 1077.6 | 1089.3 | 1148.2 | 1144.3 | 1073.1 | 1083.3 | 1217.5 | 903.2 | 917.7 | 1145.5 | 1132 | 1008.7 | 1097.7 | 1094.5 | 938.1 | 1155 | 1075.2 | 1114.9 | 1021.3 | 1093 | 1034.9 | 1081.6 | 1078.5 | 1028.1 | 1119.9 | 996.1 | 1061.3 | 1019.5 | 946.8 | 1092.3 | 1106.8 | 1114.3 | 1019.2 | 1167.1 | 1024.6 | 1006 | 1005 | 1010.5 | 1006.4 | 960.3 | 944.4 | 1090.2 | 951.1 | 1100.1 | 1109.1 | 1101.6 | 965.6 | 954.6 | 1111.8 | 960.6 | 969.3 | 965.6 | 967.1 | 1090.1 | 992.1 | 1109.1 | 948.8 | 957.2 | 953.3 | 1101.4 | 955.1 | 1070.7 | 1101.1 | 1111.9 | 971.2 | 1067.1 | 1107.8 | 1000.1 | 1001.1 | 1011.2 | 1069.1 | 1054.4 | 1050.3 | 1055.2 | 1068.9 | 1064.1 | 1059.9 | 900 | 1083.8 |  |  | 960.1 | 723.8 | 1060 |  | 1144.2 | 1019.3 | 1075.3 | 1071.1 | 1068.9 | 1070.8 | 1083.1 | 1079.7 | 1083.8 | 1095.4 | 1076.4 | 1086.7 | 1250.5 | 1221.7 | 980 | 955.8 | 823.3 | 694.4 | 841.2 | 961.5 | 1119.3 | 1191.7 | 1122 | 1121.1 | 1105.5 | 1134.5 | 1171.7 | 1182.8 | 1008.4 | 1100.7 | 996 | 1052.3 | 985.5 |  | 1400.5 | 1097.4 | 484.3 | 1021.1 | 991.1 |  |  | 1079.8 | 1091.7 | 1090.1 | 1018.9 | 912.1 | 32.2 | 41.3 | 3.2 | 4.8 |  | 5.82 | 5.25 |  |  | 85990477.919 | 282794.351 | 58982150.982 | 62461.416 | 86703331.58 | 187817.204 | 62966455.413 | 56765.973 | 325748697.178 | 86518.649 | 68227.27 | 38.029 | 68017.442 | 50.293 | 66792.326 | 37.102 | 54746.513 | 76.106 | 257628.344 | 156.812 | 136156.39 | 257471.532 | 12.6833 | 5.82 | 5.25 | 32.2 | 41.3 | 3.2 | 4.8 | 259288.99
2025-06-03 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:19 | 18:33 | 891.8 | 902.2 | 825.3 | 977.8 | 1052.6 | 976.4 | 976.5 | 924.2 | 1010.1 | 1016.3 | 992.7 | 988.2 | 971.4 | 912.8 | 971.3 | 966.6 | 922.9 | 961.3 | 1039.7 | 1043.5 | 972.5 | 973.6 | 1066.8 | 1095.1 | 1060.1 | 1051.7 | 1044.5 | 1082.6 | 1094.4 | 1081.4 | 1101.5 | 1105.5 | 726.3 | 831.2 | 853.5 | 959 | 857.9 | 837.3 | 853.8 | 866.4 | 846.6 | 840 | 857.6 | 860.5 | 855.5 | 860.8 | 928.3 | 834.5 | 885.5 | 870.1 | 857.7 | 867.8 | 980.4 | 966.6 | 922.2 | 975.7 | 972.3 | 866 | 956.7 | 967.3 | 859.7 | 971.7 | 852.2 | 835 | 1061.7 | 1056.6 | 1064.3 | 1040.5 | 980.5 | 980.3 | 991.2 | 986.2 | 1007.6 | 978.7 | 1105.3 | 1084.2 | 1115.9 | 986.6 | 980 | 1042.7 | 955.1 | 999.2 | 987.7 | 1002.3 | 990.2 | 993.4 | 999.2 | 991.7 | 984.96 | 975.3 | 1012 | 1045.5 | 1004.8 | 1001.3 | 1099.2 | 995.5 | 980.2 | 996.8 | 982.6 | 989.5 | 1013.3 | 987.1 | 1003.1 | 983.8 | 1110.4 | 994.9 | 1148.6 | 1087.8 | 996 | 1074.9 | 1065.3 | 982.9 | 1088.9 | 1098.9 | 993.4 | 934.5 | 1077.8 | 1094.1 | 1093.9 | 993.4 | 1000.1 | 1045.6 | 1030.3 | 990.8 | 1001.1 | 1112 | 812.2 | 817.2 | 918.6 | 905.9 | 839.4 | 875.6 | 870.9 | 749 | 917.6 | 857.1 | 887.7 | 810.5 | 863.1 | 820 | 862 | 762.7 | 816.9 | 889.6 | 784.4 | 872.9 | 810.1 | 673 | 871.6 | 881.4 | 887.9 | 814.6 | 930.1 | 818.4 | 836 | 814.6 | 820.5 | 821.4 | 935.5 | 929.5 | 1035.5 | 933.4 | 1031.5 | 1039.4 | 1021.5 | 975.8 | 940.5 | 1045.5 | 920.2 | 970.5 | 974.5 | 971.4 | 1034.4 | 969.1 | 1044.5 | 931.9 | 939.4 | 945.1 | 1047.5 | 933.5 | 999.5 | 1041.5 | 1037.1 | 1020.4 | 987.1 | 1045 | 965.5 | 983.7 | 971.5 | 999 | 953.3 | 940.2 | 820 | 965.4 | 962.9 | 841.5 | 816 | 979.2 |  |  | 856.3 | 662.3 | 960.4 |  | 1038.7 | 932.7 | 989.5 | 928.4 | 985.9 | 987.4 | 999 | 996.7 | 999.8 | 998.7 | 994.9 | 1000 | 1103.8 | 1122.4 | 882.4 | 866.4 | 744.8 | 625.1 | 724.2 | 849.5 | 1014.7 | 1082.8 | 1027.1 | 1005.2 | 1021.5 | 1045.5 | 1076.1 | 1021.1 | 869.4 | 977.9 | 867.1 | 931.6 | 838.4 |  | 1270.2 | 976.5 | 401.1 | 918.1 | 883 |  |  | 1002.9 | 994.3 | 980.6 | 881.8 | 831.2 | 32.1 | 40.8 | 2.8 | 7.1 |  | 5.12 | 4.62 |  |  | 86050319.559 | 282835.659 | 59044847.468 | 62500.709 | 86761490.088 | 187849.235 | 63016997.599 | 56840.709 | 325979691.535 | 86675.461 | 59841.64 | 41.308 | 62696.486 | 39.293 | 58158.508 | 32.031 | 50542.186 | 74.736 | 230994.357 | 156.812 | 122457.525 | 230837.545 | 13.2333 | 5.12 | 4.62 | 32.1 | 40.8 | 2.8 | 7.1 | 231929.06
2025-06-04 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:10 | 18:33 | 1193.4 | 1204.8 | 1072 | 1113.2 | 1198.9 | 1113.2 | 1115.2 | 1066.5 | 1157.3 | 1160.4 | 1138.8 | 1135.5 | 1116 | 1053.6 | 1116 | 1112.8 | 1067.3 | 1095.5 | 1198.3 | 1197.9 | 1113.6 | 1074.4 | 1226.6 | 1260.3 | 1210.6 | 1203.9 | 1194.6 | 1234.3 | 1256.6 | 1229.4 | 1245.5 | 1239.5 | 1031.4 | 1290.7 | 1061.2 | 1208.4 | 1084.5 | 1066.1 | 1076 | 1096.3 | 1064.4 | 1063.1 | 1079.5 | 1071.1 | 1077.5 | 1085.6 | 1172.5 | 1071.1 | 1114 | 1115.1 | 1082.2 | 1069.9 | 1240.8 | 1220.7 | 1166.7 | 1230.2 | 1233.4 | 1100 | 1219.7 | 1236.5 | 1087.7 | 1231.4 | 1069.1 | 993.2 | 1191.5 | 1183.1 | 1198.7 | 1168.5 | 1094.1 | 1086.1 | 1096 | 1092.4 | 1114.9 | 1098.5 | 1252.1 | 1230.4 | 1250.9 | 1099.5 | 1087.2 | 1197.9 | 1071.1 | 1107.7 | 1096.4 | 1110.6 | 1096 | 1098.2 | 1107.1 | 1098.3 | 1087.1 | 1075.5 | 1136.7 | 1214.5 | 1121.4 | 1109.2 | 1231.9 | 1078.5 | 1078.4 | 1108.4 | 1087.9 | 1096.2 | 1126.5 | 1091.4 | 1110.3 | 1079.5 | 1247.2 | 1107.8 | 1311.7 | 1224.1 | 1110.1 | 1230.8 | 1197.5 | 1178.4 | 1244.1 | 1238.1 | 1100.7 | 1100.5 | 1221 | 1246.9 | 1238 | 1106.3 | 1120.9 | 1244.2 | 1241.5 | 1104.9 | 1112.5 | 1261.6 | 1082.2 | 1088.8 | 1233.7 | 1215.1 | 1133.1 | 1177.1 | 1171.6 | 1003.8 | 1235.5 | 1147 | 1188.4 | 1109.1 | 1162.2 | 1099.4 | 1157.3 | 1153.7 | 1090.9 | 1193.1 | 1063.8 | 1211.5 | 1084.1 | 1008.7 | 1172.9 | 1184.6 | 1195.5 | 1094.9 | 1254.8 | 1099.7 | 1079.5 | 1069.7 | 1078.5 | 1037.5 | 1064.5 | 1069.5 | 1201.2 | 1071.5 | 1188.1 | 1181.5 | 1193.1 | 1109.2 | 1074.5 | 1189.3 | 1077.5 | 1111.8 | 1107.5 | 1109.4 | 1181.6 | 1109.5 | 1185.2 | 1079.5 | 1074.6 | 1081.6 | 1189.9 | 1069.5 | 1149.5 | 1188.2 | 1196.2 | 1104.5 | 1145.8 | 1191.2 | 1104.6 | 1109.4 | 1111.9 | 1141.4 | 1075.5 | 1083.2 | 1078.1 | 1090.3 | 1088.5 | 1094.4 | 920.9 | 1115 |  |  | 981.8 | 781.1 | 1094.5 |  | 1180.4 | 1071.2 | 1101.9 | 977.2 | 1089 | 1097.7 | 1105.4 | 1104.2 | 1107 | 1125.2 | 1104.8 | 1109.8 | 1240.7 | 1263.4 | 1020.7 | 989.4 | 850.9 | 717.9 | 852.1 | 981.2 | 1132.9 | 1216.6 | 1165.6 | 1169.2 | 1142.5 | 1174.5 | 1208.1 | 1201 | 1055.6 | 1123.2 | 1032.1 | 1071.2 | 1001.2 |  | 1455.5 | 1168 | 447.2 | 1079.2 | 1032.1 |  |  | 1123.2 | 1140.1 | 1140.1 | 1044.3 | 984.2 | 36.4 | 48 | 3.1 | 6.3 |  | 5.74 | 5.18 |  |  | 86122985.268 | 282856.967 | 59115455.755 | 62524.002 | 86834246.849 | 187871.266 | 63073854.344 | 56919.445 | 326252327.595 | 86832.273 | 72665.709 | 21.308 | 70608.287 | 23.293 | 72756.761 | 22.031 | 56856.745 | 78.736 | 272636.06 | 156.812 | 143229.395 | 272479.248 | 13.3833 | 5.74 | 5.18 | 36.4 | 48 | 3.1 | 6.3 | 273632.5
2025-06-05 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:06 | 18:36 | 1276 | 1349 | 1245 | 1245 | 1343 | 1247 | 1253 | 1228 | 1294 | 1299 | 1278 | 1272 | 1250 | 1176 | 1252 | 1244 | 1191 | 1236 | 1352 | 1351 | 1254 | 1205 | 1320 | 1416 | 1367 | 1355 | 1346 | 1391 | 1413 | 1382 | 1254 | 1289 | 1213 | 1449 | 1212 | 1422 | 1247 | 1240 | 1257 | 1278 | 1254 | 1244 | 1261 | 1138 | 1259 | 1271 | 1368 | 1197 | 1303 | 1281 | 1261 | 1213 | 1446 | 1427 | 1358 | 1432 | 1438 | 1280 | 1420 | 1440 | 1213 | 1367 | 1254 | 958 | 1421 | 1395 | 1433 | 1311 | 1311 | 1298 | 1318 | 1316 | 1338 | 1309 | 1500 | 1465 | 1493 | 1278 | 1253 | 1397 | 1319 | 1314 | 1304 | 1380 | 1313 | 1301 | 1328 | 1319 | 1315 | 1308 | 1359 | 1347 | 1348 | 1341 | 1325 | 1157 | 1286 | 1317 | 1298 | 1305 | 1340 | 1303 | 1325 | 1293 | 1474 | 1321 | 1538 | 1445 | 1318 | 1441 | 1422 | 1298 | 1457 | 1465 | 1310 | 1190 | 1438 | 1478 | 1469 | 1316 | 1328 | 1400 | 1376 | 1312 | 1324 | 1253 | 1105 | 1124 | 1401 | 1383 | 1285 | 1340 | 1334 | 1142 | 1402 | 1289 | 1337 | 1221 | 1307 | 1248 | 1319 | 1301 | 1241 | 1357 | 1207 | 1332 | 1238 | 1153 | 1337 | 1352 | 1362 | 1249 | 1430 | 1255 | 1232 | 1221 | 1254 | 1223 | 1310 | 1270 | 1458 | 1264 | 1437 | 1411 | 1449 | 1350 | 1243 | 1428 | 1303 | 1302 | 1325 | 1358 | 1418 | 1328 | 1416 | 1292 | 1306 | 1273 | 1439 | 1325 | 1398 | 1412 | 1475 | 1365 | 1415 | 1425 | 1365 | 1365 | 1319 | 1412 | 1266 | 1277 | 1248 | 1280 | 1270 | 1283 | 1066 | 1300 |  |  | 1131 | 898 | 1264 |  | 1353 | 1298 | 1320 | 1283 | 1310 | 1307 | 1326 | 1325 | 1326 | 1334 | 1318 | 1319 | 1468 | 1495 | 1190 | 1161 | 903 | 825 | 965 | 1132 | 1360 | 1457 | 1404 | 1362 | 1294 | 1377 | 1447 | 1392 | 1230 | 1297 | 1198 | 1298 | 1210 |  | 1698 | 1357 | 488 | 1298 | 1359 |  |  | 1341 | 1184 | 1310 | 1198 | 1122 | 36.8 | 52.03 | 3.2 | 8.3 |  | 6.7 | 6.3 |  |  | 86205731.344 | 282896.231 | 59198310.589 | 62568.023 | 86917129.675 | 187898.132 | 63141168.652 | 56991.445 | 326567840.292 | 86987.148 | 82746.076 | 39.264 | 82854.834 | 44.021 | 82882.826 | 26.866 | 67314.308 | 72 | 315512.697 | 154.875 | 165517.625 | 315357.822 | 13.5 | 6.7 | 6.3 | 36.8 | 52.03 | 3.2 | 8.3 | 317965
2025-06-06 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:09 | 18:36 | 1375 | 1406 | 1249 | 1299 | 1395 | 1296 | 1296 | 1191 | 1344 | 1351 | 1318 | 1312 | 1292 | 1216 | 1292 | 1287 | 1228 | 1277 | 1388 | 1388 | 1291 | 1242 | 1365 | 1458 | 1404 | 1391 | 1383 | 1433 | 1452 | 1428 | 1270 | 1332 | 1232 | 1578 | 1231 | 1446 | 1294 | 1263 | 1282 | 1301 | 1278 | 1269 | 1286 | 1154 | 1281 | 1293 | 1390 | 1220 | 1279 | 1262 | 1290 | 1236 | 1472 | 1450 | 1384 | 1465 | 1463 | 1300 | 1441 | 1457 | 1297 | 1461 | 1268 | 968 | 1398 | 1387 | 1389 | 1278 | 1287 | 1250 | 1265 | 1289 | 1290 | 1290 | 1423 | 1387 | 1403 | 1250 | 1207 | 1308 | 1209 | 1278 | 1289 | 1209 | 1267 | 1290 | 1265 | 1293 | 1245 | 1246 | 1301 | 1296 | 1291 | 1295 | 1308 | 1152 | 1250 | 1295 | 1280 | 1285 | 1320 | 1283 | 1309 | 1281 | 1471 | 1301 | 1538 | 1438 | 1300 | 1421 | 1407 | 1376 | 1440 | 1450 | 1285 | 1164 | 1433 | 1462 | 1456 | 1299 | 1312 | 1400 | 1359 | 1295 | 1305 | 1298 | 1149 | 1168 | 1456 | 1437 | 1336 | 1395 | 1389 | 1189 | 1465 | 1355 | 1406 | 1287 | 1376 | 1311 | 1374 | 1354 | 1304 | 1419 | 1269 | 1438 | 1291 | 1198 | 1392 | 1407 | 1416 | 1299 | 1489 | 1305 | 1282 | 1269 | 1300 | 1275 | 1298 | 1239 | 1443 | 1257 | 1429 | 1401 | 1412 | 1348 | 1221 | 1413 | 1278 | 1290 | 1302 | 1340 | 1398 | 1302 | 1421 | 1278 | 1301 | 1257 | 1401 | 1313 | 1378 | 1401 | 1460 | 1368 | 1402 | 1411 | 1378 | 1360 | 1311 | 1419 | 1285 | 1256 | 1241 | 1267 | 1269 | 1278 | 1082 | 1298 |  |  | 1151 | 912 | 1284 |  | 1395 | 1303 | 1301 | 1272 | 1289 | 1295 | 1303 | 1300 | 1303 | 1321 | 1301 | 1303 | 1456 | 1485 | 1192 | 1164 | 978 | 780 | 978 | 1152 | 1339 | 1444 | 1379 | 1389 | 1310 | 1391 | 1434 | 1398 | 1247 | 1310 | 1228 | 1289 | 1191 |  | 1678 | 1398 | 481 | 1287 | 1212 |  |  | 1173 | 1210 | 1270 | 1178 | 1108 | 30.8 | 50.3 | 31.1 | 8.5 |  | 6.6 | 6.32 |  |  | 86290534.396 | 282928.059 | 59280165.923 | 62601.116 | 87002384.052 | 187939.878 | 63207771.983 | 57066.456 | 326886109.748 | 87143.419 | 84803.052 | 31.828 | 81855.334 | 33.093 | 85254.377 | 41.746 | 66603.331 | 75.011 | 318269.456 | 156.271 | 166593.465 | 318113.185 | 13.45 | 6.6 | 6.32 | 30.8 | 50.3 | 31.1 | 8.5 | 319248
2025-06-07 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:07 | 18:36 | 1464 | 1500 | 1332 | 1388 | 1487 | 1381 | 1381 | 1275 | 1428 | 1435 | 1405 | 1396 | 1377 | 1296 | 1374 | 1370 | 1308 | 1361 | 1475 | 1480 | 1379 | 1323 | 1459 | 1556 | 1501 | 1484 | 1477 | 1532 | 1546 | 1526 | 1310 | 1424 | 1363 | 1678 | 1307 | 1533 | 1372 | 1343 | 1363 | 1388 | 1363 | 1348 | 1371 | 1243 | 1374 | 1382 | 1489 | 1306 | 1359 | 1343 | 1373 | 1316 | 1571 | 1548 | 1470 | 1562 | 1557 | 1383 | 1532 | 1549 | 1380 | 1552 | 1363 | 1100 | 1455 | 1435 | 1442 | 1369 | 1327 | 1324 | 1331 | 1325 | 1338 | 1328 | 1500 | 1475 | 1490 | 1328 | 1289 | 1397 | 1319 | 1378 | 1352 | 1308 | 1345 | 1342 | 1328 | 1344 | 1332 | 1329 | 1385 | 1463 | 1348 | 1341 | 1410 | 1240 | 1353 | 1381 | 1365 | 1371 | 1407 | 1369 | 1392 | 1360 | 1561 | 1382 | 1609 | 1531 | 1388 | 1502 | 1502 | 1445 | 1506 | 1544 | 1378 | 1250 | 1524 | 1549 | 1539 | 1384 | 1402 | 1502 | 1458 | 1381 | 1390 | 1385 | 1221 | 1240 | 1549 | 1527 | 1417 | 1479 | 1477 | 1267 | 1548 | 1444 | 1497 | 1369 | 1449 | 1374 | 1458 | 1423 | 1385 | 1501 | 1341 | 1467 | 1360 | 1266 | 1476 | 1489 | 1501 | 1376 | 1572 | 1383 | 1363 | 1350 | 1390 | 1357 | 1378 | 1322 | 1578 | 1363 | 1588 | 1563 | 1510 | 1498 | 1363 | 1563 | 1478 | 1410 | 1408 | 1478 | 1510 | 1398 | 1508 | 1398 | 1408 | 1363 | 1563 | 1410 | 1478 | 1498 | 1563 | 1463 | 1502 | 1503 | 1498 | 1478 | 1498 | 1510 | 1360 | 1350 | 1334 | 1368 | 1365 | 1371 | 1159 | 1399 |  |  | 1229 | 998 | 1365 |  | 1487 | 1385 | 1381 | 1342 | 1374 | 1387 | 1390 | 1388 | 1391 | 1406 | 1393 | 1400 | 1560 | 1591 | 1272 | 1245 | 998 | 1010 | 1068 | 1342 | 1420 | 1506 | 1445 | 1455 | 1391 | 1480 | 1520 | 1503 | 1300 | 1394 | 1319 | 1392 | 1298 |  | 1785 | 1487 | 520 | 1332 | 1297 |  |  | 1198 | 1305 | 1364 | 1261 | 1219 | 31.9 | 52.8 | 3.9 | 6.4 |  | 6.98 | 6.78 |  |  | 86380975.695 | 282973 | 59366988.104 | 62645 | 87093065.921 | 187994.148 | 63278498.708 | 57141 | 327224555.014 | 87299.1 | 90441.299 | 44.941 | 86822.181 | 43.884 | 90681.869 | 54.27 | 70726.725 | 74.544 | 338445.266 | 155.681 | 177174.655 | 338289.585 | 13.4833 | 6.98 | 6.78 | 31.9 | 52.8 | 3.9 | 6.4 | 340883
2025-06-08 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:08 | 18:36 | 1418.2 | 1451 | 1308.4 | 1342.1 | 1441.1 | 1338.1 | 1338.8 | 1342 | 1384.4 | 1392 | 1308.9 | 1357 | 1335.3 | 1257.1 | 1336.3 | 1330 | 1298.4 | 1323.7 | 1439.1 | 1439.6 | 1341 | 1311.1 | 1412.6 | 1508.9 | 1460 | 1442.4 | 1435.8 | 1486.6 | 1505.9 | 1481.3 | 1405.2 | 1441.5 | 1271.2 | 1634.2 | 1301.3 | 1493.2 | 1337.8 | 1305.9 | 1333.9 | 1349.1 | 1323.8 | 1312.2 | 1337.6 | 1325.8 | 1345.6 | 1348.7 | 1456 | 1329.6 | 1379.8 | 1356.8 | 1344 | 1344.6 | 1539.3 | 1516.9 | 1429.2 | 1513.5 | 1511.3 | 1345 | 1491.96 | 1509.9 | 1342.5 | 1513.8 | 1283.6 | 1293.7 | 1442.2 | 1433.2 | 1453.7 | 1412.2 | 1322.3 | 1331.2 | 1338.9 | 1333 | 1363.5 | 1319.8 | 1522.5 | 1490.1 | 1517 | 1337.1 | 1321.1 | 1424.8 | 1341.1 | 1346.6 | 1329.6 | 1348.2 | 1343.2 | 1346.2 | 1349.8 | 1257 | 1327.3 | 1311.6 | 1374.5 | 1412.4 | 1367.6 | 1368.6 | 1493.5 | 1261.2 | 1314.2 | 1341.4 | 1324.6 | 1330.4 | 1364.8 | 1328.4 | 1352.7 | 1321.5 | 1519.2 | 1342.7 | 1577.8 | 1480.4 | 1346.1 | 1465.4 | 1450.2 | 1403.8 | 1472.4 | 1499.6 | 1338.1 | 1269.9 | 1484.9 | 1506.4 | 1497.7 | 1343.9 | 1358.4 | 1491.5 | 1498.5 | 1338.7 | 1347.4 | 1501.5 | 1194.7 | 1215.4 | 1511.7 | 1489.6 | 1401 | 1441.2 | 1436.8 | 1232.9 | 1516 | 1411.4 | 1458.2 | 1343.1 | 1416.6 | 1344.2 | 1421.1 | 1401 | 1351.1 | 1463.4 | 1311.5 | 1431.3 | 1327.7 | 1234.4 | 1435.8 | 1448.3 | 1462.5 | 1341.8 | 1531.5 | 1345.4 | 1325.2 | 1312.9 | 1324.5 | 1335.4 | 1311.1 | 1315.4 | 1484.4 | 1312.5 | 1487.1 | 1467.5 | 1481.5 | 1501.1 | 1311.5 | 1477 | 1321.5 | 1345.5 | 1349.4 | 1389.4 | 1443.4 | 1341.5 | 1488.4 | 1321.5 | 1319.4 | 1315.9 | 1481.4 | 1324.5 | 1424.8 | 1488.4 | 1496.4 | 1405.5 | 1441.1 | 1496.4 | 1349.5 | 1339.2 | 1342.5 | 1398.4 | 1322.1 | 1318.9 | 1216.23 | 1311.4 | 1323.7 | 1225.4 | 1129.5 | 1356.4 |  |  | 1193.3 | 929.4 | 1328.5 |  | 1467.5 | 1296.5 | 1341.2 | 1314.4 | 1334.6 | 1338.4 | 1349.1 | 1346.6 | 1348.6 | 1365.3 | 1359 | 1363.6 | 1516.2 | 1551 | 1230.1 | 1173.4 | 1006 | 866.2 | 1009.1 | 1171.4 | 1382.1 | 1485.1 | 1413.1 | 1411.1 | 1401.1 | 1434.5 | 1478.1 | 1511.1 | 1298.4 | 1411.1 | 1321.4 | 1375.4 | 1255.4 |  | 1799.4 | 1401 | 495.1 | 1296.4 | 1265.4 |  |  | 1208.4 | 1294.4 | 1323.7 | 1241.1 | 1215.5 | 38.8 | 45.5 | 1.23 | 6.3 |  | 6.9 | 6.38 |  |  | 86469599.092 | 283017.941 | 59451373.583 | 62688.884 | 87181638.97 | 188048.418 | 63347683.734 | 57215.544 | 327555142.666 | 87454.781 | 88623.397 | 44.941 | 84385.479 | 43.884 | 88573.049 | 54.27 | 69185.026 | 74.544 | 330587.652 | 155.681 | 172920.051 | 330431.971 | 13.4667 | 6.9 | 6.38 | 38.8 | 45.5 | 1.23 | 6.3 | 332985.59
2025-06-09 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:08 | 18:36 | 1460.9 | 1473.2 | 1324.6 | 1379.1 | 1477.2 | 1376.3 | 1356.5 | 1364.9 | 1410.8 | 1421.6 | 1383.3 | 1376.6 | 1356 | 1231 | 1354.3 | 1349.2 | 1346.2 | 1344.2 | 1460.8 | 1463.5 | 1360.3 | 1363 | 1462.4 | 1531.8 | 1484 | 1464.9 | 1458.4 | 1511 | 1531.5 | 1504.2 | 1511.1 | 1501.5 | 1283.6 | 1650.7 | 1285.4 | 1511.6 | 1354.6 | 1322.4 | 1342.2 | 1363.8 | 1355.6 | 1325.7 | 1351.1 | 1339 | 1359.8 | 1362.2 | 1472.9 | 1344.5 | 1409.8 | 1388.3 | 1367.5 | 1365.4 | 1531.2 | 1538 | 1458.8 | 1521.1 | 1532.8 | 1363.6 | 1516.6 | 1530.8 | 1361.9 | 1534.9 | 1367.4 | 1307.9 | 1478.2 | 1469 | 1489.3 | 1438 | 1337.4 | 1352.2 | 1360.1 | 1354.5 | 1361 | 1331.6 | 1542.8 | 1512 | 1539.1 | 1352.4 | 1339.1 | 1442.1 | 1357.7 | 1363.8 | 1346.5 | 1363.7 | 1361.2 | 1365.6 | 1367.2 | 1302 | 1345.6 | 1331.6 | 1398.9 | 1431.1 | 1359 | 1374.4 | 1528.4 | 1277.5 | 1331.4 | 1360.6 | 1341.2 | 1350.4 | 1356 | 1347.7 | 1355 | 1340.9 | 1547.1 | 1365.9 | 1501 | 1511.9 | 1366.8 | 1483.3 | 1476.2 | 1431.1 | 1482.6 | 1519.3 | 1356.4 | 1276.5 | 1500.3 | 1531.4 | 1524.5 | 1367.9 | 1382.1 | 1489.3 | 1494.9 | 1361.1 | 1370.5 | 1550.3 | 1317.6 | 1337 | 1529.5 | 1510.7 | 1402.7 | 1461.3 | 1456.9 | 1223 | 1454 | 1425.7 | 1483.6 | 1386.3 | 1421 | 1351 | 1442.4 | 1422.6 | 1373.4 | 1504.2 | 1352.5 | 1472.3 | 1363.7 | 1257.2 | 1460.9 | 1471.4 | 1487.5 | 1362.8 | 1527 | 1367.3 | 1345.6 | 1331.1 | 1344.7 | 1337.9 | 1333.5 | 1332.2 | 1525.5 | 1331.5 | 1531.5 | 1511.1 | 1516.1 | 1384.2 | 1328.1 | 1539.1 | 1334.5 | 1379.4 | 1391.5 | 1386.7 | 1521.8 | 1393.4 | 1501 | 1340.5 | 1323.4 | 1333.6 | 1502 | 1328.4 | 1429.4 | 1497 | 1525.8 | 1389.4 | 1437.8 | 1499 | 1389.4 | 1396.1 | 1384.7 | 1434.8 | 1346.8 | 1342 | 1313.1 | 1337 | 1346.7 | 1356.7 | 1147.1 | 1377.9 |  |  | 1218.1 | 941.5 | 1340.1 |  | 1487.1 | 1325.3 | 1366.7 | 1322.6 | 1357.3 | 1358.4 | 1370.7 | 1368.2 | 1368.5 | 1379.4 | 1379.3 | 1387 | 1543.7 | 1569.4 | 1201.1 | 1198 | 1022.5 | 843.3 | 1036.5 | 1201.1 | 1405.7 | 1508.5 | 1437.7 | 1437.4 | 1425.5 | 1455.5 | 1502.8 | 1501 | 1312.4 | 1392.2 | 1278.3 | 1345.4 | 1255 |  | 1785.5 | 1434.2 | 501 | 1323 | 1284.6 |  |  | 1250 | 1332.2 | 1355 | 1265.2 | 1189 | 40.38 | 45.99 | 2.41 | 7.7 |  | 7.2 | 6.66 |  |  | 86559923.409 | 283057.882 | 59536817.374 | 62724.768 | 87271938.549 | 188098.688 | 63418184.82 | 57284.088 | 327891536.652 | 87601.462 | 90324.317 | 39.941 | 85443.791 | 35.884 | 90299.579 | 50.27 | 70501.086 | 68.544 | 336393.986 | 146.681 | 175692.283 | 336247.305 | 13.4667 | 7.2 | 6.66 | 40.38 | 45.99 | 2.41 | 7.7 | 338140.4
2025-06-10 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:09 | 18:38 | 1556.6 | 1591.8 | 1474.2 | 1469.9 | 1582.7 | 1472.9 | 1465.7 | 1471.4 | 1519.2 | 1528.1 | 1423.1 | 1444.1 | 1466.4 | 1332.1 | 1464.9 | 1458.6 | 1455.1 | 1448.9 | 1554.9 | 1560.1 | 1462.6 | 1467.5 | 1574.1 | 1587.9 | 1578.2 | 1558.9 | 1551.1 | 1607.3 | 1626.1 | 1600.1 | 1601.1 | 1596.4 | 1366.4 | 1763.6 | 1427 | 1625.6 | 1446.7 | 1409.6 | 1435.5 | 1455.3 | 1425.7 | 1464.5 | 1459.5 | 1425 | 1454.1 | 1456.6 | 1572.7 | 1430.5 | 1498.4 | 1476.6 | 1454.9 | 1451.9 | 1663.6 | 1636.7 | 1566 | 1634.4 | 1585 | 1431.1 | 1633.3 | 1628.1 | 1449.9 | 1633.1 | 1453.4 | 1301.1 | 1576.2 | 1565.2 | 1563.2 | 1525.3 | 1418.5 | 1442 | 1449.8 | 1443.6 | 1455.2 | 1456.1 | 1630.2 | 1602 | 1633.2 | 1428.2 | 1424.7 | 1555 | 1445.6 | 1451.2 | 1433.8 | 1452 | 1448.8 | 1453.5 | 1456.9 | 1446 | 1435.1 | 1420.7 | 1477.9 | 1554.1 | 1443 | 1432.2 | 1631.3 | 1419.5 | 1415.4 | 1450.5 | 1423.3 | 1441.1 | 1401.1 | 1438.2 | 1464.1 | 1433.4 | 1596.1 | 1458.7 | 1621.2 | 1615.2 | 1465 | 1591.1 | 1580.7 | 1531.1 | 1599.1 | 1623.6 | 1454.5 | 1481.6 | 1586.3 | 1633.4 | 1617.8 | 1452.5 | 1459.2 | 1587.1 | 1591.1 | 1468.4 | 1467.9 | 1650.8 | 1417.7 | 1446.8 | 1653.5 | 1634.2 | 1577 | 1584.5 | 1551.1 | 1311.1 | 1558.1 | 1544.9 | 1557.1 | 1541.2 | 1511.1 | 1440.1 | 1563.3 | 1531.1 | 1439 | 1555.1 | 1453.1 | 1575.5 | 1438 | 1338.9 | 1558.1 | 1569.6 | 1583.9 | 1453.2 | 1616.2 | 1434.6 | 1454.2 | 1424.8 | 1425.5 | 1430.5 | 1401.1 | 1398.2 | 1621.1 | 1411.1 | 1619.1 | 1601 | 1597.4 | 1462.1 | 1415.1 | 1596.1 | 1407.6 | 1459.8 | 1462.4 | 1455.8 | 1611.2 | 1447 | 1591.2 | 1409.1 | 1415.5 | 1405.1 | 1596.5 | 1412.6 | 1534.2 | 1604 | 1594.4 | 1459.1 | 1527.1 | 1651.1 | 1455.1 | 1449.5 | 1457.4 | 1529.8 | 1436.1 | 1427.2 | 1393.2 | 1399 | 1437.2 | 1447.7 | 1176.3 | 1411.1 |  |  | 1302.6 | 1011.1 | 1434.1 |  | 1581.6 | 1411.1 | 1454.4 | 1434.1 | 1448.3 | 1451.9 | 1461.7 | 1429.1 | 1459.2 | 1450.7 | 1409.2 | 1444.5 | 1634.4 | 1623.2 | 1254.1 | 1254.1 | 1087.5 | 861.1 | 1101.1 | 1272.2 | 1526.2 | 1627 | 1557.7 | 1530.1 | 1496.1 | 1564.5 | 1623.5 | 1601.1 | 1371.8 | 1465.1 | 1378.1 | 1434.1 | 1331.1 |  | 1879.2 | 1515.1 | 541.1 | 1434.1 | 1367.8 |  |  | 1312.7 | 1403 | 1153.4 | 1376.5 | 1277.7 | 41.33 | 46.5 | 3.21 | 8.7 |  | 7.54 | 7.03 |  |  | 86656408.961 | 283097.823 | 59628020.794 | 62760.652 | 87368567.069 | 188148.958 | 63492214.783 | 57352.632 | 328249588.859 | 87748.143 | 96485.552 | 39.941 | 91203.42 | 35.884 | 96628.52 | 50.27 | 74029.963 | 68.544 | 358052.207 | 146.681 | 187613.147 | 357905.526 | 13.4833 | 7.54 | 7.03 | 41.33 | 46.5 | 3.21 | 8.7 | 359956.5
2025-06-11 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:10 | 18:37 | 1454.2 | 1488.4 | 1322.3 | 1374 | 1478.6 | 1359.1 | 1370.5 | 1361.1 | 1420.2 | 1428.9 | 1371.1 | 1351.1 | 1372 | 1288.1 | 1373 | 1367.7 | 1366.2 | 1363.5 | 1484.4 | 1487.3 | 1379.6 | 1380.6 | 1450.1 | 1531.1 | 1467.1 | 1485 | 1478.7 | 1531.7 | 1542.5 | 1536.2 | 1545.6 | 1524.2 | 1279.7 | 1678.6 | 1334.9 | 1516.1 | 1350.7 | 1326.1 | 1340.7 | 1357.8 | 1332.6 | 1317.9 | 1342 | 1330.1 | 1353.6 | 1358.6 | 1467.7 | 1337.8 | 1402.3 | 1380.2 | 1359.7 | 1357.6 | 1555.6 | 1528.1 | 1459.5 | 1519.1 | 1548 | 1361.1 | 1535 | 1521.1 | 1354.9 | 1527.8 | 1358 | 1223.1 | 1476.9 | 1468.8 | 1487.9 | 1445.8 | 1342.4 | 1345.5 | 1354.2 | 1348.7 | 1377 | 1330.1 | 1521.1 | 1520.6 | 1523.1 | 1352.7 | 1332 | 1434.1 | 1353.3 | 1358.4 | 1340.1 | 1355.7 | 1352.6 | 1357.4 | 1361.7 | 1338 | 1339.4 | 1327.7 | 1401.4 | 1431.2 | 1361.2 | 1368.8 | 1533.47 | 1330.6 | 1319.7 | 1359.3 | 1340.4 | 1368.7 | 1361.9 | 1351.9 | 1372 | 1326.8 | 1485.4 | 1375.3 | 1496.1 | 1511.1 | 1351.2 | 1497.2 | 1451.1 | 1442.2 | 1486.1 | 1543.5 | 1345.2 | 1386.5 | 1517.2 | 1551.6 | 1501 | 1355.2 | 1356.2 | 1501 | 1496.3 | 1361.2 | 1356.7 | 1541.1 | 1321 | 1352.7 | 1547.6 | 1527 | 1473 | 1477.6 | 1475.5 | 1265.7 | 1456 | 1443.9 | 1466.7 | 1458.9 | 1444.4 | 1378.8 | 1460.2 | 1438.5 | 1357.5 | 1459.1 | 1348.7 | 1469.6 | 1360.7 | 1237.2 | 1479.7 | 1453.3 | 1475.2 | 1351.2 | 1547.2 | 1353.1 | 1349.6 | 1351.2 | 1355.5 | 1339.6 | 1310.2 | 1320.5 | 1482.2 | 1311.5 | 1465.5 | 1481.1 | 1467.6 | 1367.2 | 1321.5 | 1471.5 | 1312.5 | 1387.1 | 1369.2 | 1371.2 | 1469.5 | 1366.9 | 1471.5 | 1311.5 | 1315.5 | 1309.5 | 1471.2 | 1311.5 | 1461.2 | 1485.2 | 1486.8 | 1369.1 | 1471.5 | 1481.5 | 1371.2 | 1401.2 | 1378.2 | 1471.9 | 1340.6 | 1331.5 | 1313.2 | 1332.8 | 1342.2 | 1351 | 1101.1 | 1323.2 |  |  | 1215.9 | 950.1 | 1341.8 |  | 1483.2 | 1341.2 | 1359.9 | 1335.6 | 1352.5 | 1356 | 1365.7 | 1362.9 | 1363.2 | 1378.8 | 1336.6 | 1387 | 1538.5 | 1541.2 | 1181.1 | 1131.1 | 971.2 | 823.2 | 1050.2 | 1212.1 | 1425.6 | 1533 | 1455.5 | 1429.1 | 1435.5 | 1461.5 | 1488.2 | 1487.6 | 1275.2 | 1377.5 | 1287 | 1343.1 | 1241.2 |  | 1955.1 | 1434.2 | 521.1 | 1323 | 1277.6 |  |  | 1276 | 1365.1 | 1401.2 | 1272.2 | 1234.2 | 40.35 | 47.76 | 2.22 | 5.5 |  | 7.17 | 6.59 |  |  | 86747016.976 | 283137.764 | 59713989.758 | 62796.536 | 87459071.419 | 188199.228 | 63561866.987 | 57421.176 | 328586168.023 | 87894.824 | 90608.015 | 39.941 | 85968.964 | 35.884 | 90504.35 | 50.27 | 69652.204 | 68.544 | 336579.164 | 146.681 | 176501.154 | 336432.483 | 13.45 | 7.17 | 6.59 | 40.35 | 47.76 | 2.22 | 5.5 | 338030.77
2025-06-12 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:09 | 18:35 | 1321.1 | 1352.8 | 1233.2 | 1249.8 | 1344.5 | 1252.1 | 1250.1 | 1251.1 | 1291.9 | 1298.8 | 1232 | 1231 | 1246.7 | 1134 | 1246.6 | 1242.9 | 1240.3 | 1236.6 | 1352 | 1349.9 | 1251.3 | 1212 | 1351 | 1392 | 1348 | 1352.9 | 1345.8 | 1400 | 1412 | 1392.7 | 1389.1 | 1396.4 | 1195.6 | 1515.5 | 1251.2 | 1356.8 | 1258.6 | 1222.3 | 1220.1 | 1239.3 | 1236.5 | 1214.3 | 1222.4 | 1211.5 | 1230.9 | 1235.4 | 1336 | 1220 | 1275.3 | 1257.3 | 1236.2 | 1235.6 | 1418 | 1389.1 | 1334.3 | 1408.3 | 1411.8 | 1256.2 | 1395.1 | 1391 | 1259.87 | 1376 | 1236.3 | 1106 | 1340 | 1329.9 | 1349.6 | 1314.3 | 1223.3 | 1222 | 1230.8 | 1225.2 | 1251 | 1229.2 | 1388 | 1400.3 | 1424 | 1255.5 | 1240.3 | 1324.4 | 1244 | 1235 | 1248.8 | 1243 | 1226.3 | 1230.3 | 1259.5 | 1250 | 1220.4 | 1211.1 | 1276.4 | 1355.2 | 1234 | 1229 | 1392.1 | 1247.5 | 1230.5 | 1233 | 1246.6 | 1245.5 | 1234 | 1246.3 | 1244 | 1212.3 | 1370.5 | 1256.6 | 1387 | 1380.1 | 1255.4 | 1381.1 | 1348.9 | 1323.2 | 1369.3 | 1398.2 | 1247.1 | 1251.7 | 1378.2 | 1400 | 1395.8 | 1240.1 | 1262.8 | 1378.5 | 1381.3 | 1246.6 | 1257 | 1409 | 1223 | 1229.1 | 1408.8 | 1387 | 1336.7 | 1341.9 | 1338.7 | 1149.4 | 1334 | 1316.6 | 1332 | 1332 | 1301 | 1248.7 | 1319.9 | 1323 | 1243 | 1351 | 1216.5 | 1333 | 1236.3 | 1157.8 | 1350.9 | 1367.9 | 1349 | 1254.7 | 1421.8 | 1253 | 1236.6 | 1230.1 | 1235.5 | 1239.9 | 1230.5 | 1235.5 | 1356.5 | 1231.5 | 1355.5 | 1364.5 | 1359.1 | 1275.5 | 1245.5 | 1374.5 | 1239.4 | 1279.4 | 1271.5 | 1269.5 | 1366.5 | 1281.4 | 1375.5 | 1231.5 | 1249 | 1234.4 | 1369.4 | 1236.5 | 1313.2 | 1361.5 | 1369.4 | 1279.4 | 1321.2 | 1371.5 | 1269.6 | 1268.7 | 1288.5 | 1326 | 1239.9 | 1227 | 1212 | 1244.4 | 1238.6 | 1250 | 1033 | 1223 |  |  | 1095.5 | 869.4 | 1232.2 |  | 1342.8 | 1211 | 1249.2 | 1212 | 1246.5 | 1229.1 | 1227.8 | 1238.3 | 1255.4 | 1252.7 | 1222.7 | 1252.3 | 1389.4 | 1417.1 | 1055 | 1095.7 | 901 | 755 | 945 | 1089 | 1289.8 | 1387.8 | 1315.7 | 1323 | 1301.2 | 1321.2 | 1382 | 1371 | 1212 | 1261 | 1201 | 1212 | 1121 |  | 1755 | 1342 | 476 | 1212 | 1232 |  |  | 1176 | 1256 | 1275.5 | 1165 | 1100 | 39.97 | 49.84 | 2.3 | 5.5 |  | 6.58 | 6.05 |  |  | 86829808.384 | 283177.705 | 59792684.301 | 62832.42 | 87541481.108 | 188249.498 | 63625249.37 | 57489.72 | 328893320.931 | 88041.505 | 82791.408 | 39.941 | 78694.543 | 35.884 | 82409.689 | 50.27 | 63382.383 | 68.544 | 307152.908 | 146.681 | 161410.126 | 307006.227 | 13.4333 | 6.58 | 6.05 | 39.97 | 49.84 | 2.3 | 5.5 | 309854.97
2025-06-13 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:11 | 16:34 | 1178.3 | 1208.4 | 1099.7 | 1113.8 | 1200.4 | 1117.2 | 1115.4 | 1116.3 | 1151.9 | 1154.4 | 1137.1 | 1127.3 | 1110.6 | 1046.1 | 1112.6 | 1109.9 | 1107.8 | 1105.5 | 1207.2 | 1206.5 | 1119.6 | 1122.3 | 1231.1 | 1271.5 | 1227.5 | 1212.8 | 1209.1 | 1258.1 | 1269.2 | 1249.8 | 1255.5 | 1261.1 | 1069.5 | 1369.2 | 1119.5 | 1221.1 | 1126.9 | 1099.6 | 1123 | 1139.8 | 1116.4 | 1104.3 | 1128.5 | 1117.2 | 1130.9 | 1130.4 | 1222.3 | 1119.2 | 1145.5 | 1139.3 | 1110.4 | 1115 | 1287.4 | 1266.4 | 1190.5 | 1260.5 | 1260.3 | 1122.1 | 1245.9 | 1262.9 | 1133.2 | 1275.3 | 1106.3 | 1011 | 1233.2 | 1209.5 | 1222.9 | 1185.9 | 1092.6 | 1124.4 | 1131.6 | 1126.1 | 1148.1 | 1091.1 | 1267.2 | 1249.2 | 1262.6 | 1114 | 1114.1 | 1186.1 | 1126.7 | 1128.7 | 1119.2 | 1135.1 | 1127.5 | 1125.2 | 1134 | 1124.1 | 1119.8 | 1112.5 | 1148.5 | 1180.5 | 1144.4 | 1142.4 | 1278.8 | 1119.3 | 1109 | 1130.9 | 1120.7 | 1121.7 | 1121 | 1122 | 1138.9 | 1100.3 | 1227.3 | 1129.9 | 1242 | 1220.3 | 1132.3 | 1242.9 | 1212.5 | 1181.1 | 1223 | 1246.3 | 1123.4 | 1132.8 | 1231.4 | 1239.7 | 1236.7 | 1121.8 | 1135.2 | 1226.6 | 1230 | 1126.6 | 1133.5 | 1223.9 | 1089.3 | 1096.6 | 1262 | 1241 | 1192.9 | 1196.1 | 1194.2 | 1027.6 | 1188 | 1179.6 | 1201 | 1205.8 | 1170.7 | 1109.1 | 1178.7 | 1178 | 1118.1 | 1210.9 | 1106 | 1186.9 | 1103.1 | 1034.4 | 1210.1 | 1222.3 | 1221 | 1122 | 1272.6 | 1123.8 | 1109.8 | 1101 | 1115.5 | 1120.5 | 1114 | 1111.1 | 1255.9 | 1090.8 | 1239 | 1255.5 | 1244 | 1165.8 | 1108.2 | 1263.5 | 1118 | 1121.5 | 1137.6 | 1121.1 | 1232.1 | 1148.4 | 1223 | 1117.1 | 1116 | 1103.4 | 1241 | 1111 | 1180.6 | 1236.2 | 1243.4 | 1131 | 1201 | 1251 | 1154 | 1159 | 1123 | 1174.7 | 1101 | 1105.1 | 1078 | 1115 | 1119 | 1111 | 910 | 1090 |  |  | 996.4 | 782 | 1109.1 |  | 1214 | 1091.1 | 1137.4 | 1091.1 | 1121 | 1119.2 | 1123 | 1123 | 1118.3 | 1127.2 | 1125 | 1115 | 1265.4 | 1271 | 954 | 986 | 821 | 667 | 861.1 | 981.1 | 1170.2 | 1251.5 | 1182.1 | 1212 | 1189.1 | 1255.5 | 1232.7 | 1233.1 | 1056 | 1156.1 | 1050 | 1099.1 | 1017.5 |  | 1459.5 | 1176.2 | 421 | 1111.2 | 1056.2 |  |  | 1065 | 1123 | 1149.8 | 1055.5 | 1001.5 | 39.42 | 48.96 | 3.4 | 12.9 |  | 5.96 | 5.45 |  |  | 86904181.726 | 283217.646 | 59863454.302 | 62868.304 | 87615930.416 | 188299.768 | 63682724.362 | 57558.264 | 329170266.65 | 88188.186 | 74373.342 | 39.941 | 70770.001 | 35.884 | 74449.308 | 50.27 | 57474.992 | 68.544 | 276945.719 | 146.681 | 145067.518 | 276799.038 | 11.3833 | 5.96 | 5.45 | 39.42 | 48.96 | 3.4 | 12.9 | 279024.1
2025-06-14 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:08 | 18:43 | 1326 | 1354 | 1203 | 1253 | 1338 | 1246 | 1237 | 1240 | 1280 | 1291 | 1260 | 1256 | 1236 | 1161 | 1237 | 1233 | 1225 | 1224 | 1328 | 1331 | 1240 | 1244 | 1361 | 1399 | 1349 | 1336 | 1328 | 1377 | 1399 | 1374 | 1381 | 1385 | 1173 | 1513 | 1224 | 1342 | 1233 | 1202 | 1221 | 1238 | 1217 | 1208 | 1224 | 1209 | 1224 | 1228 | 1323 | 1211 | 1280 | 1258 | 1235 | 1232 | 1400 | 1377 | 1324 | 1411 | 1393 | 1241 | 1377 | 1397 | 1235 | 1395 | 1220 | 1087 | 1327 | 1317 | 1336 | 1300 | 1215 | 1209 | 1218 | 1211 | 1239 | 1219 | 1393 | 1368 | 1390 | 1224 | 1211 | 1313 | 1228 | 1232 | 1216 | 1234 | 1217 | 1220 | 1228 | 1216 | 1203 | 1194 | 1263 | 1331 | 1242 | 1232 | 1370 | 1210 | 1204 | 1229 | 1215 | 1218 | 1252 | 1213 | 1238 | 1208 | 1378 | 1231 | 1411 | 1366 | 1234 | 1371 | 1331 | 1324 | 1385 | 1394 | 1226 | 1253 | 1378 | 1397 | 1378 | 1246 | 1262 | 1352 | 1349 | 1232 | 1238 | 1351 | 1200 | 1214 | 1386 | 1367 | 1316 | 1321 | 1318 | 1131 | 1321 | 1298 | 1341 | 1335 | 1289 | 1239 | 1307 | 1311 | 1240 | 1347 | 1203 | 1319 | 1219 | 1132 | 1321 | 1331 | 1340 | 1231 | 1409 | 1236 | 1212 | 1203 | 1199 | 1211 | 1223 | 1199 | 1370 | 1181 | 1365 | 1356 | 1385 | 1260 | 1215 | 1383 | 1223 | 1252 | 1278 | 1251 | 1386 | 1289 | 1331 | 1208 | 1221 | 1198 | 1411 | 1236 | 1316 | 1388 | 1348 | 1311 | 1324 | 1375 | 1275 | 1276 | 1250 | 1323 | 1217 | 1217 | 1189 | 1227 | 1216 | 1101 | 1028 | 1248 |  |  | 1095 | 881 | 1215 |  | 1333 | 1201 | 1231 | 1206 | 1224 | 1227 | 1241 | 1233 | 1239 | 1261 | 1234 | 1247 | 1383 | 1411 | 1067 | 1071 | 886.8 | 756.6 | 941 | 1099 | 1294 | 1375 | 1319 | 1292 | 1261 | 1331 | 1373 | 1351 | 1169 | 1256 | 1199 | 1223 | 1123 |  | 1655 | 1301 | 471 | 1199 | 1178 |  |  | 1151 | 1222 | 1255 | 1155 | 1087 | 37.79 | 49.04 | 1.63 | 4.9 |  | 6.54 | 6.01 |  |  | 86986303.472 | 283257.587 | 59941488.966 | 62904.188 | 87698030.148 | 188350.038 | 63745789.345 | 57626.808 | 329475498.732 | 88334.867 | 82121.746 | 39.941 | 78034.664 | 35.884 | 82099.732 | 50.27 | 63064.983 | 68.544 | 305232.082 | 146.681 | 160080.585 | 305085.401 | 13.5833 | 6.54 | 6.01 | 37.79 | 49.04 | 1.63 | 4.9 | 307007.4
2025-06-15 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:15 | 18:29 | 970.9 | 991.1 | 901 | 910.7 | 988.2 | 916.3 | 918.3 | 920.4 | 951.3 | 953.9 | 935.2 | 930.1 | 912.7 | 871 | 911.4 | 909 | 904.4 | 913 | 979 | 981 | 897.4 | 905.8 | 998.4 | 1015.8 | 974.2 | 981 | 971 | 1021 | 1014.3 | 1022 | 1022 | 1024 | 850.1 | 1101 | 901 | 1001 | 906 | 891 | 901 | 898.1 | 893.2 | 899.5 | 901 | 901 | 906 | 888.9 | 991 | 901 | 941 | 939.2 | 901 | 904.2 | 1011 | 1017 | 971 | 1011 | 1014.1 | 904 | 1001.1 | 1012 | 905 | 1009.1 | 904.1 | 801 | 1001.6 | 993.8 | 1007.2 | 982.1 | 918.3 | 912.4 | 921.3 | 915.3 | 938.9 | 919.3 | 1049.2 | 1030.4 | 1047.4 | 923.1 | 912.6 | 1001.1 | 926.1 | 928.8 | 917.9 | 931.8 | 917.3 | 921.5 | 928.5 | 919.1 | 910.6 | 902.7 | 953.6 | 1010 | 939.3 | 932.1 | 1035.6 | 912.7 | 907.4 | 945.2 | 926.1 | 937.2 | 941 | 929.3 | 941.1 | 911.1 | 1031.1 | 918.9 | 1021 | 1045.8 | 921 | 1031.1 | 1009 | 1002.1 | 1060.8 | 1055.9 | 943.6 | 950.8 | 1039.8 | 1073.2 | 1065.2 | 949.2 | 959.7 | 1025.1 | 1012 | 948.7 | 955.4 | 1191.1 | 891 | 893.4 | 1013.4 | 1006.4 | 969.5 | 973.2 | 974.3 | 838.5 | 971 | 961 | 994.4 | 986.6 | 955.1 | 901.3 | 965.9 | 971 | 891.6 | 980.4 | 891 | 981 | 891 | 823.1 | 962.3 | 970.3 | 973.3 | 896.1 | 1027.5 | 895.9 | 898 | 891 | 893 | 889 | 881.4 | 884 | 991.1 | 901 | 1001 | 996 | 994.2 | 941 | 901 | 999.8 | 911.1 | 932 | 925.8 | 921 | 1009.1 | 931 | 992 | 911 | 885.1 | 901 | 1027.3 | 898.2 | 969.3 | 1015.5 | 1022 | 961.7 | 955.1 | 991.6 | 929.7 | 924.7 | 949.7 | 964.9 | 922.5 | 930.3 | 982.5 | 927.6 | 921.5 | 929.9 | 789.6 | 948.7 |  |  | 822 | 650.3 | 927.8 |  | 1024.4 | 900.8 | 934.3 | 914.5 | 926.8 | 931.4 | 938.1 | 934.6 | 937.3 | 955.5 | 932.3 | 942.5 | 1043.8 | 1064.8 | 801 | 798 | 656 | 555 | 699.8 | 824.3 | 985.1 | 1065.1 | 1025.7 | 1010.7 | 985 | 1021 | 1056.1 | 1011.9 | 893 | 945.3 | 872 | 902.7 | 834.3 |  | 1242 | 1001 | 349 | 901 | 901 |  |  | 851 | 901 | 934 | 868 | 820 | 34.83 | 42.57 | 3.24 | 10.7 |  | 4.87 | 4.49 |  |  | 87046079.3 | 283297.528 | 60001329.281 | 62940.072 | 87758029.79 | 188400.308 | 63794673.512 | 57695.352 | 329703925.03 | 88481.548 | 59775.828 | 39.941 | 59840.315 | 35.884 | 59999.642 | 50.27 | 48884.167 | 68.544 | 228426.298 | 146.681 | 119540.318 | 228279.617 | 13.2333 | 4.87 | 4.49 | 34.83 | 42.57 | 3.24 | 10.7 | 229066.5
2025-06-16 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 6:13 | 17:53 | 1297 | 1322.9 | 1213.2 | 1214.1 | 1317.5 | 1224.1 | 1227.1 | 1227.8 | 1265.3 | 1269.7 | 1250.4 | 1241.9 | 1223.3 | 1153.3 | 1224.6 | 1222.8 | 1217.7 | 1211.2 | 1315.9 | 1316 | 1222.6 | 1227 | 1347.3 | 1377.2 | 1331.4 | 1314.4 | 1308.5 | 1359.7 | 1373.1 | 1354.3 | 1355.5 | 1349.5 | 1142 | 1484.1 | 1209.5 | 1335.3 | 1193.7 | 1184.3 | 1222.5 | 1215.9 | 1225.4 | 1201 | 1206.9 | 1192.7 | 1206.7 | 1210.7 | 1302.4 | 1211.5 | 1243.4 | 1236 | 1209.1 | 1204.2 | 1373.6 | 1353.7 | 1292.9 | 1365.4 | 1368.1 | 1219.8 | 1351.7 | 1369.6 | 1215.7 | 1370.6 | 1206.8 | 1100 | 1326.2 | 1316.7 | 1330.7 | 1298.2 | 1218.1 | 1213.3 | 1221 | 1214.8 | 1245 | 1222.3 | 1390.4 | 1365.5 | 1392 | 1225 | 1211.1 | 1323.3 | 1230.4 | 1234.7 | 1218.8 | 1235.8 | 1218.3 | 1220.5 | 1229.1 | 1218.1 | 1205 | 1197.9 | 1261.1 | 1325 | 1242.9 | 1236.5 | 1368.4 | 1212.9 | 1207.2 | 1239.7 | 1222.1 | 1226.9 | 1255.4 | 1224.5 | 1240.4 | 1213.4 | 1387.4 | 1238.2 | 1398.1 | 1365 | 1236.2 | 1375.2 | 1330 | 1310.6 | 1385.2 | 1376.2 | 1233.3 | 1240.5 | 1356.8 | 1375.3 | 1368.8 | 1232.6 | 1248.5 | 1344 | 1349.1 | 1231.7 | 1241.7 | 1394.9 | 1177.2 | 1170.2 | 1311 | 1321.6 | 1271.7 | 1279.6 | 1277.7 | 1080 | 1250 | 1261.4 | 1261 | 1259.9 | 1221 | 1156.3 | 1263.8 | 1257.5 | 1178 | 1276 | 1162.1 | 1279 | 1180.6 | 1078 | 1271 | 1269 | 1268 | 1172 | 1318 | 1172 | 1176.5 | 1168.7 | 1163.8 | 1172 | 1212.7 | 1190.1 | 1355.9 | 1175.4 | 1345.5 | 1337.9 | 1363.5 | 1248.2 | 1198.2 | 1361.5 | 1229.4 | 1226.6 | 1248.8 | 1224.5 | 1354.7 | 1261.5 | 1350.3 | 1201.3 | 1215.6 | 1191.2 | 1385.3 | 1228.4 | 1296.4 | 1366.4 | 1328.1 | 1276 | 1309.3 | 1360.2 | 1270.8 | 1270.8 | 1277.9 | 1301.2 | 1219.9 | 1209.1 | 1201 | 1221.7 | 1221.7 | 1225.5 | 1034.6 | 1249.4 |  |  | 1117.4 | 845.6 | 1230.3 |  | 1336.1 | 1183.1 | 1230.6 | 1196.3 | 1227.6 | 1227.5 | 1238 | 1236 | 1240.1 | 1252.2 | 1234.1 | 1242 | 1381.9 | 1409.7 | 1089 | 1070 | 901 | 754 | 932 | 1083.5 | 1283.4 | 1381.7 | 1318.4 | 1313.4 | 1295.5 | 1321.5 | 1374 | 1342 | 1143 | 1237 | 1151 | 1183.9 | 1123 |  | 1580.5 | 1278.2 | 461 | 1192.1 | 1141 |  |  | 1142 | 1204 | 1234 | 1156 | 1101 | 32.82 | 40.29 | 3.89 | 8.5 |  | 6.29 | 5.78 |  |  | 87126863.647 | 283334.469 | 60079561.358 | 62971.956 | 87838349.007 | 188447.578 | 63858367.094 | 57759.896 | 330006760.635 | 88625.229 | 80784.347 | 36.941 | 78232.077 | 31.884 | 80319.217 | 47.27 | 63693.582 | 64.544 | 302835.605 | 143.681 | 158947.599 | 302691.924 | 11.6667 | 6.29 | 5.78 | 32.82 | 40.29 | 3.89 | 8.5 | 303505.1
2025-06-17 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:12 | 16:05 | 911.4 | 933.7 | 865.2 | 867.9 | 924.3 | 859.1 | 857.6 | 860.3 | 888.8 | 894 | 872.4 | 867.2 | 855.7 | 807 | 852.9 | 842.3 | 846.7 | 843.5 | 910 | 915 | 855 | 854.2 | 943.3 | 963.9 | 929 | 915 | 910.5 | 949.3 | 952 | 942.5 | 951.5 | 948.8 | 805.4 | 1044.4 | 840.8 | 946.5 | 844.2 | 826.9 | 843 | 857.4 | 835.4 | 828.2 | 843.9 | 836.1 | 846.5 | 849.6 | 915.5 | 837.8 | 877.2 | 863.9 | 850.7 | 847.8 | 970 | 953 | 915 | 971.3 | 965.3 | 856.7 | 947.6 | 955.4 | 853 | 961 | 851.9 | 812.8 | 920.6 | 913.8 | 924 | 899.7 | 841.6 | 839.6 | 844.9 | 839.3 | 861 | 833.7 | 959.1 | 939.5 | 959.5 | 843.8 | 834 | 921 | 846.8 | 850.3 | 839.9 | 850.6 | 837.9 | 842.7 | 848.7 | 842.4 | 832.2 | 828.8 | 869.9 | 913.5 | 858.6 | 853.6 | 950.2 | 835.1 | 833.2 | 854.5 | 848.2 | 850.1 | 869.9 | 846.5 | 857.3 | 834.5 | 964.1 | 850.3 | 980.4 | 949 | 857.6 | 946.8 | 915.5 | 898.9 | 952 | 954.3 | 852 | 860.2 | 941.6 | 945.1 | 943.4 | 847.2 | 865.1 | 934 | 944 | 851.9 | 856.4 | 948.5 | 841.6 | 836.2 | 963.3 | 947.8 | 909.8 | 910.7 | 910.7 | 785.7 | 902 | 900.6 | 930.6 | 916.5 | 900.1 | 834 | 899 | 894.1 | 856.5 | 931.4 | 844 | 901 | 842.3 | 782.4 | 912.5 | 920.4 | 926.9 | 849.3 | 966.5 | 852.5 | 840.4 | 833.8 | 835.8 | 838.5 | 833.4 | 819 | 931.7 | 833 | 934.1 | 922.2 | 952.4 | 861.5 | 824.8 | 938.4 | 843.2 | 861 | 856.9 | 859 | 933 | 865.6 | 945.4 | 831.4 | 837.1 | 821.8 | 953.3 | 845.1 | 890.7 | 937.4 | 921.8 | 903.8 | 906.8 | 941.1 | 878.3 | 879.3 | 876.6 | 889.6 | 839 | 831 | 840.6 | 844.4 | 842 | 847.2 | 713.5 | 864.9 |  |  | 786.1 | 601 | 842.5 |  | 935.2 | 831.7 | 845.5 | 839 | 846.6 | 847.9 | 859 | 853.7 | 860.3 | 862.1 | 853.1 | 861.5 | 963.1 | 983.6 | 755 | 751 | 631 | 531 | 651 | 747.5 | 891.6 | 956.8 | 894 | 898.8 | 901.1 | 925.5 | 953.1 | 934 | 801 | 863 | 803 | 831 | 768 |  | 1151 | 901 | 335 | 831 | 801 |  |  | 799 | 855 | 868 | 801 | 755 | 33.67 | 42.05 | 2.77 | 8.9 | 0.8 | 4.44 | 3.98 |  |  | 87183482.456 | 283371.41 | 60133871.225 | 63003.84 | 87894643.099 | 188494.848 | 63902423.975 | 57824.44 | 330217933.48 | 88768.91 | 56618.809 | 36.941 | 54309.867 | 31.884 | 56294.092 | 47.27 | 44056.881 | 64.544 | 211172.845 | 143.681 | 110859.851 | 211029.164 | 10.8833 | 4.44 | 3.98 | 33.67 | 42.05 | 2.77 | 8.9 | 212042.5
2025-06-18 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:06 | 18:34 | 1115 | 1136.1 | 1053.4 | 1050.5 | 1142.4 | 1052.8 | 1065.8 | 1065.5 | 1095.4 | 1102.4 | 1085.5 | 1079.8 | 1057.3 | 995.3 | 1061.1 | 1013.1 | 1056.5 | 1057.5 | 1150.6 | 1152.4 | 1067 | 1066.2 | 1147.5 | 1201.8 | 1165.2 | 1149.4 | 1140.5 | 1186.3 | 1200.5 | 1215.5 | 1221.5 | 1205.4 | 944 | 1111.4 | 986.1 | 1115.9 | 986.1 | 988.3 | 1001.1 | 995.5 | 980.5 | 993.1 | 981 | 994.4 | 1004.2 | 991 | 1081.1 | 996.5 | 1034.1 | 1037.5 | 999.6 | 995.5 | 1124.2 | 1122.4 | 1081.2 | 1124.5 | 1139.8 | 1003.2 | 1123.5 | 1129.1 | 1002.9 | 1110.7 | 1001.1 | 941 | 1131.9 | 1123.2 | 1135 | 1105.4 | 1044.1 | 1044.1 | 1050.4 | 1044.9 | 1075.1 | 1032.2 | 1194 | 1177.3 | 1197.4 | 1057.6 | 1055.5 | 1148.5 | 1021 | 1041 | 1053 | 1070.6 | 1057.8 | 1057.5 | 1060.2 | 1051.3 | 1037.2 | 1029.4 | 1070 | 1125.7 | 1070.2 | 1067.6 | 1161.9 | 1049.9 | 1044.1 | 1065.7 | 1051.9 | 1057.6 | 1083.1 | 1055.1 | 1071.5 | 1046.6 | 1186.7 | 1056.2 | 1217.2 | 1169.3 | 1061.2 | 1177.7 | 1135.1 | 1111 | 1164.5 | 1172.8 | 1061.4 | 1063.4 | 1151.4 | 1174.1 | 1171.85 | 1053.7 | 1062.2 | 1146 | 1149.8 | 1052.3 | 1061.3 | 1187 | 1048 | 1051 | 1198.7 | 1183.3 | 1142.2 | 1144.7 | 1151.6 | 962.6 | 1101.8 | 1136.9 | 1169.2 | 1156.1 | 1129.4 | 1020.4 | 1135.3 | 1120.1 | 1064.7 | 1161.7 | 1028.6 | 1133.7 | 1058.2 | 980.4 | 1139.7 | 1149.7 | 1146.2 | 1053.3 | 1193.7 | 1056.3 | 1043.5 | 1039.7 | 1044.7 | 1043.4 | 1041 | 1051.5 | 1197.9 | 1039.2 | 1188 | 1180.4 | 1150 | 1096 | 1051.4 | 1175.1 | 1040 | 1071.2 | 1097.2 | 1069.4 | 1190.9 | 1101.6 | 1178 | 1071.1 | 1075 | 1058.9 | 1190.1 | 1048 | 1145.7 | 1176 | 1176.2 | 1101 | 1123 | 1179 | 1121.4 | 1126.3 | 1114 | 1142 | 1039.9 | 1022.4 | 1011 | 1038.2 | 1041.6 | 1023 | 882 | 1062.7 |  |  | 930.1 | 744 | 1038.7 |  | 1123.5 | 1022 | 1052 | 971.6 | 1048.9 | 1056.4 | 1059.1 | 1058.6 | 1059.4 | 1022 | 1053.4 | 1062.4 | 1175.8 | 1194.2 | 901 | 901 | 771 | 644 | 801 | 912.4 | 1094.8 | 1164.9 | 1114.7 | 1108.8 | 1099.5 | 1129.2 | 1159.2 | 1156 | 1011 | 1055 | 981 | 1044 | 945 |  | 1378 | 1101 | 412 | 1051 | 981 |  |  | 965 | 1039 | 1071 | 981 | 931 | 31.72 | 42.78 | 1.64 | 5.1 |  | 5.32 | 4.96 |  |  | 87251038.44 | 283395.351 | 60201269.853 | 63035.724 | 87965830.574 | 188542.118 | 63956006.601 | 57882.984 | 330477604.223 | 88904.591 | 67555.984 | 23.941 | 67398.628 | 31.884 | 71187.475 | 47.27 | 53582.626 | 58.544 | 259670.743 | 135.681 | 134898.787 | 259535.062 | 13.4667 | 5.32 | 4.96 | 31.72 | 42.78 | 1.64 | 5.1 | 261299.05
2025-06-19 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:24 | 17:50 | 989 | 984 | 912.2 | 911.6 | 978.4 | 907.6 | 911.3 | 911.3 | 940.2 | 946.8 | 919.3 | 923.1 | 908.3 | 854.3 | 910 | 885 | 906.2 | 902.5 | 978 | 980.7 | 912.9 | 912 | 963.2 | 1028 | 994.4 | 981.5 | 975.3 | 1015.7 | 1024.6 | 1024.5 | 1019.1 | 1028 | 878.6 | 1113.1 | 912.7 | 1033.5 | 910.7 | 885.6 | 895.5 | 914.5 | 901.5 | 893.3 | 903.3 | 913.5 | 905 | 909.4 | 977.6 | 901.2 | 931.4 | 945 | 903.8 | 901.1 | 1030.2 | 1017.7 | 968.8 | 1023.4 | 1027.4 | 914.5 | 1016.9 | 1030.1 | 911.7 | 1034.9 | 900.2 | 872 | 978.7 | 972.8 | 979.8 | 957.4 | 902.2 | 898.5 | 902.7 | 896.5 | 921.6 | 906.8 | 1044.4 | 1020 | 1042.3 | 914.1 | 900.8 | 990.6 | 910.2 | 913.9 | 900.8 | 913.3 | 897.1 | 902 | 906.4 | 899.8 | 887.9 | 902 | 927.8 | 968.8 | 918.3 | 914.2 | 1006.2 | 899.4 | 900.1 | 916.8 | 912.1 | 909.9 | 928.9 | 908.8 | 919.4 | 896.8 | 1028.2 | 908.7 | 1065.3 | 1011.2 | 911.9 | 1011.3 | 972.7 | 961 | 1020.2 | 1018.7 | 911.1 | 914.9 | 1006.2 | 1001.2 | 1005 | 897.7 | 915.4 | 1001 | 1011 | 903.1 | 911.1 | 1022.2 | 900.9 | 905.2 | 1039.3 | 1027.7 | 989 | 989.9 | 989.7 | 853.9 | 1009.8 | 979.9 | 1017.8 | 1002.8 | 988.6 | 891.5 | 978.8 | 976.8 | 934.9 | 1018.7 | 898.5 | 971 | 921.1 | 855.4 | 991.9 | 1000.7 | 1003.9 | 915.9 | 1039.1 | 917.6 | 906.3 | 902.4 | 912.2 | 905.4 | 913.4 | 896.6 | 1022.6 | 885.2 | 1020.7 | 1016.1 | 1030.3 | 936.7 | 898.6 | 1020.3 | 921.5 | 912.9 | 934.2 | 912.4 | 1016.1 | 939.9 | 1044.5 | 913.5 | 919.7 | 902.6 | 1045 | 927.8 | 978.4 | 1026.7 | 1014.4 | 950 | 994 | 1035.1 | 962.8 | 965.5 | 950.3 | 971.9 | 882.4 | 889.1 | 891.1 | 885.2 | 887.7 | 886.1 | 754.5 | 908.3 |  |  | 827 | 643.2 | 901 |  | 982.3 | 889.2 | 893.6 | 819.8 | 892.4 | 894.6 | 905.2 | 901.2 | 907.3 | 915.9 | 904 | 912 | 1018.1 | 1039.1 | 802.2 | 808.4 | 690.7 | 562.5 | 699.2 | 802.2 | 933.9 | 1003.4 | 961.6 | 978.1 | 941.2 | 978.7 | 1025.2 | 1012 | 890 | 925.5 | 890.1 | 888.7 | 853.5 |  | 1212.5 | 961.5 | 350.4 | 901.1 | 882 |  |  | 844.5 | 902.6 | 932.5 | 881.2 | 814.5 | 30.22 | 39.34 | 3.06 | 9.5 | 0.03 | 4.53 | 4.17 |  |  | 87311402.499 | 283419.292 | 60259321.38 | 63067.608 | 88027176.227 | 188589.388 | 64002405.579 | 57941.528 | 330703683.51 | 89040.272 | 60364.059 | 23.941 | 58051.527 | 31.884 | 61345.653 | 47.27 | 46398.978 | 58.544 | 226079.287 | 135.681 | 118359.761 | 225943.606 | 12.4333 | 4.53 | 4.17 | 30.22 | 39.34 | 3.06 | 9.5 | 227578.3
2025-06-20 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:27 | 18:42 | 570 | 581 | 539.1 | 536.5 | 562.3 | 536.6 | 536.8 | 537.3 | 341 | 558.7 | 547.4 | 543.9 | 534.4 | 502 | 535.3 | 511.63 | 532.4 | 529.9 | 582.7 | 580.7 | 536.2 | 537.9 | 566.9 | 608.4 | 586.6 | 581.9 | 578.5 | 602.1 | 613.1 | 580.7 | 588.5 | 434 | 518.8 | 432 | 538.4 | 610.3 | 540.6 | 525.3 | 533.3 | 541 | 533 | 522.6 | 536.6 | 531.3 | 536.1 | 536.8 | 444 | 528.8 | 552.6 | 391 | 534.5 | 535.1 | 611.2 | 602.7 | 573.8 | 608.1 | 607.1 | 539.3 | 600.4 | 612.4 | 538.6 | 615.2 | 533.7 | 521.2 | 574.6 | 571.2 | 589 | 586 | 526.2 | 525.2 | 528.5 | 523.7 | 541.1 | 532.1 | 608.9 | 599.7 | 607.9 | 533.3 | 527.3 | 584.6 | 534.1 | 474.1 | 528 | 534.4 | 524.6 | 527.9 | 522.3 | 527.4 | 518.3 | 508.7 | 543.6 | 569.1 | 530.4 | 531.3 | 607 | 0 | 0 | 536 | 532.8 | 522.5 | 546.8 | 520.1 | 539.1 | 525 | 610.2 | 0 | 0 | 601 | 536.3 | 602.9 | 581.4 | 589 | 601.4 | 596.8 | 530 | 537.3 | 570 | 599 | 601.7 | 530.8 | 541.2 | 532 | 519 | 535.2 | 540.3 | 599.3 | 544 | 529.1 | 568.4 | 444 | 579.6 | 578.4 | 578.8 | 501.2 | 592.9 | 575.9 | 595.5 | 584.1 | 577.5 | 549 | 589 | 577.5 | 538.1 | 588.3 | 520.7 | 560.3 | 539.1 | 499.9 | 581.5 | 582.4 | 582.3 | 464.1 | 613.3 | 541.8 | 531.2 | 527.3 | 539.5 | 533.5 | 538.9 | 530.8 | 606.7 | 522.9 | 470.6 | 524 | 609.5 | 556.9 | 452.9 | 451 | 356 | 529.4 | 553.6 | 527.2 | 434.6 | 385 | 598.1 | 524.1 | 538.6 | 529.1 | 615.4 | 545.9 | 424 | 444.7 | 596.3 | 585.5 | 585.1 | 608.2 | 558.3 | 555.5 | 448.5 | 330.9 | 522.4 | 515.4 | 523 | 513 | 522.2 | 391 | 442.4 | 538.4 |  |  | 469 | 371 | 534 |  | 579 | 510 | 521 | 519.1 | 527.3 | 533.4 | 535.2 | 512 | 534.8 | 542 | 529.6 | 401 | 599 | 612.6 | 493.1 | 478 | 407.5 | 345.3 | 397.6 | 470 | 537.3 | 597.3 | 569.9 | 565.4 | 544.5 | 577.5 | 594.2 | 587.5 | 523 | 534.9 | 524 | 534 | 473.4 |  | 711 | 565 | 201 | 507.2 | 489.6 |  |  | 488 | 503 | 534 | 491.8 | 475 | 28.91 | 32.29 | 0.946 | 5.7 | 0.4 | 2.53 | 2.4 |  |  | 87345961.541 | 283443.233 | 60291502.496 | 63099.492 | 88060847.752 | 188636.658 | 64029792.6 | 58000.072 | 330831376.797 | 89175.953 | 34559.042 | 23.941 | 32181.116 | 31.884 | 33671.525 | 47.27 | 27387.021 | 58.544 | 127693.287 | 135.681 | 66684.333 | 127557.606 | 13.25 | 2.53 | 2.4 | 28.91 | 32.29 | 0.946 | 5.7 | 128207.03
2025-06-21 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:10 | 18:40 | 1162.5 | 1155 | 1069 | 1064.6 | 1179.5 | 1069 | 1059 | 1072.2 | 1084 | 1130.5 | 1061 | 1081 | 1082.4 | 985 | 1082.3 | 1035.6 | 1074.7 | 1071.4 | 1167.2 | 1167.3 | 1067.2 | 1061 | 1144.4 | 1220.4 | 1151 | 1167.9 | 1159.8 | 1202.1 | 1218.7 | 1166 | 1161 | 1101 | 1024.1 | 1296.7 | 1065.5 | 1202 | 1059.6 | 1047.4 | 1072.4 | 1086.4 | 1059.8 | 1048.3 | 1073.8 | 1059.8 | 1078.9 | 1045 | 1119.2 | 1065.2 | 1120.3 | 1124.3 | 1051 | 1087.2 | 1240.7 | 1220.9 | 1144.9 | 1180 | 1218.8 | 1080.4 | 1193.4 | 1206.6 | 1074.2 | 1211.6 | 1061 | 1002 | 1161 | 1162.8 | 1156 | 1163.1 | 1058 | 1071 | 1068 | 1071.4 | 1084.5 | 1061 | 1219.8 | 1201 | 1224.6 | 1081.8 | 1083.7 | 1056 | 1067 | 1060.8 | 1084.6 | 1076 | 1079 | 1071 | 1074 | 1071 | 1063 | 1059.8 | 1101 | 1157.7 | 1064 | 1075.9 | 1212.9 | 1035.2 | 1033 | 1044.4 | 1031 | 1029.7 | 1048.9 | 1036 | 1033.6 | 1038 | 1171 | 928 | 1059 | 1154 | 1028.4 | 1169.6 | 1134 | 1139 | 1163.6 | 1160.4 | 1042.2 | 1042.1 | 1156 | 1159 | 1169 | 1037 | 1034.8 | 1081.2 | 1082 | 1037 | 1030.8 | 1181 | 1061 | 1055 | 1167 | 1161.1 | 1148.4 | 1123 | 1146.8 | 990.8 | 1139 | 1134.6 | 1154 | 1145.7 | 1124 | 1036 | 1139.3 | 1131.1 | 1077 | 1161.7 | 1044.9 | 1121 | 1063.1 | 985.6 | 1129.6 | 1152.6 | 1155.9 | 1050.2 | 1185.3 | 1042.9 | 1034 | 1034.1 | 1035.5 | 1047.4 | 1050 | 1064.2 | 1171 | 1040 | 1166.5 | 1191.8 | 1189.1 | 1109 | 1054.9 | 1184.7 | 1051.1 | 1103.6 | 1090 | 1104.3 | 1026 | 1068 | 1190 | 1051 | 1057 | 1061 | 1201 | 1055 | 1109 | 1188.9 | 1197.9 | 1071 | 1128 | 1184 | 1081 | 1103.2 | 1081 | 1110 | 1051 | 1053.4 | 1042 | 1063.5 | 1059 | 1051 | 867 | 1044 |  |  | 951 | 736.3 | 1058.9 |  | 1188.4 | 1057.2 | 1031 | 1044 | 1076.2 | 1067.3 | 1061 | 1054 | 1071 | 1043 | 1041 | 1035 | 1213.5 | 1201 | 901 | 901 | 789 | 671 | 808.7 | 956.4 | 1101 | 1211.2 | 1158.4 | 1154.9 | 1101 | 1169.5 | 1203.9 | 1193.6 | 1001 | 1081 | 1002 | 1033.4 | 968.5 |  | 1390 | 1112 | 401 | 1035 | 1001 |  |  | 990 | 1010 | 1080 | 992 | 933.5 | 31.15 | 42.22 | 1.35 | 6.1 |  | 5.62 | 5.19 |  |  | 87417389.103 | 283465.174 | 60358361.347 | 63129.376 | 88130710.583 | 188681.928 | 64085431.87 | 58056.616 | 331095030.155 | 89309.634 | 71427.562 | 21.941 | 66858.851 | 29.884 | 69862.831 | 45.27 | 55639.27 | 56.544 | 263653.358 | 133.681 | 138234.588 | 263519.677 | 13.5 | 5.62 | 5.19 | 31.15 | 42.22 | 1.35 | 6.1 | 264314.4
2025-06-22 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 4:59 | 18:12 | 1230.5 | 1228.1 | 1129.1 | 1134.2 | 1221 | 1141 | 1138 | 1145 | 1190 | 1190 | 1127 | 1147 | 1115.3 | 1046 | 1143 | 1100 | 1134 | 1152.5 | 1246 | 1231 | 1133 | 1135 | 1226.9 | 1280 | 1231 | 1239 | 1233.7 | 1285 | 1298 | 1239 | 1255.5 | 1198 | 1090 | 1379.4 | 1150.8 | 1280 | 1154.2 | 1135.8 | 1151.1 | 1147 | 1131 | 1135.6 | 1134 | 1121 | 1148 | 1129 | 1201 | 1141 | 1166.2 | 1103.4 | 1152 | 1150.5 | 1301 | 1290 | 1235.5 | 1278 | 1271 | 1132 | 1270 | 1290 | 1138 | 1290 | 1147.1 | 1050 | 1229 | 1231 | 1246.1 | 1215.3 | 1132 | 1136.1 | 1139 | 1134 | 1121 | 1145.1 | 1270 | 1282 | 1284.3 | 1145.4 | 1142.7 | 1251.7 | 1131 | 1129.1 | 1135.4 | 1149.6 | 1151 | 1146.1 | 1143.8 | 1143.7 | 1123.9 | 1115.2 | 1169.7 | 1199 | 1131 | 1127.3 | 1273.9 | 1139 | 1132.1 | 1127 | 1146.1 | 1143.2 | 1135 | 1143.4 | 1134 | 1121.7 | 1282.2 | 1135.5 | 1222 | 1267.1 | 1146.6 | 1269 | 1221.9 | 1150 | 1268.6 | 1277.2 | 1148.8 | 1141.3 | 1234 | 1248.3 | 1257.4 | 1122.2 | 1145.5 | 1186.4 | 1161.4 | 1133.2 | 1143 | 1275.1 | 1142.8 | 1139.9 | 1241 | 1265.2 | 1229.5 | 1201 | 1241.2 | 1051 | 1219 | 1231 | 1231 | 1224 | 1180 | 1101 | 1233.6 | 1213.6 | 1132 | 1234 | 1136 | 1148.7 | 1121 | 1041 | 1236.3 | 1232.2 | 1233 | 1147.3 | 1287.8 | 1134.1 | 1134.9 | 1128.8 | 1135.1 | 1142.5 | 1129.7 | 1132.8 | 1261 | 1112 | 1253.7 | 1262.5 | 1251 | 1186.3 | 1113.8 | 1253 | 1102 | 1152.8 | 1151.6 | 1155.4 | 1266 | 1152.1 | 1268 | 1101 | 1119.7 | 1127.2 | 1280 | 1137.6 | 1198.4 | 1249.2 | 1270.7 | 1180 | 1223.5 | 1271.5 | 1160 | 1170 | 1176.1 | 1142 | 1090 | 1111 | 1123 | 1101 | 1096.2 | 1117.3 | 935.4 | 1124.3 |  |  | 1021 | 801 | 1141 |  | 1212.3 | 1121 | 1109.6 | 1121.7 | 1112 | 1106.1 | 1122.6 | 1121.4 | 1129.1 | 1119.5 | 1128.5 | 1109.4 | 1269.7 | 1298.3 | 970 | 960 | 833 | 688 | 871.5 | 1001.1 | 1149.8 | 1249.8 | 1198.4 | 1209.7 | 1155.5 | 1212 | 1243.4 | 1249.55 | 1101.1 | 1155.4 | 1103.3 | 1131 | 1058 |  | 1500.1 | 1223 | 421 | 1109 | 1071 |  |  | 1040 | 1101 | 1143 | 1071 | 1031 | 33.23 | 41.42 | 1.87 | 4.9 |  | 5.81 | 5.3 |  |  | 87494165.934 | 283487.115 | 60430998.241 | 63159.26 | 88205890.186 | 188727.198 | 64142279.414 | 58113.16 | 331376520.795 | 89443.315 | 76776.831 | 21.941 | 72636.894 | 29.884 | 75179.603 | 45.27 | 56847.544 | 56.544 | 281490.64 | 133.681 | 149361.9 | 281356.959 | 13.2167 | 5.81 | 5.3 | 33.23 | 41.42 | 1.87 | 4.9 | 282611.15
2025-06-23 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:12 | 18:30 | 1067 | 1053.4 | 978 | 973.1 | 1049.2 | 973.9 | 972.6 | 973.1 | 931.6 | 1013.1 | 981 | 986.2 | 981.1 | 891 | 968.2 | 967.8 | 965.5 | 998.2 | 1045.4 | 1043.8 | 969.2 | 972 | 1046.1 | 1099.5 | 1057.6 | 1048.3 | 1059.1 | 1088.1 | 1097.8 | 1091.2 | 1109 | 1010 | 935.2 | 1232 | 970.4 | 1071 | 976.7 | 991 | 981.2 | 977.9 | 962.4 | 989.9 | 999.1 | 994.6 | 975.4 | 979.4 | 951 | 959.1 | 1010 | 911 | 969.6 | 973 | 1090 | 1091.4 | 1034.1 | 1100 | 1099.5 | 969.9 | 1087.4 | 1104.4 | 976.1 | 1080 | 973.4 | 890 | 1052.3 | 1057.4 | 1044 | 1038.1 | 976 | 974.1 | 975.4 | 967.1 | 961 | 961 | 1080 | 1098.5 | 1078 | 982.9 | 973 | 1071.9 | 980.6 | 965.9 | 974 | 989 | 970.6 | 973.1 | 974.9 | 968.8 | 956.1 | 945.7 | 999.9 | 1017 | 955 | 958 | 1071 | 958.1 | 745 | 985.2 | 956 | 960 | 970 | 958 | 951 | 946.6 | 1080 | 951 | 1080 | 1079.4 | 951 | 1059 | 1045.2 | 1052.8 | 1070 | 1061 | 951 | 964 | 967 | 1090 | 1059 | 975.5 | 956 | 1039.6 | 1016.1 | 951 | 967 | 1089 | 940.1 | 964.1 | 1080 | 1046 | 1029 | 1019.3 | 1044.5 | 860 | 1020 | 1030.7 | 869.7 | 1029 | 990 | 934 | 1039.6 | 1020.4 | 962.4 | 1042 | 946.6 | 1044 | 965 | 876 | 1063.4 | 1060.6 | 1048 | 971.2 | 1081 | 962.4 | 974 | 962.2 | 965.1 | 953 | 959.3 | 949.1 | 1079.5 | 920.9 | 989.4 | 988.2 | 1049 | 994 | 940 | 992.6 | 940 | 965.2 | 991.6 | 968.6 | 1060 | 980 | 1076.2 | 954.1 | 941 | 944.3 | 1061.6 | 951 | 1020 | 1041 | 1071 | 990 | 1024.5 | 1072.7 | 971 | 990.9 | 920 | 1010 | 950.1 | 935.8 | 941 | 941.7 | 956.6 | 931 | 780 | 931 |  |  | 860 | 615.9 | 953.6 |  | 1065.3 | 943.5 | 901.3 | 941.3 | 959.6 | 967.8 | 977 | 976.1 | 941 | 974.1 | 977.6 | 941 | 1080 | 1100 | 830 | 819 | 698 | 591 | 741 | 867.2 | 1032.5 | 1101.1 | 1051.5 | 1064.8 | 1032.7 | 1072.6 | 1110.7 | 1092.6 | 941.6 | 981 | 929.9 | 941.6 | 876.6 |  | 1301 | 1020 | 372 | 934 | 902 |  |  | 943 | 950 | 964 | 898 | 861.2 | 30.76 | 41.42 | 1.21 | 6.5 |  | 4.95 | 4.58 |  |  | 87558522.716 | 283500.056 | 60492999.11 | 63189.144 | 88268514.617 | 188772.468 | 64192397.921 | 58169.704 | 331615308.592 | 89576.996 | 64356.782 | 12.941 | 62000.869 | 29.884 | 62624.431 | 45.27 | 50118.507 | 56.544 | 238787.797 | 133.681 | 126314.826 | 238654.116 | 13.3 | 4.95 | 4.58 | 30.76 | 41.42 | 1.21 | 6.5 | 239843.7
2025-06-24 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:11 | 18:31 | 1415.2 | 1450.2 | 1345.8 | 1327 | 1436.1 | 1338.3 | 1337.7 | 1344.2 | 1391 | 1399.9 | 1361 | 1358 | 1287 | 1265.8 | 1341.4 | 1340.6 | 1329.7 | 1326.7 | 1440.1 | 1439.8 | 1342.7 | 1348.9 | 1421.6 | 1516.6 | 1463.2 | 1450.4 | 1409.1 | 1493.2 | 1509.5 | 1455 | 1455.5 | 1451.1 | 1258 | 1698.7 | 1311.1 | 1478.2 | 1283.4 | 1292.2 | 1317 | 1329.6 | 1307.1 | 1302.5 | 1326.1 | 1316.9 | 1335.1 | 1340.9 | 1408.9 | 1314.3 | 1373.3 | 1355 | 1331.9 | 1330.5 | 1519.3 | 1499.2 | 1421.4 | 1504 | 1501.7 | 1337.2 | 1483.1 | 1503.5 | 1333.2 | 1504.5 | 1329.7 | 1289.3 | 1453.1 | 1440.1 | 1452.1 | 1406.3 | 1328.1 | 1325.7 | 1327 | 1317.3 | 1351.3 | 1322.1 | 1491.7 | 1460.2 | 1499.9 | 1329 | 1318.5 | 1446.5 | 1342.5 | 1346.7 | 1327.7 | 1340.7 | 1329.6 | 1334.8 | 1331.7 | 1329.9 | 1301.8 | 1293.8 | 1352.5 | 1401.2 | 1348.2 | 1300.7 | 1483.4 | 1310.7 | 1288 | 1347.9 | 1315.6 | 1334.9 | 1362.4 | 1323.6 | 1332.7 | 1310.1 | 1501.5 | 1297.5 | 1536.6 | 746.5 | 1345.2 | 1495.1 | 1447.14 | 1435.1 | 1490.1 | 1501 | 1348.1 | 1343.4 | 1446.5 | 1486.2 | 1488 | 1334.5 | 1352.7 | 1427.6 | 1395.65 | 1337.9 | 1309.2 | 1478.9 | 1311.4 | 1292.4 | 1485.5 | 1472.2 | 1410.1 | 1390.7 | 1415.7 | 1201.1 | 1442.6 | 1376.8 | 1423 | 1435.6 | 1382.7 | 1319 | 1410.2 | 1402.2 | 1315.2 | 1441.2 | 1283.5 | 1416.5 | 1291.9 | 1209 | 1414 | 1409.8 | 1440.6 | 1313.5 | 1479 | 1312.4 | 1289 | 1291.1 | 1282.6 | 1303.4 | 1327.1 | 1303.1 | 1478.9 | 1282.1 | 1446 | 1447.2 | 1454 | 1365.4 | 1292.7 | 1457.3 | 1288 | 1326.7 | 1367.3 | 1337.5 | 1444 | 1370.5 | 1480.3 | 1309 | 1311.6 | 1287.6 | 1455.7 | 1335.2 | 1389.1 | 1453.1 | 1441 | 1420 | 1431 | 1474.8 | 1371.5 | 1350 | 1333.8 | 1410 | 1318.3 | 1309.1 | 1278 | 1302.1 | 1311.9 | 1281.1 | 1103.2 | 1290 |  |  | 1176 | 921 | 1312 |  | 1431.4 | 1297.1 | 1303.8 | 1303.6 | 1325.6 | 1327.7 | 1335.9 | 1336.1 | 1333.8 | 1289.1 | 1325.2 | 1335 | 1490.3 | 1497.6 | 1144 | 1101 | 944 | 801 | 1024.2 | 1165.3 | 1384 | 1497.3 | 1428.5 | 1423.7 | 1395.5 | 1435.5 | 1489.8 | 1476.3 | 1245 | 1339.1 | 1242.5 | 1323.2 | 1229.1 |  | 1801 | 1401.2 | 524.5 | 1301 | 1243.5 |  |  | 1301 | 1277.2 | 1301 | 1243.3 | 1178.5 | 33.08 | 45.26 | 1.88 | 5.5 |  | 6.96 | 6.44 |  |  | 87646933.478 | 283502.997 | 60576457.037 | 63219.028 | 88355329.828 | 188817.738 | 64260621.588 | 58226.248 | 331941994.034 | 89710.677 | 88410.762 | 2.941 | 83457.927 | 29.884 | 86815.211 | 45.27 | 68223.667 | 56.544 | 326685.442 | 133.681 | 171835.864 | 326551.761 | 13.3333 | 6.96 | 6.44 | 33.08 | 45.26 | 1.88 | 5.5 | 329656.49
2025-06-25 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:11 | 18:50 | 1398.7 | 1401.2 | 1326.1 | 1324.9 | 1421.9 | 1318.4 | 1322.7 | 1301.2 | 1365.9 | 1368.9 | 1312.1 | 1309.6 | 1264.1 | 1190.2 | 1316.9 | 1315.5 | 1310 | 1304.2 | 1409.8 | 1416.2 | 1321.2 | 1321.7 | 1398.6 | 1488.3 | 1436.1 | 1418.6 | 1371.1 | 1464.9 | 1472 | 1421.2 | 1425.5 | 1417.5 | 1255.2 | 1623.1 | 1297.7 | 1463.2 | 1309.5 | 1281.4 | 1303 | 1324.7 | 1293.7 | 1282 | 1306.5 | 1295.7 | 1316.6 | 1318 | 1411.5 | 1300.5 | 1356.2 | 1313.5 | 1313.2 | 1311 | 1469.7 | 1477.9 | 1387.7 | 1467.2 | 1464.1 | 1299.7 | 1469.5 | 1464.6 | 1320.3 | 1461.8 | 1313.7 | 1258.7 | 1429.3 | 1417.1 | 1434.3 | 1391.9 | 1312.5 | 1307.3 | 1312.5 | 1299.7 | 1319.1 | 1312.7 | 1488 | 1457.3 | 1490 | 1314.5 | 1300.7 | 1435 | 1321 | 1301 | 1305.8 | 1322.1 | 1303.6 | 1310 | 1308.2 | 1305.5 | 1277.8 | 1267.4 | 1336.9 | 1376.5 | 1330.1 | 1291.1 | 1467.3 | 1299.4 | 1303.3 | 1326.6 | 1310.4 | 1317.8 | 1321.1 | 1302.9 | 1315.1 | 1301.2 | 1485.2 | 1290.1 | 1490.3 | 1414.2 | 1309.1 | 1468.2 | 1421.4 | 1420.5 | 1456.1 | 1466.2 | 1324.2 | 1267.2 | 1418.6 | 1457.8 | 1466.8 | 1316.6 | 1319.1 | 1405.6 | 1368.1 | 1316.6 | 1290.2 | 1467.1 | 1290.2 | 1293.3 | 1413.8 | 1448.1 | 1402.1 | 1389.4 | 1395.1 | 1203.3 | 1401.1 | 1374.2 | 1390.1 | 1413.2 | 1354.3 | 1272.2 | 1381.8 | 1371.8 | 1303.3 | 1401.1 | 1264.5 | 1392.8 | 1280.8 | 1197.7 | 1402.8 | 1414.8 | 1401.1 | 1298.2 | 1486.5 | 1299.1 | 1275.2 | 1272.8 | 1272.8 | 1298.9 | 1275.7 | 1251.6 | 1414.9 | 1254.6 | 1408 | 1399 | 1442.2 | 1317.3 | 1251.2 | 1431.5 | 1264.5 | 1313.5 | 1317.6 | 1313.01 | 1414.4 | 1331.4 | 1418.2 | 1261.8 | 1273.8 | 1269.5 | 1411.6 | 1284.7 | 1359.2 | 1403.4 | 1442.5 | 1362.2 | 1376.7 | 1418.8 | 1333.7 | 1330.4 | 1324 | 1355.6 | 1279.3 | 1251.7 | 1264.5 | 1264 | 1294.3 | 1267.9 | 1071.2 | 1290 |  |  | 1174.4 | 902 | 1302.4 |  | 1417.7 | 1272.1 | 1287.8 | 1271.1 | 1303.2 | 1309.1 | 1321 | 1322.8 | 1290.1 | 1271.5 | 1317.5 | 1290 | 1482.4 | 1516.8 | 1154 | 1123 | 967 | 789 | 1000 | 1142.2 | 1366.4 | 1463 | 1386 | 1386.5 | 1374.5 | 1394.5 | 1460.8 | 1431.4 | 1224 | 1321.2 | 1221 | 1268 | 1204.5 |  | 1789 | 1367.7 | 503 | 1276.6 | 1230.6 |  |  | 1261.4 | 1255 | 1313 | 1232.5 | 1190.6 | 33.46 | 42.64 | 3.12 | 7.5 |  | 6.57 | 6.18 |  |  | 87734214.23 | 283515.938 | 60659715.158 | 63240.912 | 88440708.476 | 188855.008 | 64327958.783 | 58275.792 | 332265085.404 | 89831.358 | 87280.752 | 12.941 | 83258.121 | 21.884 | 85378.648 | 37.27 | 67337.195 | 49.544 | 323091.37 | 120.681 | 170504.048 | 322970.689 | 13.65 | 6.57 | 6.18 | 33.46 | 42.64 | 3.12 | 7.5 | 324493.01
2025-06-26 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:14 | 18:40 | 1414 | 1423.1 | 1339.2 | 1335.9 | 1427.5 | 1328.1 | 1320.3 | 1325.6 | 1369.2 | 1373.8 | 1336.6 | 1327.7 | 1289.7 | 1212 | 1308.2 | 1306.2 | 1297.9 | 1291.9 | 1397.6 | 1402 | 1310 | 1312.6 | 1387.4 | 1471.9 | 1417.9 | 1401.3 | 1369.6 | 1444.2 | 1453.8 | 1444.2 | 1423.4 | 1434.8 | 1247.4 | 1674.5 | 1290.8 | 1452.6 | 1300.1 | 1271.6 | 1291.6 | 1314.8 | 1285.3 | 1273.3 | 1293.8 | 1283.1 | 1308.1 | 1315.1 | 1414.9 | 1292.6 | 1366.7 | 1321.3 | 1320.4 | 1317.4 | 1471.8 | 1478.3 | 1378.7 | 1471.2 | 1459.4 | 1316.7 | 1458.5 | 1474 | 1310.1 | 1479.9 | 1307.5 | 1268.2 | 1425.3 | 1411.3 | 1429.7 | 1396 | 1310.8 | 1303.7 | 1313.6 | 1303.1 | 1302.3 | 1301.1 | 1456.7 | 1433.4 | 1470.4 | 1301.1 | 1290.6 | 1413.5 | 1309.8 | 1315.4 | 1301.2 | 1314.9 | 1297.4 | 1307.1 | 1309.2 | 1309.7 | 1280.4 | 1273 | 1342.5 | 1381.6 | 1326.3 | 1313.5 | 1459.6 | 1290.4 | 1287.7 | 1320.7 | 1295.5 | 1307.9 | 1311.2 | 1289.7 | 1302.8 | 1286.7 | 1454.3 | 1221.5 | 1493 | 1435.5 | 1313.9 | 1455.2 | 1403.3 | 1416.3 | 1461.3 | 1467.5 | 1318.1 | 1271.1 | 1435.3 | 1431.2 | 1444.4 | 1310.2 | 1326.4 | 1401 | 1353.4 | 1304.7 | 1309.1 | 1467.8 | 1289.6 | 1288.4 | 1431.1 | 1448.3 | 1391.5 | 1391.7 | 1396.4 | 1202.4 | 1389.1 | 1373.2 | 1398.2 | 1401.2 | 1351.2 | 1300.2 | 1387.4 | 1381.1 | 1308.4 | 1425.6 | 1271.8 | 1396.6 | 1280.7 | 1194.7 | 1384.5 | 1403.8 | 1410.5 | 1285.1 | 1475.6 | 1289.9 | 1268.6 | 1278.1 | 1266.9 | 1290.1 | 1289.6 | 1271.1 | 1431.1 | 1265.7 | 1421.1 | 1434.2 | 1439.1 | 1321.1 | 1265.5 | 1451.1 | 1280 | 1355 | 1343 | 1331.4 | 1421.6 | 1341.1 | 1421 | 1271.1 | 1271.8 | 1291 | 1431.1 | 1301 | 1384.5 | 1421.5 | 1410.5 | 1371.1 | 1398.1 | 1434.7 | 1344 | 1344.1 | 1339.4 | 1371.1 | 1291.8 | 1285.4 | 1286.1 | 1289.5 | 1290 | 1278 | 1070 | 1301.1 |  |  | 1181 | 915.7 | 1302.7 |  | 1442.7 | 1285.9 | 1291.4 | 1281.6 | 1301 | 1295.8 | 1331.1 | 1323.1 | 1301.1 | 1290 | 1312 | 1324.9 | 1483.3 | 1516.9 | 1151 | 1133.6 | 974.5 | 799 | 999.3 | 1176 | 1371.6 | 1476.7 | 1411 | 1409.5 | 1371.1 | 1421.7 | 1497.2 | 1479.8 | 1241.2 | 1347.7 | 1233.8 | 1289.8 | 1190.9 |  | 1801 | 1376.6 | 513.2 | 1275.8 | 1232.5 |  |  | 1261 | 1278.6 | 1321.1 | 1225.8 | 1206.1 | 34.28 | 42.05 | 4.04 | 8.1 |  | 6.68 | 6.3 |  |  | 87821123.068 | 283528.879 | 60742286.209 | 63259.796 | 88526223.941 | 188889.278 | 64396685.26 | 58321.336 | 332588605.236 | 89948.039 | 86908.838 | 12.941 | 82571.051 | 18.884 | 85515.465 | 34.27 | 68726.477 | 45.544 | 323519.832 | 116.681 | 169448.064 | 323403.151 | 13.4333 | 6.68 | 6.3 | 34.28 | 42.05 | 4.04 | 8.1 | 325151.3
2025-06-27 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:48 | 18:41 | 1288.4 | 1291.1 | 1190 | 1201 | 1300 | 1197.5 | 1181.6 | 1198.1 | 1202.1 | 1210 | 1190.1 | 1198.7 | 1144.7 | 1060 | 1186.6 | 1191.1 | 1181 | 1179.5 | 1251.6 | 1254.1 | 1167.6 | 1171.8 | 1257.9 | 1301.1 | 1267.8 | 1265.6 | 1221.5 | 1322.8 | 1317.6 | 1269.9 | 1265.5 | 1277.1 | 1102.4 | 1456.6 | 1142.8 | 1275.5 | 1151.6 | 1130 | 1148.9 | 1172.7 | 1140.6 | 1133.1 | 1150.5 | 1140.3 | 1166.3 | 1170.6 | 1212 | 1156.3 | 1220 | 1167.8 | 1171.1 | 1173 | 1301.1 | 1313.7 | 1212 | 1301.2 | 1312.2 | 1179 | 1298.8 | 1305.6 | 1167.4 | 1311.4 | 1159.6 | 1101.5 | 1259 | 1265.8 | 1271.8 | 1251.4 | 1152.5 | 1154.6 | 1161.9 | 1171.7 | 1165.7 | 1163 | 1304.7 | 1287.1 | 1299.8 | 1170.8 | 1167.9 | 1262.8 | 1163.5 | 1157.6 | 1169.8 | 1173.2 | 1169.3 | 1158.8 | 1158.8 | 1154 | 1154.8 | 1142.9 | 1196.4 | 1226 | 1167 | 1165.6 | 1316.6 | 1171 | 764.7 | 1172.6 | 1170.3 | 1167.8 | 1162.5 | 1173.1 | 1181.2 | 1127.7 | 1305.2 | 1178.8 | 1314.8 | 1257.8 | 1171.8 | 1316.5 | 1272.9 | 1258.8 | 1305.8 | 1320.8 | 1152.2 | 1123 | 1254.1 | 1275.6 | 1282 | 1175.6 | 1187.8 | 1236.2 | 1227.5 | 1154.4 | 1163.9 | 1278 | 1154 | 1141 | 1267.1 | 1269 | 1218.2 | 1230.9 | 1233.8 | 1061.6 | 1230.2 | 1212 | 1225.7 | 1220 | 1179.7 | 1127.78 | 1232.5 | 1221.1 | 1128.5 | 1230.6 | 1131.1 | 1231.1 | 1131.1 | 1034.6 | 1231.5 | 1220.6 | 1226.2 | 1123.1 | 1282.9 | 1124.8 | 1131.1 | 1125.1 | 1145.5 | 1140.5 | 1140.9 | 1119.4 | 1263 | 1131.4 | 1252.9 | 1254.8 | 1281.4 | 1176.1 | 1129.6 | 1247.4 | 1133.3 | 1172.4 | 1174.1 | 1156.2 | 1263.2 | 1182.6 | 1254.1 | 1122.5 | 1133.4 | 1121.1 | 1251.5 | 1140.2 | 1212 | 1254.1 | 1264.5 | 1215.8 | 1226.7 | 1267.4 | 1182.8 | 1183.4 | 1197.9 | 1210 | 1132.1 | 1135.8 | 1121.1 | 1138.3 | 1131.1 | 1113.1 | 956.1 | 1124.1 |  |  | 0.1 | 806.7 | 1148.9 |  | 1278.1 | 1158.9 | 1171.1 | 1128.3 | 1171.1 | 1160.3 | 1167.7 | 1174.8 | 1154.8 | 1131.8 | 1151.2 | 1156.4 | 1322.2 | 1350.6 | 1024.1 | 1020 | 871.2 | 701.2 | 886.7 | 1041.3 | 1248.5 | 1326.3 | 1262 | 1267.9 | 1255.5 | 1285 | 1320.3 | 1299 | 1091.1 | 1187.2 | 1101 | 1141.5 | 1051.7 |  | 1621.5 | 1221.1 | 435.8 | 1132.1 | 1091.6 |  |  | 1121.1 | 1142.6 | 1181.7 | 1121 | 1055.1 | 31.5 | 41.46 | 2.01 | 6.7 |  | 6.01 | 5.64 |  |  | 87898891.252 | 283537.82 | 60816362.773 | 63272.68 | 88601459.192 | 188919.548 | 64456309.176 | 58361.88 | 332875063.14 | 90053.72 | 77768.184 | 8.941 | 74076.564 | 12.884 | 75235.251 | 30.27 | 59623.916 | 40.544 | 286457.904 | 105.681 | 151822.923 | 286352.223 | 12.8833 | 6.01 | 5.64 | 31.5 | 41.46 | 2.01 | 6.7 | 287351.88
2025-06-28 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:26 | 18:29 | 1049.2 | 1069.3 | 961.1 | 963.7 | 1068 | 984 | 990.6 | 990.6 | 1019.1 | 1024.2 | 968.8 | 997.9 | 939.4 | 878.1 | 983.3 | 974.1 | 977.7 | 976.2 | 1052.4 | 1055.7 | 951.1 | 959.8 | 1026.3 | 1093.9 | 1034.6 | 1048.5 | 1013.2 | 1069.1 | 1078.9 | 1063.2 | 1071.1 | 1051.2 | 902.1 | 1201.2 | 971.2 | 1050 | 971.2 | 966 | 871 | 974.5 | 976 | 972.6 | 971.2 | 965.6 | 961.2 | 956.8 | 1030 | 967.8 | 996.8 | 972.9 | 971.2 | 974.8 | 1093.2 | 1098.7 | 1023 | 1100.1 | 1103.6 | 872.2 | 1076.7 | 1091.2 | 991.7 | 1055 | 985.6 | 902 | 1060.5 | 1041.2 | 1056.2 | 1042.6 | 973.6 | 963.7 | 967 | 981.1 | 969.4 | 955.7 | 1072.7 | 1081.1 | 1090.7 | 969.8 | 973.3 | 1061 | 957.8 | 971.2 | 979.2 | 966.9 | 980.2 | 966.2 | 956.2 | 978.3 | 970.4 | 957.2 | 997 | 1018.6 | 961.2 | 854 | 1100.8 | 974.7 | 0 | 972.1 | 958 | 954.2 | 964.6 | 951.6 | 959.4 | 950.3 | 1071 | 967 | 1083.7 | 1051.3 | 939.9 | 1105 | 1032 | 1019.2 | 1057.9 | 1071.5 | 966.9 | 956.1 | 1061.2 | 1054 | 1069.9 | 954.2 | 967.2 | 999 | 1005 | 956 | 941 | 1059 | 956 | 946 | 1090 | 1080.4 | 957.1 | 1047.2 | 1062 | 905 | 1066.5 | 1019.5 | 1065.3 | 1060.3 | 1026.7 | 876.1 | 1049.5 | 1026.7 | 980 | 1074.1 | 952.1 | 1052.3 | 964 | 903.2 | 1045.5 | 1057.4 | 1056.8 | 957.8 | 1074.2 | 948.7 | 945.7 | 950 | 967.6 | 987.5 | 967.9 | 940.5 | 1082.9 | 928 | 1050.5 | 1044.5 | 1080.9 | 983.9 | 942.8 | 1045.1 | 934.3 | 960 | 989.2 | 969.4 | 1052.6 | 893.2 | 1068.2 | 959.2 | 975 | 964.8 | 1071.4 | 956 | 1012 | 1056.2 | 1050.2 | 1010 | 1021.1 | 1081.6 | 978 | 990 | 962.9 | 932.5 | 945.4 | 967.1 | 959.2 | 971.5 | 955.9 | 945 | 795.5 | 949.5 |  |  | 0 | 681.2 | 958.8 |  | 1034 | 971.1 | 956 | 959.1 | 857.8 | 981.2 | 966.3 | 974.1 | 946.8 | 956.8 | 948.3 | 949 | 1062.5 | 1143 | 851 | 841 | 721 | 590 | 741.7 | 849.6 | 1006.4 | 1077.4 | 1014.5 | 1015.6 | 1021.5 | 1034.5 | 1068.2 | 1078.1 | 931.1 | 1012.2 | 909 | 948.6 | 878.9 |  | 1345 | 1021 | 362.5 | 934 | 912 |  |  | 901 | 956 | 978 | 907.7 | 871 | 30.91 | 41.13 | 1.51 | 9.7 |  | 5.07 | 4.65 |  |  | 87963945.817 | 283546.761 | 60876406.429 | 63285.564 | 88665002.114 | 188949.818 | 64504361.702 | 58402.424 | 333111507.545 | 90159.401 | 65054.565 | 8.941 | 60043.656 | 12.884 | 63542.922 | 30.27 | 48052.526 | 40.544 | 236444.405 | 105.681 | 125076.396 | 236338.724 | 13.05 | 5.07 | 4.65 | 30.91 | 41.13 | 1.51 | 9.7 | 238197.7
2025-06-29 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:18 | 18:29 | 913 | 932 | 862 | 859 | 928 | 857 | 861 | 864 | 892 | 896 | 856 | 839.8 | 839 | 807 | 859 | 851.2 | 852 | 851 | 925 | 928 | 849 | 862 | 908 | 969 | 901 | 929 | 902 | 958 | 966 | 944.2 | 952 | 917.2 | 801 | 1072.2 | 849 | 958 | 856 | 829 | 844 | 860 | 836 | 834.1 | 846 | 819.2 | 853 | 856 | 901 | 846 | 882 | 861.2 | 850 | 854 | 973 | 961 | 914.7 | 954.5 | 961.2 | 846.7 | 960 | 933.4 | 856 | 972 | 865 | 788 | 923 | 919 | 928 | 894 | 845 | 848 | 852 | 838 | 839 | 847 | 965 | 953 | 967 | 849 | 845 | 930 | 854 | 860 | 846 | 852 | 838 | 848 | 840 | 843 | 839.8 | 834.2 | 879.2 | 901 | 858 | 831.2 | 948 | 844 | 0 | 847 | 852 | 839 | 833 | 855 | 836 | 852 | 965 | 841 | 983 | 952.6 | 843 | 957 | 921 | 921 | 934.3 | 927.7 | 860 | 836.8 | 945.2 | 931 | 951 | 853 | 834.7 | 899 | 883 | 854 | 828.8 | 958 | 832.3 | 839.7 | 932.5 | 955.7 | 902.7 | 916.6 | 922.6 | 766 | 899 | 900.3 | 892.8 | 903 | 871 | 861 | 919.1 | 905 | 846 | 942.1 | 831.1 | 925.5 | 848.1 | 788 | 921 | 944.2 | 934.1 | 865 | 951.2 | 845 | 852.3 | 840.8 | 856 | 871.2 | 848 | 828 | 944 | 818 | 935 | 922 | 952 | 869 | 826 | 896 | 835.4 | 851.2 | 864 | 865.9 | 939 | 820 | 929.7 | 834 | 846 | 824 | 926 | 845 | 912.7 | 931 | 927 | 872 | 892.7 | 952 | 871.2 | 865.7 | 864.2 | 902 | 821 | 834.2 | 842.7 | 835 | 834 | 829 | 689 | 823 |  |  | 0 | 601 | 856 |  | 926.5 | 849 | 845.7 | 839.7 | 840.9 | 843.7 | 836 | 848.7 | 839.7 | 846.5 | 852 | 832.2 | 961.1 | 1001 | 752.2 | 739 | 629 | 534 | 645 | 750 | 865 | 958 | 901 | 900 | 898 | 934 | 955 | 937.4 | 801 | 866 | 809 | 842.3 | 782.2 |  | 1171.2 | 909.6 | 322 | 835 | 803 |  |  | 788 | 851 | 845 | 809 | 759.7 | 30.09 | 37.22 | 2.43 | 9.3 |  | 4.19 | 3.89 |  |  | 88020668.84 | 283555.702 | 60929965.521 | 63298.448 | 88720828.316 | 188980.088 | 64547622.07 | 58442.968 | 333320660.333 | 90265.082 | 56723.023 | 8.941 | 53559.092 | 12.884 | 55826.202 | 30.27 | 43260.368 | 40.544 | 209152.788 | 105.681 | 110260.29 | 209047.107 | 13.1833 | 4.19 | 3.89 | 30.09 | 37.22 | 2.43 | 9.3 | 210024.2
2025-06-30 | 2026 | 2025 |  |  | Jun-25 | 30 | 66750 | 5:20 | 18:23 | 739 | 732 | 677 | 673 | 728 | 674 | 677 | 679 | 701 | 704 | 691 | 686 | 681 | 634 | 674 | 673 | 670 | 666 | 730 | 727 | 674 | 676 | 729 | 763 | 733 | 726 | 735 | 755 | 758 | 761 | 759 | 753 | 649 | 864 | 662 | 744 | 673 | 664 | 652 | 672 | 673 | 656 | 687 | 676 | 684 | 673 | 682 | 675.8 | 661 | 659 | 664 | 678 | 751 | 764 | 723 | 763 | 765 | 680 | 756 | 766 | 670 | 768 | 673 | 624 | 727 | 724 | 728 | 734 | 662 | 664 | 674 | 671 | 683 | 679 | 767.8 | 751 | 762 | 669 | 674.7 | 731 | 668 | 673 | 663 | 669 | 674 | 655 | 681 | 655 | 656 | 666 | 681.2 | 723 | 667 | 634 | 756 | 662 | 47.5 | 676 | 683 | 672 | 657.8 | 684.7 | 657.9 | 667 | 755 | 648 | 763.3 | 739 | 671 | 756 | 727 | 743 | 756 | 758 | 672 | 673 | 752 | 732 | 755 | 673 | 654.6 | 708 | 727 | 668 | 669 | 754 | 674 | 684 | 721 | 771 | 739 | 745 | 739 | 612 | 722 | 721 | 711 | 729 | 703 | 682 | 718.6 | 715 | 683 | 709 | 682 | 711.2 | 665.1 | 619.3 | 739 | 734 | 738.9 | 678.2 | 761.2 | 679.3 | 668.7 | 684 | 670 | 685 | 661 | 669.7 | 737 | 649 | 754 | 727 | 731 | 676 | 674 | 701 | 651 | 681 | 698 | 679 | 739 | 668 | 739 | 652.6 | 654 | 654.8 | 724 | 651 | 724 | 731 | 724 | 672.9 | 711 | 736 | 692 | 694 | 645 | 701 | 656.8 | 645 | 656 | 652 | 655 | 658.4 | 544 | 660 |  |  | 0 | 463.6 | 656 |  | 728 | 682 | 653.2 | 654 | 685 | 667 | 668 | 658.1 | 670 | 656.5 | 665 | 661 | 759 | 774 | 587 | 573 | 494 | 414 | 504 | 595 | 704 | 761 | 732 | 721 | 713 | 739 | 759 | 755 | 639 | 676 | 643 | 666 | 612 |  | 934 | 709 | 252 | 661 | 634 |  |  | 639 | 678 | 684 | 636 | 601 | 29.64 | 35.33 | 1.69 | 4.3 |  | 3.23 | 3.03 |  |  | 88065461.3 | 283564.643 | 60972342.552 | 63311.332 | 88764796.416 | 189003.358 | 64582109.651 | 58471.512 | 333486061.493 | 90360.763 | 44792.46 | 8.941 | 42377.031 | 12.884 | 43968.1 | 23.27 | 34487.581 | 28.544 | 165401.16 | 95.681 | 87147.666 | 165305.479 | 13.05 | 3.23 | 3.03 | 29.64 | 35.33 | 1.69 | 4.3 | 166212.4
Formulas:
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 12 | 0 |  | 0 |  | 35.4677 | 50.0389 | 2.5105 | 5.7 | [9 empty] | 0 |  |  |  | 66.75 | 6.6839 | 346441.9355 | 77.65% | 21.62% | 99.5% | 99.5%
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 12 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 100% |  |  | 100% |  |  |  |  | 21.45% | 0 | 343623.8886 | 61.9293 | 343561.9593 | 66.75 | 6.6839 | 346441.9355 | 77.65% | 21.62% | 99.5% | 99.5% | [9 empty] | 66.755
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 12 | 0 |  | 7.31 |  | 30.32 | 40.28 | 1.71 | 6.3 | 100% |  |  | 100% |  |  | 70.41% |  | 21.45% | 364093.2 | 343623.8886 | 61.9293 | 343561.9593 | 66.75 | 6.6839 | 346441.9355 | 77.65% | 21.62% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.18 |  | 25.08 | 40.95 | 1.76 | 5.3 | 99.99% |  |  | 100% |  |  | 71.69% |  | 21.45% | 354559 | 343623.8886 | 61.9293 | 343561.9593 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.87 |  | 26.5 | 39.7 | 1.9 | 5.9 | 99.79% |  |  | 100% |  |  | 72.98% |  | 20.89% | 341179 | 334708.37 | 58.016 | 334650.354 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 0 |  | 25.78 | 32 | 2.63 | 5.3 | 99.56% |  |  | 100% |  |  |  |  | 18.92% | 305040 | 303117.53 | 59.618 | 303057.912 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.1 |  | 35.1 | 50.1 | 1.5 | 4.3 | 100% |  |  | 100% |  |  | 77.97% |  | 19.82% | 318035 | 317553.665 | 61.857 | 317491.808 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.9 |  | 37.8 | 58.63 | 1.48 | 7.5 | 100% |  |  | 100% |  |  | 84.59% |  | 20.79% | 336772.2 | 333180.32 | 55.638 | 333124.682 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.92 |  | 39.3 | 47.4 | 1.2 | 5.33 | 100% |  |  | 100% |  |  | 71.24% |  | 20.54% | 331522.2 | 329112.576 | 55.361 | 329057.215 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.5257 |  | 41.9 | 51.1 | 1.1 | 3.13 | 99.98% |  |  | 100% |  |  | 72.85% |  | 19.81% | 324271 | 317387.001 | 54.398 | 317332.603 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.0578 |  | 43.9 | 51.1 | 1.1 | 3.13 | 99.72% |  |  | 100% |  |  | 73.87% |  | 18.65% | 315636 | 298762.742 | 57.574 | 298705.168 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.6268 |  | 39.9 | 50.1 | 1.1 | 3.4 | 100% |  |  | 100% |  |  | 75.08% |  | 17.6% | 289705 | 282018.859 | 38.081 | 281980.778 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 4.36 |  | 34.9 | 49 | 3 | 5 | 99.96% |  |  | 100% |  |  | 75.19% |  | 13.66% | 223694 | 218866.4 | 30.36 | 218836.04 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 4.88 |  | 36.6 | 55.86 | 2.52 | 13.1 | 100% |  |  | 100% |  |  | 78.29% |  | 15.92% | 257651 | 255074.896 | 62.053 | 255012.843 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.15 |  | 29.88 | 43.21 | 1.3 | 6.1 | 99.74% |  |  | 100% |  |  | 77.44% |  | 19.84% | 321089 | 317952.483 | 55.075 | 317897.408 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.14 |  | 31.82 | 40.8 | 3.02 | 7.1 | 99.85% |  |  | 100% |  |  | 81.2% |  | 20.77% | 335292 | 332864.4 | 60.962 | 332803.438 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.51 |  | 32.37 | 45.01 | 1.79 | 6.1 | 99.73% |  |  | 100% |  |  | 76.08% |  | 20.64% | 333086 | 330638.835 | 55.409 | 330583.426 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.23 |  | 32.7 | 43.6 | 1.6 | 6.5 | 99.99% |  |  | 100% |  |  | 76.67% |  | 19.9% | 326506 | 318888.957 | 53.177 | 318835.78 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.27 |  | 34.09 | 46.02 | 1.33 | 6.1 | 100% |  |  | 100% |  |  | 76.29% |  | 19.93% | 323020 | 319338.93 | 54.629 | 319284.301 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.11 |  | 35.7 | 46 | 0.6 | 6.78 | 100% |  |  | 100% |  |  | 75.56% |  | 19.24% | 314197 | 308209.27 | 60.571 | 308148.699 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.95 |  | 35.61 | 47.4 | 1.3 | 5.1 | 100% |  |  | 100% |  |  | 75.62% |  | 18.75% | 305558 | 300377.401 | 57.568 | 300319.833 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.87 |  | 35.4 | 46.4 | 1.2 | 5.3 | 99.63% |  |  | 100% |  |  | 75.46% | 0% | 18.46% | 312642 | 295745.199 | 72.432 | 295672.767 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.7 |  | 35.9 | 47.6 | 1.6 | 5.1 | 100% |  |  | 100% |  |  | 72.02% |  | 20.11% | 327345 | 322154.968 | 55.847 | 322099.121 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.75 |  | 37.4 | 47.37 | 2.08 | 5.4 | 99.65% |  |  | 100% |  |  | 71.15% |  | 20.01% | 328589 | 320631.049 | 59.061 | 320571.988 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.08 |  | 37.9 | 46.08 | 1.93 | 5.1 | 99.68% |  |  | 100% |  |  | 72.39% |  | 21.36% | 347261 | 342184.731 | 53.875 | 342130.856 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.22 |  | 38 | 46.1 | 2 | 5.3 | 99.68% |  |  | 100% |  |  | 72.85% |  | 21.92% | 355743 | 351160.163 | 54.826 | 351105.337 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.18 |  | 36.5 | 45.1 | 2.47 | 8.3 | 99.54% |  |  | 100% |  |  | 72.38% |  | 21.65% | 351420 | 346943.965 | 58.132 | 346885.833 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 7.1 |  | 37.08 | 47.02 | 1.4 | 6.5 | 99.47% |  |  | 100% |  |  | 69.54% |  | 20.57% | 335649 | 329619.258 | 51.72 | 329567.538 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.34 |  | 36.9 | 43.37 | 1.8 | 9.9 | 100% |  |  | 100% |  |  | 73.1% |  | 16.27% | 266123 | 260616.1 | 41.865 | 260574.235 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 5.5 |  | 38 | 45.8 | 1.9 | 6.1 | 94.93% |  |  | 100% |  |  | 73.17% |  | 16.77% | 274076 | 268672.384 | 58.871 | 268613.513 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.2 |  | 38.9724 | 45.8338 | 2.2649 | 5.9 | 99.92% |  |  | 100% |  |  | 73.78% |  | 19.06% | 306127.9 | 305402.761 | 61 | 305341.761 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.38 |  | 40 | 46 | 2.1 | 5.1 | 99.9% |  |  | 100% |  |  | 73.79% |  | 19.62% | 316090 | 314307.9307 | 54.003 | 314253.9277 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 12 | 0 |  | 6.29 |  | 35.51 | 43.47 | 2.54 | 6.7 | 99.9% |  |  | 100% |  |  | 73.11% |  | 19.16% | 308834.9 | 307007.4493 | 43.615 | 306963.8343 | 66.75 | 6.8867 | 349842.0895 | 76.1% | 21.84% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 6.3 |  | 34.64 | 42.7 | 3.78 | 7.5 | 100% |  |  | 100% |  |  | 70.46% |  | 18.5% | 298175.2 | 296343.885 | 22.985 | 296320.9 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 4.16 |  | 26.59 | 33.02 | 3.03 | 7.7 | 99.95% |  |  | 100% |  |  | 75.68% |  | 13.12% | 211112 | 210230.583 | 81.52 | 210149.063 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 5.85 |  | 27 | 31 | 3.1 | 5.9 | 99.84% |  |  | 100% |  |  | 74.98% |  | 18.28% | 293330 | 292856.136 | 59.17 | 292796.966 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 6.49 |  | 33.65 | 43.22 | 1.9 | 7.5 | 99.87% |  |  | 100% |  |  | 74.05% |  | 20.02% | 322757 | 320844.417 | 64.162 | 320780.255 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 12 | 0 |  | 4.14 |  | 27.91 | 34.01 | 2.69 | 9.1 | 99.71% |  |  | 100% |  |  | 76.47% |  | 13.19% | 212087.7 | 211396.792 | 63.762 | 211333.03 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 12.25 | 0 |  | 6.31 |  | 30.59 | 43.32 | 1.89 | 5.1 | 99.57% |  |  | 100% |  |  | 75.86% |  | 19.95% | 321279.5 | 319633.678 | 103.308 | 319530.37 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 12.5667 | 0 |  | 5.46 |  | 26.11 | 40.91 | 2.1 | 4.9 | 73.28% |  |  | 100% |  |  | 55.99% |  | 12.74% | 213164.2 | 204058.977 | 2.116 | 204056.861 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 12.45 | 0 |  | 6.54 |  | 31.23 | 40.22 | 2.05 | 7.9 | 98.05% |  |  | 100% |  |  | 69.67% |  | 18.99% | 302578 | 304228.486 | 66.532 | 304161.954 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 12.15 | 0 |  | 6.68 |  | 32.39 | 43.99 | 1.81 | 7.1 | 99.59% |  |  | 100% |  |  | 73.52% |  | 20.46% | 328786 | 327888.986 | 53.566 | 327835.42 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 12.0833 | 0 |  | 5.78 |  | 29.02 | 40.1 | 1.6 | 5.4 | 99.62% |  |  | 100% |  |  | 73.67% |  | 17.74% | 283650.6625 | 284293.991 | 47.886 | 284246.105 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 12.45 | 0 |  | 6.7 |  | 31.8 | 43.4 | 1.5 | 4.8 | 99.89% |  |  | 100% |  |  | 75.16% |  | 20.98% | 338732 | 336183.752 | 63.231 | 336120.521 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 12.3167 | 0 |  | 6.85 |  | 35.13 | 43.88 | 1.88 | 7.3 | 99.98% |  |  | 100% |  |  | 75.16% |  | 21.45% | 345699 | 343701.784 | 61.428 | 343640.356 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 12.45 | 0 |  | 5.73 |  | 34.36 | 42.16 | 1.65 | 11.7 | 99.49% |  |  | 100% |  |  | 75.05% |  | 17.92% | 286967.7 | 287098.603 | 65.958 | 287032.645 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 12.9167 | 0 |  | 6.95 |  | 38.2 | 45.38 | 2.6 | 7.1 | 99.64% |  |  | 100% |  |  | 75.03% |  | 21.73% | 201945 | 348122.386 | 66.671 | 348055.715 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 12.9 | 0 |  | 6.81 |  | 38.52 | 46.82 | 2.05 | 5.8 | 99.94% |  |  | 100% |  |  | 74.49% |  | 21.14% | 334705.4 | 338665.544 | 60.012 | 338605.532 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 13.15 | 0 |  | 5.56 |  | 37.78 | 42.3 | 2.3 | 11.3 | 99.97% |  |  | 100% |  |  | 75.32% |  | 17.45% | 292468 | 279612.765 | 60.495 | 279552.27 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 12.9667 | 0 |  | 4.84 |  | 34.4 | 42 | 2.7 | 19.29 | 99.96% |  |  | 100% |  |  | 76.27% |  | 15.38% | 254893 | 246466.213 | 72.164 | 246394.049 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 13.15 | 0 |  | 6.4 |  | 32.3 | 41.68 | 1.14 | 4.7 | 99.66% |  |  | 100% |  |  | 76.6% |  | 20.43% | 332920 | 327298.332 | 54.8 | 327243.532 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 13.2167 | 0 |  | 6.27 |  | 36.2 | 40 | 1.1 | 4.2 | 99.62% |  |  | 100% |  |  | 77.25% |  | 20.18% | 324288 | 323348.624 | 55.371 | 323293.253 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 13.2 | 0 |  | 6.27 |  | 36.2 | 38.23 | 1.3 | 6.3 | 99.94% |  |  | 100% |  |  | 76.72% |  | 20.04% | 323147 | 321187.681 | 90.846 | 321096.835 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 13.1833 | 0 |  | 5.79 |  | 35.5 | 28 | 1.1 | 4.3 | 99.99% |  |  | 100% |  |  | 76.26% |  | 18.4% | 297837.6 | 294810.933 | 87.974 | 294722.959 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 13.2167 | 6.88 |  | 6.41 |  | 33.8 | 43.42 | 3.64 | 8.3 | 99.96% |  |  | 100% |  |  | 75.84% |  | 20.26% | 327534.8 | 324586.013 | 90.849 | 324495.164 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 13.2667 | 6.9 |  | 6.38 |  | 34.93 | 46.23 | 3.32 | 7.1 | 99.98% |  |  | 100% |  |  | 75.88% |  | 20.17% | 326090.97 | 323230.815 | 100.849 | 323129.966 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 13.2333 | 6.17 |  | 5.67 |  | 35.89 | 44.51 | 4.63 | 7.7 | 99.77% |  |  | 100% |  |  | 76.14% |  | 17.99% | 290997.7 | 288274.486 | 120.849 | 288153.637 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 12.7667 | 6.76 |  | 6.25 |  | 36.28 | 44.75 | 2.4 | 6.5 | 99.87% |  |  | 100% |  |  | 79.48% |  | 20.7% | 333824.3 | 331724.974 | 160.849 | 331564.125 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 13.2833 | 5.25 |  | 4.81 |  | 32.47 | 39.01 | 3.18 | 8.3 | 99.66% |  |  | 100% |  |  | 79.8% |  | 15.99% | 258237.06 | 256383.486 | 160.849 | 256222.637 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 13.35 | 6.45 |  | 5.98 |  | 34.17 | 39.27 | 1.95 | 5.7 | 99.93% |  |  | 100% |  |  | 77.18% |  | 19.23% | 311840.2 | 308223.809 | 158.849 | 308064.96 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 13.4167 | 6.79 |  | 6.28 |  | 36.79 | 48.09 | 1.97 | 4.9 | 65.94% |  |  | 100% |  |  | 50.45% |  | 13.2% | 212537.6 | 211625.783 | 159.849 | 211465.934 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 13.1667 | 5.38 |  | 4.87 |  | 35.73 | 41.95 | 2.07 | 9.69 | 86.27% |  |  | 100% |  |  | 66.65% |  | 13.53% | 218430.9 | 216832.746 | 161.849 | 216670.897 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 13.0167 | 5.85 |  | 5.34 |  | 36.45 | 45.55 | 2.33 | 7.9 | 100% |  |  | 100% |  |  | 77.05% |  | 17.14% | 277904.9 | 274797.158 | 161.849 | 274635.309 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 13.1833 | 5.3 |  | 4.85 |  | 33.5 | 42 | 3.1 | 8.3 | 99.72% |  |  | 100% |  |  | 76.48% |  | 15.46% | 251303.79 | 247759.346 | 159.812 | 247599.534 | 66.75 | 6.1839 | 312542.4771 | 75.71% | 19.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 13.3167 | 4.91 |  | 4.4 |  | 31.9 | 40.8 | 3.4 | 6.2 | 99.77% |  |  | 100% |  |  | 77.97% |  | 14.29% | 229035.1 | 229145.811 | 156.812 | 228988.999 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 12.6833 | 5.82 |  | 5.25 |  | 32.2 | 41.3 | 3.2 | 4.8 | 94.53% |  |  | 100% |  |  | 73.47% |  | 16.07% | 259288.99 | 257628.344 | 156.812 | 257471.532 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 13.2333 | 5.12 |  | 4.62 |  | 32.1 | 40.8 | 2.8 | 7.1 | 94.13% |  |  | 100% |  |  | 74.85% |  | 14.41% | 231929.06 | 230994.357 | 156.812 | 230837.545 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 13.3833 | 5.74 |  | 5.18 |  | 36.4 | 48 | 3.1 | 6.3 | 99.5% |  |  | 100% |  |  | 78.8% |  | 17.01% | 273632.5 | 272636.06 | 156.812 | 272479.248 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 13.5 | 6.7 |  | 6.3 |  | 36.8 | 52.03 | 3.2 | 8.3 | 95.71% |  |  | 100% |  |  | 74.99% |  | 19.69% | 317965 | 315512.697 | 154.875 | 315357.822 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 13.45 | 6.6 |  | 6.32 |  | 30.8 | 50.3 | 31.1 | 8.5 | 100% |  |  | 100% |  |  | 75.41% |  | 19.86% | 319248 | 318269.456 | 156.271 | 318113.185 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 13.4833 | 6.98 |  | 6.78 |  | 31.9 | 52.8 | 3.9 | 6.4 | 99.74% |  |  | 100% |  |  | 74.75% |  | 21.12% | 340883 | 338445.266 | 155.681 | 338289.585 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 13.4667 | 6.9 |  | 6.38 |  | 38.8 | 45.5 | 1.23 | 6.3 | 99.89% |  |  | 100% |  |  | 77.59% |  | 20.63% | 332985.59 | 330587.652 | 155.681 | 330431.971 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 13.4667 | 7.2 |  | 6.66 |  | 40.38 | 45.99 | 2.41 | 7.7 | 99.85% |  |  | 100% |  |  | 75.64% |  | 20.99% | 338140.4 | 336393.986 | 146.681 | 336247.305 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 13.4833 | 7.54 |  | 7.03 |  | 41.33 | 46.5 | 3.21 | 8.7 | 99.96% |  |  | 100% |  |  | 76.27% |  | 22.34% | 359956.5 | 358052.207 | 146.681 | 357905.526 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 13.45 | 7.17 |  | 6.59 |  | 40.35 | 47.76 | 2.22 | 5.5 | 100% |  |  | 100% |  |  | 76.48% |  | 21% | 338030.77 | 336579.164 | 146.681 | 336432.483 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 13.4333 | 6.58 |  | 6.05 |  | 39.97 | 49.84 | 2.3 | 5.5 | 100% |  |  | 100% |  |  | 76.02% |  | 19.16% | 309854.97 | 307152.908 | 146.681 | 307006.227 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 11.3833 | 5.96 |  | 5.45 |  | 39.42 | 48.96 | 3.4 | 12.9 | 100% |  |  | 100% |  |  | 76.09% |  | 17.28% | 279024.1 | 276945.719 | 146.681 | 276799.038 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 13.5833 | 6.54 |  | 6.01 |  | 37.79 | 49.04 | 1.63 | 4.9 | 99.99% |  |  | 100% |  |  | 76.05% |  | 19.04% | 307007.4 | 305232.082 | 146.681 | 305085.401 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 13.2333 | 4.87 |  | 4.49 |  | 34.83 | 42.57 | 3.24 | 10.7 | 99.78% |  |  | 100% |  |  | 76.17% |  | 14.25% | 229066.5 | 228426.298 | 146.681 | 228279.617 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 11.6667 | 6.29 |  | 5.78 |  | 32.82 | 40.29 | 3.89 | 8.5 | 99.58% |  |  | 100% |  |  | 78.46% |  | 18.89% | 303505.1 | 302835.605 | 143.681 | 302691.924 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 10.8833 | 4.44 |  | 3.98 |  | 33.67 | 42.05 | 2.77 | 8.9 | 100% |  |  | 100% |  |  | 79.43% |  | 13.17% | 212042.5 | 211172.845 | 143.681 | 211029.164 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 13.4667 | 5.32 |  | 4.96 |  | 31.72 | 42.78 | 1.64 | 5.1 | 99.56% |  |  | 100% |  |  | 78.39% |  | 16.2% | 261299.05 | 259670.743 | 135.681 | 259535.062 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 12.4333 | 4.53 |  | 4.17 |  | 30.22 | 39.34 | 3.06 | 9.5 | 99.98% |  |  | 100% |  |  | 81.17% |  | 14.1% | 227578.3 | 226079.287 | 135.681 | 225943.606 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 13.25 | 2.53 |  | 2.4 |  | 28.91 | 32.29 | 0.946 | 5.7 | 96.01% |  |  | 100% |  |  | 79.62% |  | 7.962% | 128207.03 | 127693.287 | 135.681 | 127557.606 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 13.5 | 5.62 |  | 5.19 |  | 31.15 | 42.22 | 1.35 | 6.1 | 98.93% |  |  | 100% |  |  | 76.07% |  | 16.45% | 264314.4 | 263653.358 | 133.681 | 263519.677 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 13.2167 | 5.81 |  | 5.3 |  | 33.23 | 41.42 | 1.87 | 4.9 | 99.87% |  |  | 100% |  |  | 79.53% |  | 17.56% | 282611.15 | 281490.64 | 133.681 | 281356.959 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 13.3 | 4.95 |  | 4.58 |  | 30.76 | 41.42 | 1.21 | 6.5 | 99.31% |  |  | 100% |  |  | 78.06% |  | 14.9% | 239843.7 | 238787.797 | 133.681 | 238654.116 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 13.3333 | 6.96 |  | 6.44 |  | 33.08 | 45.26 | 1.88 | 5.5 | 99.71% |  |  | 100% |  |  | 75.97% |  | 20.38% | 329656.49 | 326685.442 | 133.681 | 326551.761 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 13.65 | 6.57 |  | 6.18 |  | 33.46 | 42.64 | 3.12 | 7.5 | 99.86% |  |  | 100% |  |  | 78.29% |  | 20.16% | 324493.01 | 323091.37 | 120.681 | 322970.689 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 13.4333 | 6.68 |  | 6.3 |  | 34.28 | 42.05 | 4.04 | 8.1 | 99.96% |  |  | 100% |  |  | 76.9% |  | 20.19% | 325151.3 | 323519.832 | 116.681 | 323403.151 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 12.8833 | 6.01 |  | 5.64 |  | 31.5 | 41.46 | 2.01 | 6.7 | 99.37% |  |  | 100% |  |  | 76.06% |  | 17.87% | 287351.88 | 286457.904 | 105.681 | 286352.223 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 13.05 | 5.07 |  | 4.65 |  | 30.91 | 41.13 | 1.51 | 9.7 | 99.06% |  |  | 100% |  |  | 76.14% |  | 14.75% | 238197.7 | 236444.405 | 105.681 | 236338.724 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 13.1833 | 4.19 |  | 3.89 |  | 30.09 | 37.22 | 2.43 | 9.3 | 99.29% |  |  | 100% |  |  | 80.51% |  | 13.05% | 210024.2 | 209152.788 | 105.681 | 209047.107 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 13.05 | 3.23 |  | 3.03 |  | 29.64 | 35.33 | 1.69 | 4.3 | 99.32% |  |  | 100% |  |  | 81.73% |  | 10.32% | 166212.4 | 165401.16 | 95.681 | 165305.479 | 66.75 | 5.2367 | 265725.8332 | 76.01% | 16.59% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 4.3548 | 224112.0662 | 77.09% | 13.99% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 4.6419 | 240509.7582 | 77.62% | 15.01% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 5.4433 | 280472.4545 | 77.19% | 17.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 5.7129 | 296607.1259 | 77.78% | 18.51% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 4.8167 | 257094.4416 | 79.96% | 16.05% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 4.271 | 232649.9622 | 81.6% | 14.52% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 4.1129 | 225160.039 | 82.01% | 14.05% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.7929 | 309344.6189 | 80% | 19.31% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.6839 | 346293.3659 | 77.61% | 21.61% | 99.5% | 99.5% | [9 empty] | 66.755
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## Modelling New
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | CC*Bugt (MTD) | CC*Bugt (YTD) | Capacity | 66.755
1 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 | 200.3 | 206.6 |  | 29.1001 |  | 10502 | 66.755 | 76.15% | 6.8867 | 0 | 0 | 0 | 350.0667 | 0 | 0 | 21.85% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
2 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 | 197.9 | 191.7 |  | 33.4 |  | 9693 | 66.755 | 75.74% | 6.1839 | 0 | 0 | 0 | 312.6774 | 0 | 0 | 19.52% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
3 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 | 165.8 | 157.1 |  | 34.8001 |  | 7976.9 | 66.755 | 76.06% | 5.2367 | 0 | 0 | 0 | 265.8967 | 0 | 0 | 16.6% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
4 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 | 141.9 | 135 |  | 33.0999 |  | 6950.5 | 66.755 | 77.13% | 4.3548 | 0 | 0 | 0 | 224.2097 | 0 | 0 | 13.99% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
5 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 | 145 | 143.9 |  | 31.8 |  | 7459 | 66.755 | 77.65% | 4.6419 | 0 | 0 | 0 | 240.6129 | 0 | 0 | 15.02% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
6 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 | 153 | 163.3 |  | 31.1999 |  | 8419.6 | 66.755 | 77.24% | 5.4433 | 0 | 0 | 0 | 280.6533 | 0 | 0 | 17.52% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
7 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 | 153.5 | 177.1 |  | 27.1001 |  | 9198.8 | 66.755 | 77.81% | 5.7129 | 0 | 0 | 0 | 296.7355 | 0 | 0 | 18.52% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
8 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 | 117.4 | 144.5 |  | 20.9 |  | 7717.8 | 66.755 | 80.01% | 4.8167 | 0 | 0 | 0 | 257.26 | 0 | 0 | 16.06% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
9 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 | 103.2 | 132.4 |  | 15.8915 |  | 7215.2 | 66.755 | 81.64% | 4.271 | 0 | 0 | 0 | 232.7484 | 0 | 0 | 14.53% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
10 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 | 102.5 | 127.5 |  | 14.3999 |  | 6983 | 66.755 | 82.04% | 4.1129 | 0 | 0 | 0 | 225.2581 | 0 | 0 | 14.06% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
11 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 | 134.2 | 162.2 |  | 17.8001 |  | 8614.6 | 66.755 | 79.56% | 5.7929 | 0 | 0 | 0 | 307.6643 | 0 | 0 | 19.2% | 0% |  |  | 66.755 |  |  |  | 99.5% | 99.5%
12 | March | 3 | 2025-03-01 | 2025 | FY25 | 31 | 185.4 | 207.2 |  | 23.6002 |  | 10739.7 | 66.755 | 77.65% | 6.6839 | 3 | 20.0516 | 20.0516 | 346.4419 | 1039.3258 | 1039.3258 | 21.62% | 2.093% | 21.62% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
13 | April | 4 | 2025-04-01 | 2025 | FY26 | 30 | 167.2997 | 206.6 |  | 29.1001 |  | 10495.2627 | 66.755 | 76.1% | 6.8867 | 30 | 206.6 | 206.6 | 349.8421 | 10495.2627 | 10495.2627 | 21.84% | 21.84% | 21.84% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
14 | May | 5 | 2025-05-01 | 2025 | FY26 | 31 | 203.1012 | 191.7 |  | 33.4 |  | 9688.8168 | 66.755 | 75.71% | 6.1839 | 31 | 191.7 | 398.3 | 312.5425 | 9688.8168 | 20184.0795 | 19.51% | 19.51% | 20.65% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
15 | June | 6 | 2025-06-01 | 2025 | FY26 | 30 | 165.8 | 157.1 |  | 34.8001 |  | 7971.775 | 66.755 | 76.01% | 5.2367 | 30 | 157.1 | 555.4 | 265.7258 | 7971.775 | 28155.8545 | 16.59% | 16.59% | 19.31% | 66.75 | 66.755 |  |  |  | 99.5% | 99.5%
16 | July | 7 | 2025-07-01 | 2025 | FY26 | 31 | 141.9 | 135 |  | 33.0999 |  | 6947.4741 | 66.755 | 77.09% | 4.3548 | 0 | 0 | 555.4 | 224.1121 | 0 | 28155.8545 | 13.99% | 0% | 19.31% |  | 66.755 |  |  |  | 99.5% | 99.5%
17 | August | 8 | 2025-08-01 | 2025 | FY26 | 31 | 145 | 143.9 |  | 31.8 |  | 7455.8025 | 66.755 | 77.62% | 4.6419 | 0 | 0 | 555.4 | 240.5098 | 0 | 28155.8545 | 15.01% | 0% | 19.31% |  | 66.755 |  |  |  | 99.5% | 99.5%
18 | September | 9 | 2025-09-01 | 2025 | FY26 | 30 | 153 | 163.3 |  | 31.1999 |  | 8414.1736 | 66.755 | 77.19% | 5.4433 | 0 | 0 | 555.4 | 280.4725 | 0 | 28155.8545 | 17.51% | 0% | 19.31% |  | 66.755 |  |  |  | 99.5% | 99.5%
19 | October | 10 | 2025-10-01 | 2025 | FY26 | 31 | 153.5 | 177.1 |  | 27.1001 |  | 9194.8209 | 66.755 | 77.78% | 5.7129 | 0 | 0 | 555.4 | 296.6071 | 0 | 28155.8545 | 18.51% | 0% | 19.31% |  | 66.755 |  |  |  | 99.5% | 99.5%
20 | November | 11 | 2025-11-01 | 2025 | FY26 | 30 | 117.4 | 144.5 |  | 20.9 |  | 7712.8332 | 66.755 | 79.96% | 4.8167 | 0 | 0 | 555.4 | 257.0944 | 0 | 28155.8545 | 16.05% | 0% | 19.31% |  | 66.755 |  |  |  | 99.5% | 99.5%
21 | December | 12 | 2025-12-01 | 2025 | FY26 | 31 | 103.2 | 132.4 |  | 15.8915 |  | 7212.1488 | 66.755 | 81.6% | 4.271 | 0 | 0 | 555.4 | 232.65 | 0 | 28155.8545 | 14.52% | 0% | 19.31% |  | 66.755 |  |  |  | 99.5% | 99.5%
22 | January | 1 | 2026-01-01 | 2026 | FY26 | 31 | 102.5 | 127.5 |  | 14.3999 |  | 6979.9612 | 66.755 | 82.01% | 4.1129 | 0 | 0 | 555.4 | 225.16 | 0 | 28155.8545 | 14.05% | 0% | 19.31% |  | 66.755 |  |  |  | 99.5% | 99.5%
23 | February | 2 | 2026-02-01 | 2026 | FY26 | 28 | 134.2 | 162.2 |  | 17.8001 |  | 8661.6493 | 66.755 | 80% | 5.7929 | 0 | 0 | 555.4 | 309.3446 | 0 | 28155.8545 | 19.31% | 0% | 19.31% |  | 66.755 |  |  |  | 99.5% | 99.5%
24 | March | 3 | 2026-03-01 | 2026 | FY26 | 31 | 185.4 | 207.2 |  | 23.6002 |  | 10735.0943 | 66.755 | 77.61% | 6.6839 | 0 | 0 | 555.4 | 346.2934 | 0 | 28155.8545 | 21.61% | 0% | 19.31% |  | 66.755 |  |  |  | 99.5% | 99.5%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## PA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  |  | 12 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Sr. No. | Date | Financial Year | Calendar Year | 9 | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Inverter Station Number (if Bd in filed) | LT Number (If breakdwon in Below LT Panel) | ACCB Number (If BD below ACCB) | Inverter number (If Inv or Str BD) | String Type(If String BD, No other filed to be inserted) | Equipment (If any BD above LT panel) | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Fault Category | Fault Code (As per HMI) | Breakdown Description | Fault Time | Acknowledgement Time | Work Start time on Fault | Work Completion time on fault | Acknow. time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(kWh/m2) | Approximate Energy Loss (KWh) | PTW No. | Job Card No.
1 | 2025-04-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 4249.75 | 6.367% |  |  | I/C trip in overcurrent | 11:41 | 11:41 | 11:44 | 11:44 | 0 | 0.05 | 0.05 | 0.05 | LT Trip due to over current , after reset LT and charge succesfully | Close | 0.0031833 | 0.015 | 48.5103
2 | 2025-04-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 300.375 | 0.45% | Inverter |  | I/C trip in overcurrent | 17:53 | 17:53 | 18:05 | 18:05 | 0 | 0.2 | 0.2 | 0.2 | Inverter trip in ground fault | Close | 0.0009 | 0.01 | 2.2858
3 | 2025-04-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 300.375 | 0.45% | Inverter |  | Ground Fault | 5:51 | 5:51 | 18:04 | 18:04 | 0 | 12.2167 | 12.2167 | 12.2167 | Inverter trip in ground fault | Close | 0.054975 | 3.05 | 697.1766
4 | 2025-04-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 300.375 | 0.45% | Inverter |  | Ground Fault | 5:53 | 5:53 | 10:11 | 12:46 | 0 | 4.3 | 6.8833 | 6.8833 | The inverter tripped due to a ground fault. After performing IR testing, we found a cable fault. Once the cable was repaired, the inverter was successfully charged | Close | 0.030975 | 2.2 | 502.8815
5 | 2025-04-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK5 |  |  | INV2 |  |  | BLK5INV2 | 267 | 0.4% | Inverter |  | Precautionry shutdown | 10:11 | 10:11 | 10:11 | 12:46 | 0 | 0 | 2.5833 | 2.5833 | The inverter tripped due to a ground fault. After performing IR testing, we found a cable fault. Once the cable was repaired, the inverter was successfully charged | Close | 0.010333 | 4.1 | 833.0562
6 | 2025-04-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 267 | 6.367% | LT Panel |  | ACB Triped in overcurrent | 11:27 | 11:27 | 11:35 | 11:50 | 0 | 0.13333 | 0.38333 | 0.38333 | LT Trip due to over current , after reset LT and charge succesfully | Close | 0.024406 | 0.328 | 66.6445
7 | 2025-04-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 240 | 6.367% | LT Panel |  | ACB Triped in overcurrent | 11:50 | 11:50 | 11:55 | 12:20 | 0 | 0.083333 | 0.5 | 0.5 | LT Trip due to over current , after reset LT and charge succesfully | Close | 0.031833 | 0.348 | 63.5579
8 | 2025-04-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV23 |  |  | BLK2INV23 | 300.375 | 0.45% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:55 | 11:50 | 14:00 | 14:00 | -0.083333 | 2.0833 | 2.0833 | 2.0833 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | Close | 0.009375 | 1.8 | 411.4485
9 | 2025-04-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV12 |  |  | BLK2INV12 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:55 | 11:50 | 14:00 | 14:00 | -0.083333 | 2.0833 | 2.0833 | 2.0833 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | Close | 0.0083333 | 1.8 | 365.732
10 | 2025-04-10 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 267 | 6.367% |  |  |  | 11:40 | 11:40 | 11:45 | 12:00 | 0 | 0.083333 | 0.33333 | 0.33333 | LT Trip due to over current , after reset LT and charge succesfully | Close | 0.021222 | 0.23 | 46.7324
11 | 2025-04-10 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK8 | LT2 |  |  |  |  | BLK8LT2 | 240 | 4.635% | LT Panel |  |  | 12:05 | 12:05 | 12:10 | 12:30 | 0 | 0.083333 | 0.41667 | 0.41667 | LT Trip due to over current , after reset LT and charge succesfully | Close | 0.019313 | 0.24 | 43.833
12 | 2025-04-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 267 | 6.367% | LT Panel |  | I/C trip in overcurrent | 12:45 | 12:45 | 12:50 | 13:20 | 0 | 0.083333 | 0.58333 | 0.58333 | LT Trip due to over current , after reset LT and charge succesfully | Close | 0.037139 | 2.13 | 432.7829
13 | 2025-04-12 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 240 | 6.367% | LT Panel |  | I/C trip in overcurrent | 11:44 | 11:44 | 11:49 | 12:20 | 0 | 0.083333 | 0.6 | 0.6 | LT Trip due to over current , after reset LT and charge succesfully | Close | 0.0382 | 2.11 | 385.3656
14 | 2025-04-13 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 507 | 6.367% | LT Panel |  | I/C trip in overcurrent | 10:58 | 10:58 | 11:10 | 11:20 | 0 | 0.2 | 0.36667 | 0.36667 | LT Trip due to over current , after reset LT and charge succesfully | Close | 0.023344 | 1.32 | 509.2852
15 | 2025-04-14 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 507 | 6.367% | LT Panel |  | I/C trip in overcurrent | 11:30 | 11:30 | 11:30 | 14:00 | 0 | 0 | 2.5 | 2.5 | LT Trip due to over current , after reset LT and charge succesfully | Close | 0 | 2.3 | 887.3909
16 | 2025-04-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 507 | 6.367% | LT Panel |  | I/C trip in overcurrent | 10:49 | 10:49 | 10:59 | 11:00 | 5 | 0.16667 | 0.18333 | 0.18333 | LT Trip due to over current , after reset LT and charge succesfully | Close | 0 | 0.1 | 38.5822
17 | 2025-04-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:10 | 11:05 | 14:00 | 14:00 | -0.083333 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | Close | 0 | 2.83 | 575.012
18 | 2025-04-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:10 | 11:05 | 14:00 | 14:00 | -0.083333 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | Close | 0 | 2.83 | 516.8647
19 | 2025-04-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:10 | 11:05 | 14:00 | 14:00 | -0.083333 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | Close | 0 | 2.95 | 599.3941
20 | 2025-04-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:10 | 11:05 | 14:00 | 14:00 | -0.083333 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | Close | 0 | 2.95 | 538.7812
[18 empty] | #N/A | [8 empty] | 0 | 0 | 0 | 0 |  | Close |  |  | 0
1724 | 2025-04-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 10:55 | 10:50 | 13:55 | 13:55 | -0.083333 | 3 | 3 | 3 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | Close | 0 | 2.82 | 572.9801
1725 | 2025-04-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 10:55 | 10:50 | 13:55 | 13:55 | -0.083333 | 3 | 3 | 3 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | Close | 0 | 2.82 | 515.0383
1726 | 2025-04-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 10:43 | 10:43 | 14:00 | 14:00 | 0 | 3.2833 | 3.2833 | 3.2833 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | Close | 0 | 2.89 | 587.203
1727 | 2025-04-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 10:43 | 10:43 | 14:00 | 14:00 | 0 | 3.2833 | 3.2833 | 3.2833 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted | Close | 0 | 2.89 | 527.823
1728 | 2025-04-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:10 | 11:10 | 14:10 | 14:10 | 0 | 3 | 3 | 3 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted…..12 Times LT2 Trip Some ratio changes on Breaker | Close | 0 | 2.83 | 575.012
1729 | 2025-04-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:10 | 11:10 | 14:10 | 14:10 | 0 | 3 | 3 | 3 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted…..12 Times LT2 Trip Some ratio changes on Breaker | Close | 0 | 2.83 | 516.8647
1730 | 2025-04-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV30 |  |  | BLK2INV30 | 240 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:20 | 11:20 | 14:10 | 14:10 | 0 | 2.8333 | 2.8333 | 2.8333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted…..12 Times LT2 Trip Some ratio changes on Breaker | Close | 0 | 2.72 | 496.7746
1731 | 2025-04-25 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 240 | 0.3584% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:00 | 11:00 | 13:20 | 13:20 | 0 | 2.3333 | 2.3333 | 2.3333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted….. | Close | 0 | 2.31 | 421.8931
1732 | 2025-04-25 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 267 | 0.4% | Inverter |  | Inv manually tripped for precautionary shutdown | 11:00 | 11:00 | 13:20 | 13:20 | 0 | 2.3333 | 2.3333 | 2.3333 | LT tripped due to overcurrent, causing the inverter to shut down. After reducing generation, the inverter was charged and restarted….. | Close | 0 | 2.31 | 469.3561
1733 | 2025-04-25 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | All_Inv |  |  | BLK2All_Inv | 4605 |  | Inverter |  | All inverter Tripped LT2 | 12:18 | 12:18 | 12:32 | 12:32 | 0 | 0.23333 | 0.23333 | 0.23333 | All inverter Tripped LT2 | Close | 0 | 0.25 | 876.0902
1734 | 2025-04-27 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK1 |  |  | All_Inv |  |  | BLK1All_Inv | 4381 |  | IDT |  | IDT tripped due to overcurrent | 11:30 | 11:30 | 11:42 | 11:42 | 0 | 0.2 | 0.2 | 0.2 | IDT tripped due to overcurrent | Close | 0 | 2.12 | 7067.866
1735 | 2025-04-27 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | All_Inv |  |  | BLK2All_Inv | 4520 |  | IDT |  | IDT tripped due to overcurrent | 11:30 | 11:30 | 11:42 | 11:42 | 0 | 0.2 | 0.2 | 0.2 | IDT tripped due to overcurrent | Close | 0 | 2.12 | 7292.1147
1735 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV5 |  |  | BLK8INV5 | 22.25 | 0.45% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 9:00 | 9:30 | 0 | 0 | 0.5 | 0.5 | Found inv string open, connected & rectified | Close | 0 | 0.555 | 9.3973
1736 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV10 |  |  | BLK8INV10 | 9.9 | 0.45% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 9:35 | 9:55 | 0 | 0.58333 | 0.91667 | 0.91667 | Found inv string open, connected & rectified | Close | 0 | 0.64 | 4.8216
1738 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV11 |  |  | BLK8INV11 | 9.9 | 0.45% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 10:10 | 10:25 | 0 | 1.1667 | 1.4167 | 1.4167 | Found inv string open, connected & rectified | Close | 0 | 0.724 | 5.4545
1739 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV12 |  |  | BLK8INV12 | 9.9 | 0.3856% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 10:30 | 10:40 | 0 | 1.5 | 1.6667 | 1.6667 | Found inv string open, connected & rectified | Close | 0 | 0.752 | 5.6654
1740 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV13 |  |  | BLK8INV13 | 9.9 | 0.4153% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 10:45 | 11:00 | 0 | 1.75 | 2 | 2 | Found inv string open, connected & rectified | Close | 0 | 0.776 | 5.8462
1741 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK3 |  |  | INV6 |  |  | BLK3INV6 | 11.13 | 0.4% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 11:10 | 11:20 | 0 | 2.1667 | 2.3333 | 2.3333 | Found inv string open, connected & rectified | Close | 0 | 0.798 | 6.7589
1742 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK3 |  |  | INV20 |  |  | BLK3INV20 | 11.13 | 0.4% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 11:25 | 11:35 | 0 | 2.4167 | 2.5833 | 2.5833 | Found inv string open, connected & rectified | Close | 0 | 0.814 | 6.8944
1743 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK1 |  |  | INV17 |  |  | BLK1INV17 | 11.13 | 0.4% | Connectors |  | Found inv string open, connected & rectified | 9:00 | 9:00 | 11:50 | 12:00 | 0 | 2.8333 | 3 | 3 | Found inv string open, connected & rectified | Close | 0 | 0.839 | 7.1062
1744 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK1 |  |  | INV18 |  |  | BLK1INV18 | 11.13 | 0.4% | String Fuses |  | Replaced the fuse and rectified | 9:00 | 9:00 | 12:05 | 12:15 | 0 | 3.0833 | 3.25 | 3.25 | Replaced the fuse and rectified | Close | 0 | 6.3 | 53.3599
1745 | 2025-04-28 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK3 |  |  | INV32 |  |  | BLK3INV32 | 31.9 |  | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 12:05 | 12:00 | 0 | 3.0833 | 3 | 3 | Replaced the fuse and rectified | Close | 0 | 6.3 | 152.9362
1746 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 66.75 | 0.3955% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 10:30 | 10:30 | 0 | 1.5 | 1.5 | 1.5 | DC cable damage caused by tractor movement. The cable was replaced with a new one | Close | 0 | 0.7 | 35.5573
1747 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 22.25 | 0.3955% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 11:30 | 11:30 | 0 | 2.5 | 2.5 | 2.5 | DC cable damage caused by tractor movement. The cables were replaced with new ones. | Close | 0 | 2.1 | 35.5573
1748 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK1 |  |  | INV24 |  |  | BLK1INV24 | 22.25 | 0.45% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 17:30 | 17:30 | 0 | 8.5 | 8.5 | 8.5 | Cable Damged due to tractor movement | Close | 0 | 6.7 | 113.4446
1749 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV28 |  |  | BLK2INV28 | 22.5 | 0.45% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 12:30 | 12:30 | 0 | 3.5 | 3.5 | 3.5 | Due to a short circuit caused by tractor movement. The cable was replaced with a new one. | Close | 0 | 3.1 | 53.0791
1750 | 2025-04-29 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV3 |  |  | BLK2INV3 | 22.5 | 0.1667% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 13:30 | 13:30 | 0 | 4.5 | 4.5 | 4.5 | Cable Damge due to grass cutting activitysame replaced | Close | 0 | 4.1 | 70.2014
1751 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK6 |  |  | INV7 |  |  | BLK6INV7 | 88 | 0.4449% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 10:00 | 11:00 | 0 | 1 | 2 | 2 | Cable Damge due to grass cutting activitysame replaced | Close | 0 | 0.8 | 53.5737
1752 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 22 | 0.4449% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 11:15 | 11:30 | 0 | 2.25 | 2.5 | 2.5 | Cable Damge due to grass cutting activitysame replaced | Close | 0 | 1 | 16.7418
1753 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 22.25 | 0.45% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 11:35 | 11:50 | 0 | 2.5833 | 2.8333 | 2.8333 | Cable Damge due to grass cutting activitysame replaced | Close | 0 | 1.5 | 25.3981
1754 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK6 |  |  | INV8 |  |  | BLK6INV8 | 22 | 0.4449% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 11:55 | 12:10 | 0 | 2.9167 | 3.1667 | 3.1667 | Cable Damge due to grass cutting activitysame replaced | Close | 0 | 1.7 | 28.461
1755 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK6 |  |  | INV15 |  |  | BLK6INV15 | 22 | 0.412% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 12:15 | 12:30 | 0 | 3.25 | 3.5 | 3.5 | Cable Damge due to grass cutting activitysame replaced | Close | 0 | 2 | 33.4836
1756 | 2025-04-30 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 30 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV24 |  |  | BLK2INV24 | 44.5 | 0.4333% | Cables |  | During Grass cutting cable cut | 9:00 | 9:00 | 16:05 | 16:25 | 0 | 7.0833 | 7.4167 | 7.4167 | Cable Damge due to grass cutting activitysame replaced | Close | 0 | 4.6 | 155.7747
1757 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK3 |  |  | INV12 |  |  | BLK3INV12 | 300.38 | 0.45% | Inverter |  | inv tripped on system fault | 7:14 | 7:18 | 11:00 | 12:45 | 0.066667 | 3.7667 | 5.5167 | 5.5167 | Inv Fault System Shudown | Close | 0 | 0.3 | 68.5759
1758 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.2 | 0.45% | Cables |  | cable short | 7:18 | 9:00 | 12:00 | 12:15 | 1.7 | 4.7 | 4.95 | 4.95 | Cable Damge due to grass cutting activity same replaced | Close | 0 | 0.293 | 4.9499
1759 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV7 |  |  | BLK8INV7 | 22.2 | 0.4333% | Cables |  | cable short | 7:18 | 9:00 | 12:18 | 12:28 | 1.7 | 5 | 5.1667 | 5.1667 | Cable Damge due to grass cutting activity same replaced | Close | 0 | 0.317 | 5.3554
1760 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV8 |  |  | BLK8INV8 | 22.2 | 0.4% | Cables |  | mc4 open | 7:18 | 9:00 | 12:35 | 12:50 | 1.7 | 5.2833 | 5.5333 | 5.5333 | MC4 Open FOUND rectified | Close | 0 | 0.326 | 5.5074
1761 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV10 |  |  | BLK8INV10 | 22.2 | 0.45% | Cables |  | cable short | 7:18 | 9:00 | 13:00 | 13:10 | 1.7 | 5.7 | 5.8667 | 5.8667 | Cable Damge due to grass cutting activity same replaced | Close | 0 | 0.326 | 5.5074
1762 | 2025-05-02 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV11 |  |  | BLK8INV11 | 22.2 | 0.45% | Cables |  | cable cut | 7:18 | 9:00 | 13:15 | 13:25 | 1.7 | 5.95 | 6.1167 | 6.1167 | Cable Damge due to grass cutting activity same replaced | Close | 0 | 0.325 | 5.4905
1763 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV21 |  |  | BLK2INV21 | 22.2 | 0.4% | Connectors |  | Open Found and rectified | 7:20 | 9:00 | 11:15 | 11:15 | 1.6667 | 3.9167 | 3.9167 | 3.9167 | MC4 Found open condition | Close | 0 | 2.3 | 38.8562
1764 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK1 |  |  | INV15 |  |  | BLK1INV15 | 22.2 | 0.4% | Connectors |  | Open Found and rectified | 7:20 | 9:00 | 11:45 | 11:45 | 1.6667 | 4.4167 | 4.4167 | 4.4167 | MC4 Found open condition | Close | 0 | 3.5 | 59.129
1765 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV17 |  |  | BLK2INV17 | 22.2 | 0.4% | Connectors |  | Opend Found MC4 Rectified | 7:20 | 9:00 | 13:10 | 13:10 | 1.6667 | 5.8333 | 5.8333 | 5.8333 | MC4 Found opend condition | Close | 0 | 3.1 | 52.3714
1766 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 44.5 | 0.4167% | Connectors |  | two string found Opend Found MC4 Rectified | 7:20 | 9:00 | 15:30 | 15:30 | 1.6667 | 8.1667 | 8.1667 | 8.1667 | 2 MC4 Found OPEN Condition | Close | 0 | 4.1 | 138.8427
1767 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 22.2 | 0.4167% | Connectors |  | Opend Found MC4 Rectified | 7:20 | 9:00 | 16:25 | 16:25 | 1.6667 | 9.0833 | 9.0833 | 9.0833 | MC4 Found opend condition | Close | 0 | 4.9 | 82.7805
1768 | 2025-05-03 |  | 2025 | Year_2 | Year_2 | 2025-04-01 | 31 | 7:00 | 19:00 | 12 | BLK8 |  |  | INV6 |  |  | BLK8INV6 | 22.2 | 0.4333% | Connectors |  | Opend Found MC4 Rectified | 7:20 | 9:00 | 17:46 | 17:46 | 1.6667 | 10.4333 | 10.4333 | 10.4333 | MC4 Found opend condition | Close | 0 | 5.3 | 89.5381
1769 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 4008 | 5.914% | LT Panel |  | Tripped due to overcurrent fault | 12:50 | 12:52 | 13:00 | 13:00 | 0.033333 | 0.16667 | 0.16667 | 0.16667 | Reset & Started | Close | 0 | 0.122 | 370.2136
1770 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV27 |  |  | BLK8INV27 | 22.2 | 0.4366% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 9:30 | 9:40 | 3.7333 | 4.2333 | 4.4 | 4.4 | 1 nos of +ve & -ve MC4 connector replaced with new one | Close | 0 | 0.9 | 15.1273
1771 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 9:50 | 10:00 | 3.7333 | 4.5667 | 4.7333 | 4.7333 | 1 nos of +ve & -ve MC4 connector replaced with new one | Close | 0 | 0.08 | 1.3446
1772 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 10:10 | 10:15 | 3.7333 | 4.9 | 4.9833 | 4.9833 | MC4 tightned | Close | 0 | 0.107 | 1.7985
1773 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 10:20 | 10:25 | 3.7333 | 5.0667 | 5.15 | 5.15 | MC4 tightned | Close | 0 | 0.12 | 2.017
1774 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 10:30 | 10:40 | 3.7333 | 5.2333 | 5.4 | 5.4 | MC4 tightned | Close | 0 | 0.11 | 1.8489
1775 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.2 | 0.3856% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 10:50 | 11:00 | 3.7333 | 5.5667 | 5.7333 | 5.7333 | MC4 tightned | Close | 0 | 0.12 | 2.017
1776 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV17 |  |  | BLK8INV17 | 22.2 | 0.2667% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 11:10 | 11:20 | 3.7333 | 5.9 | 6.0667 | 6.0667 | 1 nos of +ve & -ve MC4 connector replaced with new one | Close | 0 | 0.11 | 1.8489
1777 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV3 |  |  | BLK8INV3 | 22.2 | 0.2818% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 11:40 | 11:50 | 3.7333 | 6.4 | 6.5667 | 6.5667 | MC4 tightned | Close | 0 | 0.9 | 15.1273
1778 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22.2 | 0.4301% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 12:00 | 12:10 | 3.7333 | 6.7333 | 6.9 | 6.9 | 3 nos of +ve & -ve MC4 connector replaced with new one | Close | 0 | 0.14 | 2.3531
1779 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22.2 | 0.4301% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 12:20 | 12:30 | 3.7333 | 7.0667 | 7.2333 | 7.2333 | 2 nos of +ve & -ve MC4 connector replaced with new one | Close | 0 | 0.13 | 2.185
1780 | 2025-05-04 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:29 | 6:20 | 12 | BLK8 |  |  | INV4 |  |  | BLK8INV4 | 22.2 | 0.4167% | Connectors |  | Found MC4 connector faulty condition | 5:16 | 9:00 | 12:35 | 12:40 | 3.7333 | 7.3167 | 7.4 | 7.4 | MC4 tightned | Close | 0 | 0.13 | 2.185
1781 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK3 |  |  | INV6 |  |  | BLK3INV6 | 267 | 0.4% | Inverter |  | inv tripped on system fault | 14:20 | 14:20 | 16:00 | 16:30 | 0 | 1.6667 | 2.1667 | 2.1667 | Inv Fault System Shudown | Close | 0 | 0.131 | 26.4818
1782 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK4 |  |  | INV17 |  |  | BLK4INV17 | 289.25 | 0.4333% | Inverter |  | inv tripped on system fault | 14:20 | 14:20 | 15:40 | 16:10 | 0 | 1.3333 | 1.8333 | 1.8333 | Inv Fault System Shudown | Close | 0 | 0.8228 | 180.1907
1783 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK7 |  |  | INV12 |  |  | BLK7INV12 | 190.35 | 0.4054% | Inverter |  | inv tripped on system fault | 14:20 | 14:20 | 15:50 | 16:20 | 0 | 1.5 | 2 | 2 | One nos of MC4 connector replaced with new one | Close | 0 | 0.11194 | 16.1325
1784 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK6 |  |  | INV20 |  |  | BLK6INV20 | 264 | 0.3955% | Inverter |  | inv tripped on system fault | 14:20 | 14:20 | 15:30 | 16:10 | 0 | 1.1667 | 1.8333 | 1.8333 | One nos of MC4 connector replaced with new one | Close | 0 | 0.8227 | 164.4411
1785 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK5 |  |  | INV27 |  |  | BLK5INV27 | 300.38 | 0.4% | Inverter |  | inv tripped on system fault | 14:20 | 14:20 | 15:25 | 16:08 | 0 | 1.0833 | 1.8 | 1.8 | Inv Fault System Shudown | Close | 0 | 0.7578 | 172.3417
1786 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK5 |  |  | INV13 |  |  | BLK5INV13 | 22.25 | 0.4285% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 9:30 | 9:40 | 0 | 0.5 | 0.66667 | 0.66667 | MC4 tightned | Close | 0 | 0.623 | 10.495
1787 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK5 |  |  | INV17 |  |  | BLK5INV17 | 22.25 | 0.4333% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 9:50 | 10:00 | 0 | 0.83333 | 1 | 1 | MC4 tightned | Close | 0 | 0.651 | 10.9667
1788 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK5 |  |  | INV12 |  |  | BLK5INV12 | 22.25 | 0.4285% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 10:10 | 10:20 | 0 | 1.1667 | 1.3333 | 1.3333 | 1 nos of +ve & -ve MC4 connector replaced with new one | Close | 0 | 0.666 | 11.2194
1789 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK3 |  |  | INV6 |  |  | BLK3INV6 | 22.25 | 0.4% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 10:30 | 10:40 | 0 | 1.5 | 1.6667 | 1.6667 | MC4 tightned | Close | 0 | 0.663 | 11.1688
1790 | 2025-05-05 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:32 | 18:17 | 12 | BLK7 |  |  | INV28 |  |  | BLK7INV28 | 22.25 | 0.4% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 10:50 | 11:00 | 0 | 1.8333 | 2 | 2 | 2 nos of +ve & -ve MC4 connector replaced with new one | Close | 0 | 0.695 | 11.7079
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK2 |  |  | MVP |  |  | BLK2MVP | 4349.2 | 12.5% | IDT |  | IDT tripped on over current fault | 10:44 | 10:44 | 10:54 | 10:54 | 0 | 0.16667 | 0.16667 | 0.16667 | Normally check the all parameters & charge the idt | Close | 0 | 0.146 | 480.7586
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK2 |  |  | MVP |  |  | BLK2MVP | 4489 | 12.5% | IDT |  | IDT tripped on over current fault | 10:44 | 10:44 | 10:54 | 10:54 | 0 | 0.16667 | 0.16667 | 0.16667 | Normally check the all parameters & charge the idt | Close | 0 | 0.146 | 496.212
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV4 |  |  | BLK6INV4 | 22 | 0.4449% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 9:45 | 9:55 | 0 | 0.75 | 0.91667 | 0.91667 | 1 nos of +ve & -ve MC4 connector replaced with new one | Close | 0 | 0.0512 | 0.85282
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV14 |  |  | BLK6INV14 | 22 | 0.412% | Connectors |  | Found MC4 connectors open condition | 9:00 | 9:00 | 10:00 | 10:10 | 0 | 1 | 1.1667 | 1.1667 | MC4 tightned | Close | 0 | 0.69 | 11.4931
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV18 |  |  | BLK6INV18 | 22 | 0.4449% | Connectors |  | Found MC4 connector faulty condition | 9:00 | 9:00 | 10:15 | 10:25 | 0 | 1.25 | 1.4167 | 1.4167 | 1 nos of +ve & -ve MC4 connector replaced with new one | Close | 0 | 0.82 | 13.6584
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV20 |  |  | BLK6INV20 | 22 | 0.3955% | Connectors |  | Found Y connector shorted | 9:00 | 9:00 | 10:35 | 10:45 | 0 | 1.5833 | 1.75 | 1.75 | 1Nos y connector used | Close | 0 | 0.1 | 1.6657
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV23 |  |  | BLK6INV23 | 22 | 0.3955% | Connectors |  | Found Y connector shorted & MC4 1Pair | 9:00 | 9:00 | 10:50 | 11:00 | 0 | 1.8333 | 2 | 2 | 1 pair of mc4 connectors & 1NOs of Y connector | Close | 0 | 1.22 | 20.3211
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV26 |  |  | BLK6INV26 | 22 | 0.4449% | Connectors |  | Found MC4 connectors open condition | 9:00 | 9:00 | 11:10 | 11:20 | 0 | 2.1667 | 2.3333 | 2.3333 | mc4 tightned | Close | 0 | 1.43 | 23.819
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK6 |  |  | INV27 |  |  | BLK6INV27 | 22 | 0.412% | Connectors |  | Found Y connector shorted | 9:00 | 9:00 | 11:25 | 11:35 | 0 | 2.4167 | 2.5833 | 2.5833 | 1Nos y connector used | Close | 0 | 1.65 | 27.4835
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK7 |  |  | INV4 |  |  | BLK7INV4 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 9:00 | 9:00 | 11:50 | 12:00 | 0 | 2.8333 | 3 | 3 | mc4 tightned | Close | 0 | 2.069 | 34.4626
1790 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 257.4 | 0.2852% | Inverter |  | Inv tripped on excessive leakage current fault | 14:30 | 14:30 | 14:40 | 15:26 | 0 | 0.16667 | 0.93333 | 0.93333 | 1Nos of y connector used & reset the fault after got the password | Close | 0 | 0.571 | 111.278
1791 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 22.25 | 0.4% | Connectors |  | MC4 found open condition | 9:00 | 9:00 | 12:10 | 12:20 | 0 | 3.1667 | 3.3333 | 3.3333 | mc4 tightned | Close | 0 | 2.388 | 40.2281
1792 | 2025-05-06 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:09 | 18:24 | 12.25 | BLK7 |  |  | INV15 |  |  | BLK7INV15 | 247.5 | 0.4% | Inverter |  | Inverter tripped due to ground fault | 9:00 | 9:00 | 9:30 | 9:42 | 0 | 0.5 | 0.7 | 0.7 | Checked all string one by one and found one string was grounded and after rectified the same charge the Inverter | Close | 0 | 0.622 | 116.5549
1793 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV10 |  |  | BLK7INV10 | 22 | 0.3856% | Connectors |  | MC4 found open condition | 0.375 | 9:00 | 9:30 | 9:44 | 0 | 0.5 | 0.73333 | 0.73333 | mc4 tightned | Close | 0 | 0.1688 | 2.8116
1794 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV25 |  |  | BLK7INV25 | 22 | 0.45% | Connectors |  | Found MC4 connector faulty condition | 0.375 | 9:00 | 9:30 | 10:01 | 0 | 0.5 | 1.0167 | 1.0167 | 1 nos of +ve & -ve MC4 connector replaced with new one | Close | 0 | 0.2 | 3.3313
1795 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV17 |  |  | BLK7INV17 | 22 | 0.4% | Connectors |  | Found Y connector shorted |  |  |  | 10:18 | 0 | 0 | 10.3 | 10.3 | 1Nos y connector used and 1 nos of 15A fuse replaced with new one | Close | 0 | 0.1987 | 3.3097
1796 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22 | 0.3955% | Connectors |  | MC4 found open condition |  |  |  | 10:33 | 0 | 0 | 10.55 | 10.55 | mc4 tightned | Close | 0 | 0.21 | 3.4979
1797 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV5 |  |  | BLK7INV5 | 22 | 0.3955% | Connectors |  | MC4 found open condition |  |  |  | 11:10 | 0 | 0 | 11.1667 | 11.1667 | mc4 tightned | Close | 0 | 0.191 | 3.1814
1798 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK7 |  |  | INV16 |  |  | BLK7INV16 | 22 | 0.4% | Connectors |  | MC4 found open condition |  |  |  | 11:22 | 0 | 0 | 11.3667 | 11.3667 | mc4 tightned | Close | 0 | 0.214 | 3.5645
1799 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK3 |  |  | INV6 |  |  | BLK3INV6 | 22 | 0.4% | Connectors |  | Found Y connector shorted |  |  |  | 11:38 | 0 | 0 | 11.6333 | 11.6333 | 1Nos y connector used and 1 nos of 15A fuse replaced with new one | Close | 0 | 0.22 | 3.6645
1800 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22 | 0.45% | Connectors |  | Found Y connector shorted |  |  |  | 12:14 | 0 | 0 | 12.2333 | 12.2333 | 1Nos y connector used and 1 nos of 15A fuse replaced with new one | Close | 0 | 0.218 | 3.6311
1801 | 2025-05-07 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:56 | 18:30 | 12.5667 | POWER TRAFO |  |  | 132KV_OC |  |  | POWER TRAFO132KV_OC | 67300 |  | Power Trafo |  | Tripped on REF HV Earth Fault | 13:13 | 13:13 | 13:30 | 18:30 | 0 | 0.28333 | 5.2833 | 5.2833 | Checked all Parameter & Testing than charged the Power trafo | Close | 0 | 1.46 | 74393.1161
1802 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 | BLK2 |  |  | MVP |  |  | BLK2MVP | 7500 | 12.5% | IDT |  | Tripped on Over current | 11:10 | 11:10 | 11:15 | 11:20 | 0 | 0.083333 | 0.16667 | 0.16667 | Checked all parameter & charged the IDT | Close | 0 | 0.193 | 1095.9315
1803 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 | BLK1 |  |  | MVP |  |  | BLK1MVP | 7500 | 13.4% | IDT |  | Tripped on Over current | 11:22 | 11:22 | 11:30 | 11:34 | 0 | 0.13333 | 0.2 | 0.2 | Checked all parameter & charged the IDT | Close | 0 | 0.182 | 1033.4691
1804 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 |  |  |  | MVP |  |  | MVP | 7500 |  | IDT |  | Tripped on Over current | 11:22 | 11:22 | 11:25 | 11:40 | 0 | 0.05 | 0.3 | 0.3 | Checked all parameter & charged the IDT | Close | 0 | 0.17 | 965.3282
1805 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 |  |  |  | MVP |  |  | MVP | 7500 |  | IDT |  | Tripped on Over current | 11:22 | 11:22 | 11:28 | 11:46 | 0 | 0.1 | 0.4 | 0.4 | Checked all parameter & charged the IDT | Close | 0 | 0.173 | 982.3635
1806 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 |  |  |  | MVP |  |  | MVP | 7500 |  | IDT |  | Tripped on Over current | 12:45 | 12:45 | 12:51 | 12:55 | 0 | 0.1 | 0.16667 | 0.16667 | Checked all parameter & charged the IDT | Close | 0 | 0.16 | 908.5442
1807 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 |  |  |  | MVP |  |  | MVP | 7500 |  | IDT |  | Tripped on Over current | 12:53 | 12:55 | 13:05 | 13:08 | 0.033333 | 0.2 | 0.25 | 0.25 | Checked all parameter & charged the IDT | Close | 0 | 0.153 | 868.7954
1808 | 2025-05-08 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:40 | 12.45 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 247.5 | 0.3333% | Inverter |  | Manually shutdown | 12:45 | 12:45 | 13:45 | 14:00 | 0 | 1 | 1.25 | 1.25 | Manually tripped | Close | 0.0041667 | 1.1 | 206.126
1809 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 18:24 | 12.15 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 22 | 0.4167% | Connectors |  | MC4 found open condition | 6:15 | 12:00 | 12:02 | 12:09 | 5.75 | 5.7833 | 5.9 | 5.9 | mc4 tightned | Close | 0.024583 | 3.33 | 55.4666
1810 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 18:24 | 12.15 | BLK1 |  |  | INV13 |  |  | BLK1INV13 | 22 | 0.4% | Connectors |  | Found MC4 connector faulty condition | 6:15 | 12:00 | 12:14 | 12:18 | 5.75 | 5.9833 | 6.05 | 6.05 | 1 nos of +ve & -ve MC4 connector replaced with new one | Close | 0.0242 | 3.36 | 55.9663
1811 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 18:24 | 12.15 | BLK3 |  |  | INV10 |  |  | BLK3INV10 | 12 | 0.4% | Connectors |  | MC4 found open condition | 6:15 | 12:10 | 12:30 | 12:36 | 5.9167 | 6.25 | 6.35 | 6.35 | mc4 tightned | Close | 0.0254 | 3.4 | 30.8905
1812 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 18:24 | 12.15 | BLK1 | LT2 |  |  |  |  | BLK1LT2 | 4605.75 | 6.9% | LT Panel |  | Tripped on Over current | 11:07 | 11:07 | 11:14 | 11:18 | 0 | 0.11667 | 0.18333 | 0.18333 | Checked all parameter & charged the breaker | Close | 0.01265 | 0.18 | 627.6791
1813 | 2025-05-09 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:15 | 18:24 | 12.15 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 4008.13 | 5.914% | LT Panel |  | Tripped on Over current | 11:31 | 11:31 | 11:38 | 11:42 | 0 | 0.11667 | 0.18333 | 0.18333 | Checked all parameter & charged the breaker | Close | 0.010842 | 0.196 | 594.7887
1814 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 4008.13 | 5.914% | LT Panel |  | Tripped on Over current | 12:17 | 12:17 | 12:22 | 12:25 | 0 | 0.083333 | 0.13333 | 0.13333 | Checked all parameter & charged the breaker | Close | 0.0078851 | 0.16 | 485.5418
1815 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 6:05 | 6:05 | 15:25 | 15:30 | 0 | 9.3333 | 9.4167 | 9.4167 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | Close | 0.037243 | 4.17 | 69.4582
1816 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 6:05 | 6:05 | 15:35 | 15:40 | 0 | 9.5 | 9.5833 | 9.5833 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | Close | 0.037903 | 4.2 | 69.9579
1817 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 6:05 | 6:05 | 15:52 | 15:56 | 0 | 9.7833 | 9.85 | 9.85 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | Close | 0.038957 | 4.12 | 68.6254
1818 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 6:05 | 6:05 | 16:00 | 16:10 | 0 | 9.9167 | 10.0833 | 10.0833 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | Close | 0.03988 | 4.66 | 77.62
1819 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK6 |  |  | INV8 |  |  | BLK6INV8 | 22 | 0.4449% | Connectors |  | MC4 found open condition | 6:05 | 6:05 | 16:05 | 16:13 | 0 | 10 | 10.1333 | 10.1333 | 1 nos of +ve & -ve MC4 connector replaced with new one and 60 mtr cable replaced with new one | Close | 0 | 4.73 | 78.7859
1820 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22 | 0.4301% | Connectors |  | Theft cable | 6:05 | 6:05 | 16:45 | 16:50 | 0 | 10.6667 | 10.75 | 10.75 | 290 meter cable used ,2 pair MC4 connecter ,2 15A fuse replaced with new one | Close | 0.046237 | 4.23 | 70.4576
1821 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22 | 0.4301% | Connectors |  | Theft cable | 6:05 | 6:05 | 17:00 | 17:20 | 0 | 10.9167 | 11.25 | 11.25 | 276 meter cable used ,2 pair MC4 connecter ,2 15A fuse replaced with new one | Close | 0.048388 | 4.77 | 79.4522
1822 | 2025-05-10 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:05 | 18:10 | 12.0833 | BLK8 |  |  | INV19 |  |  | BLK8INV19 | 22 | 0.4301% | Connectors |  | Theft cable | 6:05 | 6:05 | 17:28 | 17:34 | 0 | 11.3833 | 11.4833 | 11.4833 | 260 meter cable used ,2 pair MC4 connecter ,2 15A fuse replaced with new one | Close | 0.049391 | 4.87 | 81.1179
1823 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK1 |  |  | INV8 |  |  | BLK1INV8 | 22 | 0.4% | Connectors |  | MC4 found open condition | 5:48 | 5:48 | 11:30 | 11:40 | 0 | 5.7 | 5.8667 | 5.8667 | mc4 tightned | Close | 0 | 2.12 | 35.3121
1824 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 22 | 0.4% | Connectors |  | MC4 found open condition | 5:48 | 5:48 | 11:31 | 11:50 | 0 | 5.7167 | 6.0333 | 6.0333 | mc4 tightned | Close | 0.024133 | 2.48 | 41.3085
1825 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK2 |  |  | INV28 |  |  | BLK2INV28 | 22 | 0.45% | Connectors |  | MC4 found open condition | 5:48 | 5:48 | 11:40 | 11:55 | 0 | 5.8667 | 6.1167 | 6.1167 | mc4 tightned | Close | 0.027525 | 2.31 | 38.4768
1826 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK7 |  |  | INV4 |  |  | BLK7INV4 | 22 | 0.3955% | Connectors |  | MC4 found open condition | 5:48 | 5:48 | 12:00 | 12:28 | 0 | 6.2 | 6.6667 | 6.6667 | mc4 tightned | Close | 0.026367 | 2.6 | 43.3073
1827 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK7 |  |  | INV26 |  |  | BLK7INV26 | 22 | 0.45% | Connectors |  | MC4 found open condition | 5:48 | 5:48 | 12:10 | 12:40 | 0 | 6.3667 | 6.8667 | 6.8667 | mc4 tightned | Close | 0.0309 | 2.23 | 37.1443
1828 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | Theft cable | 5:48 | 5:48 | 16:05 | 16:20 | 0 | 10.2833 | 10.5333 | 10.5333 | St-13 120 mtr cables, 2 pair of MC4 connecter replaced with new one | Close | 0.04166 | 2.44 | 40.6422
1829 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | Theft cable | 5:48 | 5:48 | 16:05 | 16:20 | 0 | 10.2833 | 10.5333 | 10.5333 | St-14 120 mtr cables, 2 pair of MC4 connecter replaced with new one | Close | 0.04166 | 2.78 | 46.3055
1830 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | Connectors |  | Theft cable | 5:48 | 5:48 | 16:05 | 16:20 | 0 | 10.2833 | 10.5333 | 10.5333 | St-15 120 mtr cables, 2 pair of MC4 connecter replaced with new one | Close | 0.04166 | 2.54 | 42.3079
1831 | 2025-05-11 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:48 | 18:15 | 12.45 | BLK7 |  |  | INV32 |  |  | BLK7INV32 | 22 | 0.239% | Connectors |  | I nos of string cable fired by short circuited | 11:02 | 11:02 | 12:45 | 17:20 | 0 | 1.7167 | 6.3 | 6.3 | St-4 ,50 mtr cables, 2 pair of MC4 connecter replaced with new one | Close | 0 | 2.64 | 43.9735
1832 | 2025-05-12 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:32 | 12.3167 | BLK2 |  |  | INV11 |  |  | BLK2INV11 | 22 | 0.4% | Connectors |  | Mc4 connecter found open | 6:13 | 6:13 | 9:00 | 9:31 | 0 | 2.7833 | 3.3 | 3.3 | mc4 tightned | Close | 0.0132 | 0.694 | 11.5597
1833 | 2025-05-12 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:32 | 12.3167 | BLK3 |  |  | INV31 |  |  | BLK3INV31 | 22 | 0.4% | Connectors |  | String cable found faulty | 6:13 | 6:13 | 10:11 | 10:23 | 0 | 3.9667 | 4.1667 | 4.1667 | mc4 tightned | Close | 0.016667 | 1.47 | 24.4853
1834 | 2025-05-12 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:32 | 12.3167 | BLK6 |  |  | INV8 |  |  | BLK6INV8 | 22 | 0.4449% | Inverter |  | Inverter tripped due to system fault | 9:59 | 9:59 | 11:00 | 11:18 | 0 | 1.0167 | 1.3167 | 1.3167 | After checking all parameter restart the inverter | Close | 0.0058584 | 1.13 | 18.822
1835 | 2025-05-12 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:13 | 18:32 | 12.3167 | BLK8 |  |  | INV15 |  |  | BLK8INV15 | 22 | 0.4004% | Connectors |  | S7-17 half string found grounded | 6:13 | 16:30 |  |  | 10.2833 | -6.2167 | -6.2167 | -6.2167 | today will close this fault | Close | -0.024895 |  | 0
1836 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK4 |  |  | INV1 |  |  | BLK4INV1 | 22 | 0.45% | Connectors |  | MC4 found open condition | 6:03 | 6:03 | 9:15 | 9:21 | 0 | 3.2 | 3.3 | 3.3 | mc4 tightned | Close | 0.01485 | 0.788 | 13.1254
1837 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22 | 0.45% | Connectors |  | Y connecter faulty | 6:03 | 6:03 | 13:10 | 13:23 | 0 | 7.1167 | 7.3333 | 7.3333 | Y connecter burrnt & 2 nos of Mc4 replaced with new one | Close | 0.033 | 3.62 | 60.2971
1838 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK5 |  |  | INV19 |  |  | BLK5INV19 | 22 | 0.4333% | Connectors |  | MC4 found open condition | 6:03 | 6:03 | 13:20 | 13:26 | 0 | 7.2833 | 7.3833 | 7.3833 | mc4 tightned | Close | 0.031994 | 3.71 | 61.7962
1839 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK5 |  |  | INV17 |  |  | BLK5INV17 | 22 | 0.4333% | Connectors |  | MC4 found open condition | 6:03 | 6:03 | 13:15 | 13:31 | 0 | 7.2 | 7.4667 | 7.4667 | mc4 tightned | Close | 0.032356 | 3.61 | 60.1305
1840 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK5 |  |  | INV4 |  |  | BLK5INV4 | 22 | 0.45% | Connectors |  | MC4 found open condition | 6:03 | 6:03 | 15:25 | 15:32 | 0 | 9.3667 | 9.4833 | 9.4833 | One nos of MC4 connector replaced with new one | Close | 0.042675 | 5.51 | 91.7781
1841 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK1 |  |  | MVP |  |  | BLK1MVP | 4338 | 13.4% | LT Panel |  | Tripped on Over current | 10:10 | 10:10 | 10:15 | 10:34 | 0 | 0.083333 | 0.4 | 0.4 | Tripped due to over current | Close | 0.0536 | 0.33 | 1083.8478
1842 | 2025-05-13 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:03 | 18:30 | 12.45 | BLK8 |  |  | INV15 |  |  | BLK8INV15 | 22 | 0.4004% | Connectors |  | S7-17 half string found grounded |  |  |  |  | 0 | 0 | 0 | 0 | today will close this fault | Close | 0 | 6.7 | 111.5995
1842 | 2025-05-14 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 6:02 | 18:33 | 12.5167 | BLK1 |  |  | MVP |  |  | BLK1MVP | 4338 | 13.4% | LT Panel |  | Tripped on Over current | 11:30 | 11:30 | 11:35 | 11:40 | 0 | 0.083333 | 0.16667 | 0.16667 | Tripped due to over current | Close | 0.022333 | 0.38 | 1248.0672
1843 | 2025-05-15 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:40 | 18:34 | 12.9 | BLK3 |  |  | INV12 |  |  | BLK3INV12 | 22.25 | 0.45% | Connectors |  | MC4 found open condition | 5:40 | 9:00 | 9:40 | 9:58 | 3.3333 | 4 | 4.3 | 4.3 | mc4 tightned | Close | 0.01935 | 0.342 | 5.7613
1844 | 2025-05-15 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:40 | 18:34 | 12.9 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 19.1 | 0.4065% | String |  | Pending for verification | 5:40 | 9:00 | 18:52 | 18:52 | 3.3333 | 13.2 | 13.2 | 13.2 | Pending for verification | Close | 0.05366 | 6.81 | 98.4794
1845 | 2025-05-15 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:40 | 18:34 | 12.9 | BLK8 |  |  | INV15 |  |  | BLK8INV15 | 19.1 | 0.4004% | String |  | mc4 Connector Found open | 5:15 | 9:00 | 18:52 | 18:52 | 3.75 | 13.6167 | 13.6167 | 13.6167 | String cable found faulty | Close | 0.054528 | 6.81 | 98.4794
1850 | 2025-05-16 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:24 | 13.15 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 19.1 | 0.2852% | String |  | mc4 Connector Found open | 5:15 | 12:15 | 12:15 | 12:15 | 7 | 7 | 7 | 7 | String Found open restored immidiate | Close | 0.019962 | 2.3 | 33.2603
1851 | 16-May-25 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:24 | 13.15 | BLK7 |  |  | INV12 |  |  | BLK7INV12 | 19.1 | 0.4054% | String |  | mc4 Connector Found open | 5:15 | 13:10 | 13:10 | 13:10 | 7.9167 | 7.9167 | 7.9167 | 7.9167 | String Found open restored immidiate | Close | 0.032094 | 3.1 | 44.8291
1852 | 2025-05-17 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:27 | 18:25 | 12.9667 | BLK4 |  |  | INV31 |  |  | BLK4INV31 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:27 | 10:55 | 10:55 | 10:55 | 5.4667 | 5.4667 | 5.4667 | 5.4667 | String Found open restored immidiate | Close | 0.021867 | 0.8 | 11.5688
1853 | 2025-05-17 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:27 | 18:25 | 12.9667 | BLK4 |  |  | INV16 |  |  | BLK4INV16 | 19.1 | 0.45% | String |  | mc4 Connector Found open | 5:27 | 11:13 | 11:13 | 11:13 | 5.7667 | 5.7667 | 5.7667 | 5.7667 | String Found open restored immidiate | Close | 0.02595 | 1.2 | 17.3532
1854 | 2025-05-17 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:27 | 18:25 | 12.9667 | BLK8 |  |  | INV7 |  |  | BLK8INV7 | 19.1 | 0.4333% | String |  | mc4 Connector Found open | 5:27 | 18:08 | 18:08 | 18:08 | 12.6833 | 12.6833 | 12.6833 | 12.6833 | String Found open restored immidiate | Close | 0.054961 | 4.2 | 60.7362
| 2025-05-18 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:23 | 13.15 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 19.1 | 0.3955% | String |  | Y Connector found open same replaced after avrifying load | 5:14 | 12:22 | 12:22 | 12:22 | 7.1333 | 7.1333 | 7.1333 | 7.1333 | String Found open restored immidiate | Close | 0.028213 | 5.1 | 73.7511
1856 | 2025-05-18 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:23 | 13.15 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 22.25 | 0.4449% | String |  | String cut by grass cutting machine same is restored after applying 2 nos Positive and Negative MC4 Connectore | 16:39 | 18:30 | 18:30 | 18:30 | 1.85 | 1.85 | 1.85 | 1.85 | String Found open restored immidiate | Close | 0.0082315 | 0.3 | 5.0538
1857 | 2025-05-18 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:23 | 13.15 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 19.1 | 0.3955% | String |  | Mc4 Connector found open same is restored after varifying the load | 5:14 | 10:05 | 10:05 | 10:05 | 4.85 | 4.85 | 4.85 | 4.85 | String Found open restored immidiate | Close | 0.019182 | 2.3 | 33.2603
1842 | 2025-05-18 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:23 | 13.15 | BLK8 |  |  | All_Inv |  |  | BLK8All_Inv | 4338 |  | LT Panel |  | Tripped on Over current | 12:54 | 12:54 | 13:04 | 13:04 | 0 | 0.16667 | 0.16667 | 0.16667 | Tripped due to over current | Close |  | 0.31 | 1018.1601
1859 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK1 |  |  | INV15 |  |  | BLK1INV15 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 10:15 | 10:15 | 10:15 | 5.0167 | 5.0167 | 5.0167 | 5.0167 | mc4 Connector Found open | Close | 0.020067 | 2.3 | 33.2603
1860 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK1 |  |  | INV21 |  |  | BLK1INV21 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 10:21 | 10:21 | 10:21 | 5.1167 | 5.1167 | 5.1167 | 5.1167 | mc4 Connector Found open | Close | 0.020467 | 2.32 | 33.5495
1861 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK3 |  |  | INV10 |  |  | BLK3INV10 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 10:33 | 10:33 | 10:33 | 5.3167 | 5.3167 | 5.3167 | 5.3167 | mc4 Connector Found open | Close | 0.021267 | 2.38 | 34.4172
1862 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK4 |  |  | INV9 |  |  | BLK4INV9 | 22.25 | 0.4% | String |  | Y Connectoor Fuse was failure | 5:14 | 10:48 | 10:48 | 10:48 | 5.5667 | 5.5667 | 5.5667 | 5.5667 |  | Close | 0.022267 | 2.38 | 40.0933
1863 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK2 |  |  | INV11 |  |  | BLK2INV11 | 22.25 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 10:57 | 10:57 | 10:57 | 5.7167 | 5.7167 | 5.7167 | 5.7167 | mc4 Connector Found open | Close | 0.022867 | 2.34 | 39.4195
1864 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK2 |  |  | INV13 |  |  | BLK2INV13 | 19.1 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 11:20 | 11:20 | 11:20 | 6.1 | 6.1 | 6.1 | 6.1 | mc4 Connector Found open | Close | 0.0244 | 2.45 | 35.4294
1865 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:27 | 13.2167 | BLK2 |  |  | INV10 |  |  | BLK2INV10 | 22.25 | 0.4% | String |  | mc4 Connector Found open | 5:14 | 11:28 | 11:28 | 11:28 | 6.2333 | 6.2333 | 6.2333 | 6.2333 | mc4 Connector Found open | Close | 0.024933 | 2.45 | 41.2725
1866 | 2025-05-19 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK8 |  |  | MVP |  |  | BLK8MVP | 4338 | 10.55% | LT Panel |  | Tripped on Over current | 11:45 | 11:45 | 11:50 | 11:50 | 0 | 0.083333 | 0.083333 | 0.083333 | Tripped on Over current | Close | 0.0087908 | 0.3 | 985.3162
1867 | 2025-05-20 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK6 |  |  | INV17 |  |  | BLK6INV17 | 22.25 | 0.412% | String |  | Yconnector Fuse burn | 5:14 | 11:14 | 11:14 | 11:14 | 6 | 6 | 6 | 6 | Y Connectoor Fuse was failure | Close | 0.024719 | 2.3 | 38.7456
1868 | 2025-05-20 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK7 |  |  | INV2 |  |  | BLK7INV2 | 22.25 | 0.3955% | String |  | mc4 Connector Found open | 5:14 | 12:30 | 12:30 | 12:30 | 7.2667 | 7.2667 | 7.2667 | 7.2667 | mc4 Connector Found open | Close | 0.02874 | 2.4 | 40.4302
1869 | 2025-05-20 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK8 |  |  | INV9 |  |  | BLK8INV9 | 22.25 | 0.4333% | String |  | Yconnector Fuse burn | 5:14 | 17:09 | 17:09 | 17:09 | 11.9167 | 11.9167 | 11.9167 | 11.9167 | Y Connectoor Fuse was failure | Close | 0.051639 | 3.4 | 57.2761
1870 | 2025-05-20 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:26 | 13.2 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 22.25 | 0.3856% | String |  | 1 module replaced | 5:14 | 15:40 | 15:40 | 15:40 | 10.4333 | 10.4333 | 10.4333 | 10.4333 | Module replaced | Close | 0.040233 | 4 | 67.3837
1871 | 2025-05-21 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:27 | 13.1833 | BLK8 |  |  | INV14 |  |  | BLK8INV14 | 22.25 | 0.3856% | String |  | Yconnector Fuse burn | 5:14 | 10:10 | 10:10 | 10:10 | 4.9333 | 4.9333 | 4.9333 | 4.9333 | Y Connectoor Fuse was failure | Close | 0.019024 | 1 | 16.8459
1872 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK3 |  |  | INV16 |  |  | BLK3INV16 | 22.25 | 0.4% | String |  | module fixing | 5:16 | 8:00 | 9:50 | 10:08 | 2.7333 | 4.5667 | 4.8667 | 4.8667 | module fixing, tighten & string rectification | Close | 0.019467 | 0.347 | 5.8455
1873 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK3 |  |  | INV13 |  |  | BLK3INV13 | 22.25 | 0.45% | String |  | module fixing | 5:16 | 8:00 | 10:10 | 10:30 | 2.7333 | 4.9 | 5.2333 | 5.2333 | module fixing, tighten & string rectification | Close | 0.02355 | 0.347 | 5.8455
1874 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK3 |  |  | INV12 |  |  | BLK3INV12 | 22.25 | 0.45% | String |  | module fixing | 5:16 | 8:00 | 10:35 | 10:45 | 2.7333 | 5.3167 | 5.4833 | 5.4833 | module fixing, tighten & string rectification | Close | 0.024675 | 0.375 | 6.3172
1875 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | String |  | module fixing | 5:16 | 8:00 | 10:10 | 10:40 | 2.7333 | 4.9 | 5.4 | 5.4 | module fixing, tighten & string rectification | Close | 0.0243 | 0.396 | 6.671
1876 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK5 |  |  | INV15 |  |  | BLK5INV15 | 22.25 | 0.4% | String |  | module fixing | 5:16 | 8:00 | 15:52 | 16:20 | 2.7333 | 10.6 | 11.0667 | 11.0667 | module fixing, tighten & string rectification | Close | 0.044267 | 0.389 | 6.5531
1877 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK5 |  |  | INV22 |  |  | BLK5INV22 | 22.25 | 0.4% | String |  | module fixing | 5:16 | 8:00 | 15:40 | 16:10 | 2.7333 | 10.4 | 10.9 | 10.9 | module fixing, tighten & string rectification | Close | 0.0436 | 0.585 | 9.8549
1878 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22.25 | 0.3955% | String |  | module fixing | 5:16 | 8:00 | 12:15 | 12:30 | 2.7333 | 6.9833 | 7.2333 | 7.2333 | module fixing, tighten & string rectification | Close | 0.028608 | 0.582 | 9.8043
1879 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK7 |  |  | INV12 |  |  | BLK7INV12 | 20.1 | 0.4054% | String |  | module fixing | 5:16 | 8:00 | 12:35 | 12:50 | 2.7333 | 7.3167 | 7.5667 | 7.5667 | module fixing, tighten & string rectification | Close | 0.030675 | 0.506 | 7.7004
1880 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK7 |  |  | INV13 |  |  | BLK7INV13 | 20.1 | 0.3667% | String |  | module fixing | 5:16 | 8:00 | 12:00 | 12:17 | 2.7333 | 6.7333 | 7.0167 | 7.0167 | module fixing, tighten & string rectification | Close | 0.025728 | 0.535 | 8.1417
1881 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV2 |  |  | BLK8INV2 | 19.1 | 0.2966% | String |  | module fixing | 5:16 | 8:00 | 10:50 | 11:11 | 2.7333 | 5.5667 | 5.9167 | 5.9167 | module fixing, tighten & string rectification | Close | 0.017551 | 0.43 | 6.2182
1882 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV2 |  |  | BLK8INV2 | 19.1 | 0.2966% | String |  | module fixing | 5:16 | 8:00 | 10:50 | 11:22 | 2.7333 | 5.5667 | 6.1 | 6.1 | module fixing, tighten & string rectification | Close | 0.018094 | 0.444 | 6.4207
1883 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV2 |  |  | BLK8INV2 | 19.1 | 0.2966% | String |  | module fixing | 5:16 | 8:00 | 10:50 | 11:35 | 2.7333 | 5.5667 | 6.3167 | 6.3167 | module fixing, tighten & string rectification | Close | 0.018737 | 0.46 | 6.6521
1884 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV17 |  |  | BLK8INV17 | 31.9 | 0.2667% | String |  | module fixing | 5:16 | 8:00 | 11:00 | 11:22 | 2.7333 | 5.7333 | 6.1 | 6.1 | module fixing, tighten & string rectification | Close | 0.016267 | 0.444 | 10.7235
1885 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 31.9 | 0.4065% | String |  | module fixing | 5:16 | 8:00 | 11:15 | 11:30 | 2.7333 | 5.9833 | 6.2333 | 6.2333 | module fixing, tighten & string rectification | Close | 0.02534 | 0.454 | 10.9651
1886 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 31.9 | 0.4065% | String |  | module fixing | 5:16 | 8:00 | 11:15 | 11:40 | 2.7333 | 5.9833 | 6.4 | 6.4 | module fixing, tighten & string rectification | Close | 0.026017 | 0.465 | 11.2307
1887 | 2025-05-22 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:16 | 18:29 | 13.2167 | BLK8 |  |  | INV28 |  |  | BLK8INV28 | 20.1 | 0.3856% | String |  | module fixing | 5:16 | 8:00 | 11:20 | 11:40 | 2.7333 | 6.0667 | 6.4 | 6.4 | module fixing, tighten & string rectification | Close | 0.02468 | 0.465 | 7.0764
1888 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK2 |  |  | INV10 |  |  | BLK2INV10 | 22.25 | 0.4% | String |  | 2 fuse was fused which was replaced with a new one & restored | 5:13 | 8:00 | 10:50 | 11:05 | 2.7833 | 5.6167 | 5.8667 | 5.8667 | fuse replaced with a new one & connect the same | Close | 0.023467 | 0.405 | 6.8226
1889 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK3 |  |  | INV7 |  |  | BLK3INV7 | 22.25 | 0.4% | String |  | mc4 open so rectify & connect the same | 5:13 | 8:00 | 11:00 | 11:20 | 2.7833 | 5.7833 | 6.1167 | 6.1167 | mc4 Connector Found open | Close | 0.024467 | 0.424 | 7.1427
1890 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK1 |  |  | INV28 |  |  | BLK1INV28 | 22.25 | 0.45% | String |  | mc4 open so rectify & connect the same | 5:13 | 8:00 | 11:35 | 11:50 | 2.7833 | 6.3667 | 6.6167 | 6.6167 | mc4 Connector Found open | Close | 0.029775 | 0.462 | 7.7828
1891 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK5 |  |  | INV15 |  |  | BLK5INV15 | 22.25 | 0.4% | String |  | module fixing | 5:13 | 8:00 | 12:10 | 13:01 | 2.7833 | 6.95 | 7.8 | 7.8 | module fixing, tighten & string rectification | Close | 0.0312 | 0.533 | 8.9789
1892 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK6 |  |  | INV12 |  |  | BLK6INV12 | 22.25 | 0.3955% | String |  | mc4 open so rectify & connect the same | 5:13 | 8:00 | 17:20 | 17:40 | 2.7833 | 12.1167 | 12.45 | 12.45 | mc4 open so rectify & connect the same | Close | 0.04924 | 0.629 | 10.5961
1893 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK6 |  |  | INV8 |  |  | BLK6INV8 | 22.25 | 0.4449% | String |  | String cable found faulty | 5:13 | 8:00 | 17:05 | 17:25 | 2.7833 | 11.8667 | 12.2 | 12.2 | String cable found faulty | Close | 0.054283 | 0.631 | 10.6298
1894 | 2025-05-23 |  | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:13 | 18:29 | 13.2667 | BLK6 |  |  | INV14 |  |  | BLK6INV14 | 22.25 | 0.412% | String |  | mc4 open so rectify & connect the same | 5:13 | 8:00 | 17:30 | 17:45 | 2.7833 | 12.2833 | 12.5333 | 12.5333 | mc4 open so rectify & connect the same | Close | 0.051635 | 0.633 | 10.6635
1895 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK6 |  |  | INV26 |  |  | BLK6INV26 | 22.25 | 0.4449% | MCCB |  | Inv MCCB (250Amp) flash-over replaced with a new one & restore | 5:15 | 5:15 | 10:40 | 11:46 | 0 | 5.4167 | 6.5167 | 6.5167 | Inv MCCB (250Amp) flash-over replaced with a new one & restore | Close | 0.028996 | 2.16 | 36.3872
1896 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK6 |  |  | INV25 |  |  | BLK6INV25 | 22.25 | 0.4449% | MCCB |  | Manually shutdown taken for restoretion work of inv 26 | 5:15 | 10:38 | 10:38 | 11:40 | 5.3833 | 5.3833 | 6.4167 | 6.4167 | Manually shutdown taken for restoretion work of inv 26 | Close | 0.028551 | 0.608 | 10.2423
1897 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK3 |  |  | INV29 |  |  | BLK3INV29 | 22.25 | 0.4333% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 15:15 | 15:28 | 3.75 | 10 | 10.2167 | 10.2167 | MC4 Connector found open Same is restored after verfying the load | Close | 0.044272 | 4.987 | 84.0106
1898 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK3 |  |  | INV24 |  |  | BLK3INV24 | 22.25 | 0.4% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 15:15 | 15:32 | 3.75 | 10 | 10.2833 | 10.2833 | MC4 Connector found open Same is restored after verfying the load | Close | 0.041133 | 5.081 | 85.5941
1899 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK2 |  |  | INV24 |  |  | BLK2INV24 | 22.25 | 0.4333% | String |  | Found Fuse burn replace with a new one & restore the same | 5:15 | 9:00 | 15:30 | 15:53 | 3.75 | 10.25 | 10.6333 | 10.6333 | Found Fuse burn replace with a new one & restore the same | Close | 0.046078 | 5.123 | 86.3017
1900 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK7 |  |  | INV5 |  |  | BLK7INV5 | 22.25 | 0.3955% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 16:25 | 16:40 | 3.75 | 11.1667 | 11.4167 | 11.4167 | MC4 Connector found open Same is restored after verfying the load | Close | 0.045154 | 5.325 | 89.7045
1901 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK7 |  |  | INV2 |  |  | BLK7INV2 | 22.25 | 0.3955% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 16:20 | 16:47 | 3.75 | 11.0833 | 11.5333 | 11.5333 | MC4 Connector found open Same is restored after verfying the load | Close | 0.045615 | 5.416 | 91.2375
1902 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | String |  | Found Fuse burn replace with a new one & restore the same | 5:15 | 9:00 | 16:50 | 17:12 | 3.75 | 11.5833 | 11.95 | 11.95 | Found Fuse burn replace with a new one & restore the same | Close | 0.053775 | 5.44 | 91.6418
1903 | 2025-05-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:15 | 18:29 | 13.2333 | BLK4 |  |  | INV31 |  |  | BLK4INV31 | 22.25 | 0.4% | String |  | Found Fuse burn replace with a new one & restore the same | 5:15 | 9:00 | 17:15 | 17:35 | 3.75 | 12 | 12.3333 | 12.3333 | Found Fuse burn replace with a new one & restore the same | Close | 0.049333 | 5.61 | 94.5056
1904 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK4 |  |  | INV24 |  |  | BLK4INV24 | 22.25 | 0.45% | String |  | Found MC4 Faulty | 5:45 | 9:00 | 11:20 | 11:36 | 3.25 | 5.5833 | 5.85 | 5.85 | 1Pair of MC4 connector replaced with new one | Close | 0.026325 | 2.53 | 42.6202
1905 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK2 |  |  | INV20 |  |  | BLK2INV20 | 44.5 | 0.4% | String |  | Found MC4 Faulty | 5:45 | 9:00 | 10:10 | 10:38 | 3.25 | 4.4167 | 4.8833 | 4.8833 | 1 No of MC4, 1 pcs of Y connector & 1 pair of Fuse replaced with new one | Close | 0.019533 | 1.75 | 58.9607
1906 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 22.25 | 0.3955% | String |  | Found MC4 Faulty | 5:45 | 9:00 | 11:30 | 11:56 | 3.25 | 5.75 | 6.1833 | 6.1833 | 1Pair of MC4 connector replaced with new one | Close | 0.024455 | 2.82 | 47.5055
1907 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 11.5 | 0.3955% | String |  | module displaced | 5:45 | 9:00 | 15:15 | 15:36 | 3.25 | 9.5 | 9.85 | 9.85 | Fixed with same | Close | 0.038957 | 5.76 | 50.1516
1908 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK8 |  |  | INV2 |  |  | BLK8INV2 | 9.5 | 0.2966% | String |  | module displaced | 5:45 | 9:00 | 15:20 | 15:41 | 3.25 | 9.5833 | 9.9333 | 9.9333 | Fixed with same | Close | 0.029465 | 5.77 | 41.5015
1909 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 15.75 | 0.4065% | String |  | module displaced | 5:45 | 9:00 | 15:25 | 15:44 | 3.25 | 9.6667 | 9.9833 | 9.9833 | Fixed with same | Close | 0.040584 | 5.77 | 68.8052
1910 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 11.25 | 0.45% | String |  | module displaced | 5:45 | 9:00 | 9:50 | 10:10 | 3.25 | 4.0833 | 4.4167 | 4.4167 | Fixed with same | Close | 0.019875 | 1.25 | 10.647
1911 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK5 |  |  | INV12 |  |  | BLK5INV12 | 286 | 0.4285% | Inverter |  | Module flyout due to yesterday wind strom impact , same is restored | 5:45 | 9:00 | 6:45 | 7:05 | 3.25 | 1 | 1.3333 | 1.3333 | Reset & Started | Close | 0.0057129 | 0.201 | 43.5238
1912 | 2025-05-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:45 | 18:31 | 12.7667 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | Inverter |  | Module flyout due to yesterday wind strom impact , same is restored | 7:20 | 9:00 | 7:20 | 7:40 | 1.6667 | 0 | 0.33333 | 0.33333 | Reset & Started | Close | 0.0013333 | 0.349 | 70.5507
1913 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:31 | 13.2833 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 3947.5 | 5.914% | LT Panel |  | LT1 trippedon over current fault | 10:28 | 10:28 | 10:33 | 10:40 | 0 | 0.083333 | 0.2 | 0.2 | Check the all parmeter & charged | Close | 0.011828 | 0.113 | 337.7267
1914 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:31 | 13.2833 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | Inverter |  | Inverter tripped on excessive leakage current fault | 11:30 | 11:30 | 11:35 | 12:14 | 0 | 0.083333 | 0.73333 | 0.73333 | Reset & Started | Close | 0.0029333 | 0.393 | 79.4454
1915 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:31 | 13.2833 | BLK5 |  |  | INV23 |  |  | BLK5INV23 | 22.25 | 0.3667% | String |  | Module flyout due to day before yesterday wind strom impact , same is restored | 5:14 | 9:00 | 12:05 | 12:40 | 3.7667 | 6.85 | 7.4333 | 7.4333 | Fixed with same | Close | 0.027256 | 2.319 | 39.0657
1916 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:31 | 13.2833 | BLK1 |  |  | INV17 |  |  | BLK1INV17 | 22.25 | 0.4% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:14 | 9:00 | 12:35 | 13:00 | 3.7667 | 7.35 | 7.7667 | 7.7667 | MC4 Connector found open Same is restored after verfying the load | Close | 0.031067 | 2.46 | 41.441
1917 | 2025-05-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:14 | 18:31 | 13.2833 | BLK1 | LT2 |  |  |  |  | BLK1LT2 | 4605.75 | 6.9% | LT Panel |  | LT1 trippedon over current fault | 13:18 | 13:18 | 13:29 | 13:29 | 0 | 0.18333 | 0.18333 | 0.18333 | Check the all parmeter & charged | Close | 0.01265 | 0.111 | 387.0688
1918 | 2025-05-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:10 | 18:31 | 13.35 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 16:25 | 16:25 | 3.75 | 11.1667 | 11.1667 | 11.1667 | MC4 Connector found open Same is restored after verfying the load | Close | 0.05025 | 5 | 84.2296
1919 | 2025-05-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:10 | 18:31 | 13.35 | BLK5 |  |  | INV2 |  |  | BLK5INV2 | 22.25 | 0.4% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 16:09 | 16:09 | 3.75 | 10.9 | 10.9 | 10.9 | MC4 Connector found open Same is restored after verfying the load | Close | 0.0436 | 4.3 | 72.4375
1920 | 2025-05-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:10 | 18:31 | 13.35 | BLK5 |  |  | INV32 |  |  | BLK5INV32 | 22.25 | 0.4% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 9:00 | 15:50 | 15:50 | 3.75 | 10.5833 | 10.5833 | 10.5833 | MC4 Connector found open Same is restored after verfying the load | Close | 0.042333 | 4.2 | 70.7529
1921 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK1 | LT1 |  |  |  |  | BLK1LT1 | 4338.75 | 6.5% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:00 | 13:10 |  |  |  |  | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0 | 1.746 | 5735.5319
1922 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK1 | LT2 |  |  |  |  | BLK1LT2 | 4605.75 | 6.9% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:00 | 13:10 |  |  |  |  | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0 | 1.746 | 6088.4877
1923 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK2 | LT1 |  |  |  |  | BLK2LT1 | 4094 | 6.133% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:00 | 13:10 | 0 | 1.8167 | 1.9833 | 1.9833 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0.12164 | 1.746 | 5411.989
1924 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 4249.75 | 6.367% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:00 | 13:10 | 0 | 1.8167 | 1.9833 | 1.9833 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0.12627 | 1.746 | 5617.8799
1925 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK3 | LT1 |  |  |  |  | BLK3LT1 | 4483.375 | 6.717% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:05 | 13:13 | 0 | 1.9 | 2.0333 | 2.0333 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0.13657 | 1.791 | 6079.4667
1926 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK3 | LT2 |  |  |  |  | BLK3LT2 | 4071.75 | 6.1% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:05 | 13:13 | 0 | 1.9 | 2.0333 | 2.0333 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0.12403 | 1.791 | 5521.3022
1927 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK4 | LT1 |  |  |  |  | BLK4LT1 | 4394.375 | 6.583% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:05 | 13:13 | 0 | 1.9 | 2.0333 | 2.0333 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0.13386 | 1.791 | 5958.7825
1928 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK4 | LT2 |  |  |  |  | BLK4LT2 | 4260.875 | 6.383% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:05 | 13:13 | 0 | 1.9 | 2.0333 | 2.0333 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0.12979 | 1.791 | 5777.7562
1929 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK7 | LT1 |  |  |  |  | BLK7LT1 | 3298.1 | 4.941% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:12 | 13:17 | 0 | 2.0167 | 2.1 | 2.1 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0.10376 | 1.725 | 4307.4252
1930 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK7 | LT2 |  |  |  |  | BLK7LT2 | 4071.75 | 6.1% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:12 | 13:17 | 0 | 2.0167 | 2.1 | 2.1 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0.1281 | 1.725 | 5317.8372
1931 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 3947.5 | 5.914% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:12 | 13:17 | 0 | 2.0167 | 2.1 | 2.1 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0.12419 | 1.725 | 5155.5626
1932 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK8 | LT2 |  |  |  |  | BLK8LT2 | 3093.9 | 4.635% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 13:12 | 13:17 | 0 | 2.0167 | 2.1 | 2.1 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0.097336 | 1.725 | 4040.7334
1933 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK5 | LT1 |  |  |  |  | BLK5LT1 | 4514.875 | 6.764% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 15:30 | 15:39 | 0 | 4.3167 | 4.4667 | 4.4667 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0.30212 | 2.152 | 7356.1881
1934 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK5 | LT2 |  |  |  |  | BLK5LT2 | 4349.875 | 6.517% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 15:30 | 15:39 | 0 | 4.3167 | 4.4667 | 4.4667 | After Isolation of Block-6 and all parameter checking & physical inspection of all equipment we restored it | Close | 0.29108 | 2.152 | 7087.3499
1935 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK6 | LT1 |  |  |  |  | BLK6LT1 | 4477 | 6.707% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 18:31 | 18:31 | 0 | 7.3333 | 7.3333 | 7.3333 | Jointing work in progress, It will be restored after joint work. | Close | 0.49186 | 4.381 | 14849.9564
1936 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 4499 | 6.74% | LT Panel |  | Plant was in breakdown due to HT cable failure(It was failure during civil construction(Vendor Name:- Govind Yadav(O2 Power)) work at near between block-5 & 6 river area. Same is restored after isolate the block-6 Cable Failure Details:- Block-6 O/G cable (Rating 3C*300 Sqmm) | 11:11 | 11:11 | 18:31 | 18:31 | 0 | 7.3333 | 7.3333 | 7.3333 | Jointing work in progress, It will be restored after joint work. | Close | 0.49427 | 4.381 | 14922.9291
1937 | 2025-05-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:06 | 18:31 | 13.4167 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 22.25 | 0.3333% | string |  | Inverter was tripped due to excessive leakage current, | 13:15 | 13:15 | 13:20 | 12:42 | 0 | 0.083333 | -0.55 | -0.55 | we have physically checked all parameter of this inverter & string's then we found that string no-2 MC4 Connector Positive & negative was failure same is restored after replaced it new one. | Close | -0.0018333 | 0.398 | 6.7047
1938 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:09 | 18:19 | 13.1667 | BLK5 | LT1 |  |  |  |  | BLK5LT1 | 4514.875 | 6.764% | LT Panel |  | HT Cables jointing work has been done of Block-6 O/G Cable, we have to take manually shutdown of incommer-3(Connected Block 5&6) for take load of Block which is connected to block -5 | 13:20 | 13:20 | 13:40 | 13:56 | 0 | 0.33333 | 0.6 | 0.6 | After connected the load of block-6 to block -5, checked the all parameters then charged the Block 5 | Close | 0.040583 | 0.456 | 1558.7462
1939 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:09 | 18:19 | 13.1667 | BLK5 | LT2 |  |  |  |  | BLK5LT2 | 4349.875 | 6.517% | LT Panel |  | HT Cables jointing work has been done of Block-6 O/G Cable, we have to take manually shutdown of incommer-3(Connected Block 5&6) for take load of Block which is connected to block -5 | 13:20 | 13:20 | 13:40 | 13:56 | 0 | 0.33333 | 0.6 | 0.6 | After connected the load of block-6 to block -5, checked the all parameters then charged the Block 5 | Close | 0.0391 | 0.456 | 1501.7805
1940 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:09 | 18:19 | 13.1667 | BLK6 | LT1 |  |  |  |  | BLK6LT1 | 4477 | 6.707% | LT Panel |  | HT Cable jointing work | 5:09 | 5:09 | 14:00 | 14:13 | 0 | 8.85 | 9.0667 | 9.0667 | after checking all the parameter & visual inspection of block 6 we charge the ICR | Close | 0.60811 | 4.47 | 15151.6332
1941 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:09 | 18:19 | 13.1667 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 4499 | 6.74% | LT Panel |  | HT Cable jointing work | 5:09 | 5:09 | 14:00 | 14:13 | 0 | 8.85 | 9.0667 | 9.0667 | after checking all the parameter & visual inspection of block 6 we charge the ICR | Close | 0.6111 | 4.47 | 15226.0884
1942 | 2025-05-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 5:09 | 18:19 | 13.1667 | BLK8 | LT1 |  |  |  |  | BLK8LT1 | 3947.5 | 5.914% | LT Panel |  | LT-1 was in breakdown under over current | 13:42 | 13:50 | 14:35 | 14:48 | 0.13333 | 0.88333 | 1.1 | 1.1 | after checking all the parameter & visual inspection of block 8 LT-1 we charge it. | Close | 0.065052 | 0.345 | 1031.1125
1943 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 22.25 | 6.74% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 10:30 | 10:30 | 1924.75 | 5.25 | 5.25 | 5.25 | MC4 Connector found open Same is restored after verfying the load | Close | 0.35385 | 2.2 | 37.061
1944 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 22.25 | 6.74% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 11:00 | 11:00 | 1924.75 | 5.75 | 5.75 | 5.75 | MC4 Connector found open Same is restored after verfying the load | Close | 0.38755 | 2.1 | 35.3764
1945 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK6 | LT2 |  |  |  |  | BLK6LT2 | 22.25 | 6.74% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 11:05 | 11:05 | 1924.75 | 5.8333 | 5.8333 | 5.8333 | MC4 Connector found open Same is restored after verfying the load | Close | 0.39317 | 2.1 | 35.3764
1946 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK1 | LT1 |  |  |  |  | BLK1LT1 | 22.25 | 6.5% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 14:28 | 14:28 | 1924.75 | 9.2167 | 9.2167 | 9.2167 | MC4 Connector found open Same is restored after verfying the load | Close | 0.59908 | 4.3 | 72.4375
1947 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK1 | LT1 |  |  |  |  | BLK1LT1 | 22.25 | 6.5% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 14:38 | 14:38 | 1924.75 | 9.3833 | 9.3833 | 9.3833 | MC4 Connector found open Same is restored after verfying the load | Close | 0.60992 | 4.4 | 74.1221
1948 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 22.25 | 6.367% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 14:53 | 14:53 | 1924.75 | 9.6333 | 9.6333 | 9.6333 | MC4 Connector found open Same is restored after verfying the load | Close | 0.61332 | 4.5 | 75.8067
1949 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK2 | LT2 |  |  |  |  | BLK2LT2 | 22.25 | 6.367% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:15 | 1930:00 | 15:38 | 15:38 | 1924.75 | 10.3833 | 10.3833 | 10.3833 | MC4 Connector found open Same is restored after verfying the load | Close | 0.66107 | 5 | 84.2296
1950 | 2025-05-31 | 2025 | 2025 | Year_2 | Year_2 | 2025-05-01 | 31 | 05:13 | 18:24 | 13.1833 | BLK8 | LT2 |  |  |  |  | BLK8LT2 | 67.25 | 4.635% | string |  | Block8 Inv No 28 3 nos String add after replaced all faulty module(Jakson-335wp),Now Inverter isrunning with total 12.5 String | 5:15 | 1930:00 | 16:40 | 16:40 | 1924.75 | 11.4167 | 11.4167 | 11.4167 | Block8 Inv No 28 3 nos String add after replaced all faulty module(Jakson-335wp),Now Inverter isrunning with total 12.5 String | Close | 0.52917 | 5.3 | 269.8566
1951 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:33 | 13.3167 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 267 | 0.3955% | Inverter |  | Inv 6 Under breakdown due to insulation fault | 5:14 | 10:00 | 9:32 | 9:32 | 4.7667 | 4.3 | 4.3 | 4.3 | Inv 6 Under breakdown due to insulation fault | Close | 0.017007 | 2.1 | 426.2119
1952 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:33 | 13.3167 | BLK6 |  |  | INV24 |  |  | BLK6INV24 | 22.3 | 0.4285% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:14 | 10:00 | 10:20 | 10:20 | 4.7667 | 5.1 | 5.1 | 5.1 | MC4 Connector found open Same is restored after verfying the load | Close | 0.021852 | 1.3 | 22.0365
1953 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:33 | 13.3167 | BLK8 |  |  | INV14 |  |  | BLK8INV14 | 22.3 | 0.3856% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:14 | 10:00 | 10:38 | 10:38 | 4.7667 | 5.4 | 5.4 | 5.4 | MC4 Connector found open Same is restored after verfying the load | Close | 0.020823 | 1.4 | 23.7317
1954 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:33 | 13.3167 | BLK2 |  |  | INV29 |  |  | BLK2INV29 | 22.3 | 0.45% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:14 | 10:00 | 11:20 | 11:20 | 4.7667 | 6.1 | 6.1 | 6.1 | MC4 Connector found open Same is restored after verfying the load | Close | 0.02745 | 1.5 | 25.4268
1955 | 2025-06-01 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:33 | 13.3167 | BLK8 |  |  | INV26 |  |  | BLK8INV26 | 22.3 | 0.4065% | string |  | MC4 Connector found open Same is restored after verfying the load | 5:14 | 10:00 | 2:45 | 2:45 | 4.7667 | -2.4833 | -2.4833 | -2.4833 | MC4 Connector found open Same is restored after verfying the load | Close | -0.010095 | 1.4 | 23.7317
1956 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:36 | 11:36 | 11:36 | 11:46 | 0 | 0 | 0.16667 | 0.16667 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.022333 | 0.3 | 2039.7285
1957 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8909 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:36 | 11:36 | 11:46 | 11:46 | 0 | 0.16667 | 0.16667 | 0.16667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.022134 | 0.3 | 2031.633
1958 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8944.5 | 13.45% | IDT |  | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:38 | 11:38 | 11:48 | 11:48 | 0 | 0.16667 | 0.16667 | 0.16667 | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.022412 | 0.3 | 2039.7285
1959 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:38 | 11:38 | 11:53 | 11:53 | 0 | 0.25 | 0.25 | 0.25 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.0335 | 0.4 | 2719.638
1960 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:24 | 12:24 | 12:31 | 12:31 | 0 | 0.11667 | 0.11667 | 0.11667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.014583 | 0.28 | 1887.9113
1961 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:24 | 12:24 | 12:35 | 12:35 | 0 | 0.18333 | 0.18333 | 0.18333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.024348 | 0.29 | 1978.6815
1963 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8909.25 | 13.45% | IDT |  | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:24 | 12:24 | 12:38 | 12:38 | 0 | 0.23333 | 0.23333 | 0.23333 | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.031377 | 0.31 | 2099.413
1964 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK5 |  |  | INV20 |  |  | BLK5INV20 | 22.5 | 0.4% | string |  | Found Fuse, Y- connector & MC4 burn replace with a new one & restore the same | 12:24 | 12:24 | 12:40 | 12:40 | 0 | 0.26667 | 0.26667 | 0.26667 | Found Fuse, Y- connector & MC4 burn replace with a new one & restore the same | Close | 0.0010667 | 0.31 | 5.302
1965 | 2025-06-02 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 17:56 | 12.6833 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22.5 | 0.45% | string |  | MC4 connector melted causes failure so replaced it with new one | 5:15 | 9:00 | 15:06 | 15:06 | 3.75 | 9.85 | 9.85 | 9.85 | MC4 connector melted causes failure so replaced it with new one | Close | 0.044325 | 5.1 | 87.2264
1966 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 |  | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:11 | 11:26 | 11:17 | 11:17 | 0.25 | 0.1 |  |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0 | 0.35 | 2359.8892
1967 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:20 | 11:25 | 11:25 | 11:25 | 0.083333 | 0.083333 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.011067 | 0.21 | 1432.8383
1968 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:48 | 12:00 | 11:55 | 11:55 | 0.2 | 0.11667 | 0.11667 | 0.11667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.014583 | 0.21 | 1415.9335
1969 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:48 | 11:56 | 11:55 | 11:55 | 0.13333 | 0.11667 | 0.11667 | 0.11667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.015494 | 0.21 | 1432.8383
1970 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:09 | 12:22 | 12:15 | 12:15 | 0.21667 | 0.1 | 0.1 | 0.1 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.0134 | 0.15 | 1019.8643
1971 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:09 | 12:20 | 12:15 | 12:15 | 0.18333 | 0.1 | 0.1 | 0.1 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.0125 | 0.15 | 1011.3811
1972 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:15 | 12:21 | 12:22 | 12:22 | 0.1 | 0.11667 | 0.11667 | 0.11667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.015494 | 0.16 | 1091.6863
1973 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:28 | 12:34 | 12:35 | 12:35 | 0.1 | 0.11667 | 0.11667 | 0.11667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.014583 | 0.16 | 1078.8065
1974 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:29 | 12:36 | 12:35 | 12:35 | 0.11667 | 0.1 | 0.1 | 0.1 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.013281 | 0.14 | 955.2255
1975 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8976 | 13.45% | IDT |  | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:29 | 12:38 | 12:35 | 12:35 | 0.15 | 0.1 | 0.1 | 0.1 | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.013447 | 0.145 | 989.3407
1976 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK7 | LT1 |  |  |  |  | BLK7LT1 | 4071.75 | 4.941% | LT Panel |  | Block-7 LT1 tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:25 | 12:32 | 12:35 | 12:35 | 0.11667 | 0.16667 | 0.16667 | 0.16667 | Block-7 LT1 tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.008235 | 0.13 | 402.3644
1977 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK1 |  |  | INV1 |  |  | BLK1INV1 | 289.25 | 0.4333% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:17 | 13:12 | 12:24 | 12:24 | 0.91667 | 0.11667 | 0.11667 | 0.11667 | As per O2 Team, instruction we have taken manually shutdown for active power control | Close | 0.00050556 | 0.44 | 96.7433
1978 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK1 |  |  | INV2 |  |  | BLK1INV2 | 289.25 | 0.4333% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:17 | 13:12 | 12:24 | 12:24 | 0.91667 | 0.11667 | 0.11667 | 0.11667 | As per O2 Team, instruction we have taken manually shutdown for active power control | Close | 0.00050556 | 0.44 | 96.7433
1979 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK1 |  |  | INV3 |  |  | BLK1INV3 | 289.25 | 0.4% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:17 | 13:13 | 12:24 | 12:24 | 0.93333 | 0.11667 | 0.11667 | 0.11667 | As per O2 Team, instruction we have taken manually shutdown for active power control | Close | 0.00046667 | 0.44 | 96.7433
1980 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | INV1 |  |  | BLK2INV1 | 243.275 | 0.45% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:16 | 12:59 | 12:24 | 12:24 | 0.71667 | 0.13333 | 0.13333 | 0.13333 | As per O2 Team, instruction we have taken manually shutdown for active power control | Close | 0.0006 | 0.46 | 85.0649
1981 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 334.55 | 0.3333% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:16 | 13:05 | 12:24 | 12:24 | 0.81667 | 0.13333 | 0.13333 | 0.13333 | As per O2 Team, instruction we have taken manually shutdown for active power control | Close | 0.00044444 | 0.46 | 116.9806
1982 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | INV16 |  |  | BLK5INV16 | 289.25 | 0.4333% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:20 | 13:10 | 12:24 | 12:24 | 0.83333 | 0.066667 | 0.066667 | 0.066667 | As per O2 Team, instruction we have taken manually shutdown for active power control | Close | 0.00028889 | 0.31 | 68.1601
1983 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | INV22 |  |  | BLK5INV22 | 244.75 | 0.4% | Inverter |  | As per O2 Team, instruction we have taken manually shutdown for active power control | 12:20 | 13:10 | 12:24 | 12:24 | 0.83333 | 0.066667 | 0.066667 | 0.066667 | As per O2 Team, instruction we have taken manually shutdown for active power control | Close | 0.00026667 | 0.31 | 57.6739
1984 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV24 |  |  | BLK8INV24 | 31.9 | 0.4065% | String |  | MC4 Connector found melted, Same is restored after verfying the load | 5:19 | 9:00 | 10:31 | 10:31 | 3.6833 | 5.2 | 5.2 | 5.2 | MC4 Connector found melted, Same is restored after verfying the load | Close | 0.021139 | 1.28 | 31.0381
1985 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV15 |  |  | BLK8INV15 | 20.1 | 0.4004% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:19 | 9:00 | 10:45 | 10:45 | 3.6833 | 5.4333 | 5.4333 | 5.4333 | MC4 Connector found open Same is restored after verfying the load | Close | 0.021758 | 1.41 | 21.5432
1986 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV21 |  |  | BLK8INV21 | 20.1 | 0.4004% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:19 | 9:00 | 11:00 | 11:00 | 3.6833 | 5.6833 | 5.6833 | 5.6833 | MC4 Connector found open Same is restored after verfying the load | Close | 0.022759 | 1.56 | 23.835
1987 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV10 |  |  | BLK8INV10 | 20.1 | 0.45% | String |  | MC4 Connector found melted, Same is restored after verfying the load | 5:19 | 9:00 | 15:15 | 15:15 | 3.6833 | 9.9333 | 9.9333 | 9.9333 | MC4 Connector found melted, Same is restored after verfying the load | Close | 0.0447 | 3.7 | 56.5318
1988 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK8 |  |  | INV18 |  |  | BLK8INV18 | 20.1 | 0.3333% | String |  | MC4 Connector found open Same is restored after verfying the load | 5:19 | 9:00 | 15:30 | 15:30 | 3.6833 | 10.1833 | 10.1833 | 10.1833 | MC4 Connector found open Same is restored after verfying the load | Close | 0.033944 | 3.76 | 57.4485
1989 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22.25 | 0.3955% | String |  | Y connector & fuse failure so replaced it with new one | 5:19 | 9:00 | 15:45 | 15:45 | 3.6833 | 10.4333 | 10.4333 | 10.4333 | Y connector & fuse failure so replaced it with new one | Close | 0.041264 | 3.82 | 64.6083
1990 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 22.25 | 0.3955% | String |  | MC4 Connector found melted, Same is restored after verfying the load | 5:19 | 9:00 | 16:10 | 16:10 | 3.6833 | 10.85 | 10.85 | 10.85 | MC4 Connector found melted, Same is restored after verfying the load | Close | 0.042912 | 3.92 | 66.2996
1991 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK3 |  |  | INV28 |  |  | BLK3INV28 | 22.25 | 0.4167% | sTring |  | Y connector & fuse failure so replaced it with new one | 5:19 | 9:00 | 16:20 | 16:20 | 3.6833 | 11.0167 | 11.0167 | 11.0167 | Y connector & fuse failure so replaced it with new one | Close | 0.045903 | 3.95 | 66.807
1992 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK4 |  |  | INV4 |  |  | BLK4INV4 | 22.25 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:19 | 9:00 | 16:35 | 16:35 | 3.6833 | 11.2667 | 11.2667 | 11.2667 | MC4 Connecto found open Same is restored after verfying the load | Close | 0.045067 | 4.01 | 67.8218
1993 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | INV8 |  |  | BLK5INV8 | 22.25 | 0.4333% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:19 | 9:00 | 16:55 | 16:55 | 3.6833 | 11.6 | 11.6 | 11.6 | MC4 Connecto found open Same is restored after verfying the load | Close | 0.050267 | 4.07 | 68.8366
1994 | 2025-06-03 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:19 | 18:33 | 13.2333 | BLK5 |  |  | INV21 |  |  | BLK5INV21 | 22.25 | 0.4333% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:19 | 9:00 | 17:10 | 17:10 | 3.6833 | 11.85 | 11.85 | 11.85 | MC4 Connecto found open Same is restored after verfying the load | Close | 0.05135 | 4.11 | 69.5131
1995 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK2 |  |  | mvp |  |  | BLK2mvp | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:13 | 11:13 | 11:15 | 11:18 | 0 | 0.033333 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.010417 | 0.065 | 438.2651
1996 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | mvp |  |  | BLK5mvp | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:12 | 11:12 | 11:14 | 11:17 | 0 | 0.033333 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.011067 | 0.064 | 436.6745
1997 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV32 |  |  | BLK5INV32 | 22.23 | 0.4% | String |  | Y connector, fuse & mc4 failure | 5:10 | 9:00 | 11:55 | 12:10 | 3.8333 | 6.75 | 7 | 7 | Y connector, fuse & mc4 failure so replaced it with new one | Close | 0.028 | 2.061 | 34.8267
1998 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV29 |  |  | BLK5INV29 | 22.23 | 0.4% | String |  | MC4 Connector found melted | 5:10 | 9:00 | 12:10 | 12:25 | 3.8333 | 7 | 7.25 | 7.25 | MC4 Connector found melted, Same is restored after verfying the load | Close | 0.029 | 2.21 | 37.3445
1999 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV30 |  |  | BLK5INV30 | 22.23 | 0.4% | String |  | MC4 Connecto found open | 5:10 | 9:00 | 12:25 | 12:45 | 3.8333 | 7.25 | 7.5833 | 7.5833 | MC4 Connecto found open Same is restored after verfying the load | Close | 0.030333 | 2.38 | 40.2172
2000 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV28 |  |  | BLK5INV28 | 22.23 | 0.45% | String |  | MC4 Connecto found open | 5:10 | 9:00 | 12:45 | 13:05 | 3.8333 | 7.5833 | 7.9167 | 7.9167 | MC4 Connecto found open Same is restored after verfying the load | Close | 0.035625 | 2.54 | 42.9208
2001 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV31 |  |  | BLK5INV31 | 22.23 | 0.4% | String |  | MC4 Connecto found open | 5:10 | 9:00 | 14:50 | 15:10 | 3.8333 | 9.6667 | 10 | 10 | MC4 Connecto found open Same is restored after verfying the load | Close | 0.04 | 3.84 | 64.8882
2002 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV12 |  |  | BLK5INV12 | 22.23 | 0.4285% | String |  | MC4 Connecto found open | 5:10 | 9:00 | 15:10 | 15:30 | 3.8333 | 10 | 10.3333 | 10.3333 | MC4 Connecto found open Same is restored after verfying the load | Close | 0.044275 | 4.08 | 68.9437
2003 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22.23 | 0.45% | String |  | Found 1 fuse failure | 5:10 | 9:00 | 15:25 | 15:45 | 3.8333 | 10.25 | 10.5833 | 10.5833 | Found 1 fuse failure so replaced it with new one | Close | 0.047625 | 4.22 | 71.3094
2004 | 2025-06-04 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:33 | 13.3833 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | String |  | Inverter frequently shutdown on fault of excessive leakage current | 8:00 | 8:00 | 8:15 | 9:41 | 0 | 0.25 | 1.6833 | 1.6833 | Inverter frequently shutdown on fault of excessive leakage current after reset the fault & verify all parameter charge the inverter | Close | 0.0067333 | 0.65 | 131.9227
2005 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 | 18:36 | 13.5 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:44 | 12:44 | 12:46 | 12:57 | 0 | 0.033333 | 0.21667 | 0.21667 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.029033 | 0.38 | 2583.6561
2006 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:44 | 12:44 | 12:46 | 12:55 | 0 | 0.033333 | 0.18333 | 0.18333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.022917 | 0.38 | 2562.1654
2007 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:44 | 12:44 | 12:46 | 12:51 | 0 | 0.033333 | 0.11667 | 0.11667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | Close | 0.015494 | 0.28 | 1910.4511
2008 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK6 |  |  | MVP |  |  | BLK6MVP | 8976 | 13.45% | IDT |  | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:44 | 12:44 | 12:46 | 12:50 | 0 | 0.033333 | 0.1 | 0.1 | Block-6 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | close | 0.013447 | 0.26 | 1773.9903
2009 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 13:04 | 13:04 | 13:06 | 13:19 | 0 | 0.033333 | 0.25 | 0.25 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | close | 0.03125 | 0.28 | 1887.9113
2010 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 13:12 | 13:12 | 13:14 | 13:17 | 0 | 0.033333 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | close | 0.011067 | 0.25 | 1705.7599
2011 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK7 |  |  | MVP |  |  | BLK7MVP | 8870.1 | 11.04% | IDT |  | Block-7 LT1 tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:40 | 12:40 | 12:42 | 12:50 | 0 | 0.033333 | 0.16667 | 0.16667 | Block-7 LT1 tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | close | 0.018402 | 0.22 | 1483.3589
2012 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK1 |  |  | INV1 |  |  | BLK1INV1 | 289.25 | 0.4333% | Inverter |  | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | 10:39 | 10:55 | 10:55 | 10:55 | 0.26667 | 0.26667 | 0.26667 | 0.26667 | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | close | 0.0011556 | 0.31 | 68.1601
2013 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK2 |  |  | INV29 |  |  | BLK2INV29 | 267 | 0.45% | Inverter |  | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | 10:39 | 10:55 | 10:55 | 10:55 | 0.26667 | 0.26667 | 0.26667 | 0.26667 | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | close | 0.0012 | 0.31 | 62.917
2014 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK2 |  |  | INV30 |  |  | BLK2INV30 | 298 | 0.4% | Inverter |  | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | 10:39 | 10:55 | 10:55 | 10:55 | 0.26667 | 0.26667 | 0.26667 | 0.26667 | As per O2 Power instruction, manual shutdown taken to avoid unexpected tripping | close | 0.0010667 | 0.31 | 70.222
2015 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK3 |  |  | INV17 |  |  | BLK3INV17 | 22.5 | 0.4333% | String |  | MC4 Connecto found open Same is restored after verfying the load | 9:00 | 10:55 | 10:55 | 10:55 | 1.9167 | 1.9167 | 1.9167 | 1.9167 | MC4 Connecto found open Same is restored after verfying the load | close | 0.0083056 | 0.33 | 5.6441
2016 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK4 |  |  | INV21 |  |  | BLK4INV21 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 9:00 | 15:10 | 15:10 | 15:10 | 6.1667 | 6.1667 | 6.1667 | 6.1667 | MC4 Connecto found open Same is restored after verfying the load | close | 0.024667 | 0.64 | 10.9461
2017 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 9:00 | 15:30 | 15:30 | 15:30 | 6.5 | 6.5 | 6.5 | 6.5 | MC4 Connecto found open Same is restored after verfying the load | close | 0.026 | 0.61 | 10.433
2018 | 2025-06-05 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 |  | -5.1 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 9:00 | 15:50 | 15:50 | 15:50 | 6.8333 | 6.8333 | 6.8333 | 6.8333 | MC4 Connecto found open Same is restored after verfying the load | close | 0.027333 | 0.62 | 10.604
2019 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK1 |  |  | INV31 |  |  | BLK1INV31 | 22.5 | 0.45% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 15:45 | 15:45 | 16:08 | 10.6333 | 10.6333 | 11.0167 | 11.0167 | MC4 Connecto found open Same is restored after verfying the load | close | 0.049575 | 5.23 | 89.4498
2020 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK1 |  |  | INV8 |  |  | BLK1INV8 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 16:20 | 16:20 | 16:27 | 11.2167 | 11.2167 | 11.3333 | 11.3333 | MC4 Connecto found open Same is restored after verfying the load | close | 0.045333 | 5.32 | 90.9891
2021 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK1 |  |  | INV8 |  |  | BLK1INV8 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 16:10 | 16:10 | 16:29 | 11.05 | 11.05 | 11.3667 | 11.3667 | MC4 Connecto found open Same is restored after verfying the load | close | 0.045467 | 5.41 | 92.5284
2022 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 22.5 | 0.45% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 16:10 | 16:10 | 16:43 | 11.05 | 11.05 | 11.6 | 11.6 | MC4 Connecto found open Same is restored after verfying the load | close | 0.0522 | 5.46 | 93.3835
2023 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK2 |  |  | INV20 |  |  | BLK2INV20 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 16:20 | 16:20 | 16:47 | 11.2167 | 11.2167 | 11.6667 | 11.6667 | MC4 Connecto found open Same is restored after verfying the load | close | 0.046667 | 5.51 | 94.2387
2024 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK2 |  |  | INV17 |  |  | BLK2INV17 | 22.5 | 0.4% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 16:32 | 16:32 | 16:52 | 11.4167 | 11.4167 | 11.75 | 11.75 | MC4 Connecto found open Same is restored after verfying the load | close | 0.047 | 5.59 | 95.6069
2025 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 22.5 | 0.4167% | String |  | MC4 Connecto found open Same is restored after verfying the load | 5:07 | 16:44 | 16:44 | 16:56 | 11.6167 | 11.6167 | 11.8167 | 11.8167 | MC4 Connecto found open Same is restored after verfying the load | close | 0.049236 | 6.12 | 104.6716
2026 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK2 |  |  | INV16 |  |  | BLK2INV16 | 22.5 | 0.4333% | String |  | MC4 connector failure | 5:07 | 16:56 | 16:56 | 17:08 | 11.8167 | 11.8167 | 12.0167 | 12.0167 | MC4 Connecto found open Same is restored after verfying the load | close | 0.052072 | 6.18 | 105.6978
2027 | 2025-06-07 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:07 | 18:36 | 13.4833 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 22.5 | 0.3333% | String |  | MC4 connector failure | 5:07 | 17:00 | 17:00 | 17:13 | 11.8833 | 11.8833 | 12.1 | 12.1 | MC4 Connecto found open Same is restored after verfying the load | close | 0.040333 | 6.26 | 107.0661
2028 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK3 |  |  | INV24 |  |  | BLK3INV24 | 22.5 | 0.4% | String |  | MC4 Connecto found open | 5:08 | 10:11 | 10:11 | 10:25 | 5.05 | 5.05 | 5.2833 | 5.2833 | MC4 Connecto found open Same is restored after verfying the load | close | 0.021133 | 0.95 | 16.248
2029 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK7 |  |  | INV3 |  |  | BLK7INV3 | 22.5 | 0.3955% | String |  | MC4 Connecto found open | 5:08 | 10:20 | 10:20 | 10:45 | 5.2 | 5.2 | 5.6167 | 5.6167 | MC4 Connecto found open Same is restored after verfying the load | close | 0.022214 | 1.2 | 20.5238
2030 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 22.5 | 0.3955% | String |  | MC4 Connecto found open | 5:08 | 11:02 | 11:02 | 11:10 | 5.9 | 5.9 | 6.0333 | 6.0333 | MC4 Connecto found open Same is restored after verfying the load | close | 0.023862 | 1.47 | 25.1417
2031 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK8 |  |  | INV10 |  |  | BLK8INV10 | 22.5 | 0.45% | String |  | MC4 Connecto found open | 5:08 | 11:02 | 11:02 | 11:30 | 5.9 | 5.9 | 6.3667 | 6.3667 | MC4 Connecto found open Same is restored after verfying the load | close | 0.02865 | 1.88 | 32.154
2032 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 22.5 | 0.4% | String |  | Y connector & fuse failure so replaced it with new one | 5:08 | 11:55 | 11:55 | 12:10 | 6.7833 | 6.7833 | 7.0333 | 7.0333 | Y connector & fuse failure so replaced it with new one | close | 0.028133 | 2.29 | 39.1663
2033 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK2 |  |  | INV31 |  |  | BLK2INV31 | 22.5 | 0.4% | String |  | Y connector & fuse failure so replaced it with new one | 5:08 | 11:55 | 11:55 | 12:20 | 6.7833 | 6.7833 | 7.2 | 7.2 | Y connector & fuse failure so replaced it with new one | close | 0.0288 | 2.77 | 47.3759
2034 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK1 |  |  | INV31 |  |  | BLK1INV31 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 5:08 | 9:00 | 16:10 | 16:20 | 3.8667 | 11.0333 | 11.2 | 11.2 | MC4 Connecto found open Same is restored after verfying the load | close | 0.0504 | 5.88 | 99.4495
2035 | 2025-06-08 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 5:08 | 9:00 | 16:40 | 16:55 | 3.8667 | 11.5333 | 11.7833 | 11.7833 | MC4 Connecto found open Same is restored after verfying the load | close | 0.053025 | 5.88 | 99.4495
2036 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 5:08 | 9:00 | 9:00 | 9:45 | 3.8667 | 3.8667 | 4.6167 | 4.6167 | MC4 Connecto found open Same is restored after verfying the load | close | 0.020775 | 1.19 | 20.1267
2037 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK5 |  |  | INV1 |  |  | BLK5INV1 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 5:08 | 9:20 | 9:20 | 9:55 | 4.2 | 4.2 | 4.7833 | 4.7833 | MC4 Connecto found open Same is restored after verfying the load | close | 0.021525 | 1.22 | 20.6341
2038 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK5 |  |  | INV2 |  |  | BLK5INV2 | 22.25 | 0.4% | String |  | MC4 Connecto found open | 5:08 | 10:00 | 10:00 | 10:15 | 4.8667 | 4.8667 | 5.1167 | 5.1167 | MC4 Connecto found open Same is restored after verfying the load | close | 0.020467 | 1.78 | 30.1054
2039 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 22.25 | 0.45% | String |  | MC4 Connecto found open | 5:08 | 10:10 | 10:10 | 10:35 | 5.0333 | 5.0333 | 5.45 | 5.45 | MC4 Connecto found open Same is restored after verfying the load | close | 0.024525 | 2.76 | 46.6804
2040 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK5 |  |  | INV12 |  |  | BLK5INV12 | 22.25 | 0.4285% | String |  | MC4 Connecto found open | 5:08 | 11:00 | 11:00 | 11:10 | 5.8667 | 5.8667 | 6.0333 | 6.0333 | MC4 Connecto found open Same is restored after verfying the load | close | 0.025851 | 2.98 | 50.4013
2041 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK4 |  |  | INV1 |  |  | BLK4INV1 | 22.25 | 0.45% | String |  | During String current measurement activity we have observed that String-12 is grounded | 5:08 | 12:05 | 12:05 | 12:15 | 6.95 | 6.95 | 7.1167 | 7.1167 | During String current measurement activity we have observed that String-12 is grounded, so replaced with new one. | close | 0.032025 | 3.55 | 60.0418
2042 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK3 |  |  | INV24 |  |  | BLK3INV24 | 22.25 | 0.4% | String |  | MC4 Connector melted | 5:08 | 15:05 | 15:05 | 15:10 | 9.95 | 9.95 | 10.0333 | 10.0333 | MC4 Connector melted so replace it with new one | close | 0.040133 | 5.11 | 86.4263
2043 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK2 |  |  | INV3 |  |  | BLK2INV3 | 22.25 | 0.1667% | String |  | fuse failure | 5:08 | 15:10 | 15:10 | 15:30 | 10.0333 | 10.0333 | 10.3667 | 10.3667 | fuse failure so replaced it with new one | close | 0.017278 | 5.45 | 92.1768
2044 | 2025-06-09 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:36 | 13.4667 | BLK2 |  |  | INV17 |  |  | BLK2INV17 | 22.25 | 0.4% | String |  | MC4 Connector found open | 5:08 | 15:20 | 15:20 | 15:55 | 10.2 | 10.2 | 10.7833 | 10.7833 | MC4 Connecto found open Same is restored after verfying the load[@[Action taken]] | close | 0.043133 | 6.11 | 103.3395
2045 | 2025-06-10 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:09 | 18:38 | 13.4833 | BLK8 |  |  | INV26 |  |  | BLK8INV26 | 271.35 | 0.4065% | Inverter |  | Inv Shut down on the fault of 47 (Relay Card Faulty) | 8:55 | 9:00 | 9:35 | 11:25 | 0.083333 | 0.66667 | 2.5 | 2.5 | after discussion with OEM we replaced the Inv with a new one | close | 0.010163 | 0.746 | 153.8735
2046 | 2025-06-14 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:08 | 18:43 | 13.5833 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 264 | 0.3955% | Inverter |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 7:45 | 7:50 | 8:05 | 8:22 | 0.083333 | 0.33333 | 0.61667 | 0.61667 | after checking the all strin found string no 4 &11 floating is not ok, after rectification connected the string & restore | close | 0.002439 | 0.186 | 37.326
2047 | 2025-06-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 18:29 | 13.2333 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:25 | 12:25 | 12:27 | 12:29 | 0 | 0.033333 | 0.066667 | 0.066667 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | close | 0.0083333 | 0.0371 | 250.1483
2048 | 2025-06-15 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 18:29 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:24 | 12:24 | 12:28 | 12:29 | 0 | 0.066667 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | close | 0.011067 | 0.0371 | 253.1348
2049 | 2025-06-16 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 6:13 | 17:53 | 11.6667 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8870.1 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:52 | 12:52 | 12:56 | 12:57 | 0 | 0.066667 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | close | 0.010417 | 0.075 | 505.6905
2050 | 2025-06-16 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:15 | 18:29 | 13.2333 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8976 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:55 | 11:55 | 11:58 | 11:59 | 0 | 0.05 | 0.066667 | 0.066667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | close | 0.0088537 | 0.112 | 764.1804
2051 | 2025-06-18 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 | 18:34 | 13.4667 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 11:47 | 11:47 | 11:52 | 11:52 | 0 | 0.083333 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | close | 0.010417 | 0.101 | 640.5864
2052 | 2025-06-18 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 | 18:34 | 13.4667 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:54 | 12:54 | 12:58 | 12:58 | 0 | 0.066667 | 0.066667 | 0.066667 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | close | 0.0088537 | 0.069 | 464.9547
2053 | 2025-06-18 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 | 18:34 | 13.4667 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 22.25 | 0.3333% | Inverter |  | Inv tripped on fault of string back fedded current | 11:52 | 11:52 | 12:00 | 12:26 | 0 | 0.13333 | 0.56667 | 0.56667 | we have physically checked all parameter of this inverter & string's then we found that all string are healthy same is store. | close | 0.0018889 | 0.559 | 9.4545
2054 | 2025-06-18 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:06 | 18:34 | 13.4667 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | Inverter |  | INV tripped on fault of excessive leakage current | 10:00 | 10:02 | 10:10 | 10:30 | 0.033333 | 0.16667 | 0.5 | 0.5 | we have physically checked all parameter of this inverter & string's then we found that string no-4,9,11 MC4 Connector Positive & negative was failure same is restored after replaced it new one. | close | 0.002 | 0.219 | 44.4478
2055 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:24 | 17:50 | 12.4333 | BLK7 |  |  | INV18 |  |  | BLK7INV18 | 267 | 0.4% | Inverter |  | INV tripped on fault of excessive leakage current | 8:08 | 8:10 | 8:20 | 9:03 | 0.033333 | 0.2 | 0.91667 | 0.91667 | we have physically checked all parameter of this inverter & string's then we found that string no-6,10, MC4 Connector Positive & negative was failure same is restored after replaced it new one. | close | 0.0036667 | 0.217 | 44.0419
2056 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:24 | 17:50 | 12.4333 | BLK4 |  |  | MVP |  |  | BLK4MVP | 8655.25 | 12.97% | IDT |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 17:04 | 17:04 | 8:20 | 22:06 | 0 | -8.7333 | 5.0333 | 5.0333 | after checking the all parameters & verifying the load charge the IDT | close | 0.65266 | 0 | 0
2057 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:24 | 17:50 | 12.4333 | BLK4 | LT1 | ACCB1 |  |  |  | BLK4LT1ACCB1 | 534 | 0.8% | ACCB |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 17:04 | 17:04 | 8:20 |  | 0 | -8.7333 |  | -17.0667 | MCCB meggaring value is not good | open | -0.13653 | 0 | 0
2058 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:24 | 17:50 | 12.4333 | BLK4 | LT1 | ACCB2 |  |  |  | BLK4LT1ACCB2 | 534 | 0.8% | ACCB |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 17:04 | 17:04 | 8:20 | 22:39 | 0 | -8.7333 | 5.5833 | 5.5833 | After checking the all paramerters & meggaring the MCCB & found MCCB Healthy same is restore | close | 0.044667 | 0 | 0
2059 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:24 | 17:50 | 12.4333 | BLK4 | LT1 | ACCB5 |  |  |  | BLK4LT1ACCB5 | 567.375 | 0.85% | ACCB |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 17:04 | 17:04 | 8:20 | 22:39 | 0 | -8.7333 |  | 5.5833 | MCCB meggaring value is not good | open | 0.047458 | 0 | 0
2060 | 2025-06-19 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:24 | 17:50 | 12.4333 | BLK4 | LT1 | ACCB6 |  |  |  | BLK4LT1ACCB6 | 567.375 | 0.85% | ACCB |  | B-4 IDT tripped due to 2 Nos. of 500Amp MCCb failure after generation | 17:04 | 17:04 | 8:20 | 11:30 | 0 | -8.7333 | -5.5667 | -5.5667 | After checking the all paramerters & meggaring the MCCB & found MCCB Healthy same is restore | close | -0.047317 | 0 | 0
2061 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV1 |  |  | BLK4INV1 | 300.375 | 0.45% | Inverter |  | Due to Block-4 Inverter failure this impact 500 Amp MCCB of this inverter also failure. | 5:45 | 5:45 | 18:45 | 20:00 | 0 | 13 | 14.25 | 14.25 | It will be restored after rectification of MCCB or Replacment of MCCB. | close | 0.064125 | 2.4 | 547.9868
2062 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | Due to Block-4 Inverter failure this impact 500 Amp MCCB of this inverter also failure. | 5:45 | 5:45 | 18:45 | 20:00 | 0 | 13 | 14.25 | 14.25 | It will be restored after rectification of MCCB or Replacment of MCCB. | close | 0.057 | 2.4 | 487.0994
2063 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV11 |  |  | BLK4INV11 | 300.375 | 0.45% | Inverter |  | Block-4 Inverter No-11 IGBT Failure , it was restored after MCCB replacment work. | 5:45 | 5:45 |  |  | 0 | -5.75 |  | -5.75 | Block-4 Inverter No-11 IGBT Failure , it was restored after MCCB replacment work. | open | -0.025875 | 2.4 | 547.9868
2064 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV12 |  |  | BLK4INV12 | 267 | 0.4% | Inverter |  | Due to Block-4 Inverter failure this impact 500 Amp MCCB of this inverter also failure. | 5:45 | 5:45 |  |  | 0 | -5.75 | -5.75 | -5.75 | It will be restored after rectification of MCCB or Replacment of MCCB. | Close | -0.023 | 2.4 | 487.0994
2065 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 267 | 0.4% | string |  | As per observation we observed that String no -13 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 5:45 | 7:35 | 10:30 | 10:45 | 1.8333 | 4.75 | 5 | 5 | During VOC we got string no 13 DC cable shorted so isolated the string & charge | open | 0.02 | 0.64 | 129.8932
2066 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 300.375 | 0.45% | string |  | As per observation we observed that String no -13 &14 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 5:45 | 7:35 | 10:50 | 11:10 | 1.8333 | 5.0833 | 5.4167 | 5.4167 | During VOC we got string no 13 & 14 DC cable shorted so isolated the string & charge | open | 0.024375 | 0.827 | 188.8271
2067 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 278.125 | 0.4167% | string |  | As per observation we observed that String no -9 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 5:45 | 7:35 | 11:45 | 12:06 | 1.8333 | 6 | 6.35 | 6.35 | During VOC we got string np 9 faulty so isolated this string & charge | closed | 0.026458 | 1.26 | 266.3825
2068 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK1 |  |  | INV18 |  |  | BLK1INV18 | 267 | 0.4% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 8:55 | 9:19 | 1.8333 | 3.1667 | 3.5667 | 3.5667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.014267 | 0.236 | 47.8981
2069 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 300.375 | 0.45% | string |  | As per observation we observed that String no -13 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 5:45 | 7:35 | 11:15 | 11:42 | 1.8333 | 5.5 | 5.95 | 5.95 | As per observation we observed that String no -13 was grounded due to this inverter was in breakdown on exxcusive leakage current. | closed | 0.026775 | 1.03 | 235.1777
2070 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 222.5 | 0.3333% | string |  | As per observation we observed that String no -5 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 5:45 | 7:35 | 11:30 | 11:56 | 1.8333 | 5.75 | 6.1833 | 6.1833 | As per observation we observed that String no -5 was grounded due to this inverter was in breakdown on exxcusive leakage current. | closed | 0.020611 | 1.51 | 255.3889
2071 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK2 |  |  | INV9 |  |  | BLK2INV9 | 267 | 0.4% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:00 | 9:24 | 1.8333 | 3.25 | 3.65 | 3.65 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.0146 | 0.267 | 54.1898
2072 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 267 | 0.4% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 8:40 | 9:10 | 1.8333 | 2.9167 | 3.4167 | 3.4167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.013667 | 0.203 | 41.2005
2073 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 278.125 | 0.4167% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 10:35 | 11:04 | 1.8333 | 4.8333 | 5.3167 | 5.3167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.022153 | 0.781 | 165.1148
2074 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK2 |  |  | INV32 |  |  | BLK2INV32 | 239.25 | 0.3584% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 8:50 | 9:16 | 1.8333 | 3.0833 | 3.5167 | 3.5167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.012605 | 0.222 | 40.3738
2075 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK3 |  |  | INV18 |  |  | BLK3INV18 | 267 | 0.4% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:05 | 9:32 | 1.8333 | 3.3333 | 3.7833 | 3.7833 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.015133 | 0.314 | 63.7288
2076 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK5 |  |  | INV4 |  |  | BLK5INV4 | 300.375 | 0.45% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 11:15 | 11:40 | 1.8333 | 5.5 | 5.9167 | 5.9167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.026625 | 1.021 | 233.1227
2077 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK5 |  |  | INV26 |  |  | BLK5INV26 | 289.25 | 0.4333% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:20 | 9:43 | 1.8333 | 3.5833 | 3.9667 | 3.9667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.017189 | 0.361 | 79.3735
2078 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 297 | 0.4449% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 8:35 | 9:00 | 1.8333 | 2.8333 | 3.25 | 3.25 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.014461 | 0.189 | 42.6691
2079 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV9 |  |  | BLK6INV9 | 275 | 0.412% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:05 | 9:25 | 1.8333 | 3.3333 | 3.6667 | 3.6667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.015106 | 0.27 | 56.4406
2080 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 264 | 0.3955% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:30 | 9:55 | 1.8333 | 3.75 | 4.1667 | 4.1667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.016479 | 0.414 | 83.0805
2081 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV11 |  |  | BLK6INV11 | 297 | 0.4449% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 10:00 | 10:30 | 1.8333 | 4.25 | 4.75 | 4.75 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.021135 | 0.527 | 118.9768
2082 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV15 |  |  | BLK6INV15 | 275 | 0.412% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 10:40 | 11:02 | 1.8333 | 4.9167 | 5.2833 | 5.2833 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.021767 | 0.766 | 160.124
2083 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV16 |  |  | BLK6INV16 | 297 | 0.4449% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 10:30 | 10:50 | 1.8333 | 4.75 | 5.0833 | 5.0833 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.022618 | 0.663 | 149.6804
2084 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV23 |  |  | BLK6INV23 | 264 | 0.3955% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:30 | 9:49 | 1.8333 | 3.75 | 4.0667 | 4.0667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.016084 | 0.388 | 77.8629
2085 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV24 |  |  | BLK6INV24 | 286 | 0.4285% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:45 | 10:16 | 1.8333 | 4 | 4.5167 | 4.5167 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.019352 | 0.475 | 103.2654
2086 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV31 |  |  | BLK6INV31 | 275 | 0.412% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:30 | 9:54 | 1.8333 | 3.75 | 4.15 | 4.15 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.017097 | 0.411 | 85.9151
2087 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK6 |  |  | INV32 |  |  | BLK6INV32 | 275 | 0.412% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 9:34 | 10:03 | 1.8333 | 3.8167 | 4.3 | 4.3 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.017715 | 0.432 | 90.3049
2088 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK7 |  |  | INV6 |  |  | BLK7INV6 | 264 | 0.3955% | string |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 5:45 | 7:35 | 10:00 | 10:23 | 1.8333 | 4.25 | 4.6333 | 4.6333 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.018325 | 0.499 | 100.1381
2089 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK7 |  |  | INV26 |  |  | BLK7INV26 | 300.375 | 0.45% | string |  | As per observation we observed that String no -1,10 & 12 was grounded due to this inverter was in breakdown on exxcusive leakage current. | 5:45 | 7:35 | 10:45 | 11:10 | 1.8333 | 5 | 5.4167 | 5.4167 | As per observation we observed that String no -1,10 & 12 was grounded due to this inverter was in breakdown on exxcusive leakage current. | closed | 0.024375 | 0.826 | 188.5988
2090 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:45 | 7:35 |  | 18:42 | 1.8333 | -5.75 |  | 12.95 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.0518 | 2.4 | 21.8921
2091 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:45 | 7:35 |  | 18:42 | 1.8333 | -5.75 |  | 12.95 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.058275 | 2.4 | 40.5916
2092 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:45 | 7:35 |  | 18:42 | 1.8333 | -5.75 |  | 12.95 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.058275 | 2.4 | 21.8921
2093 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 22.25 | 0.4167% | string |  | 1 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | 5:45 | 7:35 | 11:50 | 12:10 | 1.8333 | 6.0833 | 6.4167 | 6.4167 | 1 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | closed | 0.026736 | 1.303 | 22.0379
2094 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK2 |  |  | INV2 |  |  | BLK2INV2 | 22.25 | 0.3333% | string |  | 1 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | 5:45 | 7:35 | 11:50 | 12:10 | 1.8333 | 6.0833 | 6.4167 | 6.4167 | 1 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | closed | 0.021389 | 1.303 | 22.0379
2095 | 2025-06-20 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:27 | 18:42 | 13.25 | BLK7 |  |  | INV26 |  |  | BLK7INV26 | 66.75 | 0.45% | string |  | 3 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | 5:45 | 7:35 | 11:05 | 11:30 | 1.8333 | 5.3333 | 5.75 | 5.75 | 3 Nos. string VOC is not accurate so we open the Y connector of these string so cleaned & verify the voltage than restore the same | closed | 0.025875 | 0.951 | 48.2533
2096 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK3 |  |  | INV16 |  |  | BLK3INV16 | 267 | 0.4% | Inverter |  | During morning after few time of plant start Block-3 inverter-16 Shut down on fault of ecxcessive leakage current, When Done VOC we got that String NO. 8 yconnector & fuse was failure so replace it with new one, restore | 7:10 | 7:15 | 9:02 | 9:27 | 0.083333 | 1.8667 | 2.2833 | 2.2833 | During morning after few time of plant start Block-3 inverter-16 Shut down on fault of ecxcessive leakage current, When Done VOC we got that String NO. 8 yconnector & fuse was failure so replace it with new one, restore | closed | 0.0091333 | 0.585 | 118.7305
2097 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK4 |  |  | INV12 |  |  | BLK4INV12 | 267 | 0.4% | Inverter |  | During morning after few time of plant start Block-4 inverter-12 shut down on fault of ecxcessive leakage current, When Done VOC we got that String NO. 13 MC4 connector & fuse was failure so replace it with new one, restore | 5:23 | 5:25 | 9:00 | 9:23 | 0.033333 | 3.6167 | 4 | 4 | During morning after few time of plant start Block-4 inverter-12 shut down on fault of ecxcessive leakage current, When Done VOC we got that String NO. 13 MC4 connector & fuse was failure so replace it with new one, restore | closed | 0.016 | 0.911 | 184.8948
2098 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK6 |  |  | INV15 |  |  | BLK6INV15 | 275 | 0.412% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 7:00 | 7:10 | 7:35 | 8:06 | 0.16667 | 0.58333 | 1.1 | 1.1 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0045318 | 0.341 | 71.2824
2099 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK4 |  |  | INV11 |  |  | BLK4INV11 | 300.375 | 0.45% | Inverter |  | Restoretion of Inverter & 250 Amp MCCB, after verifying the all parameter connect the same | 5:23 | 5:25 | 8:45 | 9:13 | 0.033333 | 3.3667 | 3.8333 | 3.8333 | Restoretion of Inverter & 250 Amp MCCB, after verifying the all parameter connect the same | closed | 0.01725 | 0.834 | 190.4254
2100 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK1 |  |  | MVP |  |  | BLK1MVP | 8944.5 | 13.4% | IDT |  | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:05 | 12:06 | 12:07 | 12:10 | 0.016667 | 0.033333 | 0.083333 | 0.083333 | Block-1 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011167 | 0.102 | 693.5077
2101 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:02 | 12:03 | 12:06 | 12:07 | 0.016667 | 0.066667 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.010417 | 0.104 | 659.6137
2102 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK5 |  |  | MVP |  |  | BLK5MVP | 8864.75 | 13.28% | IDT |  | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:15 | 12:16 | 12:19 | 12:20 | 0.016667 | 0.066667 | 0.083333 | 0.083333 | Block-5 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.011067 | 0.112 | 754.7091
2103 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:45 | 5:45 |  | 18:29 | 0 | -5.75 | 12.7333 | 12.7333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.050933 | 5.19 | 47.3417
2104 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:45 | 5:45 |  | 18:29 | 0 | -5.75 | 12.7333 | 12.7333 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0573 | 5.19 | 87.7794
2105 | 2025-06-21 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:10 | 18:29 | 13.3167 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:45 | 5:45 |  | 18:29 | 0 | -5.75 | 12.7333 | 12.7333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | closed | 0.0573 | 5.19 | 47.3417
2106 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | 6:59 | 7:05 | 7:20 | 8:15 | 0.1 | 0.35 | 1.2667 | 1.2667 | We have checked all string & found that few string's VOC is not acuurate so we Open the all Y- Connector of this inverter & found that moisture ingress issue in Y-Connector , after cleaned of these & voltage verifcation we restored the same. | closed | 0.0050667 | 0.42 | 85.2424
2107 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK5 |  |  | INV20 |  |  | BLK5INV20 | 22.25 | 0.4% | string |  | During morining string checking we got that 1 string MC4 connector open, same restore | 4:59 | 9:00 | 9:50 | 10:10 | 4.0167 | 4.85 | 5.1833 | 5.1833 | During morining string checking we got that 1 string MC4 connector open, same restore | closed | 0.020733 | 1.135 | 19.1965
2108 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK6 |  |  | INV32 |  |  | BLK6INV32 | 22.25 | 0.412% | string |  | During morining string checking we got that 1 string MC4 connector open, same restore | 4:59 | 9:00 | 10:00 | 10:30 | 4.0167 | 5.0167 | 5.5167 | 5.5167 | During morining string checking we got that 1 string MC4 connector open, same restore | closed | 0.022728 | 1.219 | 20.6172
2109 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK4 |  |  | INV17 |  |  | BLK4INV17 | 22.25 | 0.4333% | string |  | Morning string checking found that String no 9 , Y connector, fuse & MC4 connector melted | 4:59 | 9:00 | 10:25 | 10:45 | 4.0167 | 5.4333 | 5.7667 | 5.7667 | Morning string checking found that String no 9 , Y connector, fuse & MC4 connector melted, so replace it with new one, restored | closed | 0.024989 | 1.663 | 28.1266
2110 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK4 |  |  | INV12 |  |  | BLK4INV12 | 12 | 0.4% | string |  | Morning string checking found that String no 13 MC4 connector melted | 4:59 | 9:00 | 10:33 | 10:50 | 4.0167 | 5.5667 | 5.85 | 5.85 | Morning string checking found that String no 13 MC4 connector melted, same is replace it with new one, restored | closed | 0.0234 | 1.717 | 15.662
2111 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 4:59 |  |  | 18:12 | -4.9833 | -4.9833 |  | 13.2167 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.052867 | 5.3 | 48.3451
2112 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 4:59 |  |  | 18:12 | -4.9833 | -4.9833 |  | 13.2167 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.059475 | 5.3 | 89.6398
2113 | 2025-06-22 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 4:59 | 18:12 | 13.2167 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 4:59 |  |  | 18:12 | -4.9833 | -4.9833 |  | 13.2167 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.059475 | 5.3 | 48.3451
2114 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK1 |  |  | INV9 |  |  | BLK1INV9 | 278.125 | 0.4167% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 7:30 | 8:15 | 1.4167 | 2 | 2.75 | 2.75 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | Closed | 0.011458 | 0.222 | 46.9341
2115 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 8:00 | 8:30 | 1.4167 | 2.5 | 3 | 3 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | Closed | 0.012 | 0.293 | 59.4667
2116 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 278.125 | 0.4167% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 8:15 | 8:45 | 1.4167 | 2.75 | 3.25 | 3.25 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | Closed | 0.013542 | 0.37 | 78.2234
2117 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | During morning after few time of plant start Block-4 inverter-2 shut down on fault of ecxcessive leakage current & fault 47, When Done VOC we got that String NO. 12 MC4 connector & fuse was failure so replace it with new one & also share Log file of Inverter to OEm after got permission from OEM reset it, restore | 5:30 | 6:55 | 10:30 | 11:00 | 1.4167 | 5 | 5.5 | 5.5 | During morning after few time of plant start Block-4 inverter-2 shut down on fault of ecxcessive leakage current & fault 47, When Done VOC we got that String NO. 12 MC4 connector & fuse was failure so replace it with new one & also share Log file of Inverter to OEm after got permission from OEM reset it, restore | Closed | 0.022 | 1.656 | 336.0986
2118 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK4 |  |  | INV22 |  |  | BLK4INV22 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 8:05 | 8:25 | 1.4167 | 2.5833 | 2.9167 | 2.9167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | Closed | 0.011667 | 0.269 | 54.5957
2119 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK6 |  |  | INV5 |  |  | BLK6INV5 | 264 | 0.3955% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 7:15 | 7:45 | 1.4167 | 1.75 | 2.25 | 2.25 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | Closed | 0.0088989 | 0.132 | 26.4894
2120 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK6 |  |  | INV6 |  |  | BLK6INV6 | 297 | 0.4449% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 8:45 | 9:15 | 1.4167 | 3.25 | 3.75 | 3.75 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | Closed | 0.016685 | 0.564 | 127.33
2121 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 264 | 0.3955% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 9:00 | 9:25 | 1.4167 | 3.5 | 3.9167 | 3.9167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | Closed | 0.015491 | 0.639 | 128.233
2122 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK6 |  |  | INV31 |  |  | BLK6INV31 | 275 | 0.412% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 7:40 | 8:10 | 1.4167 | 2.1667 | 2.6667 | 2.6667 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | Closed | 0.010986 | 0.203 | 42.435
2123 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK7 |  |  | INV12 |  |  | BLK7INV12 | 270.6 | 0.4054% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 8:10 | 8:35 | 1.4167 | 2.6667 | 3.0833 | 3.0833 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | Closed | 0.0125 | 0.319 | 65.6166
2124 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK7 |  |  | INV17 |  |  | BLK7INV17 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 8:50 | 9:15 | 1.4167 | 3.3333 | 3.75 | 3.75 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | Closed | 0.015 | 0.563 | 114.2654
2125 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK5 |  |  | INV11 |  |  | BLK5INV11 | 286 | 0.4285% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:30 | 6:55 | 11:00 | 11:30 | 1.4167 | 5.5 | 6 | 6 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | Closed | 0.025708 | 1.881 | 408.9309
2126 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:30 |  |  | 18:30 | -5.5 | -5.5 |  | 13 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.052 | 4.58 | 41.7774
2127 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.3 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:30 |  |  | 18:30 | -5.5 | -5.5 |  | 13 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.0585 | 4.58 | 77.6364
2128 | 2025-06-23 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:12 | 18:30 | 13.3 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 12 | 0.45% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:30 |  |  | 18:30 | -5.5 | -5.5 |  | 13 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.0585 | 4.58 | 41.7774
2129 | 2025-06-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:11 | 18:31 | 13.3333 | Blk4 |  |  | INV13 |  |  | Blk4INV13 | 300.375 | 0.45% | Inverter |  | Block-4 inverter 13 failure on fault of 1616 & 21 in morning, after sharing the log file to OEM, inverter has been replaced with spare one | 5:11 | 6:00 | 12:00 | 12:49 | 0.81667 | 6.8167 | 7.6333 | 7.6333 | Block-4 inverter 13 failure on fault of 1616 & 21 in morning, after sharing the log file to OEM, inverter has been replaced with spare one | closed | 0.03435 | 3.4 | 776.3146
2130 | 2025-06-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:11 | 18:31 | 13.3333 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:11 |  |  | 18:31 | -5.1833 | -5.1833 |  | 13.3333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.053333 | 6.46 | 58.9263
2131 | 2025-06-24 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:11 | 18:31 | 13.3333 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:11 |  |  | 18:31 | -5.1833 | -5.1833 |  | 13.3333 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.06 | 6.46 | 109.2591
2132 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:11 | 18:50 | 13.65 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:11 |  |  | 18:50 | -5.1833 | -5.1833 |  | 13.65 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.0546 | 6.18 | 56.3722
2133 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:11 | 18:50 | 13.65 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:11 |  |  | 18:50 | -5.1833 | -5.1833 |  | 13.65 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.061425 | 6.18 | 104.5234
2134 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:40 | 13.4333 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:14 |  |  | 18:40 | -5.2333 | -5.2333 |  | 13.4333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.053733 | 6.3 | 57.4668
2135 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:40 | 13.4333 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:14 |  |  | 18:40 | -5.2333 | -5.2333 |  | 13.4333 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.06045 | 6.3 | 106.553
2136 | 2025-06-25 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:14 | 18:40 | 13.4333 | BLK4 |  |  | INV11 |  |  | BLK4INV11 | 300.375 | 0.45% | Inverter |  | As per obsservation we found that Block-4 Inverter11 running with derating generation, after Discussion with Oem & sharing Log file to OEM, they instructed to change control card, After changing the Control card now its under observation | 16:15 | 16:15 | 16:30 | 18:05 | 0 | 0.25 | 1.8333 | 1.8333 | As per obsservation we found that Block-4 Inverter11 running with derating generation, after Discussion with Oem & sharing Log file to OEM, they instructed to change control card, After changing the Control card now its under observation | closed | 0.00825 | 0.513 | 117.1322
2137 | 2025-06-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 |  |  | 0 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:14 |  |  | 18:40 | -5.2333 | -5.2333 |  | 13.4333 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.053733 | 6.3 | 57.4668
2138 | 2025-06-26 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 |  |  | 0 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:14 |  |  | 18:40 | -5.2333 | -5.2333 |  | 13.4333 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.06045 | 6.3 | 58.664
2139 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:48 | 18:41 | 12.8833 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | Inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 5:48 | 7:00 | 9:30 | 18:41 | 1.2 | 3.7 |  | 12.8833 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | open | 0.036739 | 5.64 | 816.0693
2140 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:48 | 18:41 | 12.8833 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | Inverter shutdown in morining on fault of excessive leakage current, after removing the faulty string inverter fault reset, restore | 5:48 | 7:00 | 9:10 | 9:35 | 1.2 | 3.3667 | 3.7833 | 3.7833 | Inverter shutdown in morining on fault of excessive leakage current, after removing the faulty string inverter fault reset, restore | closed | 0.015133 | 1.025 | 208.032
2141 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:48 | 18:41 | 12.8833 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | 17:45 | 17:45 | 17:50 | 18:41 | 0 | 0.083333 |  | 0.93333 | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | open | 0.0037333 | 0.0961 | 19.5043
2142 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:48 | 18:41 | 12.8833 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:48 |  |  | 18:41 | -5.8 | -5.8 |  | 12.8833 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.051533 | 5.64 | 51.4464
2143 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:48 | 18:41 | 12.8833 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:48 |  |  | 18:41 | -5.8 | -5.8 | 12.8833 | 12.8833 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.057975 | 5.64 | 95.3903
2144 | 2025-06-27 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:48 | 18:41 | 12.8833 | BLK2 |  |  | MVP |  |  | BLK2MVP | 8343.75 | 12.5% | IDT |  | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | 12:37 | 12:37 | 12:41 | 12:42 | 0 | 0.066667 | 0.083333 | 0.083333 | Block-2 IDT tripped due to over current ( Weather flactuating ( moving cloud)) as line voltage not stable at our plant | closed | 0.010417 | 0.097 | 615.2166
2145 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | string |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:26 |  |  | 18:29 | -5.4333 | -5.4333 |  | 13.05 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.0522 | 4.65 | 42.416
2146 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | string |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:26 |  |  | 18:29 | -5.4333 | -5.4333 |  | 13.05 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.058725 | 4.65 | 78.6462
2147 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK5 |  |  | INV5 |  |  | BLK5INV5 | 300.375 | 0.45% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 7:15 | 7:35 | 0.73333 | 1.8167 | 2.15 | 2.15 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.009675 | 0.189 | 43.154
2148 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK5 |  |  | INV14 |  |  | BLK5INV14 | 278.125 | 0.4167% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 7:25 | 7:45 | 0.73333 | 1.9833 | 2.3167 | 2.3167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0096528 | 0.232 | 49.0482
2149 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK6 |  |  | INV32 |  |  | BLK6INV32 | 275 | 0.412% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 7:40 | 8:10 | 0.73333 | 2.2333 | 2.7333 | 2.7333 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.011261 | 0.351 | 73.3728
2150 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK6 |  |  | INV16 |  |  | BLK6INV16 | 297 | 0.4449% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 8:10 | 8:30 | 0.73333 | 2.7333 | 3.0667 | 3.0667 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.013645 | 0.489 | 110.3978
2151 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK2 |  |  | INV7 |  |  | BLK2INV7 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 8:25 | 8:45 | 0.73333 | 2.9833 | 3.3167 | 3.3167 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.013267 | 0.455 | 92.3459
2152 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK3 |  |  | INV30 |  |  | BLK3INV30 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 6:55 | 7:20 | 0.73333 | 1.4833 | 1.9 | 1.9 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.0076 | 0.132 | 26.7905
2153 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK7 |  |  | INV19 |  |  | BLK7INV19 | 267 | 0.4% | Inverter |  | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | 5:26 | 6:10 | 8:45 | 9:10 | 0.73333 | 3.3167 | 3.7333 | 3.7333 | We have checked all string & found that few string's Voc is not accurate so we open the all Y-connector of this inverter & found that moisture ingress issue in Y connector, after cleaned of these & voltage verification we restored the same. | closed | 0.014933 | 0.589 | 119.5423
2154 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | 5:26 |  |  | 18:29 | -5.4333 | -5.4333 |  | 13.05 | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | open | 0.0522 | 4.65 | 943.755
2155 | 2025-06-28 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:26 | 18:29 | 13.05 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | Inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 5:26 |  |  | 18:29 | -5.4333 | -5.4333 |  | 13.05 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | open | 0.037214 | 4.65 | 672.8231
2156 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | Inverter |  | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | 5:18 |  |  | 18:29 | -5.3 | -5.3 |  | 13.1833 | In evening inverter shows intial standby mode, SO we take the log file & share to OEM, After discuusion With OEM inverter replacement (Under warranty) Claimed | open | 0.052733 | 3.89 | 789.5069
2157 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | Inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 5:18 |  |  | 18:29 | -5.3 | -5.3 |  | 13.1833 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | open | 0.037595 | 3.89 | 562.8563
2158 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | String |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:18 |  |  | 18:29 | -5.3 | -5.3 |  | 13.1833 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.052733 | 3.89 | 35.4835
2159 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 22.25 | 0.45% | String |  | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:18 |  |  | 18:29 | -5.3 | -5.3 |  | 13.1833 | 2 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.059325 | 3.89 | 65.7922
2160 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK1 |  |  | INV32 |  |  | BLK1INV32 | 22.25 | 0.45% | String |  | During String current measurement activity we have observed that String-1 MC4 connector was melted so replace it with spare one. | 6:40 | 7:00 | 7:45 | 8:15 | 0.33333 | 1.0833 | 1.5833 | 1.5833 | During String current measurement activity we have observed that String-1 MC4 connector was melted so replace it with spare one. | closed | 0.007125 | 0.207 | 3.501
2161 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 22 | 0.3955% | String |  | During String current measurement activity we have observed that String-10 MC4 connector was melted so replace it with spare one. | 6:40 | 7:00 | 8:15 | 8:40 | 0.33333 | 1.5833 | 2 | 2 | During String current measurement activity we have observed that String-10 MC4 connector was melted so replace it with spare one. | closed | 0.0079101 | 0.379 | 6.3381
2162 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK6 |  |  | INV16 |  |  | BLK6INV16 | 22 | 0.4449% | String |  | During String current measurement activity we have observed that String-5 MC4 connector was melted so replace it with spare one. | 6:40 | 7:00 | 8:40 | 9:00 | 0.33333 | 2 | 2.3333 | 2.3333 | During String current measurement activity we have observed that String-5 MC4 connector was melted so replace it with spare one. | closed | 0.010382 | 0.547 | 9.1476
2163 | 2025-06-29 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:18 | 18:29 | 13.1833 | BLK2 |  |  | INV12 |  |  | BLK2INV12 | 22.25 | 0.4% | String |  | During String current measurement activity we have observed that String No.-6 MC4 connector was melted so replace it with spare one. | 6:40 | 7:00 | 9:10 | 9:30 | 0.33333 | 2.5 | 2.8333 | 2.8333 | During String current measurement activity we have observed that String No.-6 MC4 connector was melted so replace it with spare one. | closed | 0.011333 | 0.788 | 13.3276
2164 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK4 |  |  | INV27 |  |  | BLK4INV27 | 12 | 0.4% | String |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:20 |  |  | 18:23 | -5.3333 | -5.3333 |  | 13.05 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.0522 | 3.09 | 28.1861
2165 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | String |  | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | 5:20 |  |  | 18:23 | -5.3333 | -5.3333 |  | 13.05 | 1 Nos. string VOC is not accurate so after checking we got DC string cable failure | open | 0.058725 | 3.09 | 28.1861
2166 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK4 |  |  | INV2 |  |  | BLK4INV2 | 267 | 0.4% | inverter |  | Inverter IGBT was failure so replace it with spare one | 5:20 | 3:55 | 4:05 | 4:46 | -1.4167 | -1.25 | -0.56667 | -0.56667 | Inverter IGBT was failure so replace it with spare one | closed | -0.0022667 | 2.79 | 566.253
2167 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK7 |  |  | INV11 |  |  | BLK7INV11 | 190.35 | 0.2852% | inverter |  | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | 5:20 |  |  | 18:23 | -5.3333 | -5.3333 |  | 13.05 | During morning Inverter IGBT failure on fault of 21, after discussion with OEM, Inverter log file has been shared & replacement raised for the Inverter | open | 0.037214 | 3.09 | 447.1018
2168 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK4 |  |  | INV28 |  |  | BLK4INV28 | 12 | 0.45% | String |  | String no. 13 load shifted to string no. 14 & string no. 6 splited to 2 half string, now restore | 5:20 | 7:00 | 7:10 | 7:25 | 1.6667 | 1.8333 | 2.0833 | 2.0833 | String no. 13 load shifted to string no. 14 & string no. 6 splited to 2 half string, now restore | closed | 0.009375 | 0.075 | 0.68413
2169 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK6 |  |  | INV31 |  |  | BLK6INV31 | 275 | 0.412% | String |  | During string monitoring found string no. 1 shows ground fault, rectified now restore | 5:20 | 7:00 | 7:35 | 7:55 | 1.6667 | 2.25 | 2.5833 | 2.5833 | During string monitoring found string no. 1 shows ground fault, rectified now restore | closed | 0.010643 | 0.121 | 25.2937
2170 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK6 |  |  | INV10 |  |  | BLK6INV10 | 44 | 0.3955% | String |  | During string monitoring found string no. 3& 6 in ground fault now rectified & restore | 5:20 | 7:00 | 8:10 | 8:30 | 1.6667 | 2.8333 | 3.1667 | 3.1667 | During string monitoring found string no. 3& 6 in ground fault now rectified & restore | closed | 0.012524 | 0.178 | 5.9534
2171 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK2 |  |  | INV15 |  |  | BLK2INV15 | 22 | 0.4% | String |  | During string monitoring found string no. 12 in ground fault now rectified & restore | 5:20 | 7:00 | 8:40 | 8:55 | 1.6667 | 3.3333 | 3.5833 | 3.5833 | During string monitoring found string no. 12 in ground fault now rectified & restore | closed | 0.014333 | 0.221 | 3.6958
2172 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK2 |  |  | INV17 |  |  | BLK2INV17 | 22 | 0.4% | String |  | during string monitoring found string no. 7 MC4 connector open, now restore | 5:20 | 7:00 | 9:10 | 9:20 | 1.6667 | 3.8333 | 4 | 4 | during string monitoring found string no. 7 MC4 connector open, now restore | closed | 0.016 | 0.3 | 5.0169
2173 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK2 |  |  | INV18 |  |  | BLK2INV18 | 22 | 0.4167% | String |  | during string monitoring found string no. 3 MC4 connector open, now restore | 5:20 | 7:00 | 9:25 | 9:35 | 1.6667 | 4.0833 | 4.25 | 4.25 | during string monitoring found string no. 3 MC4 connector open, now restore | closed | 0.017708 | 0.342 | 5.7193
2174 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK3 |  |  | INV30 |  |  | BLK3INV30 | 22.25 | 0.4% | String |  | during string monitoring found string no. 1 MC4 connector melted so replace it with spare one, now restore | 5:20 | 7:00 | 10:00 | 10:25 | 1.6667 | 4.6667 | 5.0833 | 5.0833 | during string monitoring found string no. 1 MC4 connector melted so replace it with spare one, now restore | closed | 0.020333 | 0.39 | 6.5961
2175 | 2025-06-30 | 2025 | 2025 | Year_2 | Year_2 | 2025-06-01 | 30 | 5:20 | 18:23 | 13.05 | BLK5 |  |  | INV3 |  |  | BLK5INV3 | 44.5 | 0.4% | String |  | during string monitoring found string no. 9on ground fault while string no.12 Fuse & y connector melted so replace it with spare one, now restore | 5:20 | 7:00 | 10:40 | 11:00 | 1.6667 | 5.3333 | 5.6667 | 5.6667 | during string monitoring found string no. 9on ground fault while string no.12 Fuse & y connector melted so replace it with spare one, now restore | closed | 0.022667 | 0.514 | 17.3867
[7 empty] | 31 |  |  | 0 | [7 empty] | #N/A | [8 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0
Formulas:
Days = DAY(EOMONTH(PA[[#This Row],[Date]], 0))
Days = DAY(EOMONTH(PA!$[Date], 0))

## Basic Data (hidden)
Equipment | Affected DC Capacity | Plant Equivalent Weightage | Fault Category Plant BD sheet | IS Number | LT Number | String Type | Equipment | Inverter Number | Status | Plant capacity | LT Number
BLK1INV1 | 289.25 | 0.4333% | Module | BLK1 | ACCB1 | Str_Typ1(445*50) | Tx | INV1 | Open | 66750 | LT1
BLK1INV2 | 289.25 | 0.4333% | Cables | BLK2 | ACCB2 | Str_Typ2 (330*60) | MVP | INV2 | Close |  | LT2
BLK1INV3 | 267 | 0.4% | String Fuses | BLK3 | ACCB3 | Str_Typ3(335*60) | Aux_Tx | INV3
BLK1INV4 | 267 | 0.4% | ACCB | BLK4 | ACCB4 | Str_Typ4(440*60) | MCR_MVP_IC_1 | INV4
BLK1INV5 | 289.25 | 0.4333% | Inverter | BLK5 | ACCB5 |  | MCR_MVP_IC_2 | INV5
BLK1INV6 | 267 | 0.4% | IDT | BLK6 | ACCB6 |  | MCR_MVP_IC_3 | INV6
BLK1INV7 | 267 | 0.4% | PTR | BLK7 | ACCB7 |  | MCR_MVP_IC_4 | INV7
BLK1INV8 | 267 | 0.4% | MV Panel | BLK8 | ACCB8 |  | MCR_MVP_OG | INV8
BLK1INV9 | 278.125 | 0.4167% | Metering System Plant |  |  |  | PWR_Tx | INV9
BLK1INV10 | 278.125 | 0.4167% | Grid System |  |  |  | Line_Bay1 | INV10
BLK1INV11 | 267 | 0.4% | Metering System Grid |  |  |  |  | INV11
BLK1INV12 | 267 | 0.4% | WMS |  |  |  |  | INV12
BLK1INV13 | 267 | 0.4% | MMS |  |  |  |  | INV13
BLK1INV14 | 244.75 | 0.3667% | Battery Charger_MCR |  |  |  |  | INV14
BLK1INV15 | 267 | 0.4% | IC_UPS |  |  |  |  | INV15
BLK1INV16 | 267 | 0.4% | IC_Auxiliary Tranformer |  |  |  |  | INV16
BLK1INV17 | 267 | 0.4% | IC_Auxiliary DB |  |  |  |  | INV17
BLK1INV18 | 267 | 0.4% | IC_SCADA Panel |  |  |  |  | INV18
BLK1INV19 | 289.25 | 0.4333% | Connectors |  |  |  |  | INV19
BLK1INV20 | 289.25 | 0.4333% | LT Panel |  |  |  |  | INV20
BLK1INV21 | 267 | 0.4% | SS |  |  |  |  | INV21
BLK1INV22 | 267 | 0.4% | Force Majeure |  |  |  |  | INV22
BLK1INV23 | 289.25 | 0.4333% | [5 empty] | INV23
BLK1INV24 | 300.375 | 0.45% | [5 empty] | INV24
BLK1INV25 | 289.25 | 0.4333% | [5 empty] | INV25
BLK1INV26 | 289.25 | 0.4333% | [5 empty] | INV26
BLK1INV27 | 289.25 | 0.4333% | [5 empty] | INV27
BLK1INV28 | 300.375 | 0.45% | [5 empty] | INV28
BLK1INV29 | 300.375 | 0.45% | [5 empty] | INV29
BLK1INV30 | 300.375 | 0.45% | [5 empty] | INV30
BLK1INV31 | 300.375 | 0.45% | [5 empty] | INV31
BLK1INV32 | 300.375 | 0.45% | [5 empty] | INV31
BLK2INV1 | 300.375 | 0.45% | [5 empty] | INV32
BLK2INV2 | 222.5 | 0.3333% | [5 empty] | All_Inv
BLK2INV3 | 111.25 | 0.1667%
BLK2INV4 | 267 | 0.4%
BLK2INV5 | 267 | 0.4%
BLK2INV6 | 267 | 0.4%
BLK2INV7 | 267 | 0.4%
BLK2INV8 | 267 | 0.4%
BLK2INV9 | 267 | 0.4%
BLK2INV10 | 267 | 0.4%
BLK2INV11 | 267 | 0.4%
BLK2INV12 | 267 | 0.4%
BLK2INV13 | 267 | 0.4%
BLK2INV14 | 267 | 0.4%
BLK2INV15 | 267 | 0.4%
BLK2INV16 | 289.25 | 0.4333%
BLK2INV17 | 267 | 0.4%
BLK2INV18 | 278.125 | 0.4167%
BLK2INV19 | 278.125 | 0.4167%
BLK2INV20 | 267 | 0.4%
BLK2INV21 | 267 | 0.4%
BLK2INV22 | 300.375 | 0.45%
BLK2INV23 | 300.375 | 0.45%
BLK2INV24 | 289.25 | 0.4333%
BLK2INV25 | 300.375 | 0.45%
BLK2INV26 | 300.375 | 0.45%
BLK2INV27 | 267 | 0.4%
BLK2INV28 | 300.375 | 0.45%
BLK2INV29 | 300.375 | 0.45%
BLK2INV30 | 267 | 0.4%
BLK2INV31 | 267 | 0.4%
BLK2INV32 | 239.25 | 0.3584%
BLK3INV1 | 267 | 0.4%
BLK3INV2 | 289.25 | 0.4333%
BLK3INV3 | 289.25 | 0.4333%
BLK3INV4 | 289.25 | 0.4333%
BLK3INV5 | 289.25 | 0.4333%
BLK3INV6 | 267 | 0.4%
BLK3INV7 | 267 | 0.4%
BLK3INV8 | 267 | 0.4%
BLK3INV9 | 267 | 0.4%
BLK3INV10 | 267 | 0.4%
BLK3INV11 | 267 | 0.4%
BLK3INV12 | 300.375 | 0.45%
BLK3INV13 | 300.375 | 0.45%
BLK3INV14 | 300.375 | 0.45%
BLK3INV15 | 267 | 0.4%
BLK3INV16 | 267 | 0.4%
BLK3INV17 | 289.25 | 0.4333%
BLK3INV18 | 267 | 0.4%
BLK3INV19 | 267 | 0.4%
BLK3INV20 | 267 | 0.4%
BLK3INV21 | 267 | 0.4%
BLK3INV22 | 267 | 0.4%
BLK3INV23 | 267 | 0.4%
BLK3INV24 | 267 | 0.4%
BLK3INV25 | 267 | 0.4%
BLK3INV26 | 267 | 0.4%
BLK3INV27 | 267 | 0.4%
BLK3INV28 | 278.125 | 0.4167%
BLK3INV29 | 289.25 | 0.4333%
BLK3INV30 | 267 | 0.4%
BLK3INV31 | 267 | 0.4%
BLK4INV1 | 300.375 | 0.45%
BLK4INV2 | 267 | 0.4%
BLK4INV3 | 267 | 0.4%
BLK4INV4 | 267 | 0.4%
BLK4INV5 | 267 | 0.4%
BLK4INV6 | 267 | 0.4%
BLK4INV7 | 267 | 0.4%
BLK4INV8 | 267 | 0.4%
BLK4INV9 | 267 | 0.4%
BLK4INV10 | 267 | 0.4%
BLK4INV11 | 300.375 | 0.45%
BLK4INV12 | 267 | 0.4%
BLK4INV13 | 300.375 | 0.45%
BLK4INV14 | 267 | 0.4%
BLK4INV15 | 267 | 0.4%
BLK4INV16 | 300.375 | 0.45%
BLK4INV17 | 289.25 | 0.4333%
BLK4INV18 | 289.25 | 0.4333%
BLK4INV19 | 300.375 | 0.45%
BLK4INV20 | 300.375 | 0.45%
BLK4INV21 | 267 | 0.4%
BLK4INV22 | 267 | 0.4%
BLK4INV23 | 267 | 0.4%
BLK4INV24 | 300.375 | 0.45%
BLK4INV25 | 300.375 | 0.45%
BLK4INV26 | 267 | 0.4%
BLK4INV27 | 267 | 0.4%
BLK4INV28 | 300.375 | 0.45%
BLK4INV29 | 300.375 | 0.45%
BLK4INV30 | 267 | 0.4%
BLK4INV31 | 267 | 0.4%
BLK5INV1 | 300.375 | 0.45%
BLK5INV2 | 267 | 0.4%
BLK5INV3 | 267 | 0.4%
BLK5INV4 | 300.375 | 0.45%
BLK5INV5 | 300.375 | 0.45%
BLK5INV6 | 289.25 | 0.4333%
BLK5INV7 | 289.25 | 0.4333%
BLK5INV8 | 289.25 | 0.4333%
BLK5INV9 | 244.75 | 0.3667%
BLK5INV10 | 286 | 0.4285%
BLK5INV11 | 286 | 0.4285%
BLK5INV12 | 286 | 0.4285%
BLK5INV13 | 286 | 0.4285%
BLK5INV14 | 278.125 | 0.4167%
BLK5INV15 | 267 | 0.4%
BLK5INV16 | 289.25 | 0.4333%
BLK5INV17 | 289.25 | 0.4333%
BLK5INV18 | 267 | 0.4%
BLK5INV19 | 289.25 | 0.4333%
BLK5INV20 | 267 | 0.4%
BLK5INV21 | 289.25 | 0.4333%
BLK5INV22 | 267 | 0.4%
BLK5INV23 | 244.75 | 0.3667%
BLK5INV24 | 267 | 0.4%
BLK5INV25 | 267 | 0.4%
BLK5INV26 | 289.25 | 0.4333%
BLK5INV27 | 267 | 0.4%
BLK5INV28 | 300.375 | 0.45%
BLK5INV29 | 267 | 0.4%
BLK5INV30 | 267 | 0.4%
BLK5INV31 | 267 | 0.4%
BLK5INV32 | 267 | 0.4%
BLK6INV1 | 267 | 0.4%
BLK6INV2 | 264 | 0.3955%
BLK6INV3 | 264 | 0.3955%
BLK6INV4 | 297 | 0.4449%
BLK6INV5 | 264 | 0.3955%
BLK6INV6 | 297 | 0.4449%
BLK6INV7 | 297 | 0.4449%
BLK6INV8 | 297 | 0.4449%
BLK6INV9 | 275 | 0.412%
BLK6INV10 | 264 | 0.3955%
BLK6INV11 | 297 | 0.4449%
BLK6INV12 | 264 | 0.3955%
BLK6INV13 | 275 | 0.412%
BLK6INV14 | 275 | 0.412%
BLK6INV15 | 275 | 0.412%
BLK6INV16 | 297 | 0.4449%
BLK6INV17 | 275 | 0.412%
BLK6INV18 | 297 | 0.4449%
BLK6INV19 | 264 | 0.3955%
BLK6INV20 | 264 | 0.3955%
BLK6INV21 | 264 | 0.3955%
BLK6INV22 | 297 | 0.4449%
BLK6INV23 | 264 | 0.3955%
BLK6INV24 | 286 | 0.4285%
BLK6INV25 | 297 | 0.4449%
BLK6INV26 | 297 | 0.4449%
BLK6INV27 | 275 | 0.412%
BLK6INV28 | 286 | 0.4285%
BLK6INV29 | 297 | 0.4449%
BLK6INV30 | 275 | 0.412%
BLK6INV31 | 275 | 0.412%
BLK6INV32 | 275 | 0.412%
BLK7INV1 | 286 | 0.4285%
BLK7INV2 | 264 | 0.3955%
BLK7INV3 | 264 | 0.3955%
BLK7INV4 | 264 | 0.3955%
BLK7INV5 | 264 | 0.3955%
BLK7INV6 | 264 | 0.3955%
BLK7INV7 | 264 | 0.3955%
BLK7INV8 | 220 | 0.3296%
BLK7INV9 | 264 | 0.3955%
BLK7INV10 | 257.4 | 0.3856%
BLK7INV11 | 190.35 | 0.2852%
BLK7INV12 | 270.6 | 0.4054%
BLK7INV13 | 244.75 | 0.3667%
BLK7INV14 | 267 | 0.4%
BLK7INV15 | 267 | 0.4%
BLK7INV16 | 267 | 0.4%
BLK7INV17 | 267 | 0.4%
BLK7INV18 | 267 | 0.4%
BLK7INV19 | 267 | 0.4%
BLK7INV20 | 267 | 0.4%
BLK7INV21 | 267 | 0.4%
BLK7INV22 | 267 | 0.4%
BLK7INV23 | 267 | 0.4%
BLK7INV24 | 267 | 0.4%
BLK7INV25 | 300.375 | 0.45%
BLK7INV26 | 300.375 | 0.45%
BLK7INV27 | 267 | 0.4%
BLK7INV28 | 267 | 0.4%
BLK7INV29 | 267 | 0.4%
BLK7INV30 | 267 | 0.4%
BLK7INV31 | 267 | 0.4%
BLK7INV32 | 159.5 | 0.239%
BLK8INV1 | 267 | 0.4%
BLK8INV2 | 198 | 0.2966%
BLK8INV3 | 188.1 | 0.2818%
BLK8INV4 | 278.125 | 0.4167%
BLK8INV5 | 300.375 | 0.45%
BLK8INV6 | 289.25 | 0.4333%
BLK8INV7 | 289.25 | 0.4333%
BLK8INV8 | 267 | 0.4%
BLK8INV9 | 289.25 | 0.4333%
BLK8INV10 | 300.375 | 0.45%
BLK8INV11 | 300.375 | 0.45%
BLK8INV12 | 257.4 | 0.3856%
BLK8INV13 | 277.2 | 0.4153%
BLK8INV14 | 257.4 | 0.3856%
BLK8INV15 | 267.3 | 0.4004%
BLK8INV16 | 188.1 | 0.2818%
BLK8INV17 | 178 | 0.2667%
BLK8INV18 | 222.5 | 0.3333%
BLK8INV19 | 287.1 | 0.4301%
BLK8INV20 | 257.4 | 0.3856%
BLK8INV21 | 267.3 | 0.4004%
BLK8INV22 | 257.4 | 0.3856%
BLK8INV23 | 271.35 | 0.4065%
BLK8INV24 | 271.35 | 0.4065%
BLK8INV25 | 261.3 | 0.3915%
BLK8INV26 | 271.35 | 0.4065%
BLK8INV27 | 291.45 | 0.4366%
BLK8INV28 | 257.4 | 0.3856%
BLK1LT1 | 4338.75 | 6.5%
BLK1LT2 | 4605.75 | 6.9%
BLK2LT1 | 4094 | 6.133%
BLK2LT2 | 4249.75 | 6.367%
BLK3LT1 | 4483.375 | 6.717%
BLK3LT2 | 4071.75 | 6.1%
BLK4LT1 | 4394.375 | 6.583%
BLK4LT2 | 4260.875 | 6.383%
BLK5LT1 | 4514.875 | 6.764%
BLK5LT2 | 4349.875 | 6.517%
BLK6LT1 | 4477 | 6.707%
BLK6LT2 | 4499 | 6.74%
BLK7LT1 | 3298.1 | 4.941%
BLK7LT2 | 4071.75 | 6.1%
BLK8LT1 | 3947.5 | 5.914%
BLK8LT2 | 3093.9 | 4.635%
BLK1LT1ACCB1 | 578.5 | 0.8667%
BLK1LT1ACCB2 | 534 | 0.8%
BLK1LT1ACCB3 | 556.25 | 0.8333%
BLK1LT1ACCB4 | 534 | 0.8%
BLK1LT1ACCB5 | 556.25 | 0.8333%
BLK1LT1ACCB6 | 534 | 0.8%
BLK1LT1ACCB7 | 511.75 | 0.7667%
BLK1LT1ACCB8 | 534 | 0.8%
BLK1LT2ACCB1 | 534 | 0.8%
BLK1LT2ACCB2 | 578.5 | 0.8667%
BLK1LT2ACCB3 | 534 | 0.8%
BLK1LT2ACCB4 | 589.625 | 0.8833%
BLK1LT2ACCB5 | 578.5 | 0.8667%
BLK1LT2ACCB6 | 589.625 | 0.8833%
BLK1LT2ACCB7 | 600.75 | 0.9%
BLK1LT2ACCB8 | 600.75 | 0.9%
BLK2LT1ACCB1 | 333.75 | 0.5%
BLK2LT1ACCB2 | 534 | 0.8%
BLK2LT1ACCB3 | 534 | 0.8%
BLK2LT1ACCB4 | 534 | 0.8%
BLK2LT1ACCB5 | 534 | 0.8%
BLK2LT1ACCB6 | 534 | 0.8%
BLK2LT1ACCB7 | 534 | 0.8%
BLK2LT1ACCB8 | 556.25 | 0.8333%
BLK2LT2ACCB1 | 556.25 | 0.8333%
BLK2LT2ACCB2 | 534 | 0.8%
BLK2LT2ACCB3 | 600.75 | 0.9%
BLK2LT2ACCB4 | 589.625 | 0.8833%
BLK2LT2ACCB5 | 567.375 | 0.85%
BLK2LT2ACCB6 | 600.75 | 0.9%
BLK2LT2ACCB7 | 534 | 0.8%
BLK2LT2ACCB8 | 267 | 0.4%
BLK3LT1ACCB1 | 578.5 | 0.8667%
BLK3LT1ACCB2 | 556.25 | 0.8333%
BLK3LT1ACCB3 | 534 | 0.8%
BLK3LT1ACCB4 | 534 | 0.8%
BLK3LT1ACCB5 | 567.375 | 0.85%
BLK3LT1ACCB6 | 600.75 | 0.9%
BLK3LT1ACCB7 | 534 | 0.8%
BLK3LT1ACCB8 | 578.5 | 0.8667%
BLK3LT2ACCB1 | 534 | 0.8%
BLK3LT2ACCB2 | 534 | 0.8%
BLK3LT2ACCB3 | 534 | 0.8%
BLK3LT2ACCB4 | 534 | 0.8%
BLK3LT2ACCB5 | 545.125 | 0.8167%
BLK3LT2ACCB6 | 556.25 | 0.8333%
BLK3LT2ACCB7 | 567.375 | 0.85%
BLK3LT2ACCB8 | 267 | 0.4%
BLK4LT1ACCB1 | 534 | 0.8%
BLK4LT1ACCB2 | 534 | 0.8%
BLK4LT1ACCB3 | 534 | 0.8%
BLK4LT1ACCB4 | 534 | 0.8%
BLK4LT1ACCB5 | 567.375 | 0.85%
BLK4LT1ACCB6 | 567.375 | 0.85%
BLK4LT1ACCB7 | 534 | 0.8%
BLK4LT1ACCB8 | 589.625 | 0.8833%
BLK4LT2ACCB1 | 589.625 | 0.8833%
BLK4LT2ACCB2 | 567.375 | 0.85%
BLK4LT2ACCB3 | 534 | 0.8%
BLK4LT2ACCB4 | 600.75 | 0.9%
BLK4LT2ACCB5 | 534 | 0.8%
BLK4LT2ACCB6 | 600.75 | 0.9%
BLK4LT2ACCB7 | 534 | 0.8%
BLK4LT2ACCB8 | 300.375 | 0.45%
BLK5LT1ACCB1 | 534 | 0.8%
BLK5LT1ACCB2 | 600.75 | 0.9%
BLK5LT1ACCB3 | 578.5 | 0.8667%
BLK5LT1ACCB4 | 534 | 0.8%
BLK5LT1ACCB5 | 572 | 0.8569%
BLK5LT1ACCB6 | 572 | 0.8569%
BLK5LT1ACCB7 | 545.125 | 0.8167%
BLK5LT1ACCB8 | 578.5 | 0.8667%
BLK5LT2ACCB1 | 556.25 | 0.8333%
BLK5LT2ACCB2 | 556.25 | 0.8333%
BLK5LT2ACCB3 | 511.75 | 0.7667%
BLK5LT2ACCB4 | 534 | 0.8%
BLK5LT2ACCB5 | 556.25 | 0.8333%
BLK5LT2ACCB6 | 567.375 | 0.85%
BLK5LT2ACCB7 | 534 | 0.8%
BLK5LT2ACCB8 | 534 | 0.8%
BLK6LT1ACCB1 | 528 | 0.791%
BLK6LT1ACCB2 | 561 | 0.8404%
BLK6LT1ACCB3 | 594 | 0.8899%
BLK6LT1ACCB4 | 572 | 0.8569%
BLK6LT1ACCB5 | 561 | 0.8404%
BLK6LT1ACCB6 | 539 | 0.8075%
BLK6LT1ACCB7 | 550 | 0.824%
BLK6LT1ACCB8 | 572 | 0.8569%
BLK6LT2ACCB1 | 561 | 0.8404%
BLK6LT2ACCB2 | 528 | 0.791%
BLK6LT2ACCB3 | 561 | 0.8404%
BLK6LT2ACCB4 | 583 | 0.8734%
BLK6LT2ACCB5 | 572 | 0.8569%
BLK6LT2ACCB6 | 583 | 0.8734%
BLK6LT2ACCB7 | 550 | 0.824%
BLK6LT2ACCB8 | 561 | 0.8404%
BLK7LT1ACCB1 | 528 | 0.791%
BLK7LT1ACCB2 | 528 | 0.791%
BLK7LT1ACCB3 | 528 | 0.791%
BLK7LT1ACCB4 | 484 | 0.7251%
BLK7LT1ACCB5 |  | 0%
BLK7LT1ACCB6 | 447.75 | 0.6708%
BLK7LT1ACCB7 | 270.5 | 0.4052%
BLK7LT1ACCB8 | 511.75 | 0.7667%
BLK7LT2ACCB1 | 534 | 0.8%
BLK7LT2ACCB2 | 534 | 0.8%
BLK7LT2ACCB3 | 534 | 0.8%
BLK7LT2ACCB4 | 534 | 0.8%
BLK7LT2ACCB5 | 534 | 0.8%
BLK7LT2ACCB6 | 600.75 | 0.9%
BLK7LT2ACCB7 | 534 | 0.8%
BLK7LT2ACCB8 | 267 | 0.4%
BLK8LT1ACCB1 | 386.1 | 0.5784%
BLK8LT1ACCB2 | 578.5 | 0.8667%
BLK8LT1ACCB3 | 578.5 | 0.8667%
BLK8LT1ACCB4 | 556.25 | 0.8333%
BLK8LT1ACCB5 | 600.75 | 0.9%
BLK8LT1ACCB6 | 534.6 | 0.8009%
BLK8LT1ACCB7 | 524.7 | 0.7861%
BLK8LT1ACCB8 | 188.1 | 0.2818%
BLK8LT2ACCB1 | 400.5 | 0.6%
BLK8LT2ACCB2 | 544.5 | 0.8157%
BLK8LT2ACCB3 | 524.7 | 0.7861%
BLK8LT2ACCB4 | 542.7 | 0.813%
BLK8LT2ACCB5 | 532.65 | 0.798%
BLK8LT2ACCB6 | 548.85 | 0.8222%
BLK1TX | 8944.5 | 13.4%
BLK2TX | 8343.75 | 12.5%
BLK3TX | 8555.125 | 12.82%
BLK4TX | 8655.25 | 12.97%
BLK5TX | 8864.75 | 13.28%
BLK6TX | 8976 | 13.45%
BLK7TX | 7369.85 | 11.04%
BLK8TX | 7041.4 | 10.55%
MCR_MVP_IC_1 | 17288.25 | 25.9%
MCR_MVP_IC_2 | 17210.375 | 25.78%
MCR_MVP_IC_3 | 17840.75 | 26.73%
MCR_MVP_IC_4 | 14411.25 | 21.59%
MCR_MVP_OG | 66750.25 | 100%
PWR_TX | 66750.25 | 100%
132KV_OC | 66750.25 | 100%
Line_Bay1 | 66750.25 | 100%
Str_Typ1(445*50) | 22.25 | 0.03333%
Str_Typ2 (330*60) | 19.8 | 0.02966%
Str_Typ3(335*60) | 20.1 | 0.03011%
Str_Typ4(440*60) | 22 | 0.03296%
BLK1MVP | 8944.5 | 13.4%
BLK2MVP | 8343.75 | 12.5%
BLK3MVP | 8555.125 | 12.82%
BLK4MVP | 8655.25 | 12.97%
BLK5MVP | 8864.75 | 13.28%
BLK6MVP | 8976 | 13.45%
BLK7MVP | 7369.85 | 11.04%
BLK8MVP | 7041.4 | 10.55%
BLK1Aux_Tx | 8944.5 | 13.4%
BLK2Aux_Tx | 8343.75 | 12.5%
BLK3Aux_Tx | 8555.125 | 12.82%
BLK4Aux_Tx | 8655.25 | 12.97%
BLK5Aux_Tx | 8864.75 | 13.28%
BLK6Aux_Tx | 8976 | 13.45%
BLK7Aux_Tx | 7369.85 | 11.04%
BLK8Aux_Tx | 7041.4 | 10.55%
All_Inv | 66750.25 | 100%

## GA
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
Sr. No. | Date | Financial Year | Calendar Year | Contractual Year | Operating Year | Month Year | Days | Sunrise Time (POA>20 W/m2) | Sunset Time (POA<20 W/m2) | Total Generation Time | Affected Equipment | DC Capacity Affected (kW) | Plant Equivalent Weightage | Breakdown Description | Fault Time | Work Completion time on fault | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Lost PoA(kWh/m2) | Approximate Energy Loss (KWh)
1 |  | 1900 | 1900 | Year-2 | Year-2 | 1899-12-31 | 31 | 0:00 | 0:00 | 0 |  | 0 | 0% |  |  |  | 0 |  |  | 0
2 |  | 1900 | 1900 | Year-2 | Year-2 | 1899-12-31 | 31 | 0:00 | 0:00 | 0 |  | 0 | 0% |  |  |  | 0 |  |  | 0
3 |  | 1900 | 1900 | Year-2 | Year-2 | 1899-12-31 | 31 | 0:00 | 0:00 | 0 |  | 0 | 0% |  |  |  | 0 |  |  | 0
4 |  | 1900 | 1900 | Year-2 | Year-2 | 1899-12-31 | 31 | 0:00 | 0:00 | 0 |  | 0 | 0% |  |  |  | 0 |  |  | 0
[6 empty] | 1899-12-31 | [10 empty] | 0 |  |  | 0
[6 empty] | 1899-12-31 | [10 empty] | 0 |  |  | 0
[6 empty] | 1899-12-31 | [10 empty] | 0 |  |  | 0
Formulas:
Month Year = GA[[#This Row],[Date]]-DAY(GA[[#This Row],[Date]])+1
Days = DAY(EOMONTH(GA[[#This Row],[Month Year]],0))

## Inv_SY_B
| 289.25 | 289.25 | 267 | 267 | 289.25 | 267 | 267 | 267 | 278.125 | 278.125 | 267 | 267 | 267 | 244.75 | 267 | 267 | 267 | 267 | 289.25 | 289.25 | 267 | 267 | 289.25 | 300.375 | 289.25 | 289.25 | 289.25 | 300.375 | 300.375 | 300.375 | 300.375 | 300.375 | 254.4 | 334.55 | 267 | 298.9 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 289.25 | 267 | 278.125 | 278.125 | 267 | 267 | 300.375 | 300.375 | 289.25 | 300.375 | 300.375 | 267 | 300.375 | 300.375 | 267 | 298.9 | 267 | 239.25 | 289.25 | 289.25 | 289.25 | 289.25 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 300.375 | 300.375 | 267 | 267 | 289.25 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 278.125 | 289.25 | 267 | 267 | 300.375 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 267 | 300.375 | 298.9 | 267 | 300.375 | 289.25 | 289.25 | 300.375 | 300.375 | 267 | 267 | 298.9 | 300.375 | 300.375 | 267 | 267 | 300.375 | 300.375 | 267 | 267 | 300.375 | 267 | 267 | 300.375 | 300.375 | 289.25 | 289.25 | 289.25 | 244.75 | 286 | 286 | 286 | 286 | 278.125 | 267 | 289.25 | 289.25 | 267 | 289.25 | 267 | 289.25 | 267 | 244.75 | 289.25 | 289.25 | 289.25 | 267 | 300.375 | 267 | 267 | 267 | 267 | 267 | 264 | 264 | 297 | 264 | 297 | 297 | 297 | 275 | 264 | 297 | 264 | 275 | 275 | 275 | 297 | 275 | 297 | 264 | 264 | 264 | 297 | 264 | 286 | 297 | 297 | 275 | 286 | 297 | 275 | 275 | 275 | 286 | 264 | 264 | 264 | 264 | 264 | 264 | 220 | 264 | 0 | 0 | 257.4 | 190.35 | 270.6 | 0 | 292.6 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 300.375 | 223.3 | 223.3 | 191.4 | 159.5 | 207.9 | 239.8 | 278.125 | 300.375 | 289.25 | 289.25 | 278.125 | 289.25 | 300.375 | 300.375 | 257.4 | 277.2 | 257.4 | 267.3 | 247.5 | 0 | 353.3 | 287.1 | 100.5 | 267.3 | 257.4 | 0 | 0 | 239.25 | 255.2 | 291.45 | 257.4 | 241.2 | 67049.85
| 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 | 120 | 121 | 122 | 123 | 124 | 125 | 126 | 127 | 128 | 129 | 130 | 131 | 132 | 133 | 134 | 135 | 136 | 137 | 138 | 139 | 140 | 141 | 142 | 143 | 144 | 145 | 146 | 147 | 148 | 149 | 150 | 151 | 152 | 153 | 154 | 155 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 163 | 164 | 165 | 166 | 167 | 168 | 169 | 170 | 171 | 172 | 173 | 174 | 175 | 176 | 177 | 178 | 179 | 180 | 181 | 182 | 183 | 184 | 185 | 186 | 187 | 188 | 189 | 190 | 191 | 192 | 193 | 194 | 195 | 196 | 197 | 198 | 199 | 200 | 201 | 202 | 203 | 204 | 205 | 206 | 207 | 208 | 209 | 210 | 211 | 212 | 213 | 214 | 215 | 216 | 217 | 218 | 219 | 220 | 221 | 222 | 223 | 224 | 225 | 226 | 227 | 228 | 229 | 230 | 231 | 232 | 233 | 234 | 235 | 236 | 237 | 238 | 239 | 240 | 241 | 242 | 243 | 244 | 245 | 246 | 247 | 248 | 249 | 250 | 251 | 252 | 253 | 254 | 255 | 256 | 257 | 258 | 259 | 260 | 261
Date | BLK1_INV1 | BLK1_INV2 | BLK1_INV3 | BLK1_INV4 | BLK1_INV5 | BLK1_INV6 | BLK1_INV7 | BLK1_INV8 | BLK1_INV9 | BLK1_INV10 | BLK1_INV11 | BLK1_INV12 | BLK1_INV13 | BLK1_INV14 | BLK1_INV15 | BLK1_INV16 | BLK1_INV17 | BLK1_INV18 | BLK1_INV19 | BLK1_INV20 | BLK1_INV21 | BLK1_INV22 | BLK1_INV23 | BLK1_INV24 | BLK1_INV25 | BLK1_INV26 | BLK1_INV27 | BLK1_INV28 | BLK1_INV29 | BLK1_INV30 | BLK1_INV31 | BLK1_INV32 | BLK2_INV1 | BLK2_INV2 | BLK2_INV3 | BLK2_INV4 | BLK2_INV5 | BLK2_INV6 | BLK2_INV7 | BLK2_INV8 | BLK2_INV9 | BLK2_INV10 | BLK2_INV11 | BLK2_INV12 | BLK2_INV13 | BLK2_INV14 | BLK2_INV15 | BLK2_INV16 | BLK2_INV17 | BLK2_INV18 | BLK2_INV19 | BLK2_INV20 | BLK2_INV21 | BLK2_INV22 | BLK2_INV23 | BLK2_INV24 | BLK2_INV25 | BLK2_INV26 | BLK2_INV27 | BLK2_INV28 | BLK2_INV29 | BLK2_INV30 | BLK2_INV31 | BLK2_INV32 | BLK3_INV1 | BLK3_INV2 | BLK3_INV3 | BLK3_INV4 | BLK3_INV5 | BLK3_INV6 | BLK3_INV7 | BLK3_INV8 | BLK3_INV9 | BLK3_INV10 | BLK3_INV11 | BLK3_INV12 | BLK3_INV13 | BLK3_INV14 | BLK3_INV15 | BLK3_INV16 | BLK3_INV17 | BLK3_INV18 | BLK3_INV19 | BLK3_INV20 | BLK3_INV21 | BLK3_INV22 | BLK3_INV23 | BLK3_INV24 | BLK3_INV25 | BLK3_INV26 | BLK3_INV27 | BLK3_INV28 | BLK3_INV29 | BLK3_INV30 | BLK3_INV31 | BLK4_INV1 | BLK4_INV2 | BLK4_INV3 | BLK4_INV4 | BLK4_INV5 | BLK4_INV6 | BLK4_INV7 | BLK4_INV8 | BLK4_INV9 | BLK4_INV10 | BLK4_INV11 | BLK4_INV12 | BLK4_INV13 | BLK4_INV14 | BLK4_INV15 | BLK4_INV16 | BLK4_INV17 | BLK4_INV18 | BLK4_INV19 | BLK4_INV20 | BLK4_INV21 | BLK4_INV22 | BLK4_INV23 | BLK4_INV24 | BLK4_INV25 | BLK4_INV26 | BLK4_INV27 | BLK4_INV28 | BLK4_INV29 | BLK4_INV30 | BLK4_INV31 | BLK5_INV1 | BLK5_INV2 | BLK5_INV3 | BLK5_INV4 | BLK5_INV5 | BLK5_INV6 | BLK5_INV7 | BLK5_INV8 | BLK5_INV9 | BLK5_INV10 | BLK5_INV11 | BLK5_INV12 | BLK5_INV13 | BLK5_INV14 | BLK5_INV15 | BLK5_INV16 | BLK5_INV17 | BLK5_INV18 | BLK5_INV19 | BLK5_INV20 | BLK5_INV21 | BLK5_INV22 | BLK5_INV23 | BLK5_INV24 | BLK5_INV25 | BLK5_INV26 | BLK5_INV27 | BLK5_INV28 | BLK5_INV29 | BLK5_INV30 | BLK5_INV31 | BLK5_INV32 | BLK6_INV1 | BLK6_INV2 | BLK6_INV3 | BLK6_INV4 | BLK6_INV5 | BLK6_INV6 | BLK6_INV7 | BLK6_INV8 | BLK6_INV9 | BLK6_INV10 | BLK6_INV11 | BLK6_INV12 | BLK6_INV13 | BLK6_INV14 | BLK6_INV15 | BLK6_INV16 | BLK6_INV17 | BLK6_INV18 | BLK6_INV19 | BLK6_INV20 | BLK6_INV21 | BLK6_INV22 | BLK6_INV23 | BLK6_INV24 | BLK6_INV25 | BLK6_INV26 | BLK6_INV27 | BLK6_INV28 | BLK6_INV29 | BLK6_INV30 | BLK6_INV31 | BLK6_INV32 | BLK7_INV1 | BLK7_INV2 | BLK7_INV3 | BLK7_INV4 | BLK7_INV5 | BLK7_INV6 | BLK7_INV7 | BLK7_INV8 | BLK7_INV9 | BLK7_INV10 | BLK7_INV11 | BLK7_INV12 | BLK7_INV13 | BLK7_INV14 | BLK7_INV15 | BLK7_INV16 | BLK7_INV17 | BLK7_INV18 | BLK7_INV19 | BLK7_INV20 | BLK7_INV21 | BLK7_INV22 | BLK7_INV23 | BLK7_INV24 | BLK7_INV25 | BLK7_INV26 | BLK7_INV27 | BLK7_INV28 | BLK7_INV29 | BLK7_INV30 | BLK7_INV31 | BLK7_INV32 | BLK8_INV1 | BLK8_INV2 | BLK8_INV3 | BLK8_INV4 | BLK8_INV5 | BLK8_INV6 | BLK8_INV7 | BLK8_INV8 | BLK8_INV9 | BLK8_INV10 | BLK8_INV11 | BLK8_INV12 | BLK8_INV13 | BLK8_INV14 | BLK8_INV15 | BLK8_INV16 | BLK8_INV17 | BLK8_INV18 | BLK8_INV19 | BLK8_INV20 | BLK8_INV21 | BLK8_INV22 | BLK8_INV23 | BLK8_INV24 | BLK8_INV25 | BLK8_INV26 | BLK8_INV27 | BLK8_INV28 | Plnat
2025-05-30 | 4.1286 | 4.1137 | 4.3367 | 4.1704 | 4.0505 | 4.161 | 4.1509 | 4.1637 | 4.1312 | 4.1693 | 4.233 | 4.2124 | 4.1547 | 4.2566 | 4.1453 | 4.1266 | 4.0652 | 4.1206 | 4.0391 | 4.1169 | 4.1622 | 4.1599 | 4.1964 | 4.1481 | 4.1791 | 4.1455 | 4.1455 | 4.0965 | 4.1012 | 4.1715 | 4.1931 | 4.1218 | 4.0507 | 4.0673 | 4.0648 | 4.1214 | 4.2075 | 4.1026 | 4.1652 | 4.2315 | 4.1517 | 4.1082 | 4.1757 | 4.0989 | 4.1685 | 4.1625 | 4.1822 | 4.2719 | 4.101 | 4.0313 | 4.0813 | 4.1375 | 4.227 | 4.1608 | 4.1096 | 4.1788 | 4.1695 | 4.1884 | 4.1302 | 4.0236 | 4.2176 | 4.2449 | 4.1367 | 4.494 | 4.1376 | 4.1131 | 4.1673 | 4.0678 | 4.1067 | 4.0978 | 4.1258 | 4.1127 | 4.1948 | 4.124 | 4.2187 | 4.1322 | 4.2137 | 4.173 | 4.0921 | 4.0885 | 4.17 | 4.1742 | 4.1052 | 4.1625 | 4.1581 | 4.1378 | 4.1693 | 4.1292 | 4.1071 | 4.0663 | 4.1086 | 4.0985 | 4.2101 | 4.1779 | 4.1318 | 4.0712 | 4.0903 | 4.1659 | 4.1337 | 4.1363 | 4.2554 | 4.1476 | 4.236 | 4.1592 | 4.2324 | 4.1873 | 4.3752 | 4.1218 | 4.1854 | 4.0939 | 4.1583 | 4.1089 | 4.1641 | 4.1412 | 4.1464 | 4.0509 | 4.1077 | 4.1495 | 4.1255 | 4.1798 | 4.227 | 4.1398 | 4.293 | 4.1693 | 4.1993 | 4.2171 | 4.0491 | 4.039 | 4.1908 | 4.1402 | 4.065 | 4.1618 | 4.1227 | 4.1777 | 4.3878 | 4.0703 | 4.2318 | 4.1024 | 4.2337 | 4.182 | 4.0681 | 4.0525 | 4.1831 | 4.1957 | 4.0446 | 4.0377 | 4.1408 | 4.2096 | 4.1328 | 4.1791 | 4.2064 | 4.1891 | 4.273 | 4.2232 | 4.1599 | 4.1094 | 4.1255 | 4.0745 | 4.0576 | 4.0894 | 4.0778 | 4.0322 | 4.0936 | 4.0444 | 4.0263 | 4.0782 | 4.0595 | 4.0519 | 4.0322 | 4.0418 | 4.0298 | 4.0782 | 4.067 | 4.2513 | 4.096 | 4.0295 | 4.0496 | 4.0739 | 4.0859 | 4.0864 | 4.1241 | 4.0444 | 4.032 | 4.0789 | 4.0367 | 4.1094 | 4.0429 | 4.0716 | 4.0309 | 4.0538 | 4.1508 | 4.0871 | 4.0928 | 4.2117 | 4.1875 | 4.2197 | 4.2336 | 4.2955 |  |  | 3.9169 | 4.1613 | 4.0828 |  | 4.1118 | 4.0045 | 4.1667 | 4.0491 | 4.1461 | 4.1521 | 4.221 | 4.2 | 4.2101 | 4.2831 | 4.1835 | 4.2277 | 4.1828 | 4.2607 | 4.5902 | 4.4631 | 4.4932 | 4.5398 | 4.0659 | 4.0938 | 4.1312 | 4.1385 | 4.0557 | 4.3111 | 4.1399 | 4.0619 | 4.1099 | 4.1665 | 4.2401 | 4.0931 | 4.2063 | 4.0696 | 4.1527 |  | 4.1763 | 4.147 | 4.3532 | 4.034 | 4.0824 |  |  | 4.5183 | 4.3954 | 3.7787 | 4.0544 | 4.1335 | 4.1477
2025-05-31 | 3.711 | 3.4676 | 3.7528 | 3.7476 | 3.4607 | 3.7288 | 3.736 | 3.7382 | 3.7084 | 3.7379 | 3.7981 | 3.7805 | 3.727 | 3.8284 | 3.7243 | 3.712 | 3.7341 | 3.7049 | 3.6923 | 3.7041 | 3.7753 | 3.8318 | 3.7988 | 3.7986 | 3.7995 | 3.7386 | 3.7027 | 3.6937 | 3.7603 | 3.6881 | 3.7347 | 3.72 | 3.7138 | 3.6897 | 3.7026 | 3.7063 | 3.7693 | 3.673 | 3.73 | 3.7981 | 3.7082 | 3.6921 | 3.7071 | 3.6536 | 3.7835 | 3.7049 | 3.7912 | 3.7217 | 3.739 | 3.7127 | 3.4041 | 3.785 | 3.8658 | 3.8099 | 3.6996 | 3.7563 | 3.7526 | 3.7569 | 3.7054 | 3.3605 | 3.7764 | 3.7989 | 3.7655 | 4.0196 | 3.748 | 3.7213 | 3.7784 | 3.6754 | 3.715 | 3.718 | 3.7408 | 3.724 | 3.8094 | 3.73 | 3.8548 | 3.7753 | 3.8489 | 3.8015 | 3.7232 | 3.6747 | 3.7839 | 3.7936 | 3.7157 | 3.7757 | 3.7813 | 3.8004 | 3.7835 | 3.7412 | 3.7161 | 3.6775 | 3.7156 | 3.6826 | 3.8139 | 3.7903 | 3.741 | 3.6921 | 3.7154 | 3.7824 | 3.7521 | 3.7577 | 3.8659 | 3.764 | 3.8509 | 3.7738 | 3.8558 | 3.7906 | 3.727 | 3.7407 | 3.7948 | 3.6731 | 3.7583 | 3.7086 | 3.7117 | 3.7463 | 3.761 | 3.736 | 3.723 | 3.7397 | 3.7307 | 3.7678 | 3.821 | 3.706 | 3.7423 | 3.7685 | 3.7993 | 3.8116 | 3.7412 | 3.697 | 3.7949 | 3.7307 | 3.72 | 3.7483 | 3.7137 | 3.7638 | 3.7042 | 3.6734 | 3.8126 | 3.8479 | 3.813 | 3.7723 | 3.6633 | 3.6671 | 3.7727 | 3.7884 | 3.6457 | 3.5793 | 3.7472 | 3.8112 | 3.7383 | 3.7808 | 3.8116 | 3.794 | 3.8762 | 3.8288 | 3.7682 | 3.7228 | 3.7659 | 3.7378 | 3.7481 | 3.7155 | 3.7751 | 3.6841 | 3.7694 | 3.7896 | 3.7714 | 3.7655 | 3.7178 | 3.7657 | 3.7557 | 3.7509 | 3.7705 | 3.7629 | 3.7862 | 3.752 | 3.4394 | 3.7598 | 3.7481 | 3.7178 | 3.8034 | 3.7405 | 3.7909 | 3.7582 | 3.7815 | 3.7436 | 3.7818 | 3.4135 | 3.7436 | 3.5956 | 3.7324 | 3.7745 | 3.7307 | 3.7167 | 3.7557 | 3.797 | 3.7826 | 3.7947 | 3.8223 | 3.8701 |  |  | 3.5218 | 3.7326 | 3.6656 |  | 3.7054 | 3.673 | 3.7876 | 3.6712 | 3.7562 | 3.7727 | 3.8326 | 3.8161 | 3.8303 | 3.8712 | 3.7978 | 3.8352 | 3.8052 | 3.8745 | 4.1379 | 4.026 | 4.0455 | 4.1135 | 3.6999 | 3.6668 | 3.7196 | 3.6944 | 3.6875 | 3.879 | 3.7088 | 3.6695 | 3.6761 | 3.704 | 3.6908 | 3.6829 | 3.6577 | 3.7074 | 3.7414 |  | 3.7645 | 3.7189 | 4.1204 | 3.7239 | 3.6472 |  |  | 4.2825 | 4.076 | 3.6154 | 3.6783 | 3.7355 | 3.7514
2025-06-01 | 3.4064 | 3.4403 | 3.4011 | 3.4491 | 3.4382 | 3.439 | 3.4498 | 3.4176 | 3.4308 | 3.4495 | 3.5161 | 3.4989 | 3.4378 | 3.5256 | 3.4348 | 3.4513 | 3.2719 | 3.4082 | 3.4154 | 3.4251 | 3.4479 | 3.4464 | 3.4835 | 3.449 | 3.4811 | 3.4479 | 3.4182 | 3.4014 | 3.4643 | 3.4074 | 3.4347 | 3.4317 | 3.4009 | 3.4058 | 3.379 | 3.4523 | 3.4667 | 3.3745 | 3.439 | 3.4891 | 3.4199 | 3.3981 | 3.4479 | 3.1165 | 3.4382 | 3.4521 | 3.4417 | 3.4139 | 3.4039 | 3.3463 | 3.433 | 3.4416 | 3.4956 | 3.445 | 3.4164 | 3.4627 | 3.4707 | 3.4738 | 3.4241 | 3.467 | 3.4648 | 3.5008 | 3.4412 | 3.7292 | 3.4154 | 3.3901 | 3.4451 | 3.3573 | 3.3929 | 3.3749 | 3.4075 | 3.3925 | 3.4742 | 3.4154 | 3.499 | 3.4304 | 3.4806 | 3.4311 | 3.3933 | 3.4064 | 3.4457 | 3.4536 | 3.4052 | 3.4502 | 3.4139 | 3.4213 | 3.4457 | 3.4161 | 3.3906 | 3.4341 | 3.3895 | 3.4254 | 3.4824 | 3.4543 | 3.4057 | 3.3712 | 3.3839 | 3.43 | 3.406 | 3.4026 | 3.4959 | 3.403 | 3.4749 | 3.4105 | 3.488 | 3.4187 | 3.6291 | 3.4028 | 3.4371 | 3.3778 | 3.3943 | 3.3991 | 3.4257 | 3.4111 | 3.4131 | 3.4288 | 3.3958 | 3.3878 | 3.3778 | 3.4169 | 3.4719 | 3.3928 | 3.4141 | 3.4116 | 3.4322 | 3.4007 | 3.376 | 3.4079 | 3.4267 | 3.3914 | 3.1364 | 3.4209 | 3.4078 | 3.4468 | 3.6224 | 3.6413 | 3.6077 | 3.6311 | 3.4984 | 3.47 | 3.6024 | 3.5838 | 3.4502 | 3.47 | 3.3255 | 3.2781 | 3.4232 | 3.4737 | 3.3943 | 3.4389 | 3.4527 | 3.4169 | 3.4647 | 3.4296 | 3.4517 | 3.4142 | 3.4067 | 3.4363 | 3.3617 | 3.3758 | 3.4596 | 3.3799 | 3.4724 | 3.4663 | 3.4532 | 3.3436 | 3.3693 | 3.4394 | 3.3542 | 3.3458 | 3.3145 | 3.3298 | 3.47 | 3.3287 | 3.4394 | 3.3754 | 3.3576 | 3.3739 | 3.4492 | 3.364 | 3.3483 | 3.4327 | 3.4623 | 3.3324 | 3.3787 | 3.4492 | 3.3469 | 3.3582 | 3.3505 | 3.3724 | 3.4148 | 3.4515 | 3.4375 | 3.472 | 3.4386 | 2.5625 | 3.4964 | 3.5189 |  |  | 3.1892 | 3.2661 | 3.3544 |  | 3.3951 | 3.2884 | 3.4382 | 3.3427 | 3.4217 | 3.4255 | 3.4655 | 3.4491 | 3.4652 | 3.5064 | 3.4483 | 3.4839 | 3.4537 | 3.5183 | 3.8052 | 3.7071 | 3.7126 | 3.7693 | 3.4507 | 3.3711 | 3.392 | 3.3884 | 3.4009 | 3.3272 | 3.3636 | 3.4216 | 3.3648 | 3.7164 | 3.3446 | 3.3532 | 3.3768 | 3.4669 | 3.5091 |  | 3.5052 | 3.3615 | 4.2239 | 3.3591 | 3.3932 |  |  | 3.7893 | 3.7261 | 3.1282 | 3.3291 | 3.3802 | 3.4314
2025-06-02 | 3.5267 | 3.5471 | 3.6888 | 3.8427 | 3.7978 | 3.8082 | 3.8 | 3.4933 | 3.7807 | 3.8015 | 3.873 | 3.8577 | 3.7966 | 3.8917 | 3.7921 | 3.7685 | 3.6071 | 3.7629 | 3.7739 | 3.7763 | 3.8056 | 3.8067 | 3.8396 | 3.8106 | 3.8417 | 3.8057 | 3.7808 | 3.7646 | 3.8395 | 3.762 | 3.8469 | 3.8136 | 3.9513 | 3.4509 | 3.9333 | 3.9575 | 3.9476 | 3.8371 | 3.9064 | 3.9558 | 3.888 | 3.8596 | 3.9228 | 3.8996 | 3.9037 | 3.9288 | 3.9094 | 3.8794 | 3.877 | 3.8062 | 3.9007 | 3.9116 | 3.978 | 3.9194 | 3.8845 | 3.9917 | 3.9451 | 3.9487 | 3.8931 | 3.9481 | 3.9352 | 3.992 | 3.8843 | 4.2679 | 4.0339 | 4.0145 | 4.0449 | 3.9468 | 4.0045 | 3.9985 | 4.0142 | 3.9951 | 4.0599 | 3.9936 | 4.02 | 3.9517 | 4.0306 | 3.9933 | 3.9581 | 3.9471 | 3.8423 | 4.0311 | 3.9749 | 4.036 | 3.9712 | 3.9798 | 4.012 | 3.9723 | 3.9805 | 3.9401 | 3.9838 | 4.0383 | 4.0566 | 4.0277 | 4.005 | 3.9539 | 3.9487 | 4.0386 | 3.9783 | 4.0075 | 4.1116 | 3.9903 | 4.0715 | 3.985 | 4.0469 | 4.0363 | 4.2114 | 3.9746 | 4.0468 | 3.9397 | 4.0128 | 3.943 | 3.982 | 3.984 | 4.0199 | 3.8479 | 3.9518 | 3.9947 | 3.9907 | 4.036 | 4.0798 | 3.8226 | 3.8096 | 4.0191 | 4.0573 | 4.0533 | 3.3828 | 3.4371 | 3.8136 | 3.7686 | 3.4873 | 3.795 | 3.7839 | 3.8329 | 4.0385 | 3.7594 | 3.8983 | 3.571 | 3.9299 | 3.876 | 3.7393 | 3.7286 | 3.8506 | 3.8717 | 3.7307 | 3.6691 | 3.8184 | 3.8684 | 3.7763 | 3.8264 | 3.8524 | 3.8172 | 3.8855 | 3.8375 | 3.7678 | 3.764 | 3.7846 | 3.7693 | 3.6375 | 3.5773 | 3.6707 | 3.6027 | 3.704 | 3.7343 | 3.7091 | 3.5113 | 3.6159 | 3.7434 | 3.6386 | 3.5247 | 3.5113 | 3.5167 | 3.6704 | 3.6076 | 3.7343 | 3.5939 | 3.6258 | 3.611 | 3.7084 | 3.6178 | 3.7437 | 3.7074 | 3.7438 | 3.5316 | 3.7311 | 3.73 | 3.6367 | 3.6404 | 3.6771 | 3.7381 | 3.9939 | 3.9784 | 3.997 | 4.0489 | 4.0307 | 4.0148 | 4.0909 | 4.1053 |  |  | 3.73 | 3.8025 | 3.9172 |  | 3.9105 | 3.8176 | 4.0273 | 4.0116 | 4.0034 | 4.0105 | 4.0566 | 4.0438 | 4.0592 | 4.1026 | 4.0315 | 4.07 | 4.1631 | 4.0672 | 4.3887 | 4.2803 | 4.3015 | 4.3536 | 4.0462 | 4.0096 | 4.0244 | 3.9674 | 3.879 | 3.8759 | 3.9748 | 3.9222 | 3.9008 | 3.9377 | 3.9176 | 3.9708 | 3.8695 | 3.9368 | 3.9818 |  | 3.9641 | 3.8224 | 4.8189 | 3.8201 | 3.8504 |  |  | 4.5133 | 4.2778 | 3.7403 | 3.9584 | 3.7815 | 3.8872
2025-06-03 | 3.0831 | 3.1191 | 3.091 | 3.6622 | 3.6391 | 3.6569 | 3.6573 | 3.4614 | 3.6318 | 3.6541 | 3.718 | 3.7011 | 3.6382 | 3.7295 | 3.6378 | 3.6202 | 3.4566 | 3.6004 | 3.5945 | 3.6076 | 3.6423 | 3.6464 | 3.6882 | 3.6458 | 3.665 | 3.636 | 3.6111 | 3.6042 | 3.6434 | 3.6002 | 3.6671 | 3.6804 | 2.855 | 2.4845 | 3.1966 | 3.2084 | 3.2131 | 3.136 | 3.1978 | 3.2449 | 3.1708 | 3.1461 | 3.212 | 3.2228 | 3.2041 | 3.224 | 3.2093 | 3.1255 | 3.1838 | 3.1284 | 3.2124 | 3.2502 | 3.2639 | 3.218 | 3.1882 | 3.2483 | 3.237 | 3.2434 | 3.185 | 3.2203 | 3.2199 | 3.2509 | 3.1918 | 3.4901 | 3.6705 | 3.6529 | 3.6795 | 3.5972 | 3.6723 | 3.6715 | 3.7124 | 3.6936 | 3.7738 | 3.6655 | 3.6797 | 3.6095 | 3.715 | 3.6951 | 3.6704 | 3.6048 | 3.5772 | 3.7423 | 3.6993 | 3.7539 | 3.7086 | 3.7206 | 3.7423 | 3.7142 | 3.689 | 3.6528 | 3.6387 | 3.6145 | 3.7633 | 3.7502 | 3.6594 | 3.7285 | 3.6712 | 3.7333 | 3.6801 | 3.706 | 3.7951 | 3.697 | 3.7569 | 3.6846 | 3.6967 | 3.7262 | 3.8239 | 3.6393 | 3.7303 | 3.5785 | 3.683 | 3.3981 | 3.6251 | 3.6584 | 3.7206 | 3.5 | 3.6059 | 3.6424 | 3.6418 | 3.7206 | 3.7457 | 3.481 | 3.43 | 3.7109 | 3.7494 | 3.702 | 3.0419 | 3.0607 | 3.0582 | 3.0159 | 2.902 | 3.0271 | 3.0109 | 3.0603 | 3.2084 | 2.9969 | 3.1038 | 2.8339 | 3.1033 | 3.0712 | 2.9801 | 2.6368 | 3.0596 | 3.0755 | 2.9378 | 3.0178 | 3.0341 | 2.7497 | 3.0133 | 3.0472 | 3.0697 | 3.0509 | 3.0965 | 3.0652 | 3.1311 | 3.0509 | 3.073 | 3.0764 | 3.5436 | 3.5208 | 3.4865 | 3.5356 | 3.4731 | 3.4997 | 3.4394 | 3.5484 | 3.5625 | 3.5202 | 3.4856 | 3.5291 | 3.5436 | 3.5324 | 3.4828 | 3.524 | 3.5168 | 3.5299 | 3.5583 | 3.5799 | 3.5269 | 3.536 | 3.4948 | 3.5067 | 3.4919 | 3.7105 | 3.4514 | 3.5185 | 3.5109 | 3.5771 | 3.5327 | 3.493 | 3.611 | 3.5614 | 3.1061 | 3.6568 | 3.6473 | 3.1875 | 3.7091 | 3.7091 |  |  | 3.3267 | 3.4794 | 3.5492 |  | 3.5499 | 3.4933 | 3.706 | 3.4772 | 3.6925 | 3.6981 | 3.7416 | 3.733 | 3.7446 | 3.7404 | 3.7262 | 3.7453 | 3.6747 | 3.7367 | 3.9516 | 3.88 | 3.8913 | 3.9191 | 3.4834 | 3.5425 | 3.6484 | 3.6048 | 3.5509 | 3.4752 | 3.6728 | 3.6145 | 3.5825 | 3.3994 | 3.3776 | 3.5278 | 3.3687 | 3.4852 | 3.3875 |  | 3.5952 | 3.4013 | 3.991 | 3.4347 | 3.4305 |  |  | 4.1918 | 3.8962 | 3.3646 | 3.4258 | 3.4461 | 3.4767
2025-06-04 | 4.1258 | 4.1653 | 4.015 | 4.1693 | 4.1449 | 4.1693 | 4.1768 | 3.9944 | 4.1611 | 4.1722 | 4.2652 | 4.2528 | 4.1798 | 4.3048 | 4.1798 | 4.1678 | 3.9974 | 4.103 | 4.1428 | 4.1414 | 4.1708 | 4.024 | 4.2406 | 4.1958 | 4.1853 | 4.1621 | 4.13 | 4.1092 | 4.1834 | 4.0929 | 4.1465 | 4.1265 | 4.0542 | 3.858 | 3.9745 | 4.0428 | 4.0618 | 3.9929 | 4.03 | 4.106 | 3.9865 | 3.9816 | 4.0431 | 4.0116 | 4.0356 | 4.0659 | 4.0536 | 4.0116 | 4.0054 | 4.0093 | 4.0532 | 4.0071 | 4.1308 | 4.0639 | 4.0335 | 4.0955 | 4.1062 | 4.1199 | 4.0606 | 4.1165 | 4.0738 | 4.1198 | 4.0041 | 4.1513 | 4.1193 | 4.0902 | 4.1442 | 4.0398 | 4.0978 | 4.0678 | 4.1049 | 4.0914 | 4.1757 | 4.1142 | 4.1685 | 4.0962 | 4.1645 | 4.118 | 4.0719 | 4.1414 | 4.0116 | 4.1487 | 4.1064 | 4.1596 | 4.1049 | 4.1131 | 4.1464 | 4.1135 | 4.0715 | 4.0281 | 4.087 | 4.1988 | 4.2 | 4.1543 | 4.1012 | 4.0393 | 4.039 | 4.1513 | 4.0745 | 4.1056 | 4.2191 | 4.0876 | 4.1584 | 4.0431 | 4.1521 | 4.1491 | 4.3669 | 4.0953 | 4.1577 | 4.0975 | 4.14 | 4.074 | 4.1418 | 4.1218 | 4.1225 | 4.1217 | 4.085 | 4.1511 | 4.1215 | 4.1434 | 4.1981 | 4.1422 | 4.1332 | 4.1382 | 4.1667 | 4.2001 | 4.0532 | 4.0779 | 4.1072 | 4.0453 | 3.9174 | 4.0695 | 4.0505 | 4.1013 | 4.3199 | 4.0105 | 4.1552 | 3.878 | 4.1787 | 4.1176 | 4.001 | 3.9886 | 4.0858 | 4.1248 | 3.9843 | 4.1884 | 4.0603 | 4.1213 | 4.055 | 4.0954 | 4.1331 | 4.1007 | 4.1774 | 4.1187 | 4.0431 | 4.0064 | 4.0393 | 3.8858 | 4.0322 | 4.0511 | 4.0444 | 4.0587 | 4.0003 | 3.9781 | 4.0172 | 4.0335 | 4.0701 | 4.0044 | 4.0814 | 4.0429 | 4.0273 | 4.0342 | 3.9785 | 4.0345 | 3.9906 | 4.089 | 4.0705 | 4.097 | 4.0064 | 4.0511 | 4.0192 | 4.0007 | 4.0276 | 4.0164 | 4.0063 | 4.0108 | 4.0167 | 4.0342 | 4.0433 | 3.9909 | 4.0739 | 4.103 | 4.0837 | 4.1299 | 4.1231 | 4.1455 | 4.1859 | 4.2235 |  |  | 3.8143 | 4.1035 | 4.0447 |  | 4.0342 | 4.012 | 4.127 | 3.6599 | 4.0787 | 4.1112 | 4.1401 | 4.1356 | 4.1461 | 4.2142 | 4.1378 | 4.1566 | 4.1305 | 4.2061 | 4.571 | 4.4308 | 4.4457 | 4.5009 | 4.0986 | 4.0917 | 4.0733 | 4.0503 | 4.0297 | 4.0422 | 4.1079 | 4.0605 | 4.022 | 3.9983 | 4.101 | 4.0519 | 4.0097 | 4.0075 | 4.0453 |  | 4.1197 | 4.0683 | 4.4498 | 4.0374 | 4.0097 |  |  | 4.6947 | 4.4675 | 3.9118 | 4.0571 | 4.0804 | 4.0991
2025-06-05 | 4.4114 | 4.6638 | 4.6629 | 4.6629 | 4.643 | 4.6704 | 4.6929 | 4.5993 | 4.6526 | 4.6706 | 4.7865 | 4.764 | 4.6816 | 4.8049 | 4.6891 | 4.6592 | 4.4607 | 4.6292 | 4.6742 | 4.6707 | 4.6966 | 4.5131 | 4.5635 | 4.7141 | 4.726 | 4.6845 | 4.6534 | 4.6309 | 4.7041 | 4.6009 | 4.1748 | 4.2913 | 4.7681 | 4.3312 | 4.5393 | 4.7574 | 4.6704 | 4.6442 | 4.7079 | 4.7865 | 4.6966 | 4.6592 | 4.7228 | 4.2622 | 4.7154 | 4.7603 | 4.7295 | 4.4831 | 4.6849 | 4.6058 | 4.7228 | 4.5431 | 4.814 | 4.7507 | 4.6949 | 4.7674 | 4.7873 | 4.794 | 4.7274 | 4.794 | 4.5431 | 4.5734 | 4.6966 | 4.0042 | 4.9127 | 4.8228 | 4.9542 | 4.5324 | 4.9101 | 4.8614 | 4.9363 | 4.9288 | 5.0112 | 4.9026 | 4.9938 | 4.8772 | 4.9705 | 4.7865 | 4.6929 | 4.8297 | 4.9401 | 4.9213 | 4.8839 | 5.1685 | 4.9176 | 4.8727 | 4.9738 | 4.9401 | 4.9251 | 4.8989 | 4.8863 | 4.6569 | 5.0487 | 5.0225 | 4.4112 | 4.3333 | 4.8165 | 4.9326 | 4.8614 | 4.8876 | 5.0187 | 4.8801 | 4.9625 | 4.8427 | 4.9072 | 4.9476 | 5.1203 | 4.8344 | 4.9363 | 4.7973 | 4.9162 | 4.4875 | 4.8506 | 4.8772 | 4.9064 | 4.4569 | 4.811 | 4.9205 | 4.8906 | 4.9288 | 4.9738 | 4.6608 | 4.5809 | 4.9139 | 4.9588 | 4.1715 | 4.1386 | 4.2097 | 4.6642 | 4.6042 | 4.4425 | 4.6327 | 4.6119 | 4.666 | 4.9021 | 4.507 | 4.6748 | 4.2692 | 4.6993 | 4.6742 | 4.5601 | 4.4978 | 4.6479 | 4.6914 | 4.5206 | 4.605 | 4.6367 | 4.7109 | 4.6223 | 4.6742 | 4.7087 | 4.6779 | 4.7607 | 4.7004 | 4.6142 | 4.573 | 4.6966 | 4.5805 | 4.9621 | 4.8106 | 4.9091 | 4.7879 | 4.8384 | 4.7508 | 4.8788 | 4.9091 | 4.7083 | 4.8081 | 4.9356 | 4.7345 | 4.8182 | 4.9382 | 4.7744 | 4.8291 | 4.7677 | 4.8939 | 4.947 | 4.822 | 4.8451 | 5.0189 | 4.8881 | 4.7542 | 4.9663 | 4.9636 | 4.9476 | 4.798 | 4.9636 | 4.9636 | 4.7964 | 4.9371 | 4.7955 | 4.8371 | 4.7273 | 4.8485 | 4.8106 | 4.8598 | 4.8455 | 4.9242 |  |  | 4.3939 | 4.7176 | 4.6711 |  | 4.6241 | 4.8614 | 4.9438 | 4.8052 | 4.9064 | 4.8951 | 4.9663 | 4.9625 | 4.9663 | 4.9963 | 4.9363 | 4.9401 | 4.8872 | 4.9771 | 5.3292 | 5.1993 | 4.7179 | 5.1724 | 4.6417 | 4.7206 | 4.8899 | 4.8506 | 4.8539 | 4.7087 | 4.6526 | 4.7606 | 4.8173 | 4.6342 | 4.7786 | 4.6789 | 4.6542 | 4.856 | 4.8889 |  | 4.8061 | 4.7266 | 4.8557 | 4.856 | 5.2797 |  |  | 5.605 | 4.6395 | 4.4948 | 4.6542 | 4.6517 | 4.7625
2025-06-06 | 4.7537 | 4.8608 | 4.6779 | 4.8652 | 4.8228 | 4.8539 | 4.8539 | 4.4607 | 4.8324 | 4.8575 | 4.9363 | 4.9139 | 4.839 | 4.9683 | 4.839 | 4.8202 | 4.5993 | 4.7828 | 4.7986 | 4.7986 | 4.8352 | 4.6517 | 4.7191 | 4.8539 | 4.8539 | 4.809 | 4.7813 | 4.7707 | 4.834 | 4.7541 | 4.228 | 4.4345 | 4.8428 | 4.7168 | 4.6105 | 4.8377 | 4.8464 | 4.7303 | 4.8015 | 4.8727 | 4.7865 | 4.7528 | 4.8165 | 4.3221 | 4.7978 | 4.8427 | 4.8055 | 4.5693 | 4.5987 | 4.5375 | 4.8315 | 4.6292 | 4.9005 | 4.8273 | 4.7848 | 4.8772 | 4.8706 | 4.8689 | 4.7973 | 4.8506 | 4.8577 | 4.8879 | 4.7491 | 4.046 | 4.8332 | 4.7952 | 4.8021 | 4.4183 | 4.8202 | 4.6816 | 4.7378 | 4.8277 | 4.8315 | 4.8315 | 4.7374 | 4.6176 | 4.6708 | 4.6816 | 4.5206 | 4.522 | 4.5281 | 4.7865 | 4.8277 | 4.5281 | 4.7453 | 4.8315 | 4.7378 | 4.8427 | 4.6629 | 4.6667 | 4.6778 | 4.4806 | 4.8352 | 4.8502 | 4.3546 | 4.3146 | 4.6816 | 4.8502 | 4.794 | 4.8127 | 4.9438 | 4.8052 | 4.9026 | 4.7978 | 4.8972 | 4.8727 | 5.1203 | 4.811 | 4.8689 | 4.7308 | 4.8643 | 4.7571 | 4.794 | 4.8273 | 4.8127 | 4.3596 | 4.7942 | 4.8672 | 4.8473 | 4.8652 | 4.9139 | 4.6608 | 4.5243 | 4.8502 | 4.8876 | 4.3213 | 4.3034 | 4.3745 | 4.8473 | 4.784 | 4.6188 | 4.8228 | 4.8021 | 4.858 | 5.1224 | 4.7378 | 4.9161 | 4.5 | 4.9474 | 4.9101 | 4.7502 | 4.6811 | 4.8839 | 4.9058 | 4.7528 | 4.9715 | 4.8352 | 4.8948 | 4.8124 | 4.8643 | 4.8954 | 4.8652 | 4.9571 | 4.8876 | 4.8015 | 4.7528 | 4.8689 | 4.7753 | 4.9167 | 4.6932 | 4.8586 | 4.7614 | 4.8114 | 4.7172 | 4.7542 | 4.9018 | 4.625 | 4.7576 | 4.8409 | 4.6909 | 4.7345 | 4.8727 | 4.7071 | 4.7345 | 4.7845 | 4.8409 | 4.928 | 4.7614 | 4.7172 | 4.9735 | 4.8182 | 4.7172 | 4.9158 | 4.9745 | 4.9021 | 4.7508 | 5.0109 | 4.9455 | 4.7673 | 4.9615 | 4.8674 | 4.7576 | 4.7008 | 4.7992 | 4.8068 | 4.8409 | 4.9182 | 4.9167 |  |  | 4.4716 | 4.7912 | 4.745 |  | 4.7676 | 4.8801 | 4.8727 | 4.764 | 4.8277 | 4.8502 | 4.8801 | 4.8689 | 4.8801 | 4.9476 | 4.8727 | 4.8801 | 4.8473 | 4.9438 | 5.3381 | 5.2127 | 5.1097 | 4.8903 | 4.7042 | 4.804 | 4.8144 | 4.8073 | 4.7675 | 4.8021 | 4.7101 | 4.809 | 4.774 | 4.6542 | 4.8446 | 4.7258 | 4.7708 | 4.8223 | 4.8121 |  | 4.7495 | 4.8694 | 4.7861 | 4.8148 | 4.7086 |  |  | 4.9028 | 4.7414 | 4.3575 | 4.5765 | 4.5937 | 4.7802
2025-06-07 | 5.0614 | 5.1858 | 4.9888 | 5.1985 | 5.1409 | 5.1723 | 5.1723 | 4.7753 | 5.1344 | 5.1596 | 5.2622 | 5.2285 | 5.1573 | 5.2952 | 5.1461 | 5.1311 | 4.8989 | 5.0974 | 5.0994 | 5.1167 | 5.1648 | 4.9551 | 5.0441 | 5.1802 | 5.1893 | 5.1305 | 5.1063 | 5.1003 | 5.1469 | 5.0803 | 4.3612 | 4.7407 | 5.3577 | 5.0157 | 4.8951 | 5.1288 | 5.1386 | 5.03 | 5.1049 | 5.1985 | 5.1049 | 5.0487 | 5.1348 | 4.6554 | 5.1461 | 5.176 | 5.1478 | 4.8914 | 4.8863 | 4.8288 | 5.1423 | 4.9288 | 5.2301 | 5.1536 | 5.0821 | 5.2002 | 5.1835 | 5.1798 | 5.1003 | 5.1569 | 5.1685 | 5.1924 | 5.1049 | 4.5977 | 5.0303 | 4.9611 | 4.9853 | 4.7329 | 4.97 | 4.9588 | 4.985 | 4.9625 | 5.0112 | 4.9738 | 4.9938 | 4.9105 | 4.9605 | 4.9738 | 4.8277 | 4.8297 | 4.9401 | 5.161 | 5.0637 | 4.8989 | 5.0375 | 5.0262 | 4.9738 | 5.0337 | 4.9888 | 4.9775 | 4.9798 | 5.0579 | 5.0487 | 5.0225 | 4.6941 | 4.6442 | 5.0674 | 5.1723 | 5.1124 | 5.1348 | 5.2697 | 5.1273 | 5.2135 | 5.0936 | 5.1968 | 5.176 | 5.3566 | 5.1221 | 5.1985 | 5.0004 | 5.1927 | 4.9957 | 5.0137 | 5.1402 | 5.161 | 4.6816 | 5.0987 | 5.1569 | 5.1236 | 5.1835 | 5.2509 | 5.0004 | 4.8539 | 5.1723 | 5.206 | 4.6109 | 4.573 | 4.6442 | 5.1569 | 5.0836 | 4.8989 | 5.1132 | 5.1063 | 5.1767 | 5.4126 | 5.049 | 5.2343 | 4.7867 | 5.2099 | 5.1461 | 5.0406 | 4.9196 | 5.1873 | 5.1893 | 5.0225 | 5.0717 | 5.0936 | 5.1726 | 5.1029 | 5.1478 | 5.1893 | 5.1536 | 5.2335 | 5.1798 | 5.1049 | 5.0562 | 5.206 | 5.0824 | 5.2197 | 5.0076 | 5.3131 | 5.1629 | 5.3468 | 5.2626 | 5.0842 | 5.4473 | 5.1629 | 5.2626 | 5.5985 | 5.1273 | 5.12 | 5.3745 | 5.0842 | 5.0836 | 5.0774 | 5.2955 | 5.3333 | 5.1629 | 5.2626 | 5.3409 | 5.1678 | 5.0438 | 5.2626 | 5.32 | 5.2517 | 5.0606 | 5.4473 | 5.3745 | 5.4473 | 5.2797 | 5.1515 | 5.1136 | 5.053 | 5.1818 | 5.1705 | 5.1932 | 5.2682 | 5.2992 |  |  | 4.7747 | 5.243 | 5.0443 |  | 5.082 | 5.1873 | 5.1723 | 5.0262 | 5.1461 | 5.1948 | 5.206 | 5.1985 | 5.2097 | 5.2659 | 5.2172 | 5.2434 | 5.1935 | 5.2967 | 5.6964 | 5.5755 | 5.2142 | 6.3323 | 5.1371 | 5.5963 | 5.1056 | 5.0137 | 4.9957 | 5.0303 | 5.0013 | 5.1167 | 5.0603 | 5.0037 | 5.0505 | 5.0289 | 5.1243 | 5.2076 | 5.2444 |  | 5.0524 | 5.1794 | 5.1741 | 4.9832 | 5.0389 |  |  | 5.0073 | 5.1136 | 4.68 | 4.899 | 5.0539 | 5.1068
2025-06-08 | 4.903 | 5.0164 | 4.9004 | 5.0266 | 4.9822 | 5.0116 | 5.0142 | 5.0262 | 4.9776 | 5.0049 | 4.9022 | 5.0824 | 5.0011 | 5.1363 | 5.0049 | 4.9813 | 4.8629 | 4.9577 | 4.9753 | 4.977 | 5.0225 | 4.9105 | 4.8837 | 5.0234 | 5.0475 | 4.9867 | 4.9639 | 4.9491 | 5.0134 | 4.9315 | 4.6782 | 4.799 | 4.9969 | 4.8848 | 4.8738 | 4.9957 | 5.0105 | 4.891 | 4.9959 | 5.0528 | 4.9581 | 4.9146 | 5.0097 | 4.9655 | 5.0397 | 5.0513 | 5.0337 | 4.9798 | 4.9611 | 4.8784 | 5.0337 | 5.036 | 5.1246 | 5.05 | 4.9411 | 5.0387 | 5.0314 | 5.0375 | 4.967 | 5.0267 | 5.0281 | 5.0646 | 4.8075 | 5.4073 | 4.986 | 4.9549 | 5.0258 | 4.8823 | 4.9524 | 4.9858 | 5.0146 | 4.9925 | 5.1067 | 4.9431 | 5.0687 | 4.9608 | 5.0504 | 5.0079 | 4.9479 | 4.9258 | 5.0228 | 5.0434 | 4.9798 | 5.0494 | 5.0307 | 5.0419 | 5.0554 | 4.7079 | 4.9712 | 4.9124 | 4.942 | 4.883 | 5.1221 | 5.1258 | 4.9721 | 4.7236 | 4.9221 | 5.024 | 4.961 | 4.9828 | 5.1116 | 4.9753 | 5.0663 | 4.9494 | 5.0577 | 5.0288 | 5.2528 | 4.9528 | 5.0416 | 4.8786 | 5.0137 | 4.8532 | 4.9019 | 4.9924 | 5.0116 | 4.7562 | 4.9679 | 5.0151 | 4.9861 | 5.0333 | 5.0876 | 4.9655 | 4.9888 | 5.0139 | 5.0464 | 4.9988 | 4.4745 | 4.5521 | 5.0327 | 4.9591 | 4.8436 | 4.9825 | 4.9673 | 5.0374 | 5.3007 | 4.935 | 5.0986 | 4.6962 | 5.0934 | 5.0345 | 4.9131 | 4.8436 | 5.0603 | 5.0593 | 4.912 | 4.9483 | 4.9727 | 5.0435 | 4.9639 | 5.0071 | 5.0562 | 5.0255 | 5.0986 | 5.039 | 4.9633 | 4.9172 | 4.9607 | 5.0015 | 4.9663 | 4.9826 | 4.998 | 4.9716 | 5.0071 | 4.9411 | 4.9882 | 5.4585 | 4.9678 | 4.9731 | 5.0057 | 4.8927 | 4.9069 | 5.0524 | 4.8599 | 4.8782 | 5.0114 | 5.0057 | 4.9977 | 4.9845 | 4.9879 | 5.017 | 4.9818 | 5.0114 | 5.0384 | 5.1109 | 5.0388 | 5.0384 | 4.9073 | 4.8698 | 4.8818 | 4.8895 | 5.008 | 4.9958 | 4.6069 | 4.9674 | 5.014 | 4.6417 | 5.1341 | 5.1379 |  |  | 4.636 | 4.8826 | 4.9095 |  | 5.0154 | 4.8558 | 5.0232 | 4.9228 | 4.9985 | 5.0127 | 5.0528 | 5.0434 | 5.0509 | 5.1135 | 5.0899 | 5.1071 | 5.0477 | 5.1635 | 5.5087 | 5.2548 | 5.256 | 5.4307 | 4.8538 | 4.8849 | 4.9693 | 4.9442 | 4.8854 | 4.8785 | 5.0377 | 4.9594 | 4.9208 | 5.0307 | 5.0443 | 5.0905 | 5.1336 | 5.1455 | 5.0723 |  | 5.0931 | 4.8798 | 4.9264 | 4.85 | 4.9161 |  |  | 5.0508 | 5.0721 | 4.5418 | 4.8217 | 5.0394 | 4.9859
2025-06-09 | 5.0506 | 5.0932 | 4.961 | 5.1652 | 5.107 | 5.1547 | 5.0805 | 5.112 | 5.0725 | 5.1114 | 5.1809 | 5.1558 | 5.0787 | 5.0296 | 5.0723 | 5.0532 | 5.0419 | 5.0345 | 5.0503 | 5.0596 | 5.0948 | 5.1049 | 5.0558 | 5.0996 | 5.1305 | 5.0645 | 5.042 | 5.0304 | 5.0986 | 5.0077 | 5.0307 | 4.9988 | 5.0456 | 4.9341 | 4.8142 | 5.0572 | 5.0734 | 4.9528 | 5.027 | 5.1079 | 5.0772 | 4.9652 | 5.0603 | 5.015 | 5.0929 | 5.1019 | 5.0921 | 5.0356 | 5.0689 | 4.9916 | 5.1217 | 5.1139 | 5.0976 | 5.1203 | 5.0434 | 5.064 | 5.103 | 5.1071 | 5.049 | 5.0963 | 5.1007 | 5.1352 | 5.1213 | 5.4667 | 5.1105 | 5.0787 | 5.1488 | 4.9715 | 5.009 | 5.0644 | 5.094 | 5.073 | 5.0974 | 4.9873 | 5.1362 | 5.0337 | 5.1239 | 5.0652 | 5.0154 | 4.9857 | 5.085 | 5.1079 | 5.0431 | 5.1075 | 5.0981 | 5.1146 | 5.1206 | 4.8764 | 5.0397 | 4.9873 | 5.0298 | 4.9476 | 5.0899 | 5.1476 | 5.0883 | 4.7846 | 4.9865 | 5.0959 | 5.0232 | 5.0577 | 5.0787 | 5.0476 | 5.0749 | 5.0221 | 5.1506 | 5.1157 | 4.9971 | 5.0582 | 5.1191 | 4.9382 | 5.1035 | 4.9476 | 4.9358 | 5.058 | 5.0801 | 4.7809 | 5.0194 | 5.0983 | 5.0753 | 5.1232 | 5.1764 | 4.9581 | 4.9768 | 5.0978 | 5.133 | 5.1612 | 4.9348 | 5.0075 | 5.092 | 5.0294 | 4.8494 | 5.052 | 5.0368 | 4.9969 | 5.0839 | 4.985 | 5.1874 | 4.8472 | 5.1092 | 5.0599 | 4.9867 | 4.9182 | 5.1438 | 5.2003 | 5.0655 | 5.0901 | 5.1075 | 5.1367 | 5.0506 | 5.0869 | 5.1426 | 5.1041 | 5.0836 | 5.121 | 5.0397 | 4.9854 | 5.0363 | 5.0109 | 5.0511 | 5.0462 | 5.1364 | 5.0436 | 5.1566 | 5.0879 | 5.1047 | 5.0335 | 5.0307 | 5.1822 | 5.0549 | 5.016 | 5.06 | 5.0425 | 5.1239 | 5.0669 | 5.0539 | 5.0777 | 5.0129 | 5.0515 | 5.0572 | 5.0318 | 4.9979 | 5.0404 | 5.1374 | 5.0524 | 5.0273 | 5.0471 | 5.0524 | 5.0767 | 5.0353 | 5.0168 | 5.1015 | 5.0833 | 4.9739 | 5.0644 | 5.1011 | 5.139 | 5.2141 | 5.2193 |  |  | 4.7323 | 4.9462 | 4.9523 |  | 5.0824 | 4.9637 | 5.1187 | 4.9536 | 5.0835 | 5.0876 | 5.1337 | 5.1243 | 5.1255 | 5.1663 | 5.1659 | 5.1948 | 5.1392 | 5.2248 | 5.3789 | 5.365 | 5.3422 | 5.2871 | 4.9856 | 5.0088 | 5.0542 | 5.0221 | 4.9704 | 4.9694 | 5.1254 | 5.032 | 5.0031 | 4.9971 | 5.0987 | 5.0224 | 4.9662 | 5.0333 | 5.0707 |  | 5.0538 | 4.9955 | 4.9851 | 4.9495 | 4.9907 |  |  | 5.2247 | 5.2202 | 4.6492 | 4.9153 | 4.9295 | 5.0627
2025-06-10 | 5.3815 | 5.5032 | 5.5213 | 5.5052 | 5.4717 | 5.5165 | 5.4895 | 5.5109 | 5.4623 | 5.4943 | 5.33 | 5.4086 | 5.4921 | 5.4427 | 5.4865 | 5.4629 | 5.4498 | 5.4266 | 5.3756 | 5.3936 | 5.4779 | 5.4963 | 5.442 | 5.2864 | 5.4562 | 5.3895 | 5.3625 | 5.351 | 5.4136 | 5.327 | 5.3303 | 5.3147 | 5.3711 | 5.2716 | 5.3446 | 5.4386 | 5.4184 | 5.2794 | 5.3764 | 5.4506 | 5.3397 | 5.485 | 5.4663 | 5.3371 | 5.4461 | 5.4554 | 5.4372 | 5.3577 | 5.3875 | 5.3091 | 5.4491 | 5.4378 | 5.5384 | 5.4489 | 5.414 | 5.4412 | 5.2767 | 5.3599 | 5.4375 | 5.4202 | 5.4303 | 5.4637 | 5.4434 | 5.4382 | 5.4493 | 5.4112 | 5.4043 | 5.2733 | 5.3127 | 5.4007 | 5.43 | 5.4067 | 5.4502 | 5.4536 | 5.4272 | 5.3333 | 5.4372 | 5.3491 | 5.336 | 5.376 | 5.4142 | 5.4352 | 5.37 | 5.4382 | 5.4262 | 5.4438 | 5.4566 | 5.4157 | 5.3749 | 5.321 | 5.3138 | 5.3729 | 5.4045 | 5.364 | 5.4309 | 5.3165 | 5.3011 | 5.4326 | 5.3307 | 5.3974 | 5.2476 | 5.3865 | 5.4835 | 5.3685 | 5.3137 | 5.4633 | 5.3973 | 5.4038 | 5.4869 | 5.297 | 5.4648 | 5.2933 | 5.3237 | 5.4052 | 5.4476 | 5.5491 | 5.3071 | 5.4379 | 5.3859 | 5.4401 | 5.4652 | 5.2837 | 5.297 | 5.4996 | 5.4978 | 5.4958 | 5.3097 | 5.4187 | 5.5048 | 5.4405 | 5.452 | 5.478 | 5.3625 | 5.3569 | 5.4479 | 5.4017 | 5.4444 | 5.3888 | 5.4332 | 5.3936 | 5.4047 | 5.2933 | 5.3895 | 5.3763 | 5.4423 | 5.4468 | 5.3858 | 5.4705 | 5.3867 | 5.4264 | 5.4759 | 5.4427 | 5.3806 | 5.373 | 5.4464 | 5.3363 | 5.339 | 5.3577 | 5.3072 | 5.2962 | 5.4582 | 5.3451 | 5.4515 | 5.3906 | 5.3785 | 5.3167 | 5.3602 | 5.3741 | 5.3318 | 5.3084 | 5.3178 | 5.2938 | 5.4249 | 5.2618 | 5.3576 | 5.3375 | 5.3617 | 5.3223 | 5.3754 | 5.3508 | 5.3643 | 5.4007 | 5.3684 | 5.3058 | 5.3395 | 5.5593 | 5.2913 | 5.2709 | 5.2996 | 5.349 | 5.4398 | 5.4061 | 5.2773 | 5.2992 | 5.4439 | 5.4837 | 5.3468 | 5.3451 |  |  | 5.0606 | 5.3118 | 5.2997 |  | 5.4053 | 5.285 | 5.4472 | 5.3712 | 5.4243 | 5.4378 | 5.4745 | 5.3524 | 5.4652 | 5.4333 | 5.2779 | 5.4101 | 5.4412 | 5.4039 | 5.6162 | 5.6162 | 5.6818 | 5.3987 | 5.2963 | 5.3053 | 5.4875 | 5.4166 | 5.3853 | 5.2899 | 5.3792 | 5.4088 | 5.4049 | 5.3303 | 5.3294 | 5.2854 | 5.3539 | 5.3651 | 5.3782 |  | 5.319 | 5.2773 | 5.3841 | 5.3651 | 5.3139 |  |  | 5.4867 | 5.4976 | 3.9575 | 5.3477 | 5.2973 | 5.3889
2025-06-11 | 5.0275 | 5.1457 | 4.9524 | 5.1461 | 5.1118 | 5.0903 | 5.133 | 5.0978 | 5.1063 | 5.1376 | 5.1352 | 5.0603 | 5.1386 | 5.2629 | 5.1423 | 5.1225 | 5.1169 | 5.1067 | 5.1319 | 5.1419 | 5.167 | 5.1708 | 5.0133 | 5.0973 | 5.0721 | 5.134 | 5.1122 | 5.0993 | 5.1352 | 5.1143 | 5.1456 | 5.0743 | 5.0303 | 5.0175 | 4.9996 | 5.0723 | 5.0588 | 4.9667 | 5.0213 | 5.0854 | 4.991 | 4.936 | 5.0262 | 4.9816 | 5.0697 | 5.0884 | 5.0742 | 5.0105 | 5.042 | 4.9625 | 5.0925 | 5.0846 | 5.1789 | 5.0873 | 5.0458 | 5.0573 | 5.1536 | 5.0978 | 5.1103 | 5.064 | 5.0745 | 5.1114 | 5.0861 | 5.1122 | 5.106 | 5.078 | 5.144 | 4.9984 | 5.0277 | 5.0393 | 5.0719 | 5.0513 | 5.1573 | 4.9816 | 5.064 | 5.0623 | 5.0707 | 5.0663 | 4.9888 | 4.958 | 5.0685 | 5.0876 | 5.0191 | 5.0775 | 5.0659 | 5.0839 | 5.1 | 5.0112 | 5.0165 | 4.9727 | 5.0387 | 4.948 | 5.0981 | 5.1266 | 5.1052 | 4.9835 | 4.9427 | 5.091 | 5.0202 | 5.1262 | 5.1007 | 5.0633 | 5.1386 | 4.9693 | 4.9452 | 5.1509 | 4.9808 | 5.0555 | 5.0607 | 4.9844 | 5.0168 | 4.986 | 4.9475 | 5.1386 | 5.0382 | 5.1929 | 5.0759 | 5.1655 | 4.9971 | 5.0757 | 5.0794 | 4.9971 | 4.9814 | 5.0981 | 5.0813 | 5.1306 | 4.9476 | 5.0663 | 5.1522 | 5.0836 | 5.0925 | 5.1084 | 5.1011 | 5.1714 | 5.0909 | 5.0486 | 5.1283 | 5.101 | 5.1933 | 5.164 | 5.0482 | 4.9732 | 5.0843 | 5.0444 | 5.0513 | 5.0807 | 5.0963 | 5.055 | 5.1156 | 5.0244 | 5.1001 | 5.0607 | 5.1509 | 5.0678 | 5.0547 | 5.0607 | 5.0768 | 5.0172 | 4.9629 | 5.0019 | 4.9906 | 4.9678 | 4.9343 | 4.9869 | 4.9414 | 4.9716 | 5.0057 | 4.9545 | 4.9716 | 5.044 | 4.9789 | 4.9862 | 4.9478 | 4.9705 | 4.9545 | 4.9678 | 4.983 | 4.9602 | 4.9535 | 4.9678 | 5.1091 | 5.0007 | 5.0061 | 4.9785 | 5.1451 | 4.9882 | 4.9862 | 5.0953 | 5.0116 | 5.1465 | 5.078 | 5.0436 | 4.9742 | 5.0485 | 5.0841 | 5.1174 | 5.005 | 5.0121 |  |  | 4.7238 | 4.9913 | 4.9586 |  | 5.069 | 5.0232 | 5.0933 | 5.0022 | 5.0655 | 5.0787 | 5.115 | 5.1045 | 5.1056 | 5.164 | 5.006 | 5.1948 | 5.1219 | 5.1309 | 5.2893 | 5.0654 | 5.0742 | 5.1611 | 5.0515 | 5.0546 | 5.1258 | 5.1036 | 5.032 | 4.9407 | 5.1613 | 5.0527 | 4.9545 | 4.9525 | 4.9542 | 4.9693 | 5 | 5.0247 | 5.0149 |  | 5.5338 | 4.9955 | 5.1851 | 4.9495 | 4.9635 |  |  | 5.3333 | 5.3491 | 4.8077 | 4.9425 | 5.1169 | 5.06
2025-06-12 | 4.5673 | 4.6769 | 4.6187 | 4.6809 | 4.6482 | 4.6895 | 4.682 | 4.6858 | 4.645 | 4.6698 | 4.6142 | 4.6105 | 4.6693 | 4.6333 | 4.6689 | 4.6551 | 4.6453 | 4.6315 | 4.6742 | 4.6669 | 4.6865 | 4.5393 | 4.6707 | 4.6342 | 4.6603 | 4.6773 | 4.6527 | 4.6608 | 4.7008 | 4.6365 | 4.6246 | 4.6489 | 4.6997 | 4.53 | 4.6861 | 4.5393 | 4.7139 | 4.5779 | 4.5697 | 4.6416 | 4.6311 | 4.5479 | 4.5783 | 4.5375 | 4.6101 | 4.627 | 4.6188 | 4.5693 | 4.5853 | 4.5206 | 4.63 | 4.6277 | 4.7208 | 4.6246 | 4.613 | 4.6885 | 4.7001 | 4.7049 | 4.6445 | 4.6309 | 4.7186 | 4.6035 | 4.6303 | 4.6228 | 4.6327 | 4.5978 | 4.6659 | 4.5438 | 4.5816 | 4.5768 | 4.6097 | 4.5888 | 4.6854 | 4.6037 | 4.6209 | 4.6618 | 4.7407 | 4.7022 | 4.6453 | 4.5787 | 4.6592 | 4.6255 | 4.6772 | 4.6554 | 4.5929 | 4.6079 | 4.7172 | 4.6816 | 4.5708 | 4.536 | 4.5893 | 4.6852 | 4.6217 | 4.603 | 4.6345 | 4.6723 | 4.6086 | 4.618 | 4.6689 | 4.6648 | 4.6217 | 4.6678 | 4.6592 | 4.5404 | 4.5626 | 4.7064 | 4.6176 | 4.6173 | 4.7019 | 4.5979 | 4.6634 | 4.5746 | 4.5586 | 4.6548 | 4.6708 | 4.688 | 4.6109 | 4.6608 | 4.6469 | 4.6446 | 4.7296 | 4.5893 | 4.5986 | 4.6689 | 4.7079 | 4.6908 | 4.5805 | 4.6034 | 4.6901 | 4.6176 | 4.6213 | 4.6392 | 4.6282 | 4.6962 | 4.6643 | 4.6035 | 4.6573 | 4.6573 | 4.6778 | 4.6768 | 4.5632 | 4.5739 | 4.6554 | 4.6707 | 4.5562 | 4.6085 | 4.6303 | 4.7305 | 4.6704 | 4.7291 | 4.6638 | 4.6993 | 4.7334 | 4.6929 | 4.6315 | 4.6071 | 4.6273 | 4.6438 | 4.661 | 4.6799 | 4.5673 | 4.6648 | 4.564 | 4.5943 | 4.5761 | 4.6382 | 4.7178 | 4.6279 | 4.6947 | 4.6524 | 4.6236 | 4.6164 | 4.601 | 4.6596 | 4.6313 | 4.6648 | 4.7311 | 4.6758 | 4.6108 | 4.6837 | 4.5916 | 4.5842 | 4.6108 | 4.6524 | 4.6196 | 4.6178 | 4.6167 | 4.6135 | 4.6855 | 4.6364 | 4.6966 | 4.6477 | 4.5909 | 4.7136 | 4.6917 | 4.7348 | 4.6955 | 4.6326 |  |  | 4.256 | 4.5674 | 4.5536 |  | 4.5892 | 4.5356 | 4.6787 | 4.5393 | 4.6685 | 4.6034 | 4.5985 | 4.6378 | 4.7019 | 4.6918 | 4.5794 | 4.6903 | 4.6256 | 4.7178 | 4.7246 | 4.9069 | 4.7074 | 4.7335 | 4.5455 | 4.5413 | 4.6375 | 4.6202 | 4.5487 | 4.5739 | 4.6785 | 4.5677 | 4.6009 | 4.5643 | 4.7086 | 4.5491 | 4.6659 | 4.5342 | 4.5293 |  | 4.9674 | 4.6743 | 4.7363 | 4.5342 | 4.7863 |  |  | 4.9154 | 4.9216 | 4.3764 | 4.526 | 4.5605 | 4.6388
2025-06-13 | 4.0736 | 4.1777 | 4.1187 | 4.1715 | 4.15 | 4.1843 | 4.1775 | 4.1809 | 4.1417 | 4.1507 | 4.2588 | 4.2221 | 4.1596 | 4.2742 | 4.167 | 4.1569 | 4.1491 | 4.1404 | 4.1736 | 4.1711 | 4.1933 | 4.2034 | 4.2562 | 4.233 | 4.2437 | 4.1929 | 4.1801 | 4.1884 | 4.2254 | 4.1608 | 4.1798 | 4.1984 | 4.204 | 4.0927 | 4.1929 | 4.0853 | 4.2206 | 4.1184 | 4.206 | 4.2689 | 4.1813 | 4.136 | 4.2266 | 4.1843 | 4.2356 | 4.2337 | 4.2258 | 4.1918 | 4.1187 | 4.0964 | 4.1588 | 4.176 | 4.286 | 4.2161 | 4.1158 | 4.1964 | 4.1958 | 4.2026 | 4.1478 | 4.2044 | 4.2442 | 4.2666 | 4.1434 | 4.2257 | 4.2634 | 4.1815 | 4.2278 | 4.0999 | 4.0921 | 4.2112 | 4.2382 | 4.2176 | 4.3 | 4.0865 | 4.2187 | 4.1588 | 4.2034 | 4.1723 | 4.1727 | 4.1006 | 4.2199 | 4.2273 | 4.1918 | 4.2513 | 4.2228 | 4.2142 | 4.2472 | 4.2101 | 4.194 | 4.1667 | 4.1294 | 4.0812 | 4.2861 | 4.2787 | 4.2573 | 4.1921 | 4.1536 | 4.2356 | 4.1974 | 4.2011 | 4.1985 | 4.2022 | 4.2655 | 4.121 | 4.0859 | 4.2318 | 4.1348 | 4.0826 | 4.2408 | 4.1378 | 4.1919 | 4.0833 | 4.0716 | 4.1491 | 4.2075 | 4.2427 | 4.1198 | 4.1272 | 4.1172 | 4.2015 | 4.2517 | 4.0836 | 4.0949 | 4.2195 | 4.2453 | 4.0746 | 4.0798 | 4.1071 | 4.2014 | 4.1315 | 4.1241 | 4.1352 | 4.1286 | 4.1986 | 4.1538 | 4.1245 | 4.1993 | 4.2161 | 4.2093 | 4.1539 | 4.075 | 4.0726 | 4.1876 | 4.1863 | 4.1423 | 4.1034 | 4.1315 | 4.2264 | 4.1836 | 4.2258 | 4.2213 | 4.2022 | 4.2367 | 4.209 | 4.1566 | 4.1236 | 4.1779 | 4.1966 | 4.2197 | 4.2087 | 4.2286 | 4.1318 | 4.1717 | 4.2273 | 4.1886 | 4.2393 | 4.1977 | 4.2542 | 4.2348 | 4.0782 | 4.1367 | 4.0767 | 4.1485 | 4.176 | 4.1178 | 4.2314 | 4.2273 | 4.1795 | 4.1785 | 4.2083 | 4.128 | 4.1623 | 4.1865 | 4.1127 | 4.1993 | 4.2121 | 4.1964 | 4.2145 | 4.0836 | 4.1073 | 4.1705 | 4.186 | 4.0833 | 4.2235 | 4.2386 | 4.2083 | 4.1364 | 4.1288 |  |  | 3.871 | 4.1082 | 4.0987 |  | 4.149 | 4.0865 | 4.2599 | 4.0865 | 4.1985 | 4.1918 | 4.206 | 4.206 | 4.1884 | 4.2217 | 4.2135 | 4.176 | 4.2127 | 4.2314 | 4.2723 | 4.4156 | 4.2894 | 4.1818 | 4.1419 | 4.0913 | 4.2075 | 4.1665 | 4.0868 | 4.1901 | 4.2754 | 4.3405 | 4.1039 | 4.1052 | 4.1026 | 4.1706 | 4.0793 | 4.1119 | 4.1111 |  | 4.1311 | 4.0968 | 4.1891 | 4.1571 | 4.1033 |  |  | 4.4514 | 4.4005 | 3.9451 | 4.1006 | 4.1522 | 4.1775
2025-06-14 | 4.5843 | 4.6811 | 4.5056 | 4.6929 | 4.6258 | 4.6667 | 4.633 | 4.6442 | 4.6022 | 4.6418 | 4.7191 | 4.7041 | 4.6292 | 4.7436 | 4.633 | 4.618 | 4.588 | 4.5843 | 4.5912 | 4.6016 | 4.6442 | 4.6592 | 4.7053 | 4.6575 | 4.6638 | 4.6188 | 4.5912 | 4.5843 | 4.6575 | 4.5743 | 4.5976 | 4.6109 | 4.6108 | 4.5225 | 4.5843 | 4.4898 | 4.618 | 4.5019 | 4.573 | 4.6367 | 4.5581 | 4.5243 | 4.5843 | 4.5281 | 4.5843 | 4.5993 | 4.5739 | 4.5356 | 4.6022 | 4.5231 | 4.6255 | 4.6142 | 4.6608 | 4.5843 | 4.5774 | 4.6975 | 4.6375 | 4.6479 | 4.5843 | 4.6509 | 4.6255 | 4.6671 | 4.5693 | 4.5434 | 4.5877 | 4.5532 | 4.6188 | 4.4944 | 4.5506 | 4.5281 | 4.5618 | 4.5356 | 4.6404 | 4.5655 | 4.6375 | 4.5543 | 4.6275 | 4.5843 | 4.5356 | 4.5393 | 4.5993 | 4.6142 | 4.5543 | 4.6217 | 4.5581 | 4.5693 | 4.5993 | 4.5543 | 4.5056 | 4.4719 | 4.5411 | 4.6016 | 4.6517 | 4.6142 | 4.561 | 4.5318 | 4.5094 | 4.603 | 4.5506 | 4.5618 | 4.6891 | 4.5431 | 4.6367 | 4.5243 | 4.5876 | 4.6105 | 4.6975 | 4.5701 | 4.6217 | 4.5643 | 4.6016 | 4.5774 | 4.6109 | 4.6409 | 4.5918 | 4.6929 | 4.6102 | 4.6509 | 4.5876 | 4.6667 | 4.7266 | 4.501 | 4.4911 | 4.6142 | 4.6367 | 4.4977 | 4.4944 | 4.5468 | 4.6142 | 4.551 | 4.5497 | 4.567 | 4.5566 | 4.621 | 4.6189 | 4.5385 | 4.6888 | 4.6678 | 4.6346 | 4.6404 | 4.5186 | 4.5324 | 4.6442 | 4.6569 | 4.5056 | 4.5601 | 4.5655 | 4.6251 | 4.567 | 4.6016 | 4.6327 | 4.6105 | 4.6908 | 4.6292 | 4.5393 | 4.5056 | 4.4906 | 4.5356 | 4.6326 | 4.5417 | 4.6128 | 4.4735 | 4.596 | 4.5657 | 4.6633 | 4.5818 | 4.6023 | 4.6566 | 4.6326 | 4.5527 | 4.6473 | 4.5491 | 4.6667 | 4.6873 | 4.4815 | 4.5758 | 4.625 | 4.5379 | 4.7508 | 4.6818 | 4.6014 | 4.6734 | 4.5387 | 4.7673 | 4.6294 | 4.6296 | 4.6364 | 4.64 | 4.5455 | 4.6259 | 4.6098 | 4.6098 | 4.5038 | 4.6477 | 4.6061 | 4.1705 | 4.6727 | 4.7273 |  |  | 4.2541 | 4.6283 | 4.49 |  | 4.5557 | 4.4981 | 4.6105 | 4.5169 | 4.5843 | 4.5955 | 4.6479 | 4.618 | 4.6404 | 4.7228 | 4.6217 | 4.6704 | 4.6042 | 4.6975 | 4.7783 | 4.7962 | 4.6332 | 4.7436 | 4.5262 | 4.583 | 4.6526 | 4.5776 | 4.5601 | 4.4667 | 4.5339 | 4.6016 | 4.571 | 4.4977 | 4.5416 | 4.531 | 4.6581 | 4.5754 | 4.5374 |  | 4.6844 | 4.5315 | 4.6866 | 4.4856 | 4.5765 |  |  | 4.8109 | 4.7884 | 4.3061 | 4.4872 | 4.5066 | 4.5961
2025-06-15 | 3.3566 | 3.4264 | 3.3745 | 3.4109 | 3.4164 | 3.4318 | 3.4393 | 3.4472 | 3.4204 | 3.4298 | 3.5026 | 3.4835 | 3.4184 | 3.5587 | 3.4135 | 3.4045 | 3.3873 | 3.4195 | 3.3846 | 3.3915 | 3.361 | 3.3925 | 3.4517 | 3.3818 | 3.368 | 3.3915 | 3.357 | 3.3991 | 3.3768 | 3.4024 | 3.4024 | 3.4091 | 3.3416 | 3.291 | 3.3745 | 3.3489 | 3.3933 | 3.3371 | 3.3745 | 3.3637 | 3.3453 | 3.3689 | 3.3745 | 3.3745 | 3.3933 | 3.3292 | 3.4261 | 3.3745 | 3.3834 | 3.3769 | 3.3745 | 3.3865 | 3.3658 | 3.3858 | 3.357 | 3.3658 | 3.3761 | 3.3858 | 3.3328 | 3.3691 | 3.3895 | 3.376 | 3.3861 | 3.348 | 3.4627 | 3.4358 | 3.4821 | 3.3953 | 3.4393 | 3.4172 | 3.4506 | 3.4281 | 3.5165 | 3.4431 | 3.493 | 3.4304 | 3.487 | 3.4573 | 3.418 | 3.461 | 3.4685 | 3.4787 | 3.4378 | 3.4899 | 3.4356 | 3.4513 | 3.4775 | 3.4423 | 3.4105 | 3.3809 | 3.4287 | 3.4918 | 3.518 | 3.491 | 3.4477 | 3.4184 | 3.3985 | 3.5401 | 3.4685 | 3.5101 | 3.5243 | 3.4805 | 3.5247 | 3.4124 | 3.4327 | 3.4416 | 3.3991 | 3.4988 | 3.4494 | 3.4327 | 3.4883 | 3.4645 | 3.5316 | 3.5153 | 3.5341 | 3.561 | 3.4788 | 3.5729 | 3.5462 | 3.5551 | 3.5944 | 3.4127 | 3.3691 | 3.5532 | 3.5783 | 3.9654 | 3.3371 | 3.3461 | 3.3738 | 3.3505 | 3.3518 | 3.3646 | 3.3684 | 3.4259 | 3.3951 | 3.3601 | 3.4769 | 3.4497 | 3.4341 | 3.3757 | 3.3393 | 3.357 | 3.3393 | 3.3895 | 3.3371 | 3.3915 | 3.3371 | 3.363 | 3.3269 | 3.3545 | 3.3649 | 3.3562 | 3.4207 | 3.3554 | 3.3633 | 3.3371 | 3.3446 | 3.3296 | 3.3386 | 3.3485 | 3.337 | 3.4129 | 3.3704 | 3.3535 | 3.3475 | 3.4218 | 3.4129 | 3.3663 | 3.4511 | 3.3891 | 3.3665 | 3.3491 | 3.3976 | 3.3855 | 3.3401 | 3.4508 | 3.3527 | 3.4129 | 3.4589 | 3.4023 | 3.3892 | 3.4192 | 3.4411 | 3.4971 | 3.3395 | 3.3387 | 3.3807 | 3.3625 | 3.4535 | 3.3738 | 3.4943 | 3.5239 | 3.7216 | 3.5136 | 3.4905 | 3.5223 | 3.5891 | 3.5936 |  |  | 3.1935 | 3.4163 | 3.4287 |  | 3.501 | 3.3738 | 3.4993 | 3.4251 | 3.4712 | 3.4884 | 3.5135 | 3.5004 | 3.5105 | 3.5787 | 3.4918 | 3.53 | 3.475 | 3.5449 | 3.5871 | 3.5737 | 3.4274 | 3.4796 | 3.366 | 3.4374 | 3.5419 | 3.5459 | 3.5461 | 3.4942 | 3.5416 | 3.5298 | 3.5159 | 3.3688 | 3.4693 | 3.4102 | 3.3877 | 3.3771 | 3.3709 |  | 3.5154 | 3.4866 | 3.4726 | 3.3707 | 3.5004 |  |  | 3.5569 | 3.5306 | 3.2047 | 3.3722 | 3.3997 | 3.4294
2025-06-16 | 4.484 | 4.5736 | 4.5438 | 4.5472 | 4.5549 | 4.5846 | 4.5959 | 4.5985 | 4.5494 | 4.5652 | 4.6831 | 4.6513 | 4.5816 | 4.7122 | 4.5865 | 4.5798 | 4.5607 | 4.5363 | 4.5494 | 4.5497 | 4.579 | 4.5955 | 4.6579 | 4.5849 | 4.6029 | 4.5442 | 4.5238 | 4.5267 | 4.5713 | 4.5087 | 4.5127 | 4.4927 | 4.489 | 4.4361 | 4.53 | 4.4674 | 4.4708 | 4.4356 | 4.5787 | 4.5539 | 4.5895 | 4.4981 | 4.5202 | 4.467 | 4.5195 | 4.5345 | 4.5027 | 4.5375 | 4.4707 | 4.444 | 4.5285 | 4.5101 | 4.573 | 4.5067 | 4.4698 | 4.5457 | 4.5546 | 4.5685 | 4.5 | 4.5596 | 4.5532 | 4.5855 | 4.5199 | 4.5977 | 4.585 | 4.5521 | 4.6005 | 4.4882 | 4.5622 | 4.5442 | 4.573 | 4.5498 | 4.6629 | 4.5779 | 4.6289 | 4.546 | 4.6342 | 4.588 | 4.536 | 4.5749 | 4.6082 | 4.6243 | 4.5648 | 4.6285 | 4.5629 | 4.5712 | 4.6034 | 4.5622 | 4.5131 | 4.4865 | 4.5343 | 4.5808 | 4.6551 | 4.6311 | 4.5556 | 4.5427 | 4.5213 | 4.6431 | 4.5772 | 4.5951 | 4.7019 | 4.5861 | 4.6457 | 4.5446 | 4.6189 | 4.6375 | 4.6545 | 4.5667 | 4.63 | 4.5783 | 4.5981 | 4.531 | 4.6116 | 4.5816 | 4.6191 | 4.6461 | 4.5393 | 4.5786 | 4.557 | 4.6165 | 4.676 | 4.4744 | 4.4914 | 4.6131 | 4.6506 | 4.6439 | 4.409 | 4.3828 | 4.3645 | 4.3998 | 4.3965 | 4.4239 | 4.4173 | 4.4127 | 4.3706 | 4.4105 | 4.4091 | 4.4052 | 4.3901 | 4.3307 | 4.3692 | 4.3475 | 4.412 | 4.4114 | 4.3524 | 4.4218 | 4.4217 | 4.4045 | 4.3941 | 4.3872 | 4.3838 | 4.3895 | 4.3878 | 4.3895 | 4.4064 | 4.3772 | 4.3588 | 4.3895 | 4.5936 | 4.508 | 4.5653 | 4.4523 | 4.5303 | 4.5047 | 4.5909 | 4.5389 | 4.5386 | 4.5842 | 4.6568 | 4.4604 | 4.5411 | 4.4527 | 4.5613 | 4.5873 | 4.5465 | 4.5504 | 4.6045 | 4.5121 | 4.6643 | 4.653 | 4.5329 | 4.6007 | 4.4717 | 4.64 | 4.578 | 4.5798 | 4.6211 | 4.6211 | 4.6469 | 4.5497 | 4.6208 | 4.5799 | 4.5492 | 4.6277 | 4.6277 | 4.642 | 4.7027 | 4.7326 |  |  | 4.3411 | 4.4423 | 4.5466 |  | 4.5663 | 4.4311 | 4.609 | 4.4805 | 4.5978 | 4.5974 | 4.6367 | 4.6292 | 4.6446 | 4.6899 | 4.6221 | 4.6517 | 4.6006 | 4.6931 | 4.8768 | 4.7918 | 4.7074 | 4.7273 | 4.4829 | 4.5183 | 4.6145 | 4.5999 | 4.558 | 4.5407 | 4.658 | 4.5687 | 4.5743 | 4.4677 | 4.4406 | 4.4625 | 4.4716 | 4.4291 | 4.5374 |  | 4.4735 | 4.4521 | 4.5871 | 4.4598 | 4.4328 |  |  | 4.7732 | 4.7179 | 4.234 | 4.4911 | 4.5647 | 4.5446
2025-06-17 | 3.1509 | 3.228 | 3.2404 | 3.2506 | 3.1955 | 3.2176 | 3.212 | 3.2221 | 3.1957 | 3.2144 | 3.2674 | 3.2479 | 3.2049 | 3.2972 | 3.1944 | 3.1547 | 3.1712 | 3.1592 | 3.1461 | 3.1634 | 3.2022 | 3.1993 | 3.2612 | 3.209 | 3.2118 | 3.1634 | 3.1478 | 3.1604 | 3.1694 | 3.1377 | 3.1677 | 3.1587 | 3.1659 | 3.1218 | 3.1491 | 3.1666 | 3.1618 | 3.097 | 3.1573 | 3.2112 | 3.1288 | 3.1019 | 3.1607 | 3.1315 | 3.1704 | 3.182 | 3.1651 | 3.1378 | 3.154 | 3.1062 | 3.1861 | 3.1753 | 3.2293 | 3.1727 | 3.1634 | 3.2336 | 3.2136 | 3.2086 | 3.1547 | 3.1807 | 3.1948 | 3.2151 | 3.1906 | 3.3973 | 3.1827 | 3.1592 | 3.1945 | 3.1105 | 3.1521 | 3.1446 | 3.1644 | 3.1434 | 3.2247 | 3.1225 | 3.193 | 3.1278 | 3.1943 | 3.1603 | 3.1236 | 3.1841 | 3.1715 | 3.1846 | 3.1457 | 3.1858 | 3.1382 | 3.1562 | 3.1787 | 3.1551 | 3.1169 | 3.1041 | 3.1277 | 3.1582 | 3.2157 | 3.197 | 3.1634 | 3.1277 | 3.1206 | 3.2004 | 3.1768 | 3.1839 | 3.2581 | 3.1704 | 3.2109 | 3.1255 | 3.2097 | 3.1846 | 3.2639 | 3.175 | 3.212 | 3.1521 | 3.1651 | 3.1077 | 3.1694 | 3.177 | 3.191 | 3.2217 | 3.1502 | 3.1464 | 3.1407 | 3.173 | 3.2401 | 3.1094 | 3.1427 | 3.1906 | 3.2075 | 3.1577 | 3.1521 | 3.1318 | 3.207 | 3.1554 | 3.1454 | 3.1485 | 3.1485 | 3.2102 | 3.1538 | 3.149 | 3.2538 | 3.2045 | 3.2363 | 3.1236 | 3.108 | 3.0911 | 3.2079 | 3.2201 | 3.161 | 3.115 | 3.1547 | 3.1967 | 3.1547 | 3.182 | 3.2045 | 3.1809 | 3.2176 | 3.1929 | 3.1476 | 3.1228 | 3.1303 | 3.1404 | 3.1568 | 3.1023 | 3.137 | 3.1553 | 3.1451 | 3.1051 | 3.2067 | 3.1327 | 3.1242 | 3.1596 | 3.1939 | 3.1309 | 3.116 | 3.1236 | 3.1414 | 3.1476 | 3.1832 | 3.1492 | 3.1708 | 3.1129 | 3.2098 | 3.2011 | 3.1143 | 3.1562 | 3.1037 | 3.2865 | 3.1706 | 3.1687 | 3.1938 | 3.1975 | 3.1876 | 3.1105 | 3.178 | 3.1477 | 3.1841 | 3.1985 | 3.1894 | 3.2091 | 3.2432 | 3.2761 |  |  | 3.054 | 3.1573 | 3.1135 |  | 3.1962 | 3.115 | 3.1667 | 3.1423 | 3.1708 | 3.1757 | 3.2172 | 3.1974 | 3.2221 | 3.2288 | 3.1951 | 3.2266 | 3.2063 | 3.2746 | 3.3811 | 3.3632 | 3.2968 | 3.3292 | 3.1313 | 3.1172 | 3.2058 | 3.1854 | 3.0908 | 3.1073 | 3.2399 | 3.1997 | 3.173 | 3.1094 | 3.1119 | 3.1133 | 3.1197 | 3.1089 | 3.103 |  | 3.2579 | 3.1383 | 3.3333 | 3.1089 | 3.1119 |  |  | 3.3396 | 3.3503 | 2.9782 | 3.1119 | 3.1302 | 3.1753
2025-06-18 | 3.8548 | 3.9277 | 3.9453 | 3.9345 | 3.9495 | 3.9431 | 3.9918 | 3.9906 | 3.9385 | 3.9637 | 4.0655 | 4.0442 | 3.9599 | 4.0666 | 3.9742 | 3.7944 | 3.9569 | 3.9607 | 3.9779 | 3.9841 | 3.9963 | 3.9933 | 3.9672 | 4.001 | 4.0283 | 3.9737 | 3.943 | 3.9494 | 3.9967 | 4.0466 | 4.0666 | 4.013 | 3.7107 | 3.3221 | 3.6933 | 3.7334 | 3.6933 | 3.7015 | 3.7494 | 3.7285 | 3.6723 | 3.7195 | 3.6742 | 3.7243 | 3.761 | 3.7116 | 3.7376 | 3.7322 | 3.7181 | 3.7303 | 3.7438 | 3.7285 | 3.7427 | 3.7367 | 3.7379 | 3.7437 | 3.7946 | 3.7573 | 3.7403 | 3.759 | 3.7562 | 3.716 | 3.7494 | 3.9331 | 3.9132 | 3.8831 | 3.9239 | 3.8216 | 3.9105 | 3.9105 | 3.9341 | 3.9135 | 4.0266 | 3.8659 | 3.975 | 3.9194 | 3.9864 | 3.961 | 3.9532 | 3.9706 | 3.824 | 3.8989 | 3.9438 | 4.0097 | 3.9618 | 3.9607 | 3.9708 | 3.9375 | 3.8846 | 3.8554 | 3.8472 | 3.8918 | 4.0082 | 3.9985 | 3.8682 | 3.9322 | 3.9105 | 3.9914 | 3.9397 | 3.961 | 4.0566 | 3.9517 | 4.0131 | 3.9199 | 3.9507 | 3.9558 | 4.0523 | 3.912 | 3.9745 | 3.9208 | 3.9243 | 3.841 | 3.8768 | 3.9045 | 3.9753 | 3.9828 | 3.8521 | 3.9088 | 3.9013 | 3.9464 | 3.9783 | 3.8152 | 3.8279 | 3.9412 | 3.9749 | 3.9517 | 3.9251 | 3.9363 | 3.9907 | 3.9394 | 3.9488 | 3.9575 | 3.9813 | 3.933 | 3.8524 | 3.9752 | 4.0881 | 4.0423 | 4.0608 | 3.8217 | 3.925 | 3.8724 | 3.9876 | 4.0162 | 3.8524 | 3.9194 | 3.9633 | 4.0057 | 3.9402 | 3.9748 | 3.9627 | 3.9449 | 3.974 | 3.9562 | 3.9082 | 3.894 | 3.9127 | 3.9079 | 3.9432 | 3.983 | 4.0333 | 3.9364 | 4 | 3.9744 | 3.8721 | 3.9855 | 3.9826 | 3.9566 | 3.9394 | 3.8953 | 3.9898 | 3.8887 | 4.0098 | 4.0058 | 3.9663 | 4.0572 | 4.072 | 4.011 | 4.0071 | 3.9697 | 4.0059 | 3.9596 | 3.9603 | 4.0036 | 3.9266 | 3.9697 | 4.0778 | 4.0956 | 4.0509 | 3.993 | 3.939 | 3.8727 | 3.8295 | 3.9326 | 3.9455 | 3.875 | 4.0091 | 4.0254 |  |  | 3.6134 | 3.9086 | 3.8385 |  | 3.8397 | 3.8277 | 3.9401 | 3.639 | 3.9285 | 3.9566 | 3.9667 | 3.9648 | 3.9678 | 3.8277 | 3.9453 | 3.979 | 3.9144 | 3.9757 | 4.0349 | 4.0349 | 4.0282 | 4.0376 | 3.8528 | 3.8048 | 3.9364 | 3.8782 | 3.8538 | 3.8334 | 3.9533 | 3.9039 | 3.8592 | 3.8485 | 3.9277 | 3.8059 | 3.8112 | 3.9057 | 3.8182 |  | 3.9004 | 3.8349 | 4.0995 | 3.9319 | 3.8112 |  |  | 4.0334 | 4.0713 | 3.6747 | 3.8112 | 3.8599 | 3.9127
2025-06-19 | 3.4192 | 3.4019 | 3.4165 | 3.4142 | 3.3825 | 3.3993 | 3.4131 | 3.4131 | 3.3805 | 3.4042 | 3.4431 | 3.4573 | 3.4019 | 3.4905 | 3.4082 | 3.3146 | 3.394 | 3.3801 | 3.3812 | 3.3905 | 3.4191 | 3.4157 | 3.33 | 3.4224 | 3.4379 | 3.3933 | 3.3718 | 3.3814 | 3.4111 | 3.4107 | 3.3928 | 3.4224 | 3.4536 | 3.3272 | 3.4184 | 3.4577 | 3.4109 | 3.3169 | 3.3539 | 3.4251 | 3.3764 | 3.3457 | 3.3831 | 3.4213 | 3.3895 | 3.406 | 3.3798 | 3.3753 | 3.3489 | 3.3978 | 3.385 | 3.3749 | 3.4297 | 3.3881 | 3.3494 | 3.4071 | 3.4204 | 3.4251 | 3.3854 | 3.4294 | 3.4146 | 3.4624 | 3.3715 | 3.6447 | 3.3836 | 3.3632 | 3.3874 | 3.3099 | 3.379 | 3.3652 | 3.3809 | 3.3577 | 3.4517 | 3.3963 | 3.477 | 3.3958 | 3.47 | 3.4236 | 3.3738 | 3.4247 | 3.409 | 3.4228 | 3.3738 | 3.4206 | 3.3599 | 3.3783 | 3.3948 | 3.37 | 3.3255 | 3.3783 | 3.3359 | 3.3494 | 3.4393 | 3.424 | 3.3498 | 3.3685 | 3.3712 | 3.4337 | 3.4161 | 3.4079 | 3.479 | 3.4037 | 3.4434 | 3.3588 | 3.4231 | 3.4034 | 3.5466 | 3.3831 | 3.4154 | 3.3668 | 3.3628 | 3.3224 | 3.3964 | 3.3914 | 3.4124 | 3.4266 | 3.3663 | 3.3332 | 3.3458 | 3.3622 | 3.4285 | 3.3325 | 3.3658 | 3.3824 | 3.4124 | 3.4031 | 3.3742 | 3.3903 | 3.46 | 3.4214 | 3.4192 | 3.4223 | 3.4216 | 3.4889 | 3.5308 | 3.4262 | 3.5587 | 3.5063 | 3.5545 | 3.339 | 3.3839 | 3.377 | 3.5015 | 3.5219 | 3.3652 | 3.357 | 3.4498 | 3.495 | 3.4292 | 3.4596 | 3.4707 | 3.4303 | 3.4593 | 3.4367 | 3.3944 | 3.3798 | 3.4165 | 3.391 | 3.4598 | 3.3962 | 3.4431 | 3.353 | 3.4367 | 3.4212 | 3.469 | 3.4062 | 3.4038 | 3.4354 | 3.4905 | 3.3196 | 3.3971 | 3.3178 | 3.4212 | 3.4178 | 3.5168 | 3.4602 | 3.4837 | 3.4189 | 3.5185 | 3.5144 | 3.421 | 3.4569 | 3.4155 | 3.4545 | 3.4755 | 3.4852 | 3.5011 | 3.5109 | 3.4556 | 3.3983 | 3.3424 | 3.3678 | 3.3754 | 3.353 | 3.3625 | 3.3564 | 3.4295 | 3.4405 |  |  | 3.2129 | 3.379 | 3.3296 |  | 3.3571 | 3.3303 | 3.3468 | 3.0704 | 3.3423 | 3.3506 | 3.3903 | 3.3753 | 3.3981 | 3.4303 | 3.3858 | 3.4157 | 3.3894 | 3.4593 | 3.5925 | 3.6202 | 3.6087 | 3.5266 | 3.3632 | 3.3453 | 3.3578 | 3.3405 | 3.3245 | 3.3815 | 3.3841 | 3.3836 | 3.4131 | 3.3691 | 3.4577 | 3.3387 | 3.458 | 3.3247 | 3.4485 |  | 3.4319 | 3.349 | 3.4866 | 3.3711 | 3.4266 |  |  | 3.5298 | 3.5368 | 3.1995 | 3.4235 | 3.3769 | 3.4075
2025-06-20 | 1.9706 | 2.0086 | 2.0191 | 2.0094 | 1.944 | 2.0097 | 2.0105 | 2.0124 | 1.2261 | 2.0088 | 2.0502 | 2.0371 | 2.0015 | 2.0511 | 2.0049 | 1.9162 | 1.994 | 1.9846 | 2.0145 | 2.0076 | 2.0082 | 2.0146 | 1.9599 | 2.0255 | 2.028 | 2.0118 | 2 | 2.0045 | 2.0411 | 1.9333 | 1.9592 | 1.4449 | 2.0393 | 1.2913 | 2.0165 | 2.0418 | 2.0247 | 1.9674 | 1.9974 | 2.0262 | 1.9963 | 1.9573 | 2.0097 | 1.9899 | 2.0079 | 2.0105 | 1.535 | 1.9805 | 1.9869 | 1.4058 | 2.0019 | 2.0041 | 2.0348 | 2.0065 | 1.9838 | 2.0245 | 2.0211 | 2.0199 | 1.9988 | 2.0388 | 2.0172 | 2.0582 | 1.9989 | 2.1785 | 1.9865 | 1.9748 | 2.0363 | 2.0259 | 1.9708 | 1.967 | 1.9794 | 1.9614 | 2.0266 | 1.9929 | 2.0271 | 1.9965 | 2.0238 | 1.9974 | 1.9749 | 2.0211 | 2.0004 | 1.7757 | 1.9775 | 2.0015 | 1.9648 | 1.9772 | 1.9562 | 1.9753 | 1.9412 | 1.9052 | 1.9545 | 1.9675 | 1.9865 | 1.9899 | 2.0208 | 0 | 0 | 2.0075 | 1.9955 | 1.9569 | 2.0479 | 1.9479 | 2.0191 | 1.9663 | 2.0315 | 0 | 0 | 2.0107 | 2.0086 | 2.0072 | 2.01 | 2.0363 | 2.0022 | 1.9868 | 1.985 | 2.0124 | 1.907 | 1.9942 | 2.0032 | 1.988 | 2.027 | 1.7711 | 1.7278 | 2.0045 | 2.0236 | 1.9952 | 2.0375 | 1.9816 | 1.8923 | 1.4782 | 2.0038 | 1.9997 | 2.001 | 2.0478 | 2.0731 | 2.0136 | 2.0822 | 2.0423 | 2.0764 | 2.0562 | 2.0363 | 1.9965 | 2.0154 | 2.0339 | 1.9502 | 1.9371 | 2.0191 | 2.0425 | 2.0104 | 2.0135 | 2.0131 | 1.7382 | 2.0418 | 2.0292 | 1.9895 | 1.9749 | 2.0206 | 1.9981 | 2.0413 | 2.0106 | 2.0428 | 1.9807 | 1.5845 | 1.7643 | 2.0522 | 2.0251 | 1.7155 | 1.5185 | 1.3485 | 1.9251 | 2.0131 | 1.9171 | 1.4633 | 1.4 | 2.0138 | 1.9852 | 2.0402 | 2.0042 | 2.0721 | 2.0678 | 1.4825 | 1.4973 | 2.0077 | 2.1291 | 2.0458 | 2.0478 | 2.0302 | 2.02 | 1.6309 | 1.157 | 1.9788 | 1.9523 | 1.9811 | 1.9432 | 1.978 | 1.4811 | 2.0109 | 2.0394 |  |  | 1.8221 | 1.949 | 1.9734 |  | 1.9788 | 1.9101 | 1.9513 | 1.9442 | 1.9749 | 1.9978 | 2.0045 | 1.9176 | 2.003 | 2.03 | 1.9835 | 1.5019 | 1.9942 | 2.0395 | 2.2082 | 2.1406 | 2.129 | 2.1649 | 1.9125 | 1.96 | 1.9319 | 1.9885 | 1.9703 | 1.9547 | 1.9578 | 1.9965 | 1.9782 | 1.9559 | 2.0319 | 1.9297 | 2.0357 | 1.9978 | 1.9127 |  | 2.0125 | 1.968 | 2 | 1.8975 | 1.9021 |  |  | 2.0397 | 1.971 | 1.8322 | 1.9106 | 1.9693 | 1.9537
2025-06-21 | 4.019 | 3.9931 | 4.0037 | 3.9873 | 4.0778 | 4.0037 | 3.9663 | 4.0157 | 3.8975 | 4.0647 | 3.9738 | 4.0487 | 4.0539 | 4.0245 | 4.0536 | 3.8787 | 4.0251 | 4.0127 | 4.0353 | 4.0356 | 3.997 | 3.9738 | 3.9564 | 4.0629 | 3.9793 | 4.0377 | 4.0097 | 4.002 | 4.0573 | 3.8818 | 3.8652 | 3.6654 | 4.0256 | 3.876 | 3.9906 | 4.0214 | 3.9685 | 3.9228 | 4.0165 | 4.0689 | 3.9693 | 3.9262 | 4.0217 | 3.9693 | 4.0408 | 3.9139 | 3.8693 | 3.9895 | 4.028 | 4.0424 | 3.9363 | 4.0719 | 4.1305 | 4.0646 | 3.9582 | 3.9284 | 4.0576 | 4.0464 | 3.973 | 4.017 | 4.0232 | 4.0535 | 3.9738 | 4.1881 | 4.0138 | 4.0201 | 3.9965 | 4.0211 | 3.9625 | 4.0112 | 4 | 4.0127 | 4.0618 | 3.9738 | 4.0609 | 3.9983 | 4.0769 | 4.0517 | 4.0588 | 3.6508 | 3.9963 | 3.973 | 4.0622 | 4.03 | 4.0412 | 4.0112 | 4.0225 | 4.0112 | 3.9813 | 3.9693 | 3.9587 | 4.0024 | 3.985 | 4.0296 | 4.038 | 3.8772 | 3.8689 | 3.9116 | 3.8614 | 3.8566 | 3.9285 | 3.8801 | 3.8712 | 3.8876 | 3.8985 | 3.4757 | 3.5256 | 3.8608 | 3.8517 | 3.8938 | 3.9205 | 3.9378 | 3.8738 | 3.8632 | 3.9034 | 3.903 | 3.8675 | 3.8585 | 3.8918 | 3.8839 | 3.8757 | 3.5995 | 3.6022 | 3.8839 | 3.8607 | 3.9318 | 3.9738 | 3.9513 | 3.8851 | 3.8655 | 3.9703 | 3.8825 | 3.9647 | 4.0482 | 3.9825 | 3.9671 | 4.035 | 4.0059 | 4.0413 | 3.8801 | 3.9388 | 3.9105 | 4.0337 | 4.0162 | 3.9135 | 3.8755 | 3.9816 | 4.027 | 3.9053 | 3.9848 | 3.9962 | 3.9333 | 3.9461 | 3.906 | 3.8727 | 3.873 | 3.8783 | 3.9228 | 3.9773 | 4.0311 | 3.9428 | 3.9394 | 3.9276 | 4.0128 | 4.0037 | 4.0327 | 3.9958 | 3.9889 | 3.9814 | 4.0131 | 3.9636 | 4.0156 | 3.4545 | 3.8836 | 4.0067 | 3.9811 | 4.0038 | 4.0189 | 4.0438 | 3.9962 | 3.8776 | 4.003 | 4.0333 | 3.8945 | 3.9441 | 3.9865 | 3.9309 | 4.0116 | 3.9309 | 3.8811 | 3.9811 | 3.9902 | 3.947 | 4.0284 | 4.0114 | 3.9811 | 3.9409 | 3.9545 |  |  | 3.6946 | 3.8681 | 3.9132 |  | 4.0615 | 3.9596 | 3.8614 | 3.9101 | 4.0307 | 3.9974 | 3.9738 | 3.9476 | 4.0112 | 3.9064 | 3.8989 | 3.8764 | 4.04 | 3.9983 | 4.0349 | 4.0349 | 4.1223 | 4.2069 | 3.8899 | 3.9883 | 3.9587 | 4.0323 | 4.0048 | 3.9927 | 3.9587 | 4.0432 | 4.008 | 3.9737 | 3.8889 | 3.8997 | 3.8928 | 3.8661 | 3.9131 |  | 3.9343 | 3.8732 | 3.99 | 3.8721 | 3.8889 |  |  | 4.1379 | 3.9577 | 3.7056 | 3.8539 | 3.8702 | 3.9577
2025-06-22 | 4.2541 | 4.2458 | 4.2288 | 4.2479 | 4.2213 | 4.2734 | 4.2622 | 4.2884 | 4.2787 | 4.2787 | 4.221 | 4.2959 | 4.1772 | 4.2737 | 4.2809 | 4.1199 | 4.2472 | 4.3165 | 4.3077 | 4.2558 | 4.2434 | 4.2509 | 4.2417 | 4.2613 | 4.2558 | 4.2835 | 4.2652 | 4.278 | 4.3213 | 4.1248 | 4.1798 | 3.9883 | 4.2846 | 4.1232 | 4.3101 | 4.2824 | 4.3228 | 4.2539 | 4.3112 | 4.2959 | 4.236 | 4.2532 | 4.2472 | 4.1985 | 4.2996 | 4.2285 | 4.1521 | 4.2734 | 4.1931 | 3.9673 | 4.3146 | 4.309 | 4.3313 | 4.2946 | 4.2714 | 4.2547 | 4.2314 | 4.2397 | 4.228 | 4.2946 | 4.2622 | 4.3158 | 4.2963 | 4.3887 | 4.2489 | 4.2558 | 4.308 | 4.2016 | 4.2397 | 4.2551 | 4.2659 | 4.2472 | 4.1985 | 4.2888 | 4.228 | 4.268 | 4.2757 | 4.2899 | 4.2798 | 4.3274 | 4.236 | 4.2288 | 4.2524 | 4.3056 | 4.3109 | 4.2925 | 4.2839 | 4.2835 | 4.2094 | 4.1768 | 4.2057 | 4.1452 | 4.236 | 4.2221 | 4.241 | 4.2659 | 4.2401 | 4.221 | 4.2925 | 4.2816 | 4.2509 | 4.2824 | 4.2472 | 4.2011 | 4.2687 | 4.2528 | 4.0682 | 4.2392 | 4.2944 | 4.2247 | 4.2244 | 3.9758 | 4.2234 | 4.252 | 4.3026 | 4.2745 | 4.1285 | 4.1558 | 4.1861 | 4.203 | 4.2903 | 3.9497 | 3.8665 | 4.2442 | 4.2809 | 4.245 | 4.2801 | 4.2693 | 4.1315 | 4.2121 | 4.2506 | 4.1521 | 4.2911 | 4.2942 | 4.2622 | 4.3042 | 4.3042 | 4.2797 | 4.2427 | 4.1236 | 4.2648 | 4.1957 | 4.2397 | 4.2662 | 4.2547 | 3.9713 | 4.1985 | 4.2533 | 4.2742 | 4.26 | 4.2627 | 4.297 | 4.2873 | 4.2476 | 4.2506 | 4.2277 | 4.2513 | 4.279 | 4.2792 | 4.2909 | 4.2458 | 4.2121 | 4.2212 | 4.2508 | 4.2121 | 4.3138 | 4.2189 | 4.2189 | 4.1742 | 4.192 | 4.1876 | 4.2015 | 4.2626 | 4.1895 | 4.2694 | 4.1705 | 4.2413 | 4.2697 | 4.3098 | 4.3091 | 4.1902 | 4.2061 | 4.2785 | 4.2909 | 4.278 | 4.2811 | 4.2182 | 4.2545 | 4.2767 | 3.993 | 4.1288 | 4.2083 | 4.2538 | 4.1705 | 4.1523 | 4.2322 | 4.2518 | 4.2587 |  |  | 3.9666 | 4.208 | 4.2166 |  | 4.1432 | 4.1985 | 4.1558 | 4.2011 | 4.1648 | 4.1427 | 4.2045 | 4.2 | 4.2288 | 4.1929 | 4.2266 | 4.1551 | 4.227 | 4.3223 | 4.3439 | 4.2991 | 4.3521 | 4.3135 | 4.1919 | 4.1747 | 4.1341 | 4.1608 | 4.1431 | 4.1822 | 4.1546 | 4.1901 | 4.1395 | 4.16 | 4.2778 | 4.1681 | 4.2863 | 4.2312 | 4.2747 |  | 4.246 | 4.2598 | 4.1891 | 4.1489 | 4.1608 |  |  | 4.3469 | 4.3143 | 3.9218 | 4.1608 | 4.2745 | 4.2313
2025-06-23 | 3.6889 | 3.6418 | 3.6629 | 3.6446 | 3.6273 | 3.6476 | 3.6427 | 3.6446 | 3.3496 | 3.6426 | 3.6742 | 3.6936 | 3.6745 | 3.6404 | 3.6262 | 3.6247 | 3.6161 | 3.7386 | 3.6142 | 3.6086 | 3.63 | 3.6404 | 3.6166 | 3.6604 | 3.6564 | 3.6242 | 3.6615 | 3.6225 | 3.6548 | 3.6328 | 3.6921 | 3.3625 | 3.6761 | 3.6826 | 3.6345 | 3.5831 | 3.6581 | 3.7116 | 3.6749 | 3.6625 | 3.6045 | 3.7075 | 3.7419 | 3.7251 | 3.6532 | 3.6682 | 3.2878 | 3.5921 | 3.6315 | 3.2755 | 3.6315 | 3.6442 | 3.6288 | 3.6335 | 3.5751 | 3.6621 | 3.6604 | 3.6326 | 3.6201 | 3.6767 | 3.6558 | 3.6132 | 3.6457 | 3.72 | 3.638 | 3.6557 | 3.6093 | 3.5889 | 3.6554 | 3.6483 | 3.6532 | 3.6221 | 3.5993 | 3.5993 | 3.5955 | 3.6571 | 3.5888 | 3.6813 | 3.6442 | 3.7058 | 3.6727 | 3.6176 | 3.6479 | 3.7041 | 3.6352 | 3.6446 | 3.6513 | 3.6285 | 3.5809 | 3.5419 | 3.5951 | 3.516 | 3.5768 | 3.588 | 3.5655 | 3.5884 | 2.7903 | 3.6899 | 3.5805 | 3.5955 | 3.633 | 3.588 | 3.5618 | 3.5453 | 3.5955 | 3.5618 | 3.5955 | 3.6112 | 3.5618 | 3.5256 | 3.6135 | 3.6398 | 3.5622 | 3.5323 | 3.5618 | 3.6105 | 3.2352 | 3.6288 | 3.5256 | 3.6536 | 3.5805 | 3.461 | 3.3828 | 3.5618 | 3.6217 | 3.6255 | 3.521 | 3.6109 | 3.5955 | 3.4823 | 3.5575 | 3.5239 | 3.6111 | 3.5138 | 3.5664 | 3.6038 | 3.0409 | 3.5979 | 3.5596 | 3.4981 | 3.5941 | 3.5277 | 3.6045 | 3.6024 | 3.5453 | 3.6093 | 3.6142 | 3.5792 | 3.6764 | 3.6667 | 3.6232 | 3.6375 | 3.5988 | 3.6045 | 3.6479 | 3.6037 | 3.6146 | 3.5693 | 3.6337 | 3.5951 | 3.6347 | 3.4883 | 3.3313 | 3.3273 | 3.532 | 3.6145 | 3.5606 | 3.3421 | 3.5606 | 3.5098 | 3.6058 | 3.5222 | 3.569 | 3.5636 | 3.6236 | 3.614 | 3.5644 | 3.5769 | 3.5744 | 3.6023 | 3.5664 | 3.5051 | 3.6061 | 3.6 | 3.5822 | 3.6118 | 3.5309 | 3.6033 | 3.3455 | 3.5315 | 3.5989 | 3.5447 | 3.5644 | 3.567 | 3.6235 | 3.5265 | 3.5455 | 3.5265 |  |  | 3.3411 | 3.2356 | 3.524 |  | 3.6408 | 3.5337 | 3.3757 | 3.5255 | 3.594 | 3.6247 | 3.6592 | 3.6558 | 3.5243 | 3.6483 | 3.6614 | 3.5243 | 3.5955 | 3.6621 | 3.717 | 3.6677 | 3.6468 | 3.7053 | 3.5642 | 3.6163 | 3.7124 | 3.6658 | 3.6353 | 3.6812 | 3.7131 | 3.7082 | 3.6977 | 3.6375 | 3.6581 | 3.539 | 3.6127 | 3.5226 | 3.5418 |  | 3.6824 | 3.5528 | 3.7015 | 3.4942 | 3.5043 |  |  | 3.9415 | 3.7226 | 3.3076 | 3.4887 | 3.5705 | 3.5907
2025-06-24 | 4.8927 | 5.0137 | 5.0404 | 4.97 | 4.9649 | 5.0124 | 5.0101 | 5.0345 | 5.0013 | 5.0333 | 5.0974 | 5.0861 | 4.8202 | 5.1718 | 5.024 | 5.021 | 4.9801 | 4.9689 | 4.9787 | 4.9777 | 5.0288 | 5.0521 | 4.9148 | 5.049 | 5.0586 | 5.0143 | 4.8716 | 4.9711 | 5.0254 | 4.8439 | 4.8456 | 4.831 | 4.945 | 5.0776 | 4.9105 | 4.9455 | 4.8067 | 4.8397 | 4.9326 | 4.9798 | 4.8955 | 4.8783 | 4.9667 | 4.9322 | 5.0004 | 5.0221 | 4.8709 | 4.9225 | 4.9377 | 4.8719 | 4.9884 | 4.9831 | 5.058 | 4.9911 | 4.9141 | 5.0071 | 4.9994 | 5.0082 | 4.9375 | 5.0054 | 4.9933 | 5.0335 | 4.9801 | 5.3889 | 5.0237 | 4.9787 | 5.0202 | 4.8619 | 4.9742 | 4.9652 | 4.97 | 4.9337 | 5.061 | 4.9517 | 4.9661 | 4.8613 | 4.9934 | 4.9775 | 4.9382 | 5.0009 | 5.0281 | 5.0438 | 4.9727 | 5.0213 | 4.9798 | 4.9993 | 4.9876 | 4.9809 | 4.8757 | 4.8457 | 4.8629 | 4.8443 | 5.0494 | 4.8715 | 4.9385 | 4.909 | 4.824 | 5.0483 | 4.9273 | 4.9996 | 5.1026 | 4.9573 | 4.9914 | 4.9067 | 4.9988 | 4.8596 | 5.1156 | 2.4975 | 5.0382 | 4.9774 | 5.0031 | 4.9615 | 4.9608 | 4.9971 | 5.0491 | 5.0315 | 4.8394 | 4.9478 | 4.9538 | 4.9981 | 5.0663 | 4.7527 | 4.6464 | 5.0109 | 4.9034 | 4.9235 | 4.9116 | 4.8404 | 4.9455 | 4.9012 | 4.875 | 4.808 | 4.8944 | 4.9075 | 5.0441 | 4.814 | 4.9755 | 5.0196 | 4.9715 | 4.9401 | 4.8754 | 4.8477 | 4.9258 | 4.9825 | 4.8071 | 4.8971 | 4.8386 | 4.9397 | 4.8885 | 4.874 | 4.9805 | 4.9195 | 4.9238 | 4.9154 | 4.8277 | 4.8356 | 4.8037 | 4.8816 | 5.0269 | 4.936 | 4.9795 | 4.8564 | 4.8687 | 4.8727 | 4.8956 | 4.9651 | 4.8966 | 4.9067 | 4.8788 | 4.8244 | 4.972 | 4.8636 | 4.862 | 4.9836 | 4.9842 | 4.9583 | 4.9682 | 4.8773 | 4.9013 | 5.0576 | 4.857 | 4.8926 | 4.8519 | 5.1636 | 5.0035 | 4.9657 | 4.9873 | 4.9091 | 4.8502 | 4.9301 | 4.9936 | 4.9587 | 4.8409 | 4.9322 | 4.9693 | 4.8527 | 5.0145 | 4.8864 |  |  | 4.5688 | 4.8385 | 4.8485 |  | 4.892 | 4.8581 | 4.8831 | 4.8824 | 4.9648 | 4.9727 | 5.0034 | 5.0041 | 4.9955 | 4.8281 | 4.9633 | 5 | 4.9615 | 4.9858 | 5.1232 | 4.9306 | 4.9321 | 5.0219 | 4.9264 | 4.8595 | 4.9762 | 4.9848 | 4.9386 | 4.922 | 5.0175 | 4.9628 | 4.9598 | 4.9149 | 4.8368 | 4.8308 | 4.8271 | 4.9502 | 4.9661 |  | 5.0977 | 4.8805 | 5.2189 | 4.8672 | 4.831 |  |  | 5.4378 | 5.0047 | 4.4639 | 4.8302 | 4.886 | 4.9365
2025-06-25 | 4.8356 | 4.8443 | 4.9667 | 4.9622 | 4.9158 | 4.9378 | 4.9539 | 4.8734 | 4.9111 | 4.9219 | 4.9142 | 4.9049 | 4.7345 | 4.8629 | 4.9322 | 4.927 | 4.9064 | 4.8846 | 4.874 | 4.8961 | 4.9483 | 4.9502 | 4.8353 | 4.9548 | 4.9649 | 4.9044 | 4.7402 | 4.8769 | 4.9005 | 4.7314 | 4.7457 | 4.7191 | 4.934 | 4.8516 | 4.8603 | 4.8953 | 4.9045 | 4.7993 | 4.8801 | 4.9614 | 4.8453 | 4.8015 | 4.8933 | 4.8528 | 4.9311 | 4.9363 | 4.8799 | 4.8708 | 4.8762 | 4.7227 | 4.9184 | 4.9101 | 4.8929 | 4.9202 | 4.7976 | 4.8846 | 4.8742 | 4.8678 | 4.8922 | 4.8759 | 4.9449 | 4.8906 | 4.9202 | 5.261 | 4.9414 | 4.8992 | 4.9587 | 4.8121 | 4.9157 | 4.8963 | 4.9157 | 4.8678 | 4.9404 | 4.9165 | 4.9538 | 4.8516 | 4.9605 | 4.9232 | 4.8715 | 4.9611 | 4.9476 | 4.8727 | 4.8906 | 4.9517 | 4.8824 | 4.9064 | 4.8996 | 4.8895 | 4.7858 | 4.7468 | 4.8068 | 4.7589 | 4.9816 | 4.8356 | 4.8849 | 4.8667 | 4.8813 | 4.9685 | 4.9079 | 4.9356 | 4.9479 | 4.8798 | 4.9255 | 4.8734 | 4.9445 | 4.8318 | 4.9615 | 4.7313 | 4.903 | 4.8879 | 4.9141 | 4.911 | 4.8476 | 4.8812 | 4.9596 | 4.7461 | 4.7461 | 4.8533 | 4.8832 | 4.9311 | 4.9404 | 4.6795 | 4.5546 | 4.9311 | 4.8322 | 4.8842 | 4.8322 | 4.8438 | 4.7068 | 4.821 | 4.8474 | 4.8035 | 4.8232 | 4.9164 | 4.899 | 4.8049 | 4.8605 | 4.9413 | 4.8694 | 4.7648 | 4.7772 | 4.7426 | 4.8813 | 4.8439 | 4.736 | 4.8152 | 4.797 | 4.8936 | 4.8498 | 4.8913 | 4.8439 | 4.8622 | 4.9488 | 4.8655 | 4.776 | 4.767 | 4.767 | 4.8648 | 4.8322 | 4.7409 | 4.764 | 4.7523 | 4.7407 | 4.7104 | 4.8559 | 4.7902 | 4.7394 | 4.8199 | 4.7898 | 4.7764 | 4.7913 | 4.7746 | 4.7623 | 4.8415 | 4.7751 | 4.7795 | 4.825 | 4.8087 | 4.7529 | 4.8663 | 4.7524 | 4.7253 | 4.8569 | 4.9535 | 4.8136 | 4.7771 | 4.8498 | 4.8378 | 4.8145 | 4.7399 | 4.8458 | 4.7413 | 4.7898 | 4.7879 | 4.9027 | 4.8027 | 4.8691 | 4.8864 |  |  | 4.5625 | 4.7386 | 4.813 |  | 4.8452 | 4.7644 | 4.8232 | 4.7607 | 4.8809 | 4.903 | 4.9476 | 4.9543 | 4.8318 | 4.7622 | 4.9345 | 4.8315 | 4.9352 | 5.0497 | 5.1679 | 5.0291 | 5.0522 | 4.9467 | 4.81 | 4.7631 | 4.9129 | 4.8706 | 4.7917 | 4.7934 | 4.942 | 4.8211 | 4.8633 | 4.7654 | 4.7552 | 4.7662 | 4.7436 | 4.7437 | 4.8667 |  | 5.0637 | 4.7638 | 5.005 | 4.7759 | 4.7809 |  |  | 5.2723 | 4.9177 | 4.5051 | 4.7883 | 4.9362 | 4.8587
2025-06-26 | 4.8885 | 4.92 | 5.0157 | 5.0034 | 4.9352 | 4.9742 | 4.9449 | 4.9648 | 4.923 | 4.9395 | 5.006 | 4.9727 | 4.8303 | 4.952 | 4.8996 | 4.8921 | 4.861 | 4.8386 | 4.8318 | 4.847 | 4.9064 | 4.9161 | 4.7965 | 4.9002 | 4.902 | 4.8446 | 4.735 | 4.808 | 4.84 | 4.808 | 4.7387 | 4.7767 | 4.9033 | 5.0052 | 4.8345 | 4.8598 | 4.8693 | 4.7625 | 4.8375 | 4.9243 | 4.8139 | 4.7689 | 4.8457 | 4.8056 | 4.8993 | 4.9255 | 4.8916 | 4.8412 | 4.914 | 4.7507 | 4.9453 | 4.9341 | 4.8999 | 4.9215 | 4.7665 | 4.8979 | 4.8586 | 4.9315 | 4.8556 | 4.9072 | 4.9067 | 4.9512 | 4.897 | 5.3007 | 4.9276 | 4.8792 | 4.9428 | 4.8263 | 4.9094 | 4.8828 | 4.9199 | 4.8805 | 4.8775 | 4.873 | 4.8496 | 4.772 | 4.8952 | 4.873 | 4.8337 | 4.8868 | 4.9056 | 4.9266 | 4.8734 | 4.9247 | 4.8592 | 4.8955 | 4.9034 | 4.9052 | 4.7955 | 4.7678 | 4.827 | 4.7765 | 4.9674 | 4.9195 | 4.8593 | 4.833 | 4.8228 | 4.9464 | 4.8521 | 4.8985 | 4.9109 | 4.8303 | 4.8794 | 4.8191 | 4.8416 | 4.5749 | 4.9705 | 4.8026 | 4.921 | 4.8446 | 4.8515 | 4.8965 | 4.8649 | 4.8856 | 4.9367 | 4.7607 | 4.8019 | 4.7647 | 4.8087 | 4.9071 | 4.9678 | 4.6642 | 4.5057 | 4.8865 | 4.903 | 4.8866 | 4.83 | 4.8255 | 4.7644 | 4.8216 | 4.8107 | 4.8114 | 4.8277 | 4.9128 | 4.857 | 4.8014 | 4.8888 | 4.8993 | 4.8582 | 4.8697 | 4.7965 | 4.7748 | 4.9004 | 4.9286 | 4.7633 | 4.8283 | 4.7966 | 4.8813 | 4.7865 | 4.8532 | 4.8764 | 4.8131 | 4.9125 | 4.8311 | 4.7513 | 4.7869 | 4.7449 | 4.8318 | 4.8848 | 4.8148 | 4.8185 | 4.7943 | 4.7848 | 4.829 | 4.8455 | 4.804 | 4.7936 | 4.8859 | 4.8485 | 4.9273 | 4.8836 | 4.8415 | 4.7865 | 4.8767 | 4.7845 | 4.8148 | 4.8174 | 4.8902 | 4.8185 | 4.928 | 4.8409 | 4.7862 | 4.7492 | 4.9858 | 4.8885 | 4.8306 | 4.8873 | 4.8876 | 4.8705 | 4.7941 | 4.8932 | 4.8689 | 4.8716 | 4.8845 | 4.8864 | 4.8409 | 4.8636 | 4.9284 |  |  | 4.5882 | 4.8106 | 4.8141 |  | 4.9306 | 4.8161 | 4.8367 | 4.8 | 4.8727 | 4.8532 | 4.9854 | 4.9554 | 4.873 | 4.8315 | 4.9139 | 4.9622 | 4.9382 | 5.05 | 5.1545 | 5.0766 | 5.0914 | 5.0094 | 4.8066 | 4.9041 | 4.9316 | 4.9162 | 4.8781 | 4.8729 | 4.9298 | 4.9151 | 4.9844 | 4.9265 | 4.8221 | 4.8618 | 4.7933 | 4.8253 | 4.8117 |  | 5.0977 | 4.7948 | 5.1065 | 4.7729 | 4.7883 |  |  | 5.2706 | 5.0102 | 4.5329 | 4.7622 | 5.0004 | 4.869
2025-06-27 | 4.4543 | 4.4636 | 4.4569 | 4.4981 | 4.4944 | 4.485 | 4.4255 | 4.4873 | 4.3222 | 4.3506 | 4.4573 | 4.4895 | 4.2873 | 4.3309 | 4.4442 | 4.461 | 4.4232 | 4.4176 | 4.3271 | 4.3357 | 4.373 | 4.3888 | 4.3488 | 4.3316 | 4.3831 | 4.3755 | 4.223 | 4.4038 | 4.3865 | 4.2277 | 4.2131 | 4.2517 | 4.3333 | 4.3539 | 4.2801 | 4.2673 | 4.3131 | 4.2322 | 4.303 | 4.3921 | 4.2719 | 4.2438 | 4.309 | 4.2708 | 4.3682 | 4.3843 | 4.1901 | 4.3307 | 4.3865 | 4.1988 | 4.3861 | 4.3933 | 4.3316 | 4.3735 | 4.1901 | 4.3319 | 4.3685 | 4.4157 | 4.3239 | 4.3466 | 4.3723 | 4.3874 | 4.3431 | 4.604 | 4.3526 | 4.3761 | 4.3969 | 4.3264 | 4.3165 | 4.3243 | 4.3517 | 4.3884 | 4.3659 | 4.3558 | 4.3436 | 4.285 | 4.3273 | 4.385 | 4.3742 | 4.3658 | 4.3577 | 4.3356 | 4.3813 | 4.394 | 4.3794 | 4.3401 | 4.3401 | 4.3221 | 4.3251 | 4.2805 | 4.3017 | 4.2385 | 4.3708 | 4.3655 | 4.3832 | 4.3858 | 2.864 | 4.3918 | 4.3831 | 4.3738 | 4.3539 | 4.3936 | 4.424 | 4.2236 | 4.3452 | 4.415 | 4.3772 | 4.2081 | 4.3888 | 4.3829 | 4.4007 | 4.3519 | 4.3472 | 4.3972 | 4.3154 | 4.206 | 4.1957 | 4.2467 | 4.268 | 4.403 | 4.4487 | 4.1155 | 4.0866 | 4.3236 | 4.3592 | 4.2547 | 4.3221 | 4.2734 | 4.2184 | 4.2247 | 4.2116 | 4.2555 | 4.2655 | 4.3375 | 4.3014 | 4.2378 | 4.2857 | 4.2657 | 4.2416 | 4.2239 | 4.261 | 4.2216 | 4.2266 | 4.2545 | 4.2363 | 4.2562 | 4.2363 | 4.2272 | 4.2576 | 4.2199 | 4.2392 | 4.2064 | 4.271 | 4.2127 | 4.2363 | 4.2139 | 4.2903 | 4.2715 | 4.3216 | 4.2402 | 4.2525 | 4.2856 | 4.2185 | 4.2249 | 4.3145 | 4.2767 | 4.2788 | 4.2 | 4.2928 | 4.2633 | 4.2695 | 4.2044 | 4.2532 | 4.3004 | 4.2226 | 4.2519 | 4.2932 | 4.2466 | 4.2138 | 4.3189 | 4.2378 | 4.2226 | 4.2576 | 4.4211 | 4.2892 | 4.2673 | 4.3011 | 4.3033 | 4.356 | 4.2308 | 4.2883 | 4.3023 | 4.2466 | 4.3117 | 4.2845 | 4.2163 | 4.3459 | 4.258 |  |  | 0.0003885 | 4.238 | 4.2458 |  | 4.3681 | 4.3404 | 4.3861 | 4.2258 | 4.3861 | 4.3457 | 4.3734 | 4.4 | 4.3251 | 4.239 | 4.3116 | 4.3311 | 4.4018 | 4.4964 | 4.5862 | 4.5678 | 4.5517 | 4.3962 | 4.265 | 4.3424 | 4.489 | 4.4155 | 4.363 | 4.3834 | 4.5142 | 4.4425 | 4.3955 | 4.3246 | 4.2389 | 4.2828 | 4.2774 | 4.2705 | 4.2493 |  | 4.5896 | 4.2532 | 4.3363 | 4.2353 | 4.2409 |  |  | 4.6859 | 4.4773 | 4.0546 | 4.3551 | 4.3744 | 4.3189
2025-06-28 | 3.6273 | 3.6968 | 3.5996 | 3.6094 | 3.6923 | 3.6854 | 3.7101 | 3.7101 | 3.6642 | 3.6825 | 3.6285 | 3.7375 | 3.5184 | 3.5877 | 3.6828 | 3.6483 | 3.6618 | 3.6562 | 3.6384 | 3.6498 | 3.5622 | 3.5948 | 3.5481 | 3.6418 | 3.5768 | 3.6249 | 3.5029 | 3.5592 | 3.5918 | 3.5396 | 3.5659 | 3.4996 | 3.546 | 3.5905 | 3.6375 | 3.5129 | 3.6375 | 3.618 | 3.2622 | 3.6498 | 3.6554 | 3.6427 | 3.6375 | 3.6165 | 3.6 | 3.5835 | 3.5609 | 3.6247 | 3.584 | 3.4981 | 3.6375 | 3.6509 | 3.6395 | 3.6578 | 3.5367 | 3.6624 | 3.6741 | 3.2667 | 3.5845 | 3.6328 | 3.7142 | 3.5296 | 3.6914 | 3.7701 | 3.6664 | 3.5997 | 3.6515 | 3.6045 | 3.6464 | 3.6094 | 3.6217 | 3.6745 | 3.6307 | 3.5794 | 3.5712 | 3.5992 | 3.6311 | 3.6322 | 3.6453 | 3.6681 | 3.5873 | 3.6375 | 3.6674 | 3.6213 | 3.6712 | 3.6187 | 3.5813 | 3.664 | 3.6345 | 3.585 | 3.5847 | 3.5215 | 3.6 | 3.1985 | 3.6648 | 3.6506 | 0 | 3.6408 | 3.588 | 3.5738 | 3.6127 | 3.564 | 3.5933 | 3.5592 | 3.5655 | 3.6217 | 3.6078 | 3.5172 | 3.5202 | 3.6787 | 3.5678 | 3.5236 | 3.5219 | 3.5672 | 3.6213 | 3.5809 | 3.5504 | 3.5089 | 3.5619 | 3.5738 | 3.6225 | 3.3258 | 3.3458 | 3.5805 | 3.5243 | 3.5256 | 3.5805 | 3.5431 | 3.6288 | 3.5968 | 3.3089 | 3.6204 | 3.6716 | 3.6977 | 3.729 | 3.5647 | 3.7248 | 3.7073 | 3.6915 | 3.2813 | 3.6283 | 3.5495 | 3.6704 | 3.7134 | 3.5659 | 3.638 | 3.6105 | 3.6903 | 3.6145 | 3.6557 | 3.6536 | 3.5873 | 3.5762 | 3.5532 | 3.5419 | 3.5581 | 3.624 | 3.6985 | 3.6663 | 3.5625 | 3.6461 | 3.5152 | 3.537 | 3.5168 | 3.6394 | 3.5778 | 3.5712 | 3.5189 | 3.539 | 3.4909 | 3.5971 | 3.5251 | 3.5441 | 3.248 | 3.5966 | 3.6333 | 3.6932 | 3.6545 | 3.6074 | 3.6212 | 3.5385 | 3.5562 | 3.536 | 3.6727 | 3.5703 | 3.6418 | 3.5564 | 3.6 | 3.5015 | 3.2605 | 3.5811 | 3.6633 | 3.6333 | 3.6799 | 3.6208 | 3.5795 | 3.6159 | 3.5966 |  |  | 0 | 3.5787 | 3.5432 |  | 3.5338 | 3.6371 | 3.5805 | 3.5921 | 3.2127 | 3.6749 | 3.6191 | 3.6483 | 3.5461 | 3.5835 | 3.5517 | 3.5543 | 3.5372 | 3.8052 | 3.811 | 3.7662 | 3.767 | 3.6991 | 3.5676 | 3.543 | 3.6185 | 3.5868 | 3.5073 | 3.5111 | 3.6728 | 3.5765 | 3.5562 | 3.5892 | 3.6173 | 3.6515 | 3.5315 | 3.5488 | 3.5511 |  | 3.807 | 3.5563 | 3.607 | 3.4942 | 3.5431 |  |  | 3.7659 | 3.7461 | 3.3556 | 3.5264 | 3.6111 | 3.5947
2025-06-29 | 3.1564 | 3.2221 | 3.2285 | 3.2172 | 3.2083 | 3.2097 | 3.2247 | 3.236 | 3.2072 | 3.2216 | 3.206 | 3.1453 | 3.1423 | 3.2972 | 3.2172 | 3.188 | 3.191 | 3.1873 | 3.1979 | 3.2083 | 3.1798 | 3.2285 | 3.1392 | 3.226 | 3.115 | 3.2118 | 3.1184 | 3.1893 | 3.216 | 3.1434 | 3.1694 | 3.0535 | 3.1486 | 3.2049 | 3.1798 | 3.2051 | 3.206 | 3.1049 | 3.161 | 3.221 | 3.1311 | 3.124 | 3.1685 | 3.0682 | 3.1948 | 3.206 | 3.115 | 3.1685 | 3.1712 | 3.0964 | 3.1835 | 3.1985 | 3.2393 | 3.1993 | 3.1623 | 3.1777 | 3.2 | 3.1712 | 3.196 | 3.1074 | 3.206 | 3.2519 | 3.2397 | 3.2936 | 3.191 | 3.1772 | 3.2083 | 3.0908 | 3.1648 | 3.176 | 3.191 | 3.1386 | 3.1423 | 3.1723 | 3.2127 | 3.1727 | 3.2193 | 3.1798 | 3.1648 | 3.2152 | 3.1985 | 3.221 | 3.1685 | 3.191 | 3.1386 | 3.176 | 3.1461 | 3.1573 | 3.1453 | 3.1243 | 3.1612 | 3.115 | 3.2135 | 3.1131 | 3.1561 | 3.161 | 0 | 3.1723 | 3.191 | 3.1423 | 3.1199 | 3.2022 | 3.1311 | 3.191 | 3.2127 | 3.1498 | 3.2726 | 3.187 | 3.1573 | 3.186 | 3.1841 | 3.1841 | 3.1104 | 3.0885 | 3.221 | 3.1341 | 3.1623 | 3.0995 | 3.166 | 3.1948 | 3.1262 | 2.9929 | 2.9397 | 3.1985 | 3.1041 | 3.1893 | 3.1172 | 3.1449 | 3.1045 | 3.1817 | 3.1208 | 3.1689 | 3.1896 | 3.1297 | 3.1434 | 3.1479 | 3.1217 | 3.1573 | 3.1317 | 3.2247 | 3.1775 | 3.1288 | 3.1685 | 3.257 | 3.1127 | 3.1997 | 3.1764 | 3.2196 | 3.1841 | 3.2643 | 3.2294 | 3.2397 | 3.1667 | 3.1648 | 3.1921 | 3.1491 | 3.206 | 3.2629 | 3.2121 | 3.1364 | 3.1785 | 3.0985 | 3.1481 | 3.1044 | 3.2054 | 3.16 | 3.1288 | 3.0168 | 3.1644 | 3.0953 | 3.1418 | 3.1487 | 3.1616 | 2.9818 | 3.1303 | 3.1591 | 3.2045 | 3.1212 | 3.1178 | 3.2008 | 3.1913 | 3.1347 | 3.1212 | 3.1709 | 3.1213 | 3.2054 | 3.168 | 3.148 | 3.1425 | 3.1538 | 3.1098 | 3.1598 | 3.192 | 3.1629 | 3.1591 | 3.1402 | 3.1318 | 3.1174 |  |  | 0 | 3.1573 | 3.1633 |  | 3.1664 | 3.1798 | 3.1674 | 3.1449 | 3.1494 | 3.1599 | 3.1311 | 3.1787 | 3.1449 | 3.1704 | 3.191 | 3.1169 | 3.1997 | 3.3325 | 3.3686 | 3.3094 | 3.2863 | 3.348 | 3.1025 | 3.1276 | 3.1101 | 3.1893 | 3.115 | 3.1115 | 3.2288 | 3.229 | 3.1794 | 3.1208 | 3.1119 | 3.1241 | 3.143 | 3.1511 | 3.1604 |  | 3.315 | 3.1682 | 3.204 | 3.1238 | 3.1197 |  |  | 3.2936 | 3.3346 | 2.8993 | 3.143 | 3.1497 | 3.1694
2025-06-30 | 2.5549 | 2.5307 | 2.5356 | 2.5206 | 2.5169 | 2.5243 | 2.5356 | 2.5431 | 2.5204 | 2.5312 | 2.588 | 2.5693 | 2.5506 | 2.5904 | 2.5243 | 2.5206 | 2.5094 | 2.4944 | 2.5238 | 2.5134 | 2.5243 | 2.5318 | 2.5203 | 2.5402 | 2.5341 | 2.5099 | 2.5411 | 2.5135 | 2.5235 | 2.5335 | 2.5268 | 2.5069 | 2.5511 | 2.5826 | 2.4794 | 2.4891 | 2.5206 | 2.4869 | 2.4419 | 2.5169 | 2.5206 | 2.4569 | 2.573 | 2.5318 | 2.5618 | 2.5206 | 2.3578 | 2.5311 | 2.3766 | 2.3694 | 2.4869 | 2.5393 | 2.5002 | 2.5435 | 2.4996 | 2.5402 | 2.5468 | 2.5468 | 2.5169 | 2.5501 | 2.5094 | 2.5694 | 2.5206 | 2.6082 | 2.5134 | 2.503 | 2.5169 | 2.5376 | 2.4794 | 2.4869 | 2.5243 | 2.5131 | 2.5581 | 2.5431 | 2.5561 | 2.5002 | 2.5368 | 2.5056 | 2.527 | 2.5272 | 2.5019 | 2.5206 | 2.4831 | 2.5056 | 2.5243 | 2.4532 | 2.5506 | 2.4532 | 2.4569 | 2.4944 | 2.4493 | 2.4996 | 2.4981 | 2.3745 | 2.5169 | 2.4794 | 0.1779 | 2.5318 | 2.5581 | 2.5169 | 2.4637 | 2.5644 | 2.464 | 2.4981 | 2.5135 | 2.427 | 2.5412 | 2.4724 | 2.5131 | 2.5169 | 2.5134 | 2.5687 | 2.5169 | 2.5235 | 2.5169 | 2.5206 | 2.5159 | 2.437 | 2.5135 | 2.5206 | 2.4517 | 2.3571 | 2.4203 | 2.5019 | 2.5056 | 2.5102 | 2.5243 | 2.5618 | 2.4003 | 2.5668 | 2.5549 | 2.5756 | 2.5549 | 2.5005 | 2.5245 | 2.521 | 2.486 | 2.549 | 2.5276 | 2.5543 | 2.4844 | 2.4719 | 2.5581 | 2.4512 | 2.5543 | 2.4588 | 2.491 | 2.5303 | 2.5549 | 2.5376 | 2.5545 | 2.5401 | 2.5342 | 2.5442 | 2.5045 | 2.5618 | 2.5094 | 2.5655 | 2.5038 | 2.5367 | 2.4815 | 2.4583 | 2.5387 | 2.4478 | 2.4613 | 2.4582 | 2.553 | 2.3603 | 2.4659 | 2.4764 | 2.5382 | 2.4691 | 2.4882 | 2.4291 | 2.4882 | 2.472 | 2.4773 | 2.4803 | 2.4377 | 2.4659 | 2.5315 | 2.4613 | 2.4377 | 2.4469 | 2.486 | 2.4781 | 2.5164 | 2.5236 | 2.3455 | 2.451 | 2.4879 | 2.4432 | 2.4848 | 2.4697 | 2.4811 | 2.4939 | 2.4727 | 2.5 |  |  | 0 | 2.4355 | 2.4242 |  | 2.488 | 2.5543 | 2.4464 | 2.4494 | 2.5655 | 2.4981 | 2.5019 | 2.4648 | 2.5094 | 2.4588 | 2.4906 | 2.4757 | 2.5268 | 2.5768 | 2.6288 | 2.5661 | 2.581 | 2.5956 | 2.4242 | 2.4812 | 2.5312 | 2.5335 | 2.5307 | 2.4927 | 2.5636 | 2.5549 | 2.5268 | 2.5135 | 2.4825 | 2.4387 | 2.4981 | 2.4916 | 2.4727 |  | 2.6436 | 2.4695 | 2.5075 | 2.4729 | 2.4631 |  |  | 2.6708 | 2.6567 | 2.3469 | 2.4709 | 2.4917 | 2.4974
2025-07-01
2025-07-02
2025-07-03
2025-07-04
2025-07-05
2025-07-06
2025-07-07
2025-07-08
2025-07-09
2025-07-10
2025-07-11
2025-07-12
2025-07-13
2025-07-14
2025-07-15
2025-07-16
2025-07-17
2025-07-18
Formulas:
Date = [Date, row above]+1

## Inv_SY
| 289.25 | 289.25 | 267 | 267 | 289.25 | 267 | 267 | 267 | 278.125 | 278.125 | 267 | 267 | 267 | 244.75 | 267 | 267 | 267 | 267 | 289.25 | 289.25 | 267 | 267 | 289.25 | 300.375 | 289.25 | 289.25 | 289.25 | 300.375 | 300.375 | 300.375 | 300.375 | 300.375 | 254.4 | 334.55 | 267 | 298.9 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 289.25 | 267 | 278.125 | 278.125 | 267 | 267 | 300.375 | 300.375 | 289.25 | 300.375 | 300.375 | 267 | 300.375 | 300.375 | 267 | 298.9 | 267 | 239.25 | 289.25 | 289.25 | 289.25 | 289.25 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 300.375 | 300.375 | 267 | 267 | 289.25 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 278.125 | 289.25 | 267 | 267 | 300.375 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 267 | 300.375 | 298.9 | 267 | 300.375 | 289.25 | 289.25 | 300.375 | 300.375 | 267 | 267 | 298.9 | 300.375 | 300.375 | 267 | 267 | 300.375 | 300.375 | 267 | 267 | 300.375 | 267 | 267 | 300.375 | 300.375 | 289.25 | 289.25 | 289.25 | 244.75 | 286 | 286 | 286 | 286 | 278.125 | 267 | 289.25 | 289.25 | 267 | 289.25 | 267 | 289.25 | 267 | 244.75 | 289.25 | 289.25 | 289.25 | 267 | 300.375 | 267 | 267 | 267 | 267 | 267 | 264 | 264 | 297 | 264 | 297 | 297 | 297 | 275 | 264 | 297 | 264 | 275 | 275 | 275 | 297 | 275 | 297 | 264 | 264 | 264 | 297 | 264 | 286 | 297 | 297 | 275 | 286 | 297 | 275 | 275 | 275 | 286 | 264 | 264 | 264 | 264 | 264 | 264 | 220 | 264 | 0 | 0 | 257.4 | 190.35 | 270.6 | 0 | 292.6 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 267 | 300.375 | 300.375 | 223.3 | 223.3 | 191.4 | 159.5 | 207.9 | 239.8 | 278.125 | 300.375 | 289.25 | 289.25 | 278.125 | 289.25 | 300.38 | 300.375 | 257.4 | 277.2 | 257.4 | 267.3 | 247.5 | 0 | 353.2 | 287.1 | 100.5 | 267.3 | 257.4 | 0 | 0 | 239.25 | 255.2 | 291.45 | 257.4 | 241.2 | 67049.755
Date | BLK1_INV1 | BLK1_INV2 | BLK1_INV3 | BLK1_INV4 | BLK1_INV5 | BLK1_INV6 | BLK1_INV7 | BLK1_INV8 | BLK1_INV9 | BLK1_INV10 | BLK1_INV11 | BLK1_INV12 | BLK1_INV13 | BLK1_INV14 | BLK1_INV15 | BLK1_INV16 | BLK1_INV17 | BLK1_INV18 | BLK1_INV19 | BLK1_INV20 | BLK1_INV21 | BLK1_INV22 | BLK1_INV23 | BLK1_INV24 | BLK1_INV25 | BLK1_INV26 | BLK1_INV27 | BLK1_INV28 | BLK1_INV29 | BLK1_INV30 | BLK1_INV31 | BLK1_INV32 | BLK2_INV1 | BLK2_INV2 | BLK2_INV3 | BLK2_INV4 | BLK2_INV5 | BLK2_INV6 | BLK2_INV7 | BLK2_INV8 | BLK2_INV9 | BLK2_INV10 | BLK2_INV11 | BLK2_INV12 | BLK2_INV13 | BLK2_INV14 | BLK2_INV15 | BLK2_INV16 | BLK2_INV17 | BLK2_INV18 | BLK2_INV19 | BLK2_INV20 | BLK2_INV21 | BLK2_INV22 | BLK2_INV23 | BLK2_INV24 | BLK2_INV25 | BLK2_INV26 | BLK2_INV27 | BLK2_INV28 | BLK2_INV29 | BLK2_INV30 | BLK2_INV31 | BLK2_INV32 | BLK3_INV1 | BLK3_INV2 | BLK3_INV3 | BLK3_INV4 | BLK3_INV5 | BLK3_INV6 | BLK3_INV7 | BLK3_INV8 | BLK3_INV9 | BLK3_INV10 | BLK3_INV11 | BLK3_INV12 | BLK3_INV13 | BLK3_INV14 | BLK3_INV15 | BLK3_INV16 | BLK3_INV17 | BLK3_INV18 | BLK3_INV19 | BLK3_INV20 | BLK3_INV21 | BLK3_INV22 | BLK3_INV23 | BLK3_INV24 | BLK3_INV25 | BLK3_INV26 | BLK3_INV27 | BLK3_INV28 | BLK3_INV29 | BLK3_INV30 | BLK3_INV31 | BLK4_INV1 | BLK4_INV2 | BLK4_INV3 | BLK4_INV4 | BLK4_INV5 | BLK4_INV6 | BLK4_INV7 | BLK4_INV8 | BLK4_INV9 | BLK4_INV10 | BLK4_INV11 | BLK4_INV12 | BLK4_INV13 | BLK4_INV14 | BLK4_INV15 | BLK4_INV16 | BLK4_INV17 | BLK4_INV18 | BLK4_INV19 | BLK4_INV20 | BLK4_INV21 | BLK4_INV22 | BLK4_INV23 | BLK4_INV24 | BLK4_INV25 | BLK4_INV26 | BLK4_INV27 | BLK4_INV28 | BLK4_INV29 | BLK4_INV30 | BLK4_INV31 | BLK5_INV1 | BLK5_INV2 | BLK5_INV3 | BLK5_INV4 | BLK5_INV5 | BLK5_INV6 | BLK5_INV7 | BLK5_INV8 | BLK5_INV9 | BLK5_INV10 | BLK5_INV11 | BLK5_INV12 | BLK5_INV13 | BLK5_INV14 | BLK5_INV15 | BLK5_INV16 | BLK5_INV17 | BLK5_INV18 | BLK5_INV19 | BLK5_INV20 | BLK5_INV21 | BLK5_INV22 | BLK5_INV23 | BLK5_INV24 | BLK5_INV25 | BLK5_INV26 | BLK5_INV27 | BLK5_INV28 | BLK5_INV29 | BLK5_INV30 | BLK5_INV31 | BLK5_INV32 | BLK6_INV1 | BLK6_INV2 | BLK6_INV3 | BLK6_INV4 | BLK6_INV5 | BLK6_INV6 | BLK6_INV7 | BLK6_INV8 | BLK6_INV9 | BLK6_INV10 | BLK6_INV11 | BLK6_INV12 | BLK6_INV13 | BLK6_INV14 | BLK6_INV15 | BLK6_INV16 | BLK6_INV17 | BLK6_INV18 | BLK6_INV19 | BLK6_INV20 | BLK6_INV21 | BLK6_INV22 | BLK6_INV23 | BLK6_INV24 | BLK6_INV25 | BLK6_INV26 | BLK6_INV27 | BLK6_INV28 | BLK6_INV29 | BLK6_INV30 | BLK6_INV31 | BLK6_INV32 | BLK7_INV1 | BLK7_INV2 | BLK7_INV3 | BLK7_INV4 | BLK7_INV5 | BLK7_INV6 | BLK7_INV7 | BLK7_INV8 | BLK7_INV9 | BLK7_INV10 | BLK7_INV11 | BLK7_INV12 | BLK7_INV13 | BLK7_INV14 | BLK7_INV15 | BLK7_INV16 | BLK7_INV17 | BLK7_INV18 | BLK7_INV19 | BLK7_INV20 | BLK7_INV21 | BLK7_INV22 | BLK7_INV23 | BLK7_INV24 | BLK7_INV25 | BLK7_INV26 | BLK7_INV27 | BLK7_INV28 | BLK7_INV29 | BLK7_INV30 | BLK7_INV31 | BLK7_INV32 | BLK8_INV1 | BLK8_INV2 | BLK8_INV3 | BLK8_INV4 | BLK8_INV5 | BLK8_INV6 | BLK8_INV7 | BLK8_INV8 | BLK8_INV9 | BLK8_INV10 | BLK8_INV11 | BLK8_INV12 | BLK8_INV13 | BLK8_INV14 | BLK8_INV15 | BLK8_INV16 | BLK8_INV17 | BLK8_INV18 | BLK8_INV19 | BLK8_INV20 | BLK8_INV21 | BLK8_INV22 | BLK8_INV23 | BLK8_INV24 | BLK8_INV25 | BLK8_INV26 | BLK8_INV27 | BLK8_INV28
2025-05-30 | -0.4601% | -0.8185% | 4.557% | 0.5478% | -2.344% | 0.322% | 0.07823% | 0.3852% | -0.3967% | 0.5221% | 2.056% | 1.559% | 0.1685% | 2.625% | -0.05721% | -0.5087% | -1.99% | -0.6532% | -2.619% | -0.7435% | 0.3491% | 0.295% | 1.174% | 0.01101% | 0.7569% | -0.05166% | -0.05166% | -1.233% | -1.121% | 0.5729% | 1.095% | -0.6231% | -2.338% | -1.939% | -1.999% | -0.6328% | 1.442% | -1.087% | 0.4214% | 2.02% | 0.09629% | -0.9512% | 0.6742% | -1.177% | 0.5026% | 0.3582% | 0.8319% | 2.995% | -1.125% | -2.807% | -1.601% | -0.2468% | 1.913% | 0.316% | -0.9185% | 0.7495% | 0.5247% | 0.9812% | -0.4224% | -2.991% | 1.686% | 2.344% | -0.2649% | 8.35% | -0.2434% | -0.8352% | 0.4735% | -1.927% | -0.9873% | -1.204% | -0.5268% | -0.8428% | 1.135% | -0.5719% | 1.713% | -0.3743% | 1.592% | 0.611% | -1.339% | -1.427% | 0.5388% | 0.6381% | -1.023% | 0.3582% | 0.2498% | -0.2378% | 0.5207% | -0.4455% | -0.9783% | -1.963% | -0.9429% | -1.185% | 1.505% | 0.7284% | -0.3823% | -1.845% | -1.385% | 0.4394% | -0.3371% | -0.2739% | 2.598% | -0.003036% | 2.128% | 0.2769% | 2.042% | 0.9541% | 5.485% | -0.6247% | 0.909% | -1.297% | 0.2567% | -0.9352% | 0.3963% | -0.1575% | -0.03013% | -2.333% | -0.9635% | 0.04312% | -0.5348% | 0.7735% | 1.911% | -0.1897% | 3.503% | 0.5207% | 1.243% | 1.673% | -2.378% | -2.622% | 1.038% | -0.1816% | -1.994% | 0.3401% | -0.6018% | 0.7243% | 5.788% | -1.866% | 2.028% | -1.091% | 2.074% | 0.8277% | -1.919% | -2.294% | 0.8548% | 1.157% | -2.486% | -2.652% | -0.1656% | 1.493% | -0.3601% | 0.7569% | 1.415% | 0.9993% | 3.021% | 1.821% | 0.295% | -0.9241% | -0.5358% | -1.764% | -2.173% | -1.406% | -1.686% | -2.785% | -1.304% | -2.489% | -2.928% | -1.676% | -2.127% | -2.311% | -2.785% | -2.553% | -2.842% | -1.676% | -1.945% | 2.497% | -1.247% | -2.848% | -2.364% | -1.78% | -1.491% | -1.479% | -0.5682% | -2.489% | -2.79% | -1.658% | -2.676% | -0.9225% | -2.526% | -1.834% | -2.816% | -2.263% | 0.07392% | -1.46% | -1.323% | 1.544% | 0.9598% | 1.736% | 2.072% | 3.563% |  |  | -5.565% | 0.3277% | -1.565% |  | -0.8664% | -3.452% | 0.4575% | -2.378% | -0.03916% | 0.1053% | 1.767% | 1.261% | 1.505% | 3.266% | 0.8638% | 1.929% | 0.8458% | 2.724% | 10.67% | 7.603% | 8.33% | 9.454% | -1.972% | -1.299% | -0.3967% | -0.2218% | -2.219% | 3.941% | -0.1887% | -2.069% | -0.912% | 0.4525% | 2.228% | -1.317% | 1.413% | -1.883% | 0.1214% |  | 0.6906% | -0.01698% | 4.956% | -2.74% | -1.575% |  |  | 8.935% | 5.972% | -8.896% | -2.249% | -0.3422%
2025-05-31 | -1.079% | -7.567% | 0.03643% | -0.1033% | -7.751% | -0.6025% | -0.4128% | -0.3529% | -1.147% | -0.3613% | 1.244% | 0.7752% | -0.6524% | 2.051% | -0.7223% | -1.052% | -0.4628% | -1.241% | -1.576% | -1.263% | 0.6354% | 2.142% | 1.262% | 1.257% | 1.281% | -0.3414% | -1.3% | -1.539% | 0.2361% | -1.69% | -0.4472% | -0.8377% | -1.002% | -1.645% | -1.301% | -1.204% | 0.4757% | -2.09% | -0.5726% | 1.244% | -1.152% | -1.581% | -1.182% | -2.609% | 0.8551% | -1.241% | 1.059% | -0.7922% | -0.3326% | -1.032% | -9.258% | 0.895% | 3.049% | 1.558% | -1.383% | 0.1296% | 0.03199% | 0.1462% | -1.228% | -10.42% | 0.6654% | 1.266% | 0.3759% | 7.149% | -0.09259% | -0.8022% | 0.7184% | -2.028% | -0.9719% | -0.8921% | -0.283% | -0.7323% | 1.544% | -0.5726% | 2.756% | 0.6354% | 2.597% | 1.334% | -0.7523% | -2.046% | 0.8651% | 1.125% | -0.952% | 0.6454% | 0.7952% | 1.304% | 0.8551% | -0.2731% | -0.942% | -1.97% | -0.9555% | -1.834% | 1.664% | 1.035% | -0.2786% | -1.581% | -0.9619% | 0.8251% | 0.01646% | 0.1662% | 3.051% | 0.3359% | 2.652% | 0.5955% | 2.783% | 1.045% | -0.6513% | -0.2859% | 1.155% | -2.089% | 0.1839% | -1.143% | -1.06% | -0.1366% | 0.2561% | -0.4128% | -0.7586% | -0.3141% | -0.5537% | 0.4358% | 1.853% | -1.21% | -0.2431% | 0.4557% | 1.274% | 1.603% | -0.2731% | -1.451% | 1.159% | -0.5537% | -0.8391% | -0.08338% | -1.005% | 0.3305% | -1.259% | -2.08% | 1.63% | 2.571% | 1.642% | 0.5556% | -2.35% | -2.249% | 0.5656% | 0.9856% | -2.819% | -4.59% | -0.1133% | 1.594% | -0.3506% | 0.7829% | 1.603% | 1.135% | 3.324% | 2.063% | 0.4458% | -0.7623% | 0.3859% | -0.3629% | -0.08893% | -0.9573% | 0.6302% | -1.795% | 0.4776% | 1.016% | 0.5315% | 0.3735% | -0.8967% | 0.3789% | 0.113% | -0.01422% | 0.5092% | 0.3057% | 0.9264% | 0.01486% | -8.318% | 0.2241% | -0.08893% | -0.8967% | 1.384% | -0.2909% | 1.052% | 0.1814% | 0.8007% | -0.2081% | 0.8097% | -9.009% | -0.2081% | -4.153% | -0.5086% | 0.614% | -0.5534% | -0.927% | 0.113% | 1.214% | 0.8299% | 1.153% | 1.888% | 3.162% |  |  | -6.123% | -0.5023% | -2.289% |  | -1.227% | -2.09% | 0.9649% | -2.14% | 0.1263% | 0.5656% | 2.163% | 1.724% | 2.103% | 3.191% | 1.234% | 2.233% | 1.434% | 3.28% | 10.3% | 7.318% | 7.837% | 9.651% | -1.375% | -2.256% | -0.8501% | -1.521% | -1.705% | 3.4% | -1.138% | -2.185% | -2.009% | -1.264% | -1.618% | -1.827% | -2.498% | -1.173% | -0.2673% |  | 0.3482% | -0.8671% | 9.835% | -0.734% | -2.778% |  |  | 14.16% | 8.652% | -3.627% | -1.949% | -0.4253%
2025-06-01 | -0.7287% | 0.2586% | -0.8824% | 0.5147% | 0.1982% | 0.22% | 0.5365% | -0.4021% | -0.01663% | 0.5282% | 2.468% | 1.966% | 0.1873% | 2.746% | 0.09994% | 0.5802% | -4.648% | -0.675% | -0.4668% | -0.1847% | 0.482% | 0.4383% | 1.518% | 0.5135% | 1.448% | 0.4803% | -0.3862% | -0.8739% | 0.9598% | -0.6993% | 0.0963% | 0.008984% | -0.8876% | -0.747% | -1.526% | 0.6098% | 1.028% | -1.657% | 0.22% | 1.683% | -0.3367% | -0.9697% | 0.482% | -9.178% | 0.1982% | 0.602% | 0.2989% | -0.5113% | -0.8025% | -2.479% | 0.04537% | 0.2964% | 1.872% | 0.3971% | -0.4366% | 0.9113% | 1.144% | 1.235% | -0.2142% | 1.037% | 0.9731% | 2.023% | 0.2855% | 8.677% | -0.4668% | -1.202% | 0.3997% | -2.159% | -1.123% | -1.646% | -0.6968% | -1.133% | 1.246% | -0.4676% | 1.969% | -0.02982% | 1.435% | -0.009207% | -1.112% | -0.7287% | 0.4165% | 0.6457% | -0.7623% | 0.5474% | -0.5113% | -0.293% | 0.4165% | -0.4458% | -1.188% | 0.07811% | -1.222% | -0.1746% | 1.486% | 0.6675% | -0.7478% | -1.756% | -1.384% | -0.04195% | -0.7405% | -0.8387% | 1.879% | -0.8278% | 1.268% | -0.6095% | 1.649% | -0.3694% | 5.762% | -0.8332% | 0.1654% | -1.563% | -1.081% | -0.9403% | -0.1657% | -0.5925% | -0.5331% | -0.0747% | -1.038% | -1.272% | -1.563% | -0.424% | 1.181% | -1.126% | -0.5052% | -0.5768% | 0.02354% | -0.8933% | -1.614% | -0.6859% | -0.1365% | -1.165% | -8.598% | -0.3056% | -0.6884% | 0.4482% | 5.566% | 6.116% | 5.138% | 5.82% | 1.953% | 1.126% | 4.984% | 4.44% | 0.5474% | 1.125% | -3.087% | -4.467% | -0.2384% | 1.234% | -1.081% | 0.2183% | 0.6213% | -0.424% | 0.9695% | -0.05287% | 0.5911% | -0.5004% | -0.7187% | 0.1436% | -2.03% | -1.622% | 0.8216% | -1.5% | 1.195% | 1.018% | 0.6352% | -2.558% | -1.809% | 0.2329% | -2.251% | -2.494% | -3.406% | -2.96% | 1.126% | -2.992% | 0.2329% | -1.633% | -2.151% | -1.677% | 0.5175% | -1.964% | -2.423% | 0.03666% | 0.9001% | -2.886% | -1.537% | 0.5175% | -2.462% | -2.134% | -2.356% | -1.72% | -0.4846% | 0.5861% | 0.1777% | 1.182% | 0.2108% | -25.32% | 1.893% | 2.551% |  |  | -7.058% | -4.818% | -2.244% |  | -1.059% | -4.168% | 0.1982% | -2.585% | -0.2821% | -0.1729% | 0.995% | 0.5147% | 0.984% | 2.185% | 0.4929% | 1.53% | 0.6493% | 2.532% | 10.89% | 8.035% | 8.196% | 9.847% | 0.5623% | -1.756% | -1.148% | -1.252% | -0.89% | -3.036% | -1.976% | -0.2854% | -1.941% | 8.304% | -2.53% | -2.28% | -1.59% | 1.034% | 2.264% |  | 2.152% | -2.036% | 23.09% | -2.106% | -1.114% |  |  | 10.43% | 8.588% | -8.837% | -2.983% | -1.493%
2025-06-02 | -9.274% | -8.749% | -5.105% | -1.145% | -2.301% | -2.031% | -2.243% | -10.13% | -2.74% | -2.204% | -0.3645% | -0.7595% | -2.33% | 0.1164% | -2.446% | -3.053% | -7.205% | -3.197% | -2.915% | -2.853% | -2.099% | -2.07% | -1.225% | -1.971% | -1.172% | -2.097% | -2.737% | -3.153% | -1.226% | -3.222% | -1.038% | -1.894% | 1.648% | -11.22% | 1.187% | 1.809% | 1.553% | -1.289% | 0.493% | 1.765% | 0.02091% | -0.7113% | 0.917% | 0.3196% | 0.4256% | 1.071% | 0.5716% | -0.2007% | -0.2616% | -2.084% | 0.3485% | 0.6279% | 2.337% | 0.8292% | -0.06877% | 2.688% | 1.489% | 1.582% | 0.1526% | 1.566% | 1.235% | 2.695% | -0.07544% | 9.794% | 3.773% | 3.275% | 4.058% | 1.532% | 3.017% | 2.863% | 3.268% | 2.777% | 4.443% | 2.738% | 3.416% | 1.66% | 3.69% | 2.728% | 1.823% | 1.541% | -1.155% | 3.701% | 2.256% | 3.827% | 2.16% | 2.381% | 3.21% | 2.189% | 2.401% | 1.36% | 2.486% | 3.888% | 4.357% | 3.615% | 3.03% | 1.717% | 1.582% | 3.894% | 2.343% | 3.094% | 5.773% | 2.651% | 4.742% | 2.516% | 4.109% | 3.836% | 8.34% | 2.248% | 4.106% | 1.352% | 3.231% | 1.434% | 2.439% | 2.491% | 3.412% | -1.01% | 1.662% | 2.765% | 2.662% | 3.827% | 4.954% | -1.663% | -1.997% | 3.393% | 4.376% | 4.272% | -12.98% | -11.58% | -1.894% | -3.051% | -10.29% | -2.372% | -2.657% | -1.397% | 3.891% | -3.287% | 0.2843% | -8.135% | 1.098% | -0.2874% | -3.804% | -4.08% | -0.9426% | -0.3978% | -4.026% | -5.61% | -1.771% | -0.4827% | -2.853% | -1.563% | -0.8959% | -1.8% | -0.04439% | -1.28% | -3.072% | -3.168% | -2.638% | -3.033% | -6.424% | -7.973% | -5.569% | -7.32% | -4.712% | -3.932% | -4.582% | -9.671% | -6.979% | -3.698% | -6.394% | -9.325% | -9.671% | -9.531% | -5.578% | -7.192% | -3.932% | -7.544% | -6.726% | -7.106% | -4.599% | -6.93% | -3.691% | -4.625% | -3.69% | -9.147% | -4.015% | -4.045% | -6.444% | -6.35% | -5.405% | -3.835% | 2.746% | 2.346% | 2.824% | 4.159% | 3.691% | 3.282% | 5.24% | 5.611% |  |  | -4.044% | -2.18% | 0.7722% |  | 0.5983% | -1.79% | 3.605% | 3.2% | 2.988% | 3.172% | 4.357% | 4.029% | 4.424% | 5.542% | 3.711% | 4.704% | 7.098% | 4.632% | 12.9% | 10.11% | 10.66% | 12% | 4.09% | 3.149% | 3.531% | 2.062% | -0.2111% | -0.2911% | 2.254% | 0.9007% | 0.3496% | 1.3% | 0.783% | 2.15% | -0.4563% | 1.275% | 2.434% |  | 1.977% | -1.668% | 23.97% | -1.727% | -0.946% |  |  | 16.11% | 10.05% | -3.78% | 1.832% | -2.719%
2025-06-03 | -11.32% | -10.29% | -11.09% | 5.334% | 4.669% | 5.183% | 5.194% | -0.4403% | 4.461% | 5.102% | 6.939% | 6.454% | 4.644% | 7.271% | 4.634% | 4.127% | -0.5803% | 3.556% | 3.386% | 3.764% | 4.763% | 4.881% | 6.081% | 4.862% | 5.415% | 4.58% | 3.864% | 3.665% | 4.795% | 3.55% | 5.475% | 5.858% | -17.88% | -28.54% | -8.056% | -7.717% | -7.582% | -9.802% | -8.024% | -6.667% | -8.8% | -9.511% | -7.615% | -7.302% | -7.841% | -7.27% | -7.691% | -10.1% | -8.425% | -10.02% | -7.604% | -6.516% | -6.121% | -7.442% | -8.298% | -6.571% | -6.897% | -6.71% | -8.39% | -7.375% | -7.389% | -6.495% | -8.197% | 0.3837% | 5.574% | 5.067% | 5.833% | 3.466% | 5.625% | 5.603% | 6.777% | 6.239% | 8.544% | 5.431% | 5.839% | 3.818% | 6.854% | 6.282% | 5.571% | 3.685% | 2.888% | 7.639% | 6.4% | 7.973% | 6.67% | 7.014% | 7.639% | 6.831% | 6.105% | 5.064% | 4.657% | 3.963% | 8.242% | 7.865% | 5.255% | 7.241% | 5.592% | 7.381% | 5.851% | 6.594% | 9.158% | 6.336% | 8.059% | 5.98% | 6.327% | 7.176% | 9.985% | 4.677% | 7.294% | 2.928% | 5.932% | -2.262% | 4.268% | 5.226% | 7.014% | 0.6693% | 3.715% | 4.766% | 4.747% | 7.014% | 7.736% | 0.1223% | -1.343% | 6.734% | 7.844% | 6.48% | -12.51% | -11.97% | -12.04% | -13.25% | -16.53% | -12.93% | -13.4% | -11.98% | -7.718% | -13.8% | -10.73% | -18.49% | -10.74% | -11.67% | -14.28% | -24.16% | -12% | -11.54% | -15.5% | -13.2% | -12.73% | -20.91% | -13.33% | -12.35% | -11.71% | -12.25% | -10.94% | -11.84% | -9.942% | -12.25% | -11.61% | -11.51% | 1.922% | 1.268% | 0.2819% | 1.693% | -0.1055% | 0.6596% | -1.074% | 2.06% | 2.467% | 1.25% | 0.2553% | 1.506% | 1.924% | 1.6% | 0.1754% | 1.36% | 1.153% | 1.53% | 2.347% | 2.968% | 1.444% | 1.704% | 0.5184% | 0.863% | 0.4368% | 6.725% | -0.7286% | 1.202% | 0.983% | 2.887% | 1.611% | 0.4681% | 3.861% | 2.434% | -10.66% | 5.18% | 4.907% | -8.319% | 6.683% | 6.683% |  |  | -4.314% | 0.07618% | 2.083% |  | 2.104% | 0.4754% | 6.594% | 0.01214% | 6.206% | 6.368% | 7.618% | 7.37% | 7.704% | 7.585% | 7.176% | 7.725% | 5.695% | 7.476% | 13.66% | 11.6% | 11.92% | 12.72% | 0.192% | 1.893% | 4.936% | 3.684% | 2.134% | -0.04421% | 5.64% | 3.963% | 3.043% | -2.224% | -2.851% | 1.468% | -3.108% | 0.2442% | -2.567% |  | 3.409% | -2.171% | 14.79% | -1.208% | -1.331% |  |  | 20.57% | 12.06% | -3.226% | -1.465% | -0.881%
2025-06-04 | 0.6534% | 1.615% | -2.051% | 1.713% | 1.117% | 1.713% | 1.896% | -2.554% | 1.513% | 1.785% | 4.052% | 3.751% | 1.969% | 5.019% | 1.969% | 1.677% | -2.481% | 0.09605% | 1.067% | 1.033% | 1.75% | -1.832% | 3.454% | 2.359% | 2.104% | 1.539% | 0.7546% | 0.2473% | 2.058% | -0.1506% | 1.157% | 0.6697% | -1.093% | -5.88% | -3.038% | -1.372% | -0.909% | -2.59% | -1.686% | 0.1691% | -2.746% | -2.864% | -1.366% | -2.133% | -1.549% | -0.8085% | -1.109% | -2.133% | -2.285% | -2.189% | -1.119% | -2.243% | 0.7752% | -0.8572% | -1.599% | -0.08567% | 0.1742% | 0.5072% | -0.9385% | 0.426% | -0.6166% | 0.5053% | -2.316% | 1.275% | 0.4932% | -0.2153% | 1.1% | -1.447% | -0.03187% | -0.7628% | 0.1417% | -0.1872% | 1.869% | 0.3702% | 1.693% | -0.06943% | 1.596% | 0.4615% | -0.6623% | 1.033% | -2.133% | 1.211% | 0.1783% | 1.476% | 0.1417% | 0.3428% | 1.156% | 0.3519% | -0.6715% | -1.731% | -0.2939% | 2.433% | 2.463% | 1.348% | 0.0524% | -1.457% | -1.466% | 1.275% | -0.5984% | 0.16% | 2.929% | -0.2786% | 1.448% | -1.366% | 1.295% | 1.22% | 6.534% | -0.09049% | 1.43% | -0.03694% | 0.9992% | -0.6117% | 1.043% | 0.5559% | 0.5712% | 0.5529% | -0.3435% | 1.271% | 0.5478% | 1.083% | 2.417% | 1.051% | 0.8321% | 0.9549% | 1.649% | 2.465% | -1.119% | -0.5161% | 0.1986% | -1.312% | -4.432% | -0.7214% | -1.185% | 0.05535% | 5.388% | -2.161% | 1.371% | -5.394% | 1.943% | 0.4524% | -2.391% | -2.695% | -0.3243% | 0.6281% | -2.8% | 2.18% | -0.9456% | 0.5438% | -1.076% | -0.0888% | 0.8305% | 0.04123% | 1.912% | 0.4798% | -1.366% | -2.261% | -1.457% | -5.203% | -1.631% | -1.169% | -1.332% | -0.9843% | -2.408% | -2.951% | -1.998% | -1.6% | -0.7071% | -2.31% | -0.4298% | -1.37% | -1.751% | -1.583% | -2.942% | -1.574% | -2.647% | -0.245% | -0.6978% | -0.05097% | -2.261% | -1.169% | -1.947% | -2.4% | -1.743% | -2.017% | -2.263% | -2.154% | -2.009% | -1.583% | -1.361% | -2.638% | -0.6147% | 0.09688% | -0.3744% | 0.753% | 0.5866% | 1.132% | 2.119% | 3.035% |  |  | -6.947% | 0.1082% | -1.326% |  | -1.583% | -2.124% | 0.6808% | -10.71% | -0.4979% | 0.2971% | 1.001% | 0.891% | 1.147% | 2.81% | 0.9458% | 1.403% | 0.7671% | 2.611% | 11.51% | 8.093% | 8.456% | 9.804% | -0.01107% | -0.1785% | -0.6272% | -1.19% | -1.691% | -1.388% | 0.2148% | -0.9406% | -1.881% | -2.457% | 0.0476% | -1.149% | -2.18% | -2.234% | -1.313% |  | 0.5042% | -0.7512% | 8.555% | -1.504% | -2.18% |  |  | 14.53% | 8.988% | -4.568% | -1.023% | -0.4544%
2025-06-05 | -7.371% | -2.072% | -2.09% | -2.09% | -2.508% | -1.933% | -1.461% | -3.427% | -2.307% | -1.93% | 0.5049% | 0.03307% | -1.697% | 0.891% | -1.54% | -2.169% | -6.337% | -2.798% | -1.854% | -1.927% | -1.382% | -5.236% | -4.177% | -1.015% | -0.7655% | -1.637% | -2.29% | -2.763% | -1.225% | -3.392% | -12.34% | -9.893% | 0.1178% | -9.056% | -4.685% | -0.1055% | -1.933% | -2.483% | -1.147% | 0.5049% | -1.382% | -2.169% | -0.832% | -10.51% | -0.9893% | -0.04557% | -0.6929% | -5.865% | -1.628% | -3.289% | -0.832% | -4.607% | 1.082% | -0.2465% | -1.419% | 0.103% | 0.5224% | 0.6622% | -0.7359% | 0.6622% | -4.607% | -3.969% | -1.382% | -15.92% | 3.155% | 1.267% | 4.026% | -4.831% | 3.1% | 2.078% | 3.651% | 3.493% | 5.223% | 2.943% | 4.856% | 2.41% | 4.367% | 0.5049% | -1.461% | 1.412% | 3.729% | 3.336% | 2.55% | 8.526% | 3.257% | 2.314% | 4.437% | 3.729% | 3.415% | 2.864% | 2.6% | -2.217% | 6.01% | 5.459% | -7.377% | -9.011% | 1.134% | 3.572% | 2.078% | 2.628% | 5.381% | 2.471% | 4.201% | 1.685% | 3.039% | 3.887% | 7.513% | 1.51% | 3.651% | 0.7321% | 3.227% | -5.774% | 1.851% | 2.41% | 3.021% | -6.416% | 1.018% | 3.319% | 2.689% | 3.493% | 4.437% | -2.134% | -3.812% | 3.179% | 4.122% | -12.41% | -13.1% | -11.61% | -2.064% | -3.322% | -6.718% | -2.725% | -3.161% | -2.026% | 2.932% | -5.364% | -1.84% | -10.36% | -1.326% | -1.854% | -4.25% | -5.557% | -2.405% | -1.491% | -5.079% | -3.306% | -2.641% | -1.082% | -2.943% | -1.854% | -1.128% | -1.776% | -0.03683% | -1.304% | -3.113% | -3.978% | -1.382% | -3.82% | 4.192% | 1.011% | 3.079% | 0.5335% | 1.594% | -0.2442% | 2.442% | 3.079% | -1.137% | 0.9577% | 3.635% | -0.5863% | 1.17% | 3.69% | 0.2507% | 1.399% | 0.1093% | 2.761% | 3.874% | 1.249% | 1.735% | 5.385% | 2.638% | -0.1735% | 4.281% | 4.224% | 3.886% | 0.7456% | 4.224% | 4.224% | 0.7117% | 3.666% | 0.6926% | 1.567% | -0.7391% | 1.806% | 1.011% | 2.045% | 1.742% | 3.397% |  |  | -7.738% | -0.9416% | -1.919% |  | -2.906% | 2.078% | 3.808% | 0.8981% | 3.021% | 2.786% | 4.28% | 4.201% | 4.28% | 4.909% | 3.651% | 3.729% | 2.62% | 4.507% | 11.9% | 9.172% | -0.9365% | 8.608% | -2.537% | -0.8792% | 2.675% | 1.851% | 1.92% | -1.128% | -2.307% | -0.03952% | 1.152% | -2.693% | 0.3377% | -1.754% | -2.273% | 1.963% | 2.654% |  | 0.9164% | -0.7537% | 1.958% | 1.963% | 10.86% |  |  | 17.69% | -2.582% | -5.621% | -2.273% | -2.325%
2025-06-06 | -0.5549% | 1.687% | -2.14% | 1.778% | 0.8916% | 1.543% | 1.543% | -6.684% | 1.091% | 1.618% | 3.266% | 2.796% | 1.229% | 3.936% | 1.229% | 0.8374% | -3.785% | 0.05385% | 0.3853% | 0.3853% | 1.151% | -2.688% | -1.278% | 1.543% | 1.543% | 0.6023% | 0.02371% | -0.1986% | 1.125% | -0.5468% | -11.55% | -7.233% | 1.309% | -1.327% | -3.55% | 1.204% | 1.386% | -1.043% | 0.4456% | 1.934% | 0.1322% | -0.573% | 0.759% | -9.583% | 0.3672% | 1.307% | 0.53% | -4.412% | -3.798% | -5.077% | 1.072% | -3.159% | 2.518% | 0.9853% | 0.09604% | 2.03% | 1.891% | 1.856% | 0.3585% | 1.473% | 1.621% | 2.254% | -0.6513% | -15.36% | 1.109% | 0.313% | 0.4577% | -7.57% | 0.8374% | -2.062% | -0.8864% | 0.9941% | 1.072% | 1.072% | -0.8951% | -3.402% | -2.288% | -2.062% | -5.431% | -5.401% | -5.274% | 0.1322% | 0.9941% | -5.274% | -0.7297% | 1.072% | -0.8864% | 1.307% | -2.453% | -2.375% | -2.143% | -6.268% | 1.151% | 1.464% | -8.904% | -9.74% | -2.062% | 1.464% | 0.2889% | 0.6807% | 3.423% | 0.524% | 2.561% | 0.3672% | 2.448% | 1.934% | 7.114% | 0.6438% | 1.856% | -1.034% | 1.759% | -0.4826% | 0.2889% | 0.9853% | 0.6807% | -8.8% | 0.2939% | 1.821% | 1.403% | 1.778% | 2.796% | -2.497% | -5.352% | 1.464% | 2.248% | -9.601% | -9.975% | -8.486% | 1.403% | 0.07996% | -3.376% | 0.8916% | 0.4577% | 1.628% | 7.158% | -0.8877% | 2.843% | -5.862% | 3.498% | 2.718% | -0.6272% | -2.074% | 2.169% | 2.627% | -0.573% | 4.002% | 1.151% | 2.397% | 0.6746% | 1.759% | 2.41% | 1.778% | 3.702% | 2.248% | 0.4456% | -0.573% | 1.856% | -0.1029% | 2.855% | -1.82% | 1.64% | -0.394% | 0.6537% | -1.318% | -0.5437% | 2.544% | -3.247% | -0.4732% | 1.27% | -1.868% | -0.955% | 1.936% | -1.53% | -0.955% | 0.09025% | 1.27% | 3.093% | -0.394% | -1.318% | 4.044% | 0.7946% | -1.318% | 2.837% | 4.066% | 2.55% | -0.6141% | 4.826% | 3.457% | -0.2704% | 3.794% | 1.825% | -0.4732% | -1.662% | 0.3984% | 0.5569% | 1.27% | 2.887% | 2.855% |  |  | -6.455% | 0.2296% | -0.7361% |  | -0.2635% | 2.091% | 1.934% | -0.3379% | 0.9941% | 1.464% | 2.091% | 1.856% | 2.091% | 3.501% | 1.934% | 2.091% | 1.403% | 3.423% | 11.67% | 9.048% | 6.893% | 2.303% | -1.59% | 0.498% | 0.7151% | 0.5675% | -0.2656% | 0.4577% | -1.466% | 0.6023% | -0.129% | -2.636% | 1.347% | -1.137% | -0.1969% | 0.8807% | 0.6678% |  | -0.6421% | 1.866% | 0.1228% | 0.7242% | -1.497% |  |  | 2.565% | -0.8121% | -8.842% | -4.261% | -3.901%
2025-06-07 | -0.8901% | 1.547% | -2.312% | 1.795% | 0.667% | 1.282% | 1.282% | -6.492% | 0.5397% | 1.033% | 3.042% | 2.382% | 0.9886% | 3.689% | 0.7685% | 0.4752% | -4.072% | -0.1849% | -0.1454% | 0.1931% | 1.135% | -2.972% | -1.229% | 1.437% | 1.615% | 0.4639% | -0.009984% | -0.1278% | 0.7848% | -0.519% | -14.6% | -7.168% | 4.913% | -1.784% | -4.145% | 0.4305% | 0.6219% | -1.505% | -0.03819% | 1.795% | -0.03819% | -1.138% | 0.5485% | -8.839% | 0.7685% | 1.355% | 0.8024% | -4.219% | -4.318% | -5.445% | 0.6952% | -3.485% | 2.415% | 0.9152% | -0.4839% | 1.828% | 1.502% | 1.429% | -0.1278% | 0.9804% | 1.209% | 1.675% | -0.03819% | -9.969% | -1.499% | -2.853% | -2.379% | -7.321% | -2.678% | -2.898% | -2.385% | -2.825% | -1.872% | -2.605% | -2.214% | -3.844% | -2.866% | -2.605% | -5.465% | -5.426% | -3.265% | 1.062% | -0.8449% | -4.072% | -1.358% | -1.578% | -2.605% | -1.432% | -2.312% | -2.532% | -2.488% | -0.9578% | -1.138% | -1.652% | -8.081% | -9.059% | -0.7716% | 1.282% | 0.1085% | 0.5485% | 3.189% | 0.4018% | 2.089% | -0.2582% | 1.763% | 1.355% | 4.892% | 0.2995% | 1.795% | -2.084% | 1.682% | -2.176% | -1.823% | 0.6545% | 1.062% | -8.326% | -0.1591% | 0.9804% | 0.3285% | 1.502% | 2.822% | -2.084% | -4.952% | 1.282% | 1.942% | -9.711% | -10.45% | -9.059% | 0.9804% | -0.4538% | -4.072% | 0.1254% | -0.009984% | 1.369% | 5.987% | -1.133% | 2.496% | -6.268% | 2.018% | 0.7685% | -1.296% | -3.666% | 1.575% | 1.615% | -1.652% | -0.687% | -0.2582% | 1.289% | -0.07768% | 0.8024% | 1.615% | 0.9152% | 2.48% | 1.429% | -0.03819% | -0.9916% | 1.942% | -0.4782% | 2.21% | -1.943% | 4.04% | 1.098% | 4.699% | 3.051% | -0.4434% | 6.667% | 1.098% | 3.051% | 9.628% | 0.4005% | 0.2581% | 5.243% | -0.4434% | -0.454% | -0.5753% | 3.694% | 4.436% | 1.098% | 3.051% | 4.584% | 1.195% | -1.235% | 3.051% | 4.174% | 2.838% | -0.9049% | 6.667% | 5.243% | 6.667% | 3.386% | 0.8752% | 0.1335% | -1.053% | 1.469% | 1.246% | 1.691% | 3.16% | 3.768% |  |  | -6.504% | 2.666% | -1.223% |  | -0.4855% | 1.575% | 1.282% | -1.578% | 0.7685% | 1.722% | 1.942% | 1.795% | 2.015% | 3.115% | 2.162% | 2.675% | 1.698% | 3.718% | 11.54% | 9.177% | 2.103% | 24% | 0.5927% | 9.585% | -0.02352% | -1.823% | -2.176% | -1.499% | -2.065% | 0.1931% | -0.9101% | -2.018% | -1.103% | -1.527% | 0.3427% | 1.974% | 2.695% |  | -1.066% | 1.421% | 1.318% | -2.421% | -1.331% |  |  | -1.948% | 0.1335% | -8.357% | -4.07% | -1.036%
2025-06-08 | -1.662% | 0.6127% | -1.715% | 0.8167% | -0.07372% | 0.5162% | 0.5688% | 0.8092% | -0.1655% | 0.3825% | -1.677% | 1.936% | 0.3059% | 3.016% | 0.381% | -0.09222% | -2.466% | -0.5655% | -0.2124% | -0.1777% | 0.7341% | -1.512% | -2.05% | 0.7525% | 1.237% | 0.01642% | -0.4412% | -0.7366% | 0.5521% | -1.09% | -6.172% | -3.748% | 0.2203% | -2.028% | -2.248% | 0.1961% | 0.4937% | -1.903% | 0.2007% | 1.343% | -0.558% | -1.429% | 0.4787% | -0.4077% | 1.08% | 1.313% | 0.9594% | -0.1223% | -0.4973% | -2.156% | 0.9594% | 1.005% | 2.782% | 1.287% | -0.8989% | 1.06% | 0.9127% | 1.035% | -0.3787% | 0.8192% | 0.8468% | 1.578% | -3.578% | 8.453% | 0.00255% | -0.6215% | 0.8% | -2.078% | -0.6706% | -0.002073% | 0.5763% | 0.1331% | 2.424% | -0.8584% | 1.661% | -0.5029% | 1.293% | 0.4411% | -0.7608% | -1.204% | 0.7416% | 1.155% | -0.1223% | 1.275% | 0.8994% | 1.125% | 1.395% | -5.576% | -0.295% | -1.474% | -0.8795% | -2.064% | 2.732% | 2.807% | -0.2758% | -5.26% | -1.279% | 0.7641% | -0.4979% | -0.06217% | 2.522% | -0.2124% | 1.613% | -0.7307% | 1.44% | 0.8618% | 5.353% | -0.6628% | 1.117% | -2.152% | 0.5573% | -2.66% | -1.685% | 0.1315% | 0.5162% | -4.607% | -0.3608% | 0.5855% | 0.004604% | 0.9519% | 2.041% | -0.4094% | 0.05802% | 0.5613% | 1.215% | 0.2583% | -10.26% | -8.701% | 0.9394% | -0.5363% | -2.854% | -0.06679% | -0.3719% | 1.033% | 6.314% | -1.021% | 2.261% | -5.811% | 2.157% | 0.9745% | -1.461% | -2.854% | 1.493% | 1.473% | -1.482% | -0.7533% | -0.265% | 1.156% | -0.4412% | 0.4255% | 1.41% | 0.7942% | 2.262% | 1.065% | -0.4528% | -1.377% | -0.5054% | 0.3134% | -0.3928% | -0.06609% | 0.2429% | -0.2864% | 0.4252% | -0.8984% | 0.04702% | 9.48% | -0.3624% | -0.2569% | 0.3973% | -1.868% | -1.584% | 1.334% | -2.526% | -2.16% | 0.513% | 0.3973% | 0.2378% | -0.02811% | 0.04027% | 0.6253% | -0.08129% | 0.513% | 1.053% | 2.508% | 1.062% | 1.053% | -1.576% | -2.328% | -2.087% | -1.933% | 0.4429% | 0.1998% | -7.6% | -0.37% | 0.5645% | -6.904% | 2.973% | 3.049% |  |  | -7.018% | -2.072% | -1.533% |  | 0.5918% | -2.609% | 0.7491% | -1.264% | 0.2533% | 0.5388% | 1.343% | 1.155% | 1.305% | 2.559% | 2.086% | 2.432% | 1.24% | 3.564% | 10.49% | 5.394% | 5.418% | 8.922% | -2.649% | -2.025% | -0.3314% | -0.8367% | -2.015% | -2.154% | 1.039% | -0.5314% | -1.304% | 0.8994% | 1.172% | 2.099% | 2.964% | 3.202% | 1.734% |  | 2.151% | -2.127% | -1.193% | -2.725% | -1.4% |  |  | 1.302% | 1.729% | -8.907% | -3.293% | 1.073%
2025-06-09 | -0.2371% | 0.6028% | -2.007% | 2.025% | 0.876% | 1.818% | 0.353% | 0.9744% | 0.1953% | 0.9623% | 2.336% | 1.84% | 0.316% | -0.6524% | 0.1903% | -0.187% | -0.409% | -0.5569% | -0.2439% | -0.05957% | 0.6341% | 0.8339% | -0.1347% | 0.7303% | 1.34% | 0.03604% | -0.4078% | -0.6375% | 0.7106% | -1.085% | -0.6309% | -1.262% | -0.3369% | -2.539% | -4.907% | -0.1075% | 0.2124% | -2.17% | -0.7049% | 0.8931% | 0.2864% | -1.926% | -0.04648% | -0.9416% | 0.5971% | 0.7747% | 0.5823% | -0.5347% | 0.1243% | -1.403% | 1.167% | 1.011% | 0.6908% | 1.138% | -0.3805% | 0.02668% | 0.7961% | 0.8783% | -0.2692% | 0.6645% | 0.7525% | 1.432% | 1.159% | 7.98% | 0.9443% | 0.316% | 1.702% | -1.801% | -1.06% | 0.0349% | 0.6193% | 0.2051% | 0.6859% | -1.489% | 1.454% | -0.5717% | 1.21% | 0.04969% | -0.9342% | -1.521% | 0.4418% | 0.8931% | -0.3868% | 0.8857% | 0.7007% | 1.026% | 1.145% | -3.679% | -0.4534% | -1.489% | -0.6499% | -2.272% | 0.538% | 1.677% | 0.5067% | -5.491% | -1.504% | 0.6563% | -0.7789% | -0.09827% | 0.316% | -0.298% | 0.242% | -0.8011% | 1.736% | 1.048% | -1.295% | -0.08769% | 1.115% | -2.459% | 0.8077% | -2.272% | -2.505% | -0.09169% | 0.3456% | -5.565% | -0.8543% | 0.704% | 0.2503% | 1.196% | 2.247% | -2.064% | -1.696% | 0.6933% | 1.389% | 1.947% | -2.525% | -1.09% | 0.5791% | -0.6572% | -4.212% | -0.2098% | -0.5103% | -1.298% | 0.42% | -1.535% | 2.464% | -4.256% | 0.9197% | -0.05388% | -1.5% | -2.853% | 1.603% | 2.72% | 0.05709% | 0.5414% | 0.8857% | 1.462% | -0.2371% | 0.4799% | 1.579% | 0.8191% | 0.4147% | 1.152% | -0.4534% | -1.526% | -0.5199% | -1.023% | -0.2275% | -0.3247% | 1.456% | -0.3771% | 1.855% | 0.4983% | 0.8308% | -0.5767% | -0.6315% | 2.36% | -0.1527% | -0.9215% | -0.0524% | -0.3972% | 1.21% | 0.08407% | -0.1734% | 0.2963% | -0.9832% | -0.22% | -0.1069% | -0.6091% | -1.279% | -0.4395% | 1.476% | -0.2032% | -0.6988% | -0.3065% | -0.2032% | 0.278% | -0.5408% | -0.906% | 0.7676% | 0.4085% | -1.754% | 0.03439% | 0.7601% | 1.508% | 2.991% | 3.095% |  |  | -6.525% | -2.301% | -2.179% |  | 0.3894% | -1.955% | 1.108% | -2.155% | 0.4122% | 0.4936% | 1.404% | 1.219% | 1.241% | 2.047% | 2.04% | 2.609% | 1.513% | 3.203% | 6.246% | 5.972% | 5.522% | 4.434% | -1.523% | -1.065% | -0.1669% | -0.8019% | -1.821% | -1.842% | 1.239% | -0.6059% | -1.177% | -1.295% | 0.7116% | -0.7958% | -1.905% | -0.5799% | 0.1591% |  | -0.1753% | -1.327% | -1.532% | -2.235% | -1.422% |  |  | 3.2% | 3.112% | -8.167% | -2.91% | -2.63%
2025-06-10 | -0.1367% | 2.122% | 2.458% | 2.16% | 1.538% | 2.368% | 1.868% | 2.264% | 1.362% | 1.956% | -1.093% | 0.3664% | 1.916% | 0.9988% | 1.812% | 1.374% | 1.131% | 0.7% | -0.2458% | 0.08784% | 1.652% | 1.993% | 0.986% | -1.902% | 1.249% | 0.01086% | -0.4896% | -0.7032% | 0.4583% | -1.148% | -1.086% | -1.377% | -0.3303% | -2.177% | -0.8221% | 0.923% | 0.5471% | -2.031% | -0.2313% | 1.145% | -0.9124% | 1.784% | 1.437% | -0.9611% | 1.061% | 1.235% | 0.8962% | -0.5788% | -0.02533% | -1.48% | 1.117% | 0.9085% | 2.775% | 1.113% | 0.4664% | 0.971% | -2.081% | -0.5371% | 0.9031% | 0.5818% | 0.7695% | 1.389% | 1.013% | 0.9162% | 1.121% | 0.415% | 0.2867% | -2.145% | -1.413% | 0.2204% | 0.7625% | 0.3316% | 1.138% | 1.2% | 0.7116% | -1.031% | 0.8969% | -0.7387% | -0.9819% | -0.2393% | 0.4706% | 0.8598% | -0.3495% | 0.9154% | 0.693% | 1.02% | 1.256% | 0.4984% | -0.2591% | -1.26% | -1.393% | -0.2971% | 0.2899% | -0.4607% | 0.7795% | -1.343% | -1.628% | 0.8112% | -1.079% | 0.1579% | -2.622% | -0.04368% | 1.756% | -0.3773% | -1.395% | 1.381% | 0.1556% | 0.2773% | 1.819% | -1.704% | 1.409% | -1.773% | -1.21% | 0.3038% | 1.089% | 2.973% | -1.517% | 0.9093% | -0.05449% | 0.9502% | 1.416% | -1.951% | -1.704% | 2.055% | 2.021% | 1.984% | -1.468% | 0.554% | 2.151% | 0.9587% | 1.172% | 1.653% | -0.4896% | -0.5934% | 1.095% | 0.239% | 1.031% | -0.001101% | 0.822% | 0.08838% | 0.2931% | -1.773% | 0.01192% | -0.2329% | 0.9919% | 1.076% | -0.05758% | 1.514% | -0.04047% | 0.6973% | 1.615% | 0.9988% | -0.1533% | -0.2939% | 1.068% | -0.975% | -0.9263% | -0.5788% | -1.516% | -1.719% | 1.287% | -0.8127% | 1.162% | 0.03158% | -0.1933% | -1.339% | -0.5315% | -0.2746% | -1.059% | -1.494% | -1.319% | -1.764% | 0.6689% | -2.358% | -0.5807% | -0.9533% | -0.5034% | -1.234% | -0.2496% | -0.7073% | -0.4553% | 0.219% | -0.3808% | -1.541% | -0.916% | 3.162% | -1.811% | -2.189% | -1.656% | -0.7408% | 0.9446% | 0.319% | -2.071% | -1.663% | 1.022% | 1.76% | -0.7804% | -0.8127% |  |  | -6.092% | -1.43% | -1.655% |  | 0.3055% | -1.927% | 1.082% | -0.3286% | 0.6583% | 0.9085% | 1.59% | -0.6761% | 1.416% | 0.8251% | -2.059% | 0.3942% | 0.971% | 0.2791% | 4.219% | 4.219% | 5.436% | 0.1833% | -1.718% | -1.552% | 1.83% | 0.5139% | -0.06613% | -1.837% | -0.1788% | 0.3701% | 0.2977% | -1.086% | -1.103% | -1.921% | -0.6485% | -0.4405% | -0.1983% |  | -1.297% | -2.071% | -0.0889% | -0.4405% | -1.391% |  |  | 1.816% | 2.019% | -26.56% | -0.7638% | -1.7%
2025-06-11 | -0.6418% | 1.695% | -2.125% | 1.702% | 1.025% | 0.5989% | 1.443% | 0.7469% | 0.9166% | 1.535% | 1.487% | 0.006751% | 1.554% | 4.011% | 1.628% | 1.235% | 1.124% | 0.9246% | 1.422% | 1.62% | 2.116% | 2.19% | -0.9219% | 0.7379% | 0.2396% | 1.463% | 1.032% | 0.7774% | 1.488% | 1.073% | 1.692% | 0.2839% | -0.5868% | -0.8394% | -1.192% | 0.2432% | -0.02286% | -1.844% | -0.763% | 0.5027% | -1.363% | -2.451% | -0.6668% | -1.548% | 0.1918% | 0.5619% | 0.2806% | -0.9777% | -0.3553% | -1.926% | 0.6433% | 0.4879% | 2.35% | 0.5405% | -0.2796% | -0.05164% | 1.85% | 0.7469% | 0.9945% | 0.07995% | 0.288% | 1.017% | 0.5175% | 1.033% | 0.9092% | 0.3558% | 1.661% | -1.216% | -0.6372% | -0.4078% | 0.2362% | -0.1709% | 1.924% | -1.548% | 0.07995% | 0.04705% | 0.2115% | 0.1252% | -1.407% | -2.015% | 0.1696% | 0.5471% | -0.8075% | 0.3472% | 0.1178% | 0.4731% | 0.7913% | -0.9629% | -0.8593% | -1.725% | -0.4193% | -2.213% | 0.7543% | 1.317% | 0.8938% | -1.511% | -2.317% | 0.6137% | -0.7853% | 1.309% | 0.8062% | 0.06597% | 1.554% | -1.792% | -2.269% | 1.798% | -1.565% | -0.08737% | 0.01415% | -1.493% | -0.8536% | -1.462% | -2.223% | 1.554% | -0.43% | 2.627% | 0.316% | 2.087% | -1.243% | 0.3102% | 0.3842% | -1.243% | -1.552% | 0.7543% | 0.4213% | 1.396% | -2.221% | 0.1252% | 1.824% | 0.4681% | 0.6427% | 0.957% | 0.8136% | 2.202% | 0.6117% | -0.2244% | 1.351% | 0.8121% | 2.636% | 2.057% | -0.2318% | -1.714% | 0.4805% | -0.307% | -0.1709% | 0.4104% | 0.7173% | -0.09889% | 1.101% | -0.7033% | 0.7931% | 0.01415% | 1.797% | 0.1548% | -0.1043% | 0.01415% | 0.3324% | -0.8445% | -1.919% | -1.148% | -1.371% | -1.821% | -2.483% | -1.444% | -2.343% | -1.746% | -1.073% | -2.083% | -1.746% | -0.3154% | -1.602% | -1.458% | -2.216% | -1.767% | -2.083% | -1.821% | -1.522% | -1.971% | -2.103% | -1.821% | 0.971% | -1.172% | -1.065% | -1.609% | 1.683% | -1.418% | -1.458% | 0.6979% | -0.955% | 1.71% | 0.3572% | -0.3241% | -1.694% | -0.2267% | 0.4769% | 1.136% | -1.086% | -0.9454% |  |  | -6.644% | -1.356% | -2.003% |  | 0.1794% | -0.726% | 0.6581% | -1.141% | 0.1104% | 0.3694% | 1.087% | 0.8802% | 0.9024% | 2.057% | -1.067% | 2.664% | 1.225% | 1.402% | 4.532% | 0.1072% | 0.2813% | 1.999% | -0.1678% | -0.1053% | 1.3% | 0.8629% | -0.5529% | -2.357% | 2.004% | -0.143% | -2.085% | -2.124% | -2.091% | -1.791% | -1.185% | -0.697% | -0.8895% |  | 9.365% | -1.274% | 2.473% | -2.183% | -1.907% |  |  | 5.403% | 5.715% | -4.986% | -2.321% | 1.126%
2025-06-12 | -1.541% | 0.822% | -0.4326% | 0.9077% | 0.2034% | 1.093% | 0.9319% | 1.013% | 0.1345% | 0.6693% | -0.5295% | -0.6102% | 0.6574% | -0.1184% | 0.6493% | 0.3506% | 0.1407% | -0.1581% | 0.7623% | 0.6058% | 1.029% | -2.144% | 0.6878% | -0.09887% | 0.4642% | 0.8294% | 0.3003% | 0.4753% | 1.336% | -0.04863% | -0.307% | 0.2169% | 1.313% | -2.346% | 1.021% | -2.145% | 1.618% | -1.313% | -1.49% | 0.05991% | -0.1662% | -1.959% | -1.305% | -2.185% | -0.6183% | -0.255% | -0.4301% | -1.498% | -1.152% | -2.547% | -0.1904% | -0.2388% | 1.767% | -0.307% | -0.5568% | 1.071% | 1.322% | 1.424% | 0.1236% | -0.1706% | 1.721% | -0.7598% | -0.1823% | -0.3452% | -0.132% | -0.8847% | 0.5835% | -2.047% | -1.232% | -1.337% | -0.6264% | -1.079% | 1.005% | -0.7556% | -0.3859% | 0.4968% | 2.198% | 1.368% | 0.1407% | -1.295% | 0.4394% | -0.2873% | 0.8269% | 0.3586% | -0.9897% | -0.6667% | 1.691% | 0.9238% | -1.466% | -2.217% | -1.067% | 1.001% | -0.368% | -0.7717% | -0.0917% | 0.722% | -0.6506% | -0.4487% | 0.6493% | 0.5605% | -0.368% | 0.6251% | 0.4394% | -2.12% | -1.642% | 1.457% | -0.4577% | -0.4641% | 1.36% | -0.8811% | 0.5313% | -1.384% | -1.728% | 0.3461% | 0.6897% | 1.061% | -0.6012% | 0.4753% | 0.1738% | 0.1245% | 1.957% | -1.068% | -0.8668% | 0.6493% | 1.489% | 1.121% | -1.256% | -0.7636% | 1.107% | -0.4577% | -0.3779% | 0.009608% | -0.2289% | 1.238% | 0.5506% | -0.7609% | 0.3999% | 0.3999% | 0.8399% | 0.8189% | -1.63% | -1.399% | 0.3586% | 0.6878% | -1.781% | -0.6537% | -0.1823% | 1.978% | 0.6804% | 1.947% | 0.5388% | 1.303% | 2.04% | 1.166% | -0.1581% | -0.6829% | -0.2469% | 0.1084% | 0.4784% | 0.8867% | -1.54% | 0.56% | -1.613% | -0.9597% | -1.352% | -0.01319% | 1.703% | -0.2338% | 1.205% | 0.2925% | -0.3268% | -0.4835% | -0.8145% | 0.4493% | -0.1613% | 0.56% | 1.989% | 0.7968% | -0.604% | 0.9683% | -1.017% | -1.177% | -0.604% | 0.2925% | -0.4142% | -0.4516% | -0.4757% | -0.5462% | 1.006% | -0.05239% | 1.246% | 0.1926% | -1.032% | 1.613% | 1.14% | 2.071% | 1.221% | -0.134% |  |  | -8.252% | -1.54% | -1.837% |  | -1.069% | -2.225% | 0.8592% | -2.144% | 0.6412% | -0.7636% | -0.8686% | -0.02082% | 1.36% | 1.142% | -1.28% | 1.11% | -0.2855% | 1.703% | 1.849% | 5.779% | 1.479% | 2.043% | -2.012% | -2.102% | -0.02825% | -0.4003% | -1.943% | -1.399% | 0.8554% | -1.533% | -0.8166% | -1.606% | 1.505% | -1.934% | 0.5841% | -2.254% | -2.361% |  | 7.085% | 0.7661% | 2.102% | -2.254% | 3.18% |  |  | 5.962% | 6.097% | -5.657% | -2.431% | -1.687%
2025-06-13 | -2.485% | 0.005647% | -1.406% | -0.1419% | -0.6564% | 0.1629% | 0.001509% | 0.0822% | -0.857% | -0.6419% | 1.947% | 1.068% | -0.4288% | 2.315% | -0.2495% | -0.4916% | -0.6799% | -0.8861% | -0.09366% | -0.1516% | 0.3781% | 0.6201% | 1.884% | 1.33% | 1.586% | 0.3698% | 0.06358% | 0.2625% | 1.147% | -0.399% | 0.0553% | 0.5016% | 0.6354% | -2.03% | 0.3691% | -2.206% | 1.033% | -1.415% | 0.6829% | 2.189% | 0.09116% | -0.9937% | 1.176% | 0.1629% | 1.391% | 1.346% | 1.156% | 0.3422% | -1.408% | -1.942% | -0.4468% | -0.03435% | 2.598% | 0.924% | -1.476% | 0.4538% | 0.4378% | 0.6022% | -0.7098% | 0.645% | 1.597% | 2.135% | -0.8144% | 1.155% | 2.058% | 0.09668% | 1.206% | -1.856% | -2.043% | 0.8084% | 1.454% | 0.9608% | 2.933% | -2.177% | 0.9877% | -0.4468% | 0.6211% | -0.124% | -0.115% | -1.84% | 1.015% | 1.194% | 0.3422% | 1.768% | 1.086% | 0.8801% | 1.669% | 0.7815% | 0.396% | -0.2585% | -1.15% | -2.303% | 2.602% | 2.422% | 1.912% | 0.3512% | -0.5723% | 1.391% | 0.4767% | 0.5663% | 0.5036% | 0.5932% | 2.108% | -1.352% | -2.192% | 1.302% | -1.021% | -2.27% | 1.517% | -0.9488% | 0.345% | -2.254% | -2.535% | -0.6779% | 0.7188% | 1.562% | -1.381% | -1.204% | -1.443% | 0.5753% | 1.777% | -2.248% | -1.977% | 1.006% | 1.624% | -2.463% | -2.338% | -1.684% | 0.5733% | -1.1% | -1.277% | -1.012% | -1.17% | 0.5052% | -0.5654% | -1.268% | 0.5227% | 0.9245% | 0.7611% | -0.5633% | -2.452% | -2.51% | 0.2436% | 0.2125% | -0.8413% | -1.774% | -1.101% | 1.17% | 0.1463% | 1.156% | 1.048% | 0.5932% | 1.418% | 0.7546% | -0.5006% | -1.29% | 0.01047% | 0.4588% | 1.011% | 0.748% | 1.225% | -1.093% | -0.1376% | 1.192% | 0.2654% | 1.48% | 0.485% | 1.837% | 1.374% | -2.377% | -0.9752% | -2.411% | -0.6937% | -0.03507% | -1.427% | 1.292% | 1.192% | 0.0498% | 0.02361% | 0.7389% | -1.185% | -0.3633% | 0.217% | -1.55% | 0.5227% | 0.8296% | 0.4524% | 0.8876% | -2.246% | -1.679% | -0.1678% | 0.2039% | -2.253% | 1.102% | 1.464% | 0.7389% | -0.9839% | -1.165% |  |  | -7.336% | -1.658% | -1.886% |  | -0.6812% | -2.177% | 1.974% | -2.177% | 0.5036% | 0.3422% | 0.6829% | 0.6829% | 0.2615% | 1.059% | 0.8622% | -0.03435% | 0.8443% | 1.291% | 2.27% | 5.7% | 2.681% | 0.1042% | -0.8515% | -2.062% | 0.718% | -0.2635% | -2.171% | 0.3036% | 2.345% | 3.904% | -1.762% | -1.73% | -1.793% | -0.1635% | -2.351% | -1.57% | -1.588% |  | -1.111% | -1.93% | 0.2774% | -0.4869% | -1.774% |  |  | 6.558% | 5.338% | -5.562% | -1.839% | -0.6058%
2025-06-14 | -0.2573% | 1.849% | -1.969% | 2.106% | 0.6454% | 1.535% | 0.8021% | 1.047% | 0.1339% | 0.9944% | 2.676% | 2.35% | 0.7206% | 3.21% | 0.8021% | 0.4761% | -0.1758% | -0.2573% | -0.1068% | 0.1188% | 1.047% | 1.373% | 2.375% | 1.336% | 1.473% | 0.4949% | -0.1068% | -0.2573% | 1.336% | -0.4746% | 0.03248% | 0.3222% | 0.321% | -1.601% | -0.2573% | -2.313% | 0.4761% | -2.05% | -0.5017% | 0.8836% | -0.8277% | -1.561% | -0.2573% | -1.48% | -0.2573% | 0.06869% | -0.4829% | -1.317% | 0.1339% | -1.587% | 0.6391% | 0.3946% | 1.409% | -0.2573% | -0.4077% | 2.206% | 0.9017% | 1.128% | -0.2573% | 1.191% | 0.6391% | 1.545% | -0.5832% | -1.147% | -0.182% | -0.9343% | 0.4949% | -2.213% | -0.9907% | -1.48% | -0.7462% | -1.317% | 0.9651% | -0.6647% | 0.9017% | -0.9092% | 0.6844% | -0.2573% | -1.317% | -1.235% | 0.06869% | 0.3946% | -0.9092% | 0.5576% | -0.8277% | -0.5832% | 0.06869% | -0.9092% | -1.969% | -2.702% | -1.196% | 0.1188% | 1.21% | 0.3946% | -0.7643% | -1.398% | -1.887% | 0.1502% | -0.9907% | -0.7462% | 2.024% | -1.154% | 0.8836% | -1.561% | -0.1848% | 0.3132% | 2.206% | -0.5658% | 0.5576% | -0.6919% | 0.1188% | -0.4077% | 0.3222% | 0.9741% | -0.09429% | 2.106% | 0.3077% | 1.191% | -0.1848% | 1.535% | 2.839% | -2.068% | -2.285% | 0.3946% | 0.8836% | -2.141% | -2.213% | -1.072% | 0.3946% | -0.9816% | -1.009% | -0.6334% | -0.859% | 0.5428% | 0.4958% | -1.254% | 2.017% | 1.561% | 0.838% | 0.9651% | -1.686% | -1.386% | 1.047% | 1.322% | -1.969% | -0.7838% | -0.6647% | 0.6317% | -0.6334% | 0.1188% | 0.7958% | 0.3132% | 2.061% | 0.7206% | -1.235% | -1.969% | -2.294% | -1.317% | 0.7938% | -1.184% | 0.3634% | -2.668% | -0.002919% | -0.6622% | 1.462% | -0.3106% | 0.1344% | 1.316% | 0.7938% | -0.9436% | 1.114% | -1.023% | 1.535% | 1.984% | -2.494% | -0.4425% | 0.6289% | -1.267% | 3.367% | 1.865% | 0.1154% | 1.682% | -1.248% | 3.724% | 0.724% | 0.7297% | 0.8762% | 0.9553% | -1.102% | 0.648% | 0.2993% | 0.2993% | -2.008% | 1.123% | 0.2169% | -9.261% | 1.667% | 2.854% |  |  | -7.441% | 0.7011% | -2.308% |  | -0.8787% | -2.132% | 0.3132% | -1.724% | -0.2573% | -0.0128% | 1.128% | 0.4761% | 0.9651% | 2.758% | 0.5576% | 1.617% | 0.1773% | 2.206% | 3.965% | 4.355% | 0.808% | 3.209% | -1.52% | -0.2852% | 1.229% | -0.4021% | -0.7838% | -2.815% | -1.352% | 0.1188% | -0.547% | -2.141% | -1.186% | -1.416% | 1.35% | -0.4506% | -1.278% |  | 1.921% | -1.405% | 1.968% | -2.404% | -0.4256% |  |  | 4.673% | 4.184% | -6.311% | -2.37% | -1.946%
2025-06-15 | -2.123% | -0.08684% | -1.601% | -0.5413% | -0.3792% | 0.07026% | 0.2887% | 0.518% | -0.2631% | 0.009538% | 2.134% | 1.577% | -0.3229% | 3.771% | -0.4649% | -0.727% | -1.229% | -0.2901% | -1.307% | -1.105% | -1.994% | -1.076% | 0.6491% | -1.39% | -1.791% | -1.105% | -2.113% | -0.8847% | -1.535% | -0.7877% | -0.7877% | -0.5935% | -2.561% | -4.037% | -1.601% | -2.347% | -1.055% | -2.693% | -1.601% | -1.917% | -2.453% | -1.764% | -1.601% | -1.601% | -1.055% | -2.922% | -0.09692% | -1.601% | -1.343% | -1.532% | -1.601% | -1.251% | -1.855% | -1.273% | -2.113% | -1.855% | -1.555% | -1.273% | -2.817% | -1.758% | -1.164% | -1.557% | -1.262% | -2.375% | 0.9717% | 0.1854% | 1.536% | -0.9941% | 0.2887% | -0.3557% | 0.6163% | -0.03895% | 2.538% | 0.3979% | 1.853% | 0.02779% | 1.678% | 0.8129% | -0.3338% | 0.9213% | 1.141% | 1.435% | 0.245% | 1.763% | 0.1795% | 0.6382% | 1.403% | 0.3761% | -0.5522% | -1.415% | -0.02191% | 1.818% | 2.582% | 1.796% | 0.5326% | -0.3229% | -0.9017% | 3.226% | 1.141% | 2.353% | 2.768% | 1.49% | 2.779% | -0.4976% | 0.09574% | 0.3542% | -0.8847% | 2.024% | 0.5836% | 0.09574% | 1.718% | 1.022% | 2.979% | 2.503% | 3.052% | 3.838% | 1.438% | 4.183% | 3.406% | 3.663% | 4.81% | -0.4867% | -1.758% | 3.609% | 4.34% | 15.63% | -2.693% | -2.431% | -1.623% | -2.302% | -2.264% | -1.891% | -1.78% | -0.1015% | -1.001% | -2.02% | 1.385% | 0.5897% | 0.1353% | -1.568% | -2.627% | -2.113% | -2.627% | -1.166% | -2.693% | -1.105% | -2.693% | -1.936% | -2.99% | -2.184% | -1.881% | -2.136% | -0.2537% | -2.158% | -1.928% | -2.693% | -2.474% | -2.911% | -2.647% | -2.36% | -2.694% | -0.4825% | -1.722% | -2.213% | -2.39% | -0.2218% | -0.4825% | -1.84% | 0.6331% | -1.176% | -1.834% | -2.343% | -0.9268% | -1.282% | -2.606% | 0.622% | -2.239% | -0.4825% | 0.8601% | -0.7918% | -1.174% | -0.2984% | 0.3398% | 1.973% | -2.622% | -2.645% | -1.42% | -1.95% | 0.7007% | -1.623% | 1.892% | 2.754% | 8.519% | 2.456% | 1.782% | 2.71% | 4.656% | 4.786% |  |  | -6.88% | -0.3816% | -0.02183% |  | 2.088% | -1.623% | 2.036% | -0.1263% | 1.217% | 1.719% | 2.451% | 2.069% | 2.364% | 4.351% | 1.818% | 2.932% | 1.329% | 3.367% | 4.598% | 4.206% | -0.05973% | 1.464% | -1.848% | 0.2339% | 3.281% | 3.396% | 3.401% | 1.889% | 3.27% | 2.927% | 2.523% | -1.768% | 1.163% | -0.5614% | -1.216% | -1.526% | -1.706% |  | 2.508% | 1.667% | 1.26% | -1.711% | 2.069% |  |  | 3.718% | 2.949% | -6.554% | -1.669% | -0.8677%
2025-06-16 | -1.333% | 0.6368% | -0.01744% | 0.05673% | 0.226% | 0.8809% | 1.128% | 1.186% | 0.1052% | 0.4533% | 3.048% | 2.348% | 0.8149% | 3.687% | 0.9221% | 0.7737% | 0.3534% | -0.1823% | 0.1043% | 0.1119% | 0.7572% | 1.12% | 2.493% | 0.8873% | 1.283% | -0.009832% | -0.4587% | -0.3947% | 0.5869% | -0.7903% | -0.7024% | -1.142% | -1.224% | -2.388% | -0.3224% | -1.699% | -1.624% | -2.399% | 0.749% | 0.2051% | 0.988% | -1.023% | -0.5366% | -1.707% | -0.5531% | -0.2235% | -0.9227% | -0.1575% | -1.627% | -2.213% | -0.3553% | -0.7591% | 0.6235% | -0.8342% | -1.645% | 0.02285% | 0.2206% | 0.5265% | -0.9807% | 0.3305% | 0.1886% | 0.8992% | -0.5449% | 1.168% | 0.8878% | 0.1651% | 1.23% | -1.242% | 0.3864% | -0.009198% | 0.6254% | 0.1144% | 2.603% | 0.7325% | 1.854% | 0.03018% | 1.971% | 0.955% | -0.1905% | 0.6672% | 1.4% | 1.754% | 0.4441% | 1.845% | 0.4029% | 0.5842% | 1.293% | 0.3864% | -0.6932% | -1.278% | -0.2271% | 0.7965% | 2.43% | 1.903% | 0.2426% | -0.04216% | -0.5119% | 2.166% | 0.716% | 1.112% | 3.46% | 0.9138% | 2.224% | -0.0009564% | 1.634% | 2.043% | 2.418% | 0.487% | 1.878% | 0.7408% | 1.177% | -0.2989% | 1.473% | 0.814% | 1.639% | 2.232% | -0.1167% | 0.7481% | 0.2719% | 1.581% | 2.892% | -1.545% | -1.171% | 1.507% | 2.331% | 2.184% | -2.984% | -3.561% | -3.962% | -3.186% | -3.258% | -2.657% | -2.802% | -2.903% | -3.828% | -2.951% | -2.982% | -3.067% | -3.4% | -4.707% | -3.859% | -4.338% | -2.918% | -2.931% | -4.229% | -2.703% | -2.704% | -3.083% | -3.311% | -3.464% | -3.54% | -3.413% | -3.449% | -3.413% | -3.042% | -3.685% | -4.089% | -3.413% | 1.077% | -0.8066% | 0.4556% | -2.032% | -0.3149% | -0.8779% | 1.019% | -0.1255% | -0.1315% | 0.8705% | 2.469% | -1.854% | -0.07749% | -2.022% | 0.3667% | 0.9387% | 0.04075% | 0.1269% | 1.319% | -0.7149% | 2.634% | 2.386% | -0.2585% | 1.234% | -1.604% | 2.099% | 0.734% | 0.7742% | 1.683% | 1.683% | 2.251% | 0.1108% | 1.677% | 0.777% | 0.1019% | 1.827% | 1.827% | 2.144% | 3.479% | 4.136% |  |  | -4.478% | -2.25% | 0.04292% |  | 0.4773% | -2.498% | 1.417% | -1.41% | 1.169% | 1.161% | 2.026% | 1.862% | 2.199% | 3.197% | 1.705% | 2.356% | 1.232% | 3.268% | 7.311% | 5.438% | 3.582% | 4.019% | -1.357% | -0.5779% | 1.537% | 1.217% | 0.2945% | -0.0859% | 2.494% | 0.5303% | 0.6528% | -1.691% | -2.29% | -1.807% | -1.606% | -2.542% | -0.1593% |  | -1.564% | -2.035% | 0.9341% | -1.867% | -2.461% |  |  | 5.031% | 3.812% | -6.835% | -1.178% | 0.4415%
2025-06-17 | -0.7678% | 1.66% | 2.052% | 2.371% | 0.6367% | 1.333% | 1.156% | 1.474% | 0.6424% | 1.231% | 2.901% | 2.288% | 0.9316% | 3.841% | 0.6013% | -0.6489% | -0.13% | -0.5074% | -0.9202% | -0.3758% | 0.849% | 0.7547% | 2.705% | 1.061% | 1.148% | -0.3758% | -0.8658% | -0.4694% | -0.1863% | -1.182% | -0.2387% | -0.5218% | -0.2963% | -1.684% | -0.8259% | -0.2733% | -0.4248% | -2.465% | -0.5664% | 1.132% | -1.463% | -2.312% | -0.4602% | -1.38% | -0.1535% | 0.2121% | -0.3214% | -1.18% | -0.6711% | -2.177% | 0.3419% | -0.0002068% | 1.701% | -0.08146% | -0.3758% | 1.837% | 1.208% | 1.05% | -0.6476% | 0.1702% | 0.6131% | 1.255% | 0.4834% | 6.991% | 0.2339% | -0.5065% | 0.6041% | -2.042% | -0.7315% | -0.9674% | -0.3423% | -1.003% | 1.557% | -1.663% | 0.5581% | -1.497% | 0.6% | -0.472% | -1.628% | 0.2774% | -0.1182% | 0.2947% | -0.932% | 0.3301% | -1.168% | -0.6018% | 0.106% | -0.6371% | -1.84% | -2.241% | -1.498% | -0.5392% | 1.274% | 0.6839% | -0.375% | -1.498% | -1.722% | 0.7901% | 0.04697% | 0.2711% | 2.607% | -0.1535% | 1.12% | -1.569% | 1.082% | 0.2947% | 2.791% | -0.009843% | 1.156% | -0.7315% | -0.3214% | -2.129% | -0.1863% | 0.05484% | 0.4952% | 1.462% | -0.7895% | -0.9097% | -1.088% | -0.07098% | 2.04% | -2.074% | -1.025% | 0.4834% | 1.014% | -0.5533% | -0.7315% | -1.368% | 0.9985% | -0.6267% | -0.942% | -0.844% | -0.844% | 1.1% | -0.6753% | -0.8294% | 2.474% | 0.9214% | 1.922% | -1.628% | -2.118% | -2.651% | 1.026% | 1.41% | -0.4484% | -1.9% | -0.6489% | 0.6753% | -0.648% | 0.2121% | 0.9198% | 0.1767% | 1.334% | 0.5542% | -0.8731% | -1.652% | -1.416% | -1.097% | -0.5817% | -2.299% | -1.205% | -0.6294% | -0.9501% | -2.212% | 0.9904% | -1.34% | -1.608% | -0.4942% | 0.5874% | -1.398% | -1.867% | -1.627% | -1.067% | -0.8708% | 0.2481% | -0.8202% | -0.1403% | -1.965% | 1.086% | 0.8141% | -1.92% | -0.6002% | -2.254% | 3.504% | -0.1467% | -0.2079% | 0.5836% | 0.6981% | 0.3889% | -2.041% | 0.08638% | -0.868% | 0.2772% | 0.7306% | 0.4443% | 1.065% | 2.138% | 3.176% |  |  | -3.82% | -0.5652% | -1.947% |  | 0.6577% | -1.899% | -0.2715% | -1.038% | -0.1417% | 0.01159% | 1.321% | 0.6957% | 1.474% | 1.687% | 0.6249% | 1.616% | 0.9775% | 3.127% | 6.482% | 5.918% | 3.826% | 4.846% | -1.385% | -1.83% | 0.9595% | 0.317% | -2.662% | -2.14% | 2.035% | 0.7674% | -0.07098% | -2.074% | -1.997% | -1.953% | -1.752% | -2.092% | -2.276% |  | 2.6% | -1.166% | 4.977% | -2.092% | -1.997% |  |  | 5.175% | 5.512% | -6.207% | -1.997% | -1.421%
2025-06-18 | -1.479% | 0.3854% | 0.8346% | 0.557% | 0.9421% | 0.7772% | 2.022% | 1.993% | 0.6608% | 1.304% | 3.907% | 3.362% | 1.208% | 3.934% | 1.572% | -3.023% | 1.131% | 1.227% | 1.667% | 1.826% | 2.136% | 2.06% | 1.393% | 2.258% | 2.957% | 1.561% | 0.7742% | 0.9388% | 2.147% | 3.423% | 3.934% | 2.564% | -5.162% | -15.09% | -5.608% | -4.583% | -5.608% | -5.397% | -4.172% | -4.708% | -6.144% | -4.938% | -6.096% | -4.813% | -3.875% | -5.139% | -4.474% | -4.612% | -4.972% | -4.66% | -4.315% | -4.708% | -4.345% | -4.498% | -4.466% | -4.32% | -3.018% | -3.971% | -4.405% | -3.928% | -3.999% | -5.027% | -4.172% | 0.5229% | 0.01432% | -0.7544% | 0.2882% | -2.327% | -0.05564% | -0.05564% | 0.5474% | 0.02094% | 2.912% | -1.195% | 1.594% | 0.173% | 1.883% | 1.237% | 1.036% | 1.481% | -2.267% | -0.3524% | 0.7963% | 2.481% | 1.256% | 1.227% | 1.486% | 0.6336% | -0.7161% | -1.463% | -1.673% | -0.5335% | 2.443% | 2.194% | -1.137% | 0.4996% | -0.05564% | 2.012% | 0.691% | 1.237% | 3.678% | 0.9973% | 2.567% | 0.1837% | 0.9729% | 1.103% | 3.568% | -0.01669% | 1.581% | 0.2071% | 0.2971% | -1.832% | -0.9161% | -0.2099% | 1.6% | 1.792% | -1.547% | -0.09924% | -0.2907% | 0.8633% | 1.677% | -2.49% | -2.167% | 0.7293% | 1.591% | 0.9984% | 0.3177% | 0.6049% | 1.994% | 0.6836% | 0.9244% | 1.145% | 1.755% | 0.5196% | -1.539% | 1.598% | 4.484% | 3.313% | 3.785% | -2.324% | 0.3147% | -1.028% | 1.916% | 2.647% | -1.539% | 0.1734% | 1.294% | 2.378% | 0.7035% | 1.587% | 1.278% | 0.825% | 1.568% | 1.112% | -0.1131% | -0.4768% | 0.001798% | -0.1226% | 0.78% | 1.796% | 3.084% | 0.6057% | 2.232% | 1.578% | -1.038% | 1.86% | 1.787% | 1.122% | 0.6832% | -0.4445% | 1.972% | -0.6118% | 2.482% | 2.381% | 1.372% | 3.694% | 4.072% | 2.513% | 2.413% | 1.458% | 2.384% | 1.199% | 1.217% | 2.325% | 0.3555% | 1.458% | 4.221% | 4.676% | 3.533% | 2.053% | 0.6735% | -1.021% | -2.124% | 0.5089% | 0.8381% | -0.9626% | 2.464% | 2.881% |  |  | -7.648% | -0.1041% | -1.895% |  | -1.864% | -2.171% | 0.7006% | -6.996% | 0.4038% | 1.122% | 1.38% | 1.332% | 1.409% | -2.171% | 0.8346% | 1.696% | 0.0454% | 1.611% | 3.125% | 3.125% | 2.953% | 3.194% | -1.53% | -2.756% | 0.6056% | -0.882% | -1.505% | -2.027% | 1.038% | -0.2243% | -1.367% | -1.639% | 0.3853% | -2.728% | -2.593% | -0.1774% | -2.415% |  | -0.3143% | -1.987% | 4.775% | 0.4919% | -2.593% |  |  | 3.087% | 4.055% | -6.081% | -2.593% | -1.349%
2025-06-19 | 0.3436% | -0.1637% | 0.2642% | 0.1982% | -0.7318% | -0.2414% | 0.1652% | 0.1652% | -0.7919% | -0.09547% | 1.045% | 1.462% | -0.1645% | 2.436% | 0.02236% | -2.726% | -0.3953% | -0.802% | -0.7724% | -0.4985% | 0.3411% | 0.2422% | -2.274% | 0.4376% | 0.8915% | -0.4173% | -1.046% | -0.7641% | 0.1054% | 0.09564% | -0.432% | 0.4376% | 1.354% | -2.357% | 0.3191% | 1.473% | 0.0993% | -2.66% | -1.571% | 0.517% | -0.9119% | -1.813% | -0.7141% | 0.4071% | -0.5272% | -0.04359% | -0.813% | -0.9449% | -1.72% | -0.2854% | -0.6591% | -0.9559% | 0.6525% | -0.5687% | -1.706% | -0.01184% | 0.379% | 0.517% | -0.6469% | 0.6428% | 0.2092% | 1.611% | -1.055% | 6.962% | -0.7014% | -1.3% | -0.5898% | -2.862% | -0.835% | -1.242% | -0.78% | -1.461% | 1.297% | -0.3294% | 2.04% | -0.344% | 1.835% | 0.473% | -0.9889% | 0.506% | 0.04434% | 0.451% | -0.9889% | 0.3851% | -1.396% | -0.857% | -0.3733% | -1.099% | -2.407% | -0.857% | -2.1% | -1.706% | 0.9347% | 0.484% | -1.692% | -1.143% | -1.066% | 0.7698% | 0.2532% | 0.01137% | 2.1% | -0.1095% | 1.056% | -1.429% | 0.4571% | -0.1205% | 4.082% | -0.7163% | 0.2312% | -1.194% | -1.31% | -2.497% | -0.3245% | -0.471% | 0.1433% | 0.5609% | -1.207% | -2.181% | -1.81% | -1.33% | 0.6159% | -2.2% | -1.223% | -0.7361% | 0.1433% | -0.1291% | -0.9779% | -0.5052% | 1.542% | 0.4083% | 0.3436% | 0.435% | 0.4147% | 2.389% | 3.618% | 0.5501% | 4.439% | 2.9% | 4.315% | -2.011% | -0.6912% | -0.8942% | 2.759% | 3.357% | -1.242% | -1.483% | 1.242% | 2.568% | 0.6379% | 1.531% | 1.855% | 0.6709% | 1.522% | 0.8577% | -0.3843% | -0.813% | 0.2642% | -0.4832% | 1.537% | -0.3306% | 1.045% | -1.598% | 0.8576% | 0.4031% | 1.806% | -0.03803% | -0.1083% | 0.8181% | 2.437% | -2.578% | -0.3048% | -2.631% | 0.4031% | 0.3035% | 3.209% | 1.548% | 2.237% | 0.3364% | 3.259% | 3.138% | 0.3962% | 1.45% | 0.2351% | 1.381% | 1.997% | 2.28% | 2.747% | 3.035% | 1.413% | -0.2708% | -1.909% | -1.164% | -0.942% | -1.598% | -1.32% | -1.498% | 0.6476% | 0.97% |  |  | -5.71% | -0.8346% | -2.284% |  | -1.477% | -2.264% | -1.78% | -9.892% | -1.912% | -1.67% | -0.5052% | -0.9449% | -0.2744% | 0.6709% | -0.6371% | 0.2422% | -0.5297% | 1.522% | 5.429% | 6.244% | 5.905% | 3.497% | -1.301% | -1.825% | -1.457% | -1.966% | -2.436% | -0.7623% | -0.6864% | -0.7014% | 0.164% | -1.126% | 1.473% | -2.017% | 1.484% | -2.428% | 1.203% |  | 0.7175% | -1.716% | 2.321% | -1.067% | 0.5604% |  |  | 3.589% | 3.796% | -6.103% | 0.4692% | -0.8984%
2025-06-20 | 0.868% | 2.815% | 3.35% | 2.851% | -0.4946% | 2.871% | 2.909% | 3.005% | -37.24% | 2.823% | 4.941% | 4.27% | 2.449% | 4.986% | 2.621% | -1.916% | 2.065% | 1.586% | 3.115% | 2.762% | 2.794% | 3.12% | 0.3194% | 3.676% | 3.806% | 2.974% | 2.372% | 2.602% | 4.477% | -1.044% | 0.2847% | -26.04% | 4.384% | -33.9% | 3.216% | 4.513% | 3.637% | 0.7043% | 2.238% | 3.714% | 2.18% | 0.1867% | 2.871% | 1.855% | 2.775% | 2.909% | -21.43% | 1.375% | 1.7% | -28.04% | 2.468% | 2.583% | 4.153% | 2.704% | 1.54% | 3.625% | 3.454% | 3.388% | 2.313% | 4.357% | 3.254% | 5.352% | 2.315% | 11.51% | 1.682% | 1.08% | 4.23% | 3.699% | 0.8769% | 0.6852% | 1.318% | 0.3976% | 3.733% | 2.008% | 3.761% | 2.193% | 3.591% | 2.238% | 1.088% | 3.452% | 2.391% | -9.111% | 1.222% | 2.449% | 0.5701% | 1.203% | 0.1292% | 1.107% | -0.6376% | -2.478% | 0.04408% | 0.7087% | 1.682% | 1.855% | 3.437% | -100% | -100% | 2.756% | 2.142% | 0.1675% | 4.826% | -0.2926% | 3.35% | 0.6468% | 3.983% | -100% | -100% | 2.92% | 2.813% | 2.739% | 2.885% | 4.23% | 2.483% | 1.699% | 1.605% | 3.005% | -2.389% | 2.074% | 2.534% | 1.759% | 3.752% | -9.343% | -11.56% | 2.602% | 3.58% | 2.125% | 4.289% | 1.433% | -3.14% | -24.34% | 2.567% | 2.354% | 2.425% | 4.819% | 6.113% | 3.07% | 6.578% | 4.538% | 6.283% | 5.248% | 4.23% | 2.195% | 3.158% | 4.106% | -0.1775% | -0.8485% | 3.35% | 4.547% | 2.903% | 3.062% | 3.045% | -11.03% | 4.511% | 3.868% | 1.835% | 1.088% | 3.427% | 2.276% | 4.486% | 2.915% | 4.561% | 1.383% | -18.9% | -9.692% | 5.044% | 3.656% | -12.19% | -22.27% | -30.98% | -1.462% | 3.042% | -1.872% | -25.1% | -28.34% | 3.079% | 1.616% | 4.427% | 2.585% | 6.06% | 5.843% | -24.12% | -23.36% | 2.769% | 8.98% | 4.717% | 4.819% | 3.917% | 3.396% | -16.52% | -40.78% | 1.286% | -0.07079% | 1.403% | -0.5361% | 1.248% | -24.19% | 2.931% | 4.389% |  |  | -6.736% | -0.2362% | 1.01% |  | 1.288% | -2.229% | -0.12% | -0.4843% | 1.088% | 2.257% | 2.602% | -1.845% | 2.526% | 3.906% | 1.529% | -23.13% | 2.074% | 4.392% | 13.03% | 9.57% | 8.978% | 10.81% | -2.109% | 0.323% | -1.115% | 1.784% | 0.8503% | 0.05399% | 0.2097% | 2.195% | 1.256% | 0.1143% | 4.003% | -1.229% | 4.202% | 2.257% | -2.095% |  | 3.01% | 0.7319% | 2.372% | -2.875% | -2.639% |  |  | 4.405% | 0.8879% | -6.216% | -2.202% | 0.8018%
2025-06-21 | 1.55% | 0.8947% | 1.164% | 0.7476% | 3.035% | 1.164% | 0.2177% | 1.467% | -1.52% | 2.705% | 0.4069% | 2.3% | 2.432% | 1.689% | 2.423% | -1.997% | 1.703% | 1.391% | 1.96% | 1.969% | 0.9937% | 0.4069% | -0.0313% | 2.659% | 0.5452% | 2.022% | 1.314% | 1.12% | 2.516% | -1.917% | -2.337% | -7.385% | 1.715% | -2.065% | 0.8328% | 1.61% | 0.2744% | -0.8801% | 1.486% | 2.811% | 0.2934% | -0.7949% | 1.618% | 0.2934% | 2.101% | -1.107% | -2.233% | 0.8044% | 1.778% | 2.141% | -0.5394% | 2.886% | 4.367% | 2.701% | 0.01238% | -0.7392% | 2.525% | 2.243% | 0.388% | 1.498% | 1.656% | 2.422% | 0.4069% | 5.822% | 1.419% | 1.576% | 0.982% | 1.602% | 0.123% | 1.353% | 1.069% | 1.391% | 2.631% | 0.4069% | 2.609% | 1.027% | 3.013% | 2.375% | 2.555% | -7.753% | 0.9747% | 0.388% | 2.64% | 1.826% | 2.11% | 1.353% | 1.637% | 1.353% | 0.5962% | 0.2934% | 0.02461% | 1.131% | 0.6908% | 1.817% | 2.028% | -2.035% | -2.243% | -1.164% | -2.432% | -2.555% | -0.7381% | -1.959% | -2.186% | -1.77% | -1.496% | -12.18% | -10.92% | -2.447% | -2.678% | -1.614% | -0.9398% | -0.503% | -2.119% | -2.388% | -1.372% | -1.382% | -2.278% | -2.506% | -1.665% | -1.864% | -2.072% | -9.05% | -8.983% | -1.864% | -2.451% | -0.6551% | 0.4069% | -0.1609% | -1.833% | -2.329% | 0.3181% | -1.901% | 0.1784% | 2.288% | 0.6276% | 0.2389% | 1.953% | 1.22% | 2.114% | -1.959% | -0.4768% | -1.193% | 1.921% | 1.48% | -1.117% | -2.075% | 0.6057% | 1.751% | -1.324% | 0.685% | 0.9733% | -0.6151% | -0.2934% | -1.306% | -2.148% | -2.139% | -2.006% | -0.8801% | 0.4951% | 1.854% | -0.3769% | -0.462% | -0.7597% | 1.393% | 1.163% | 1.896% | 0.9641% | 0.7886% | 0.6004% | 1.4% | 0.1506% | 1.464% | -12.71% | -1.871% | 1.24% | 0.5908% | 1.165% | 1.548% | 2.175% | 0.9737% | -2.023% | 1.146% | 1.912% | -1.595% | -0.3442% | 0.7291% | -0.6764% | 1.363% | -0.6764% | -1.934% | 0.5908% | 0.8205% | -0.2706% | 1.787% | 1.357% | 0.5908% | -0.4237% | -0.07914% |  |  | -6.646% | -2.262% | -1.125% |  | 2.624% | 0.04732% | -2.432% | -1.202% | 1.845% | 1.003% | 0.4069% | -0.2555% | 1.353% | -1.296% | -1.486% | -2.054% | 2.079% | 1.027% | 1.952% | 1.952% | 4.158% | 6.297% | -1.714% | 0.7743% | 0.02461% | 1.885% | 1.192% | 0.8859% | 0.02461% | 2.161% | 1.271% | 0.4048% | -1.738% | -1.465% | -1.64% | -2.315% | -1.126% |  | -0.5898% | -2.134% | 0.818% | -2.163% | -1.738% |  |  | 4.555% | 6.614e-05% | -6.369% | -2.622% | -2.21%
2025-06-22 | 0.5395% | 0.3434% | -0.05761% | 0.3938% | -0.2367% | 0.9957% | 0.7302% | 1.35% | 1.12% | 1.12% | -0.2435% | 1.527% | -1.279% | 1.004% | 1.173% | -2.633% | 0.3761% | 2.014% | 1.806% | 0.5804% | 0.2876% | 0.4646% | 0.2454% | 0.7105% | 0.5804% | 1.234% | 0.801% | 1.104% | 2.127% | -2.515% | -1.217% | -5.741% | 1.26% | -2.555% | 1.863% | 1.207% | 2.164% | 0.5354% | 1.89% | 1.527% | 0.1106% | 0.5177% | 0.3761% | -0.7746% | 1.615% | -0.06647% | -1.871% | 0.9957% | -0.9028% | -6.239% | 1.969% | 1.837% | 2.363% | 1.497% | 0.9481% | 0.5531% | 0.00238% | 0.1991% | -0.0763% | 1.497% | 0.7302% | 1.998% | 1.536% | 3.721% | 0.417% | 0.5804% | 1.814% | -0.7024% | 0.1991% | 0.562% | 0.8187% | 0.3761% | -0.7746% | 1.359% | -0.0763% | 0.8679% | 1.049% | 1.385% | 1.146% | 2.272% | 0.1106% | -0.05761% | 0.5% | 1.757% | 1.881% | 1.447% | 1.244% | 1.235% | -0.5179% | -1.288% | -0.6053% | -2.034% | 0.1106% | -0.2169% | 0.2306% | 0.8187% | 0.2079% | -0.2435% | 1.447% | 1.19% | 0.4646% | 1.208% | 0.3761% | -0.7126% | 0.8836% | 0.5089% | -3.853% | 0.1875% | 1.491% | -0.155% | -0.1632% | -6.038% | -0.1865% | 0.4902% | 1.686% | 1.022% | -2.43% | -1.784% | -1.068% | -0.6684% | 1.394% | -6.654% | -8.621% | 0.3053% | 1.173% | 0.325% | 1.155% | 0.8983% | -2.358% | -0.454% | 0.4578% | -1.871% | 1.414% | 1.487% | 0.7317% | 1.723% | 1.723% | 1.145% | 0.2699% | -2.545% | 0.7928% | -0.8413% | 0.1991% | 0.8255% | 0.5531% | -6.144% | -0.7746% | 0.521% | 1.013% | 0.6784% | 0.7438% | 1.553% | 1.324% | 0.385% | 0.4558% | -0.08417% | 0.4735% | 1.128% | 1.132% | 1.409% | 0.343% | -0.4527% | -0.2379% | 0.4624% | -0.4527% | 1.951% | -0.2916% | -0.2936% | -1.348% | -0.9282% | -1.031% | -0.7048% | 0.7409% | -0.9884% | 0.9% | -1.437% | 0.2366% | 0.908% | 1.855% | 1.839% | -0.9706% | -0.5959% | 1.115% | 1.409% | 1.104% | 1.179% | -0.3095% | 0.5499% | 1.074% | -5.631% | -2.422% | -0.5422% | 0.532% | -1.437% | -1.867% | 0.02175% | 0.4855% | 0.6484% |  |  | -6.256% | -0.5492% | -0.3479% |  | -2.082% | -0.7746% | -1.784% | -0.7126% | -1.571% | -2.093% | -0.633% | -0.7392% | -0.05761% | -0.9074% | -0.1107% | -1.801% | -0.0999% | 2.15% | 2.662% | 1.604% | 2.856% | 1.943% | -0.9302% | -1.336% | -2.296% | -1.666% | -2.083% | -1.16% | -1.812% | -0.972% | -2.169% | -1.685% | 1.099% | -1.493% | 1.301% | -0.001792% | 1.027% |  | 0.3472% | 0.675% | -0.9979% | -1.947% | -1.665% |  |  | 2.733% | 1.961% | -7.315% | -1.665% | 1.021%
2025-06-23 | 2.732% | 1.423% | 2.01% | 1.499% | 1.019% | 1.583% | 1.447% | 1.499% | -6.716% | 1.445% | 2.323% | 2.866% | 2.334% | 1.384% | 0.9881% | 0.9464% | 0.7065% | 4.117% | 0.6527% | 0.4987% | 1.092% | 1.384% | 0.7201% | 1.941% | 1.827% | 0.9319% | 1.972% | 0.8838% | 1.783% | 1.171% | 2.822% | -6.357% | 2.377% | 2.557% | 1.218% | -0.2116% | 1.875% | 3.366% | 2.344% | 2% | 0.3831% | 3.251% | 4.211% | 3.742% | 1.739% | 2.156% | -8.436% | 0.03891% | 1.134% | -8.779% | 1.134% | 1.489% | 1.06% | 1.19% | -0.4353% | 1.987% | 1.941% | 1.165% | 0.8189% | 2.395% | 1.812% | 0.6269% | 1.53% | 3.599% | 1.317% | 1.808% | 0.5179% | -0.05015% | 1.802% | 1.603% | 1.739% | 0.8733% | 0.2371% | 0.2371% | 0.1328% | 1.848% | -0.05265% | 2.521% | 1.489% | 3.204% | 2.281% | 0.7482% | 1.593% | 3.158% | 1.238% | 1.499% | 1.687% | 1.051% | -0.274% | -1.359% | 0.1228% | -2.082% | -0.3887% | -0.07583% | -0.7017% | -0.0654% | -22.29% | 2.761% | -0.2844% | 0.1328% | 1.176% | -0.07583% | -0.806% | -1.265% | 0.1328% | -0.806% | 0.1328% | 0.571% | -0.806% | -1.814% | 0.6334% | 1.365% | -0.7944% | -1.629% | -0.806% | 0.55% | -9.902% | 1.06% | -1.814% | 1.75% | -0.2844% | -3.613% | -5.792% | -0.806% | 0.8629% | 0.9672% | -1.943% | 0.5604% | 0.1328% | -3.02% | -0.9263% | -1.86% | 0.566% | -2.143% | -0.6769% | 0.3651% | -15.31% | 0.1995% | -0.8685% | -2.579% | 0.09427% | -1.754% | 0.3831% | 0.3253% | -1.265% | 0.5179% | 0.6543% | -0.3224% | 2.386% | 2.116% | 0.903% | 1.301% | 0.2255% | 0.3831% | 1.593% | 0.3623% | 0.6647% | -0.5974% | 1.197% | 0.1208% | 1.224% | -2.854% | -7.225% | -7.337% | -1.636% | 0.663% | -0.8392% | -6.925% | -0.8392% | -2.254% | 0.42% | -1.909% | -0.6047% | -0.7548% | 0.9143% | 0.6483% | -0.7337% | -0.3855% | -0.4547% | 0.3212% | -0.6769% | -2.386% | 0.4267% | 0.2579% | -0.2387% | 0.5861% | -1.666% | 0.3491% | -6.831% | -1.651% | 0.2263% | -1.282% | -0.7337% | -0.6598% | 0.912% | -1.789% | -1.261% | -1.789% |  |  | -6.952% | -9.89% | -1.858% |  | 1.394% | -1.588% | -5.99% | -1.818% | 0.09106% | 0.9464% | 1.906% | 1.812% | -1.849% | 1.603% | 1.969% | -1.849% | 0.1328% | 1.987% | 3.516% | 2.144% | 1.562% | 3.191% | -0.7387% | 0.7132% | 3.387% | 2.089% | 1.24% | 2.521% | 3.407% | 3.272% | 2.979% | 1.301% | 1.877% | -1.442% | 0.6107% | -1.897% | -1.362% |  | 2.553% | -1.057% | 3.084% | -2.688% | -2.408% |  |  | 9.768% | 3.671% | -7.885% | -2.841% | -0.5641%
2025-06-24 | -0.8889% | 1.562% | 2.105% | 0.6787% | 0.5748% | 1.536% | 1.49% | 1.984% | 1.313% | 1.961% | 3.258% | 3.031% | -2.356% | 4.766% | 1.771% | 1.711% | 0.8835% | 0.6559% | 0.8549% | 0.8339% | 1.87% | 2.34% | -0.4407% | 2.279% | 2.473% | 1.576% | -1.316% | 0.7006% | 1.8% | -1.876% | -1.842% | -2.139% | 0.1709% | 2.857% | -0.5276% | 0.181% | -2.629% | -1.962% | -0.08001% | 0.8759% | -0.8311% | -1.18% | 0.6104% | -0.0876% | 1.293% | 1.733% | -1.33% | -0.2849% | 0.02378% | -1.309% | 1.05% | 0.9442% | 2.461% | 1.105% | -0.4547% | 1.429% | 1.274% | 1.453% | 0.01946% | 1.395% | 1.149% | 1.963% | 0.8835% | 9.164% | 1.765% | 0.8549% | 1.695% | -1.512% | 0.7621% | 0.5801% | 0.6787% | -0.05725% | 2.522% | 0.3069% | 0.5994% | -1.525% | 1.152% | 0.8304% | 0.0338% | 1.303% | 1.855% | 2.173% | 0.7318% | 1.718% | 0.8759% | 1.27% | 1.035% | 0.8987% | -1.233% | -1.84% | -1.491% | -1.869% | 2.287% | -1.317% | 0.0397% | -0.558% | -2.28% | 2.264% | -0.1862% | 1.278% | 3.364% | 0.4207% | 1.111% | -0.6035% | 1.26% | -1.559% | 3.627% | -49.41% | 2.06% | 0.8287% | 1.348% | 0.5048% | 0.4915% | 1.227% | 2.28% | 1.923% | -1.967% | 0.2285% | 0.3499% | 1.248% | 2.629% | -3.723% | -5.878% | 1.506% | -0.6718% | -0.2638% | -0.5049% | -1.946% | 0.1813% | -0.7156% | -1.246% | -2.605% | -0.8539% | -0.589% | 2.178% | -2.482% | 0.7898% | 1.682% | 0.7084% | 0.07173% | -1.239% | -1.799% | -0.2166% | 0.932% | -2.622% | -0.7978% | -1.984% | 0.06483% | -0.9729% | -1.267% | 0.89% | -0.3456% | -0.257% | -0.429% | -2.204% | -2.045% | -2.69% | -1.112% | 1.83% | -0.01112% | 0.8696% | -1.622% | -1.374% | -1.293% | -0.8287% | 0.5785% | -0.8091% | -0.6037% | -1.17% | -2.272% | 0.7184% | -1.477% | -1.511% | 0.9542% | 0.9651% | 0.4416% | 0.6411% | -1.2% | -0.7128% | 2.452% | -1.611% | -0.8901% | -1.715% | 4.6% | 1.356% | 0.5899% | 1.028% | -0.5559% | -1.749% | -0.1309% | 1.155% | 0.4493% | -1.937% | -0.08785% | 0.6641% | -1.699% | 1.58% | -1.016% |  |  | -7.45% | -1.987% | -1.784% |  | -0.9021% | -1.59% | -1.081% | -1.097% | 0.5725% | 0.7318% | 1.354% | 1.369% | 1.195% | -2.197% | 0.5421% | 1.286% | 0.505% | 0.9973% | 3.78% | -0.1205% | -0.09024% | 1.73% | -0.2051% | -1.561% | 0.8031% | 0.9771% | 0.04255% | -0.2936% | 1.641% | 0.5328% | 0.4713% | -0.4391% | -2.02% | -2.142% | -2.216% | 0.2777% | 0.5981% |  | 3.264% | -1.134% | 5.72% | -1.405% | -2.138% |  |  | 10.15% | 1.381% | -9.574% | -2.154% | -1.024%
2025-06-25 | -0.4745% | -0.2966% | 2.223% | 2.13% | 1.176% | 1.629% | 1.961% | 0.3035% | 1.079% | 1.301% | 1.144% | 0.951% | -2.556% | 0.08767% | 1.514% | 1.406% | 0.9819% | 0.5348% | 0.3154% | 0.7708% | 1.845% | 1.884% | -0.4816% | 1.979% | 2.187% | 0.9415% | -2.438% | 0.3755% | 0.862% | -2.619% | -2.324% | -2.872% | 1.55% | -0.1455% | 0.03371% | 0.7537% | 0.9433% | -1.223% | 0.4423% | 2.115% | -0.2746% | -1.177% | 0.7121% | -0.1205% | 1.491% | 1.599% | 0.4363% | 0.2495% | 0.3615% | -2.798% | 1.229% | 1.059% | 0.7044% | 1.266% | -1.257% | 0.5331% | 0.3206% | 0.1879% | 0.6906% | 0.3549% | 1.776% | 0.6573% | 1.267% | 8.281% | 1.703% | 0.8348% | 2.059% | -0.9583% | 1.175% | 0.7737% | 1.175% | 0.1879% | 1.683% | 1.19% | 1.958% | -0.1453% | 2.095% | 1.329% | 0.265% | 2.108% | 1.83% | 0.2881% | 0.6581% | 1.915% | 0.4885% | 0.9819% | 0.8431% | 0.635% | -1.5% | -2.302% | -1.067% | -2.054% | 2.531% | -0.4751% | 0.5399% | 0.1648% | 0.4654% | 2.261% | 1.013% | 1.583% | 1.838% | 0.4346% | 1.375% | 0.3035% | 1.766% | -0.5521% | 2.116% | -2.62% | 0.9125% | 0.6016% | 1.141% | 1.077% | -0.2275% | 0.4645% | 2.076% | -2.317% | -2.317% | -0.111% | 0.5056% | 1.491% | 1.683% | -3.688% | -6.257% | 1.491% | -0.5444% | 0.5262% | -0.5444% | -0.3055% | -3.126% | -0.7757% | -0.2325% | -1.136% | -0.7306% | 1.189% | 0.8292% | -1.107% | 0.03762% | 1.7% | 0.2209% | -1.932% | -1.677% | -2.389% | 0.4654% | -0.3037% | -2.526% | -0.8943% | -1.269% | 0.7184% | -0.1827% | 0.6711% | -0.3037% | 0.07225% | 1.855% | 0.1416% | -1.701% | -1.886% | -1.886% | 0.1262% | -0.5447% | -2.424% | -1.949% | -2.19% | -2.427% | -3.051% | -0.057% | -1.409% | -2.455% | -0.7985% | -1.418% | -1.694% | -1.387% | -1.731% | -1.984% | -0.3542% | -1.72% | -1.628% | -0.6928% | -1.028% | -2.178% | 0.157% | -2.186% | -2.746% | -0.03621% | 1.951% | -0.9267% | -1.679% | -0.182% | -0.429% | -0.908% | -2.445% | -0.264% | -2.416% | -1.418% | -1.457% | 0.9054% | -1.153% | 0.2147% | 0.5702% |  |  | -6.095% | -2.47% | -0.9396% |  | -0.2775% | -1.94% | -0.7294% | -2.017% | 0.4577% | 0.9125% | 1.83% | 1.969% | -0.5521% | -1.986% | 1.56% | -0.5598% | 1.575% | 3.932% | 6.365% | 3.508% | 3.984% | 1.812% | -1.001% | -1.966% | 1.116% | 0.2453% | -1.378% | -1.343% | 1.716% | -0.7733% | 0.09452% | -1.92% | -2.129% | -1.902% | -2.368% | -2.365% | 0.1648% |  | 4.22% | -1.951% | 3.011% | -1.703% | -1.601% |  |  | 8.514% | 1.215% | -7.278% | -1.449% | 1.595%
2025-06-26 | 0.4011% | 1.047% | 3.014% | 2.76% | 1.36% | 2.16% | 1.56% | 1.968% | 1.109% | 1.449% | 2.814% | 2.13% | -0.7935% | 1.705% | 0.6295% | 0.4757% | -0.1628% | -0.6243% | -0.7634% | -0.4509% | 0.768% | 0.968% | -1.488% | 0.6415% | 0.678% | -0.5006% | -2.751% | -1.253% | -0.5961% | -1.253% | -2.675% | -1.895% | 0.705% | 2.798% | -0.7089% | -0.188% | 0.006456% | -2.186% | -0.6474% | 1.137% | -1.132% | -2.055% | -0.4782% | -1.301% | 0.6218% | 1.16% | 0.465% | -0.5705% | 0.9243% | -2.428% | 1.568% | 1.337% | 0.6347% | 1.079% | -2.105% | 0.5936% | -0.2132% | 1.283% | -0.2747% | 0.7851% | 0.7757% | 1.688% | 0.5757% | 8.868% | 1.203% | 0.2094% | 1.516% | -0.877% | 0.8295% | 0.2834% | 1.045% | 0.2372% | 0.1757% | 0.08338% | -0.3978% | -1.991% | 0.5389% | 0.08338% | -0.7243% | 0.3656% | 0.7526% | 1.183% | 0.09107% | 1.145% | -0.2012% | 0.5449% | 0.7064% | 0.7449% | -1.509% | -2.078% | -0.8628% | -1.899% | 2.022% | 1.037% | -0.1995% | -0.7397% | -0.9474% | 1.591% | -0.3474% | 0.6064% | 0.8603% | -0.7935% | 0.2141% | -1.024% | -0.5619% | -6.04% | 2.084% | -1.363% | 1.068% | -0.5004% | -0.3586% | 0.5644% | -0.08329% | 0.3406% | 1.391% | -2.224% | -1.377% | -2.141% | -1.239% | 0.7834% | 2.03% | -4.206% | -7.461% | 0.3603% | 0.6988% | 0.3612% | -0.8012% | -0.8935% | -2.148% | -0.9722% | -1.196% | -1.182% | -0.8486% | 0.8995% | -0.2461% | -1.388% | 0.4074% | 0.6229% | -0.2203% | 0.01415% | -1.488% | -1.935% | 0.6449% | 1.225% | -2.17% | -0.8344% | -1.486% | 0.2533% | -1.694% | -0.3231% | 0.1526% | -1.147% | 0.8945% | -0.7781% | -2.417% | -1.686% | -2.547% | -0.7628% | 0.326% | -1.113% | -1.036% | -1.533% | -1.728% | -0.8219% | -0.483% | -1.334% | -1.549% | 0.3468% | -0.4208% | 1.197% | 0.3011% | -0.5652% | -1.693% | 0.1592% | -1.735% | -1.113% | -1.059% | 0.4349% | -1.036% | 1.213% | -0.5764% | -1.7% | -2.461% | 2.4% | 0.4002% | -0.7873% | 0.3758% | 0.3833% | 0.03227% | -1.539% | 0.4972% | -0.0007117% | 0.05375% | 0.3183% | 0.3572% | -0.5764% | -0.1096% | 1.221% |  |  | -5.767% | -1.199% | -1.127% |  | 1.266% | -1.086% | -0.6628% | -1.417% | 0.07569% | -0.3243% | 2.391% | 1.776% | 0.08338% | -0.7705% | 0.9218% | 1.914% | 1.421% | 3.718% | 5.864% | 4.264% | 4.569% | 2.884% | -1.28% | 0.7212% | 1.286% | 0.9697% | 0.1881% | 0.0816% | 1.249% | 0.9479% | 2.371% | 1.182% | -0.9634% | -0.1467% | -1.554% | -0.8972% | -1.176% |  | 4.697% | -1.522% | 4.878% | -1.973% | -1.658% |  |  | 8.249% | 2.9% | -6.903% | -2.192% | 2.7%
2025-06-27 | 3.134% | 3.35% | 3.195% | 4.149% | 4.062% | 3.845% | 2.467% | 3.897% | 0.07455% | 0.7322% | 3.204% | 3.949% | -0.7333% | 0.2781% | 2.9% | 3.29% | 2.415% | 2.284% | 0.1879% | 0.388% | 1.253% | 1.617% | 0.6922% | 0.2928% | 1.485% | 1.309% | -2.222% | 1.966% | 1.565% | -2.112% | -2.451% | -1.557% | 0.3333% | 0.8097% | -0.8981% | -1.195% | -0.135% | -2.008% | -0.3691% | 1.695% | -1.089% | -1.739% | -0.2304% | -1.115% | 1.14% | 1.513% | -2.982% | 0.2726% | 1.565% | -2.781% | 1.556% | 1.721% | 0.2928% | 1.264% | -2.982% | 0.3006% | 1.148% | 2.241% | 0.1156% | 0.6397% | 1.235% | 1.586% | 0.5588% | 6.6% | 0.7803% | 1.325% | 1.805% | 0.1719% | -0.05692% | 0.1252% | 0.7582% | 1.608% | 1.088% | 0.8536% | 0.5703% | -0.7863% | 0.1926% | 1.53% | 1.279% | 1.084% | 0.897% | 0.3853% | 1.443% | 1.738% | 1.4% | 0.4894% | 0.4894% | 0.07316% | 0.1425% | -0.8894% | -0.4% | -1.861% | 1.201% | 1.079% | 1.488% | 1.547% | -33.69% | 1.686% | 1.487% | 1.27% | 0.8103% | 1.729% | 2.432% | -2.208% | 0.6089% | 2.224% | 1.349% | -2.566% | 1.617% | 1.48% | 1.893% | 0.7642% | 0.6551% | 1.811% | -0.08293% | -2.615% | -2.853% | -1.673% | -1.179% | 1.946% | 3.004% | -4.71% | -5.38% | 0.1078% | 0.9317% | -1.488% | 0.07316% | -1.054% | -2.328% | -2.182% | -2.486% | -1.469% | -1.237% | 0.4295% | -0.4061% | -1.88% | -0.7704% | -1.232% | -1.79% | -2.201% | -1.341% | -2.254% | -2.138% | -1.493% | -1.913% | -1.453% | -1.913% | -2.125% | -1.421% | -2.294% | -1.845% | -2.606% | -1.11% | -2.459% | -1.913% | -2.433% | -0.6639% | -1.098% | 0.06143% | -1.824% | -1.538% | -0.7718% | -2.325% | -2.177% | -0.1033% | -0.9773% | -0.9296% | -2.754% | -0.6051% | -1.289% | -1.146% | -2.653% | -1.522% | -0.4301% | -2.232% | -1.552% | -0.5963% | -1.675% | -2.434% | 4.182e-05% | -1.88% | -2.232% | -1.421% | 2.365% | -0.6894% | -1.195% | -0.4132% | -0.3627% | 0.8581% | -2.041% | -0.7104% | -0.3859% | -1.675% | -0.1666% | -0.7981% | -2.377% | 0.6245% | -1.412% |  |  | -99.99% | -1.874% | -1.695% |  | 1.138% | 0.4981% | 1.556% | -2.156% | 1.556% | 0.6195% | 1.261% | 1.877% | 0.1425% | -1.852% | -0.1697% | 0.2813% | 1.919% | 4.108% | 6.188% | 5.763% | 5.39% | 1.79% | -1.248% | 0.5425% | 3.937% | 2.235% | 1.02% | 1.493% | 4.52% | 2.861% | 1.773% | 0.131% | -1.853% | -0.8361% | -0.962% | -1.122% | -1.613% |  | 6.267% | -1.522% | 0.4024% | -1.936% | -1.808% |  |  | 8.496% | 3.666% | -6.121% | 0.8371% | 1.284%
2025-06-28 | 0.9076% | 2.841% | 0.1374% | 0.4083% | 2.716% | 2.523% | 3.211% | 3.211% | 1.933% | 2.443% | 0.9396% | 3.972% | -2.124% | -0.1932% | 2.45% | 1.492% | 1.867% | 1.711% | 1.215% | 1.533% | -0.9045% | 0.001911% | -1.295% | 1.31% | -0.4966% | 0.8402% | -2.555% | -0.9867% | -0.07913% | -1.533% | -0.8015% | -2.645% | -1.355% | -0.1166% | 1.19% | -2.276% | 1.19% | 0.6479% | -9.25% | 1.534% | 1.69% | 1.336% | 1.19% | 0.6062% | 0.1478% | -0.3107% | -0.939% | 0.8354% | -0.2973% | -2.688% | 1.19% | 1.565% | 1.245% | 1.755% | -1.612% | 1.884% | 2.208% | -9.125% | -0.2829% | 1.06% | 3.326% | -1.81% | 2.69% | 4.88% | 1.994% | 0.1382% | 1.581% | 0.2728% | 1.44% | 0.4083% | 0.7521% | 2.221% | 1.002% | -0.4253% | -0.6533% | 0.1246% | 1.014% | 1.044% | 1.408% | 2.042% | -0.2065% | 1.19% | 2.023% | 0.7417% | 2.127% | 0.6687% | -0.3732% | 1.929% | 1.106% | -0.269% | -0.2773% | -2.035% | 0.1478% | -11.02% | 1.949% | 1.554% | -100% | 1.283% | -0.1856% | -0.5816% | 0.502% | -0.8525% | -0.03977% | -0.9879% | -0.8108% | 0.7521% | 0.3654% | -2.155% | -2.071% | 2.338% | -0.7467% | -1.978% | -2.024% | -0.7645% | 0.7417% | -0.3836% | -1.233% | -2.385% | -0.9126% | -0.5816% | 0.7729% | -7.479% | -6.923% | -0.394% | -1.957% | -1.922% | -0.394% | -1.436% | 0.9489% | 0.05979% | -7.95% | 0.7152% | 2.139% | 2.864% | 3.737% | -0.8346% | 3.62% | 3.134% | 2.693% | -8.719% | 0.9364% | -1.256% | 2.107% | 3.302% | -0.8004% | 1.206% | 0.4395% | 2.66% | 0.5517% | 1.696% | 1.639% | -0.2065% | -0.5144% | -1.155% | -1.467% | -1.019% | 0.8146% | 2.888% | 1.992% | -0.8954% | 1.431% | -2.213% | -1.604% | -2.166% | 1.244% | -0.4693% | -0.6531% | -2.11% | -1.549% | -2.887% | 0.06685% | -1.936% | -1.407% | -9.644% | 0.05411% | 1.075% | 2.74% | 1.665% | 0.3538% | 0.7379% | -1.564% | -1.07% | -1.632% | 2.171% | -0.679% | 1.309% | -1.066% | 0.1478% | -2.594% | -9.297% | -0.3791% | 1.908% | 1.075% | 2.371% | 0.7273% | -0.4212% | 0.5903% | 0.05294% |  |  | -100% | -0.4456% | -1.431% |  | -1.693% | 1.179% | -0.394% | -0.07102% | -10.63% | 2.232% | 0.6791% | 1.492% | -1.353% | -0.3107% | -1.196% | -1.123% | -1.598% | 5.857% | 6.018% | 4.772% | 4.793% | 2.903% | -0.7541% | -1.439% | 0.6629% | -0.218% | -2.43% | -2.324% | 2.173% | -0.5062% | -1.07% | -0.1532% | 0.6298% | 1.581% | -1.759% | -1.276% | -1.212% |  | 5.905% | -1.069% | 0.3415% | -2.795% | -1.434% |  |  | 4.764% | 4.212% | -6.65% | -1.899% | 0.4569%
2025-06-29 | -0.4082% | 1.664% | 1.864% | 1.51% | 1.228% | 1.274% | 1.746% | 2.101% | 1.193% | 1.647% | 1.155% | -0.7591% | -0.8536% | 4.034% | 1.51% | 0.5881% | 0.6826% | 0.5645% | 0.9008% | 1.228% | 0.3281% | 1.864% | -0.9536% | 1.786% | -1.717% | 1.337% | -1.608% | 0.6301% | 1.47% | -0.8194% | -0.0001225% | -3.656% | -0.656% | 1.121% | 0.3281% | 1.127% | 1.155% | -2.035% | -0.2627% | 1.628% | -1.208% | -1.433% | -0.02638% | -3.193% | 0.8008% | 1.155% | -1.717% | -0.02638% | 0.0587% | -2.301% | 0.4463% | 0.919% | 2.206% | 0.9453% | -0.2227% | 0.2625% | 0.9663% | 0.05634% | 0.8402% | -1.954% | 1.155% | 2.605% | 2.219% | 3.92% | 0.6826% | 0.2463% | 1.228% | -2.481% | -0.1446% | 0.21% | 0.6826% | -0.9718% | -0.8536% | 0.09179% | 1.365% | 0.1049% | 1.576% | 0.3281% | -0.1446% | 1.446% | 0.919% | 1.628% | -0.02638% | 0.6826% | -0.9718% | 0.21% | -0.7354% | -0.3809% | -0.7591% | -1.421% | -0.2589% | -1.717% | 1.392% | -1.775% | -0.4203% | -0.2627% | -100% | 0.09179% | 0.6826% | -0.8536% | -1.563% | 1.037% | -1.208% | 0.6826% | 1.365% | -0.6172% | 3.256% | 0.5567% | -0.3809% | 0.5251% | 0.4645% | 0.4645% | -1.859% | -2.553% | 1.628% | -1.114% | -0.2245% | -2.206% | -0.1052% | 0.8008% | -1.362% | -5.567% | -7.248% | 0.919% | -2.059% | 0.6301% | -1.645% | -0.7709% | -2.048% | 0.3885% | -1.532% | -0.01547% | 0.639% | -1.251% | -0.8209% | -0.6775% | -1.505% | -0.3797% | -1.189% | 1.746% | 0.2572% | -1.281% | -0.02638% | 2.766% | -1.787% | 0.9554% | 0.2218% | 1.585% | 0.4645% | 2.995% | 1.893% | 2.219% | -0.08416% | -0.1446% | 0.7181% | -0.6409% | 1.155% | 2.952% | 1.349% | -1.042% | 0.2864% | -2.237% | -0.6698% | -2.051% | 1.136% | -0.2958% | -1.281% | -4.813% | -0.1572% | -2.338% | -0.8695% | -0.6515% | -0.2448% | -5.918% | -1.233% | -0.3245% | 1.11% | -1.52% | -1.626% | 0.9902% | 0.6905% | -1.095% | -1.52% | 0.04839% | -1.516% | 1.136% | -0.0434% | -0.6744% | -0.8465% | -0.49% | -1.878% | -0.3006% | 0.7153% | -0.205% | -0.3245% | -0.9221% | -1.185% | -1.639% |  |  | -100% | -0.3797% | -0.1904% |  | -0.09266% | 0.3281% | -0.06183% | -0.7709% | -0.6291% | -0.2982% | -1.208% | 0.2927% | -0.7709% | 0.0327% | 0.6826% | -1.657% | 0.9558% | 5.147% | 6.285% | 4.42% | 3.69% | 5.635% | -2.112% | -1.318% | -1.87% | 0.6301% | -1.717% | -1.826% | 1.874% | 1.883% | 0.315% | -1.534% | -1.814% | -1.429% | -0.8332% | -0.5753% | -0.2831% |  | 4.596% | -0.03601% | 1.092% | -1.437% | -1.569% |  |  | 3.92% | 5.214% | -8.522% | -0.8332% | -0.6218%
2025-06-30 | 2.301% | 1.332% | 1.528% | 0.9282% | 0.7782% | 1.078% | 1.528% | 1.828% | 0.9222% | 1.354% | 3.628% | 2.878% | 2.128% | 3.723% | 1.078% | 0.9282% | 0.4783% | -0.1216% | 1.055% | 0.6398% | 1.078% | 1.378% | 0.9166% | 1.711% | 1.47% | 0.5014% | 1.747% | 0.6449% | 1.045% | 1.445% | 1.178% | 0.3783% | 2.149% | 3.41% | -0.7215% | -0.332% | 0.9282% | -0.4215% | -2.221% | 0.7782% | 0.9282% | -1.621% | 3.028% | 1.378% | 2.578% | 0.9282% | -5.59% | 1.348% | -4.837% | -5.125% | -0.4215% | 1.678% | 0.1117% | 1.845% | 0.08606% | 1.711% | 1.978% | 1.978% | 0.7782% | 2.111% | 0.4783% | 2.883% | 0.9282% | 4.434% | 0.6398% | 0.2245% | 0.7782% | 1.609% | -0.7215% | -0.4215% | 1.078% | 0.6282% | 2.428% | 1.828% | 2.351% | 0.1117% | 1.578% | 0.3283% | 1.183% | 1.194% | 0.1783% | 0.9282% | -0.5715% | 0.3283% | 1.078% | -1.771% | 2.128% | -1.771% | -1.621% | -0.1216% | -1.928% | 0.08606% | 0.02838% | -4.921% | 0.7782% | -0.7215% | -92.88% | 1.378% | 2.428% | 0.7782% | -1.351% | 2.683% | -1.336% | 0.02838% | 0.6449% | -2.821% | 1.751% | -1.002% | 0.6282% | 0.7782% | 0.6398% | 2.855% | 0.7782% | 1.045% | 0.7782% | 0.9282% | 0.7397% | -2.421% | 0.6449% | 0.9282% | -1.831% | -5.62% | -3.088% | 0.1783% | 0.3283% | 0.5116% | 1.078% | 2.578% | -3.887% | 2.778% | 2.301% | 3.132% | 2.301% | 0.1238% | 1.083% | 0.9434% | -0.4567% | 2.063% | 1.21% | 2.278% | -0.523% | -1.021% | 2.428% | -1.852% | 2.278% | -1.547% | -0.2566% | 1.318% | 2.301% | 1.609% | 2.287% | 1.708% | 1.471% | 1.873% | 0.2833% | 2.578% | 0.4783% | 2.728% | 0.255% | 1.575% | -0.6381% | -1.565% | 1.654% | -1.986% | -1.447% | -1.571% | 2.227% | -5.492% | -1.262% | -0.8431% | 1.632% | -1.134% | -0.3685% | -2.736% | -0.3685% | -1.019% | -0.8067% | -0.6853% | -2.391% | -1.262% | 1.363% | -1.447% | -2.391% | -2.022% | -0.4567% | -0.773% | 0.7586% | 1.05% | -6.085% | -1.857% | -0.382% | -2.172% | -0.5033% | -1.11% | -0.655% | -0.1393% | -0.9887% | 0.1034% |  |  | -100% | -2.479% | -2.93% |  | -0.3756% | 2.278% | -2.041% | -1.921% | 2.728% | 0.02838% | 0.1783% | -1.306% | 0.4783% | -1.546% | -0.2716% | -0.8714% | 1.178% | 3.178% | 5.259% | 2.748% | 3.346% | 3.932% | -2.93% | -0.648% | 1.354% | 1.445% | 1.332% | -0.1908% | 2.65% | 2.301% | 1.178% | 0.6449% | -0.5967% | -2.352% | 0.02558% | -0.2337% | -0.9887% |  | 5.855% | -1.117% | 0.4022% | -0.9827% | -1.374% |  |  | 6.944% | 6.379% | -6.028% | -1.063% | -0.2287%
2025-07-01
2025-07-02
2025-07-03
2025-07-04
2025-07-05
2025-07-06
2025-07-07
2025-07-08
2025-07-09
2025-07-10
2025-07-11
2025-07-12
2025-07-13
2025-07-14
2025-07-15
2025-07-16
2025-07-17
2025-07-18
2025-07-19
2025-07-20
2025-07-21
2025-07-22
2025-07-23
2025-07-24
2025-07-25
2025-07-26
2025-07-27
Formulas:
Date = [Date, row above]+1