## O2Summary
Performance Summary TGPXIIPL
Month | 2025-06-01
Date | 2025-06-30
Financial Year | Year-1
Year Start Date | 2025-04-01
Year End Date | 2026-03-31
Sr. No. | Particular | Target | Measured | Deviation | Remarks
1 | E_Grid Daily (MWh) | 801.6133 | 1301.85 | 62.4%
| E_Grid MTD(MWh) | 24048.3982 | 26356.95 | 9.6%
| E_Grid YTD (MWh) | 73151.268 | 63931.05 | -12.6%
2 | Wind Speed Daily | 7.15 | 9.5537 | 33.62%
| Wind Speed MTD | 7.15 | 7.604 | 6.35%
| Wind Speed YTD | 6.9967 | 6.8459 | -2.155%
3 | PA Daily | 96.03% | 94.28% | -1.825%
| PA MTD | 96.03% | 96.74% | 0.7348%
| PA YTD | 96.03% | 92.74% | -3.43%
4 | EGA Daily | 99.5% | 100% | 0.5025%
| EGA MTD | 99.5% | 100% | 0.5025%
| EGA YTD | 99.5% | 100% | 0.5025%
5 | IGA Daily | 99% | 100% | 1.01%
| IGA MTD | 99% | 99.71% | 0.7132%
| IGA YTD | 99% | 95.61% | -3.428%
6 | MA Daily | 97% | 94.28% | -2.807%
| MA MTD | 97% | 97.02% | 0.02154%
| MA YTD | 97% | 97% | -0.00268%
7 | CUF Daily | 47.58% | 77.27% | 62.4%
| CUF MTD | 47.58% | 52.15% | 9.6%
| CUF YTD | 47.71% | 41.7% | -12.6%
8 | Line Loss Daily | 5% | 3.426% | 31.48%
| Line Loss MTD | 5% | 3.238% | 35.24%
| Line Loss YTD | 5% | 3.431% | 31.37%
9 | Reactive Power Daily | 5% | 2.136% | 57.27%
| Reactive Power MTD | 5% | 0.9123% | 81.75%
| Reactive Power YTD | 5% | 0.7953% | 84.09%
10 | Expected Energy Daily | 1451.83 | 1348.035 | -7.149%
| Expected Energy MTD | 27793.5 | 27231.977 | -2.02%
| Expected Energy YTD | 69424.2045 | 66139.927 | -4.731%

## MonthlyKPI
Till Date | 2025-06-30 | 0 | 0 | 0 | 0
TGPXIIPL Performance Summary (MTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | WTG Total (MWh) | Line Losses(%) | E_WS_Corrected | Expected Energy | Loss (%) | Reactive Power (%)
2025-06-01 | 30 | 7.15 | 7.604 | 24048.3982 | 26356.95 | 47.58% | 52.15% | 99.5% | 100% | 97% | 97.02% | 99% | 99.71% | 96.03% | 96.74% | 27231.977 | 3.32% | 27793.5 | 27793.5 | 3.238% | 0.9123%
Start Date | 2025-06-24
End Date | 2025-06-30
TGPXIIPL Performance Summary (WTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | E_WS_Corrected
2025-06-01 | 7 | 7.15 | 7.6373 | 5611.2929 | 6268.05 | 47.58% | 53.15% | 99.5% | 100% | 97% | 95.1% | 99% | 100% | 96.03% | 95.1% | 6825.22
Start Date | 2025-06-01
End Date | 2025-06-30
TGPXIIPL Performance Summary (LTD)
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA (%) | Measured IGA (%) | Target PA(%) | Measured PA (%)
2025-06-01 | 30 | 7.15 | 7.604 | 24048.3982 | 27231.977 | 47.58% | 53.88% | 99.7% | 100% | 98.6% | 97.02% | 99.5% | 99.71% | 98.11% | 96.74%
Formulas:
Days = [Days, row below]-6

## Analytices
Start Date | 2025-06-01
End Date | 2025-06-30 | 720 | 7.6
WTG No. | O2_01 | O2_02 | O2_03 | O2_04 | O2_05 | O2_06 | O2_07 | O2_08 | O2_09 | O2_10 | O2_11 | O2_12 | O2_13 | O2_14 | O2_15 | O2_16 | O2_17 | O2_18 | O2_19 | O2_20 | O2_21 | O2_22 | O2_23 | O2_24 | O2_25 | O2_26
MA | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46%
WTG BD Hours | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167 | 18.3167
IGA | 100% | 100% | 100% | 99.42% | 100% | 99.42% | 99.42% | 99.42% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.42% | 99.42% | 99.42% | 100% | 99.42% | 99.42% | 99.42% | 99.42% | 99.42% | 99.42%
METERING YARD
FEEDER | 0 | 0 | 0 | 4.1833 | 0 | 4.1833 | 4.1833 | 4.1833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1833 | 4.1833 | 4.1833 | 0 | 4.1833 | 4.1833 | 4.1833 | 4.1833 | 4.1833 | 4.1833
OG
TRANSFER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
USS
EGA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
External Grid | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Generation | 1042072 | 1147233 | 1039407 | 1079637 | 1100626 | 1096559 | 1042147 | 998574 | 1051173 | 1012180 | 1057901 | 466025 | 1051726 | 1073737 | 1067093 | 1021843 | 1136261 | 1098026 | 1085699 | 1041146 | 1057734 | 1113250 | 1073822 | 1078030 | 1150470 | 1049606
PA | 97.46% | 97.46% | 97.46% | 96.88% | 97.46% | 96.88% | 96.88% | 96.88% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 97.46% | 96.88% | 96.88% | 96.88% | 97.46% | 96.88% | 96.88% | 96.88% | 96.88% | 96.88% | 96.88%
Sum of BD | 18.3167 | 2.5 | 13.5167 | 14.6 | 6.9167 | 1.95 | 19.9833 | 24.75 | 6.5997 | 9.15 | 1.1833 | 349.9292 | 8.7 | 1.3833 | 8.95 | 14.1333 | 6.7667 | 3.15 | 9.9 | 5 | 2.55 | 3.3167 | 4.3 | 1.0833 | 1.5833 | 2.7333
Count of BD | 17 | 10 | 9 | 40 | 38 | 9 | 10 | 60 | 8 | 15 | 9 | 16 | 11 | 10 | 6 | 12 | 40 | 9 | 15 | 14 | 11 | 13 | 23 | 8 | 8 | 10
MTTR WTG | 1.0775 | 0.25 | 1.5019 | 0.365 | 0.18202 | 0.21667 | 1.9983 | 0.4125 | 0.82497 | 0.61 | 0.13148 | 21.8706 | 0.79091 | 0.13833 | 1.4917 | 1.1778 | 0.16917 | 0.35 | 0.66 | 0.35714 | 0.23182 | 0.25513 | 0.18696 | 0.13542 | 0.19792 | 0.27333
MTBF WTG | 41.2755 | 71.75 | 78.4981 | 17.635 | 18.7654 | 79.7833 | 70.0017 | 11.5875 | 89.175 | 47.39 | 79.8685 | 23.1294 | 64.6636 | 71.8617 | 118.5083 | 58.8222 | 17.8308 | 79.65 | 47.34 | 51.0714 | 65.2227 | 55.1295 | 31.1174 | 89.8646 | 89.8021 | 71.7267
WS (M/S) | 7.6 | 7.8 | 7.4 | 7.7 | 7.7 | 7.8 | 7.6 | 7.5 | 7.5 | 7.4 | 7.6 | 7.3 | 7.5 | 7.6 | 7.5 | 7.5 | 8 | 7.7 | 7.7 | 7.5 | 7.6 | 7.9 | 7.6 | 7.6 | 7.7 | 7.5
Fault Analysis
2023-04-01
|  |  | Put hour Here |  | Default hour for full Data
|  |  | 19704 |  | 19704
Finacial Year | (Multiple Items)
Row Labels | Sum of Breakdown Time | Count of Error Text | MTTR | MTBF
Grand Total |  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0!
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.

## Daily KPI
Date | Financial Year | Calendar Year | Month Year | Days | Operating Hours | GHI-UP (KWh/m2) | GHI-Down(KWh/m2) | POA-UP(KWh/m2) | POA-Down(KWh/m2) | Amb_Temp(°C) | Mod_Temp(°C) | WS_Avg(m/s) | WS_Max(m/s) | PA(%) | MA (%) | IGA (%) | EGA(%) | EMA (%) | TA (%) | PR(%) | WPR(%) | CUF(%) | Gen_Exp (kWh) | Mtr_Export (kWh) | Mtr_Import (kWh) | Mtr_Net_Exp (KWh) | Operational Capacity (MW) | Bugt_Resource | Bugt_Energy | Bugt PR | Bugt CUF | Bugt_PA | Bugt_EGA | Expected Energy | Actual Energy WPR | RA (%) | Mod Clean Dry (Num) | Mod Clean Wet (Num) | Line Loss(%) | Reactive Power (%) | Bugt Line loss (%) (Wind) | Bugt Reactive Power (%) (Wind) | Bugt Capacity | CC*Bugt
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 7.14 | 0 | 100% | 100% | 100% | 100% |  |  |  |  | 45.81% | 801666 | 771750 | 0 | 771750 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 843.5335 |  |  |  |  | 3.732% | 0% | 5% | 5% | 70.2
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 5.9437 | 0 | 100% | 100% | 100% | 100% |  |  |  |  | 31.78% | 552111 | 535500 | 0 | 535500 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 562.5916 |  |  |  |  | 3.009% | 0% | 5% | 5% | 70.2
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | [7 empty] | 6.513 | 0 | 100% | 100% | 100% | 100% |  |  |  |  | 38.38% | 667722 | 646650 | 0 | 646650 | 70.2 | 6.89 | 632771.0323 |  | 37.56% | 96.03% | 99.5% | 675.4049 |  |  |  |  | 3.156% | 0% | 5% | 5% | 70.2
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.0269 | 0 | 98.29% | 98.29% | 100% | 100% |  |  |  |  | 31.2% | 544118 | 525600 | 0 | 525600 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 664.4211 |  |  |  |  | 3.403% | 0% | 5% | 5% | 70.2
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.4382 | 0 | 98.14% | 98.14% | 100% | 100% |  |  |  |  | 16.37% | 285682 | 275850 | 0 | 275850 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 294.6404 |  |  |  |  | 3.442% | 0% | 5% | 5% | 70.2
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.8482 | 0 | 97.33% | 97.65% | 99.67% | 100% |  |  |  |  | 20.51% | 357239 | 346050 | 450 | 345600 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 371.21 |  |  |  |  | 3.132% | 0% | 5% | 5% | 70.2
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.285 | 0 | 97.59% | 97.59% | 100% | 100% |  |  |  |  | 15.25% | 269263 | 257400 | 450 | 256950 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 281.07 |  |  |  |  | 4.406% | 0.4846% | 5% | 5% | 70.2
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.3639 | 0 | 94.85% | 95.49% | 99.33% | 100% |  |  |  |  | 12.71% | 223271 | 214200 | 0 | 214200 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 230.95 |  |  |  |  | 4.063% | 0.403% | 5% | 5% | 70.2
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.4386 | 0 | 98.4% | 98.4% | 100% | 100% |  |  |  |  | 35.79% | 620284 | 603000 | 0 | 603000 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 667.03 |  |  |  |  | 2.786% | 0.5078% | 5% | 5% | 70.2
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.1744 | 0 | 96.93% | 97.46% | 99.45% | 100% |  |  |  |  | 47.65% | 834723 | 802800 | 0 | 802800 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 890.54 |  |  |  |  | 3.824% | 3.828% | 5% | 5% | 70.2
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.0791 | 0 | 97.18% | 97.18% | 100% | 100% |  |  |  |  | 47.09% | 823138 | 793800 | 450 | 793350 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 885.16 |  |  |  |  | 3.564% | 0.328% | 5% | 5% | 70.2
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.09 | 0 | 98.75% | 98.75% | 100% | 100% |  |  |  |  | 44.07% | 766278 | 742500 | 0 | 742500 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 808 |  |  |  |  | 3.103% | 0.3523% | 5% | 5% | 70.2
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.2136 | 0 | 98.08% | 98.08% | 100% | 100% |  |  |  |  | 57.85% | 1006142 | 974700 | 0 | 974700 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1103.33 |  |  |  |  | 3.125% | 1.655% | 5% | 5% | 70.2
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.1076 | 0 | 96.15% | 96.15% | 100% | 100% |  |  |  |  | 59.62% | 1041716 | 1004400 | 0 | 1004400 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1083.02 |  |  |  |  | 3.582% | 0.5184% | 5% | 5% | 70.2
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.9831 | 0 | 65.04% | 98.7% | 65.89% | 100% |  |  |  |  | 9.776% | 173786 | 164700 | 0 | 164700 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 176.01 |  |  |  |  | 5.228% | 0.2588% | 5% | 5% | 70.2
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.6408 | 0 | 72.22% | 95.42% | 75.69% | 100% |  |  |  |  | 35.02% | 607437 | 589950 | 0 | 589950 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 682.2 |  |  |  |  | 2.879% | 0.3704% | 5% | 5% | 70.2
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.9527 | 0 | 95.99% | 95.99% | 100% | 100% |  |  |  |  | 67.17% | 1174575 | 1131750 | 0 | 1131750 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1310.71 |  |  |  |  | 3.646% | 1.303% | 5% | 5% | 70.2
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.6514 | 0 | 93.62% | 93.62% | 100% | 100% |  |  |  |  | 62.93% | 1098717 | 1060200 | 0 | 1060200 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1204.55 |  |  |  |  | 3.506% | 1.679% | 5% | 5% | 70.2
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.9019 | 0 | 92.19% | 92.59% | 99.57% | 100% |  |  |  |  | 54.25% | 947749 | 913950 | 0 | 913950 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1042.18 |  |  |  |  | 3.566% | 2.944% | 5% | 5% | 70.2
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.2235 | 0 | 97.17% | 97.17% | 100% | 100% |  |  |  |  | 50.13% | 875991 | 845100 | 450 | 844650 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 924.98 |  |  |  |  | 3.526% | 4.212% | 5% | 5% | 70.2
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 7.6607 | 0 | 96.46% | 96.46% | 100% | 100% |  |  |  |  | 49.65% | 864039 | 836550 | 0 | 836550 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 946.76 |  |  |  |  | 3.181% | 0.2604% | 5% | 5% | 70.2
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.905 | 0 | 96.94% | 96.94% | 100% | 100% |  |  |  |  | 66.4% | 1158786 | 1118700 | 0 | 1118700 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1285.97 |  |  |  |  | 3.459% | 0.8543% | 5% | 5% | 70.2
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.8564 | 0 | 98.18% | 98.18% | 100% | 100% |  |  |  |  | 40.79% | 708938 | 687150 | 0 | 687150 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 742.63 |  |  |  |  | 3.073% | 0.1904% | 5% | 5% | 70.2
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 4.9753 | 0 | 55.26% | 97.81% | 56.5% | 100% |  |  |  |  | 15.87% | 276454 | 267300 | 0 | 267300 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 287.24 |  |  |  |  | 3.311% | 0.1627% | 5% | 5% | 70.2
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.212 | 0 | 86.8% | 96.33% | 90.1% | 100% |  |  |  |  | 19.71% | 342173 | 332100 | 0 | 332100 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 353.11 |  |  |  |  | 2.944% | 0.1315% | 5% | 5% | 70.2
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.6525 | 0 | 96.84% | 96.84% | 100% | 100% |  |  |  |  | 27.56% | 480100 | 464400 | 0 | 464400 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 502.87 |  |  |  |  | 3.27% | 0.1874% | 5% | 5% | 70.2
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.8495 | 0 | 97.63% | 97.63% | 100% | 100% |  |  |  |  | 29.01% | 502706 | 488700 | 0 | 488700 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 510 |  |  |  |  | 2.786% | 0.179% | 5% | 5% | 70.2
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.1728 | 0 | 95.96% | 95.96% | 100% | 100% |  |  |  |  | 34.03% | 592507 | 573300 | 0 | 573300 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 628.86 |  |  |  |  | 3.242% | 0.2278% | 5% | 5% | 70.2
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.2133 | 0 | 95.37% | 95.37% | 100% | 100% |  |  |  |  | 35.12% | 613361 | 591750 | 0 | 591750 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 645.69 |  |  |  |  | 3.523% | 1.761% | 5% | 5% | 70.2
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 5.668 | 0 | 95.75% | 95.75% | 100% | 100% |  |  |  |  | 30.07% | 525996 | 507150 | 450 | 506700 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 546.95 |  |  |  |  | 3.583% | 0.2566% | 5% | 5% | 70.2
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 6.61 | 0 | 94.89% | 96.39% | 98.44% | 100% |  |  |  |  | 37.9% | 659514 | 638550 | 0 | 638550 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 695.35 |  |  |  |  | 3.179% | 0.2729% | 5% | 5% | 70.2
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.3967 | 0 | 95.43% | 95.43% | 100% | 100% |  |  |  |  | 58.68% | 1021944 | 988650 | 0 | 988650 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1133.84 |  |  |  |  | 3.258% | 0.2642% | 5% | 5% | 70.2
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | [7 empty] | 8.18 | 0 | 96.88% | 96.88% | 100% | 100% |  |  |  |  | 57.91% | 1009423 | 975600 | 0 | 975600 | 70.2 | 6.65 | 697760.5425 |  | 41.42% | 96.03% | 99.5% | 1088.32 |  |  |  |  | 3.351% | 0.2675% | 5% | 5% | 70.2
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 8.4492 | 0 | 98.61% | 98.61% | 100% | 100% |  |  |  |  | 64.26% | 1122695 | 1082700 | 0 | 1082700 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 1190.71 |  |  |  |  | 3.562% | 0.2405% | 5% | 5% | 70.2
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.8017 | 0 | 98.16% | 98.16% | 100% | 100% |  |  |  |  | 40.46% | 732600 | 681750 | 0 | 681750 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 781.68 |  |  |  |  | 6.941% | 0.3071% | 5% | 5% | 70.2
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 8.6568 | 0 | 95.58% | 95.58% | 100% | 100% |  |  |  |  | 63.76% | 1085131 | 1074150 | 0 | 1074150 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 1224.47 |  |  |  |  | 1.012% | 2.654% | 5% | 5% | 70.2
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.7652 | 0 | 96.81% | 96.81% | 100% | 100% |  |  |  |  | 40.68% | 711947 | 685800 | 450 | 685350 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 773.86 |  |  |  |  | 3.673% | 2.908% | 5% | 5% | 70.2
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.2849 | 0 | 98.3% | 98.3% | 100% | 100% |  |  |  |  | 44.02% | 767792 | 741600 | 0 | 741600 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 837.33 |  |  |  |  | 3.411% | 2.93% | 5% | 5% | 70.2
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 6.8863 | 0 | 67.14% | 90% | 74.6% | 100% |  |  |  |  | 24.49% | 425147 | 412650 | 0 | 412650 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 541.99 |  |  |  |  | 2.939% | 0.5292% | 5% | 5% | 70.2
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.8334 | 0 | 81.46% | 87.46% | 93.13% | 100% |  |  |  |  | 22.38% | 391213 | 377100 | 0 | 377100 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 371.67 |  |  |  |  | 3.607% | 5.406% | 5% | 5% | 70.2
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.144 | 0 | 97.14% | 98.12% | 99.01% | 100% |  |  |  |  | 11.08% | 194603 | 187200 | 450 | 186750 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 194.403 |  |  |  |  | 3.804% | 0.2311% | 5% | 5% | 70.2
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.2123 | 0 | 88.73% | 99.71% | 88.99% | 100% |  |  |  |  | 12.47% | 218799 | 210150 | 0 | 210150 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 215.78 |  |  |  |  | 3.953% | 0.2056% | 5% | 5% | 70.2
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.929 | 0 | 74.6% | 98.54% | 75.7% | 100% |  |  |  |  | 20.22% | 352993 | 341550 | 900 | 340650 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 361.29 |  |  |  |  | 3.242% | 0.2549% | 5% | 5% | 70.2
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.7262 | 0 | 94.38% | 97.89% | 96.41% | 100% |  |  |  |  | 17.57% | 305561 | 296550 | 450 | 296100 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 313.28 |  |  |  |  | 2.949% | 0.1472% | 5% | 5% | 70.2
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.93 | 0 | 93.71% | 99.44% | 94.24% | 100% |  |  |  |  | 18.16% | 314946 | 306000 | 0 | 306000 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 314.91 |  |  |  |  | 2.84% | 0.2857% | 5% | 5% | 70.2
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.2229 | 0 | 96.92% | 98.46% | 98.43% | 100% |  |  |  |  | 23.8% | 415674 | 400950 | 0 | 400950 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 410.17 |  |  |  |  | 3.542% | 0.3248% | 5% | 5% | 70.2
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.1362 | 0 | 97.38% | 99.01% | 98.35% | 100% |  |  |  |  | 23.5% | 410395 | 396450 | 450 | 396000 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 415.16 |  |  |  |  | 3.398% | 0.3289% | 5% | 5% | 70.2
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.5069 | 0 | 89.48% | 95.98% | 93.23% | 100% |  |  |  |  | 14.74% | 258268 | 248850 | 450 | 248400 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 270.48 |  |  |  |  | 3.647% | 1.22% | 5% | 5% | 70.2
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.468 | 0 | 88.08% | 94.61% | 93.1% | 100% |  |  |  |  | 22.6% | 394190 | 380700 | 0 | 380700 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 429.76 |  |  |  |  | 3.422% | 7.877% | 5% | 5% | 70.2
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.165 | 0 | 92.88% | 93.13% | 99.73% | 100% |  |  |  |  | 19.74% | 342930 | 332550 | 0 | 332550 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 357.08 |  |  |  |  | 3.027% | 6.036% | 5% | 5% | 70.2
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.0872 | 0 | 97.05% | 98.5% | 98.53% | 100% |  |  |  |  | 19.28% | 334985 | 324900 | 0 | 324900 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 337.37 |  |  |  |  | 3.011% | 0.403% | 5% | 5% | 70.2
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.1563 | 0 | 98.66% | 98.66% | 100% | 100% |  |  |  |  | 22.41% | 390622 | 377550 | 0 | 377550 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 390.56 |  |  |  |  | 3.346% | 0.2304% | 5% | 5% | 70.2
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 5.2799 | 0 | 98.24% | 98.97% | 99.26% | 100% |  |  |  |  | 20.99% | 366523 | 354150 | 450 | 353700 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 390.19 |  |  |  |  | 3.376% | 0.2455% | 5% | 5% | 70.2
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.5324 | 0 | 80.49% | 96.12% | 83.74% | 100% |  |  |  |  | 11.08% | 193560 | 186750 | 0 | 186750 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 202.65 |  |  |  |  | 3.518% | 0.2324% | 5% | 5% | 70.2
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 3.7635 | 0 | 50.77% | 99.01% | 51.28% | 100% |  |  |  |  | 7.879% | 139747 | 134100 | 1350 | 132750 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 158.54 |  |  |  |  | 4.041% | 0.6439% | 5% | 5% | 70.2
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 4.8979 | 0 | 99.37% | 99.7% | 99.66% | 100% |  |  |  |  | 20.06% | 350115 | 337950 | 0 | 337950 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 371.21 |  |  |  |  | 3.475% | 0.257% | 5% | 5% | 70.2
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.568 | 0 | 53.83% | 98.24% | 54.8% | 100% |  |  |  |  | 46.61% | 814043 | 785250 | 0 | 785250 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 847.72 |  |  |  |  | 3.537% | 0.2211% | 5% | 5% | 70.2
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.6819 | 0 | 73.3% | 96.08% | 76.3% | 100% |  |  |  |  | 48.21% | 841018 | 812250 | 0 | 812250 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 893.8 |  |  |  |  | 3.421% | 1.819% | 5% | 5% | 70.2
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.12 | 0 | 96.2% | 97.75% | 98.42% | 100% |  |  |  |  | 43.43% | 755322 | 731700 | 0 | 731700 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 797.2 |  |  |  |  | 3.127% | 0.4766% | 5% | 5% | 70.2
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 9.4785 | 0 | 90.15% | 95.17% | 94.72% | 100% |  |  |  |  | 68.8% | 1203107 | 1159200 | 0 | 1159200 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 1294.88 |  |  |  |  | 3.649% | 0.8977% | 5% | 5% | 70.2
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 8.42 | 0 | 65.36% | 99.15% | 65.92% | 100% |  |  |  |  | 55.8% | 971819 | 940050 | 0 | 940050 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 1024.62 |  |  |  |  | 3.269% | 0.3704% | 5% | 5% | 70.2
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 7.4665 | 0 | 98.63% | 98.63% | 100% | 100% |  |  |  |  | 53.5% | 932530 | 901800 | 450 | 901350 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 986.68 |  |  |  |  | 3.295% | 0.7721% | 5% | 5% | 70.2
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 9.8923 | 0 | 98.48% | 98.48% | 100% | 100% |  |  |  |  | 81.36% | 1422464 | 1370700 | 0 | 1370700 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 1505.57 |  |  |  |  | 3.639% | 2.373% | 5% | 5% | 70.2
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | [7 empty] | 9.6238 | 0 | 96.09% | 99.23% | 96.83% | 100% |  |  |  |  | 76.74% | 1341161 | 1292850 | 0 | 1292850 | 70.2 | 7.19 | 908711.4041 |  | 53.94% | 96.03% | 99.5% | 1438.1 |  |  |  |  | 3.602% | 2.516% | 5% | 5% | 70.2
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 9.6658 | 0 | 99.29% | 99.29% | 100% | 100% |  |  |  |  | 78.1% | 1362401 | 1315800 | 0 | 1315800 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1430.08 |  |  |  |  | 3.421% | 1.982% | 5% | 5% | 70.2
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.8388 | 0 | 99.39% | 99.39% | 100% | 100% |  |  |  |  | 66.21% | 1153366 | 1115550 | 0 | 1115550 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1231.2 |  |  |  |  | 3.279% | 2.341% | 5% | 5% | 70.2
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.4555 | 0 | 98.82% | 99.27% | 99.54% | 100% |  |  |  |  | 63.33% | 1102681 | 1066950 | 0 | 1066950 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1108.56 |  |  |  |  | 3.24% | 0.3673% | 5% | 5% | 70.2
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.5477 | 0 | 99.82% | 99.82% | 100% | 100% |  |  |  |  | 39.29% | 681987 | 661950 | 0 | 661950 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 27.04 |  |  |  |  | 2.938% | 0.3299% | 5% | 5% | 70.2
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.1219 | 0 | 99.2% | 99.2% | 100% | 100% |  |  |  |  | 21.77% | 379657 | 367200 | 450 | 366750 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 385.8 |  |  |  |  | 3.281% | 2.608% | 5% | 5% | 70.2
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.1272 | 0 | 98.05% | 98.05% | 100% | 100% |  |  |  |  | 33.41% | 580148 | 562950 | 0 | 562950 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 593.58 |  |  |  |  | 2.964% | 0.4654% | 5% | 5% | 70.2
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.5199 | 0 | 98.11% | 98.11% | 100% | 100% |  |  |  |  | 51.07% | 886785 | 860400 | 0 | 860400 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 899.42 |  |  |  |  | 2.975% | 0.3045% | 5% | 5% | 70.2
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.3034 | 0 | 96.26% | 96.26% | 100% | 100% |  |  |  |  | 47.3% | 820968 | 796950 | 0 | 796950 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 846.28 |  |  |  |  | 2.926% | 1.699% | 5% | 5% | 70.2
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.9526 | 0 | 99.9% | 99.9% | 100% | 100% |  |  |  |  | 58.55% | 1019022 | 986400 | 0 | 986400 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1032.83 |  |  |  |  | 3.201% | 0.9715% | 5% | 5% | 70.2
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.1789 | 0 | 97.48% | 97.48% | 100% | 100% |  |  |  |  | 61.73% | 1075551 | 1039950 | 0 | 1039950 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1108.35 |  |  |  |  | 3.31% | 0.3765% | 5% | 5% | 70.2
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.2928 | 0 | 97.73% | 97.73% | 100% | 100% |  |  |  |  | 50.29% | 875379 | 847350 | 0 | 847350 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 911.21 |  |  |  |  | 3.202% | 1.234% | 5% | 5% | 70.2
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.6641 | 0 | 99.75% | 99.75% | 100% | 100% |  |  |  |  | 53.66% | 934724 | 904050 | 0 | 904050 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 956.64 |  |  |  |  | 3.282% | 0.2888% | 5% | 5% | 70.2
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.5996 | 0 | 99.27% | 99.27% | 100% | 100% |  |  |  |  | 54.46% | 924705 | 917550 | 0 | 917550 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 974.61 |  |  |  |  | 0.7738% | 0.2433% | 5% | 5% | 70.2
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 5.4571 | 0 | 95.85% | 97.88% | 97.93% | 100% |  |  |  |  | 25.45% | 463367 | 429300 | 450 | 428850 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 487.83 |  |  |  |  | 7.352% | 0.3885% | 5% | 5% | 70.2
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 3.5274 | 0 | 99.93% | 99.93% | 100% | 100% |  |  |  |  | 9.562% | 169966 | 162900 | 1800 | 161100 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 170.73 |  |  |  |  | 4.157% | 0.5294% | 5% | 5% | 70.2
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.205 | 0 | 90.59% | 96.68% | 93.71% | 100% |  |  |  |  | 53.37% | 924330 | 899100 | 0 | 899100 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 988.32 |  |  |  |  | 2.73% | 2.385% | 5% | 5% | 70.2
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.8158 | 0 | 95.68% | 95.68% | 100% | 100% |  |  |  |  | 54.54% | 950793 | 919350 | 450 | 918900 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 991.84 |  |  |  |  | 3.307% | 0.8992% | 5% | 5% | 70.2
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.5204 | 0 | 95.45% | 95.45% | 100% | 100% |  |  |  |  | 64.66% | 1124055 | 1089450 | 0 | 1089450 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1202.27 |  |  |  |  | 3.079% | 0.2402% | 5% | 5% | 70.2
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 10.4612 | 0 | 95.65% | 95.65% | 100% | 100% |  |  |  |  | 87.66% | 1534182 | 1476900 | 0 | 1476900 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1596.54 |  |  |  |  | 3.734% | 0.44% | 5% | 5% | 70.2
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.8839 | 0 | 93.36% | 93.36% | 100% | 100% |  |  |  |  | 56.76% | 989072 | 956250 | 0 | 956250 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1078.22 |  |  |  |  | 3.318% | 0.6824% | 5% | 5% | 70.2
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.8358 | 0 | 95.46% | 95.46% | 100% | 100% |  |  |  |  | 69.18% | 1204238 | 1165500 | 0 | 1165500 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1261.16 |  |  |  |  | 3.217% | 0.2989% | 5% | 5% | 70.2
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.0881 | 0 | 95.63% | 95.63% | 100% | 100% |  |  |  |  | 43.32% | 749752 | 729900 | 0 | 729900 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 790.8 |  |  |  |  | 2.648% | 0.2401% | 5% | 5% | 70.2
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 7.5965 | 0 | 95.68% | 95.68% | 100% | 100% |  |  |  |  | 48.69% | 840583 | 820350 | 0 | 820350 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 894.97 |  |  |  |  | 2.407% | 0.2141% | 5% | 5% | 70.2
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 8.3515 | 0 | 95.52% | 95.52% | 100% | 100% |  |  |  |  | 62.71% | 1091775 | 1056600 | 0 | 1056600 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1165.22 |  |  |  |  | 3.222% | 0.3709% | 5% | 5% | 70.2
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 4.9558 | 0 | 96.21% | 96.21% | 100% | 100% |  |  |  |  | 15.62% | 270725 | 263250 | 0 | 263250 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 286.3 |  |  |  |  | 2.761% | 0% | 5% | 5% | 70.2
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 3.9065 | 0 | 94.68% | 94.68% | 100% | 100% |  |  |  |  | 9.509% | 166407 | 161100 | 900 | 160200 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 172.06 |  |  |  |  | 3.189% | 0.2703% | 5% | 5% | 70.2
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 6.8375 | 0 | 95.08% | 95.08% | 100% | 100% |  |  |  |  | 45.86% | 794242 | 772650 | 0 | 772650 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 807.27 |  |  |  |  | 2.719% | 0.2833% | 5% | 5% | 70.2
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 9.6992 | 0 | 94.97% | 94.97% | 100% | 100% |  |  |  |  | 79.19% | 1382591 | 1334250 | 0 | 1334250 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1434.41 |  |  |  |  | 3.496% | 1.855% | 5% | 5% | 70.2
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 10.1569 | 0 | 94.97% | 94.97% | 100% | 100% |  |  |  |  | 81.86% | 1430490 | 1379250 | 0 | 1379250 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1508.13 |  |  |  |  | 3.582% | 2.926% | 5% | 5% | 70.2
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | [7 empty] | 9.5537 | 0 | 94.28% | 94.28% | 100% | 100% |  |  |  |  | 77.27% | 1348035 | 1301850 | 0 | 1301850 | 70.2 | 7.15 | 801613.2744 |  | 47.58% | 96.03% | 99.5% | 1451.83 |  |  |  |  | 3.426% | 2.136% | 5% | 5% | 70.2
2025-07-01 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-02 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-03 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-04 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-05 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-06 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-07 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-08 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-09 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-10 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-11 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-12 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-13 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-14 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-15 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-16 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-17 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-18 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-19 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-20 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-21 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-22 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-23 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-24 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-25 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-26 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-27 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-28 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-29 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-30 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-07-31 | 2026 | 2025 | 2025-07-01 | 31 | [23 empty] | 8.18 | 963883.168 |  | 57.21% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-01 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-02 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-03 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-04 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-05 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-06 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-07 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-08 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-09 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-10 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-11 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-12 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-13 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-14 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-15 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-16 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-17 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-18 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-19 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-20 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-21 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-22 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-23 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-24 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-25 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-26 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-27 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-28 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-29 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-30 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-08-31 | 2026 | 2025 | 2025-08-01 | 31 | [23 empty] | 9.01 | 895729.8127 |  | 53.17% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-01 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-02 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-03 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-04 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-05 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-06 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-07 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-08 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-09 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-10 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-11 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-12 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-13 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-14 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-15 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-16 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-17 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-18 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-19 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-20 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-21 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-22 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-23 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-24 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-25 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-26 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-27 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-28 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-29 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-09-30 | 2026 | 2025 | 2025-09-01 | 30 | [23 empty] | 8.16 | 528999.8531 |  | 31.4% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-01 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-02 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-03 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-04 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-05 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-06 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-07 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-08 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-09 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-10 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-11 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-12 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-13 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-14 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-15 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-16 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-17 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-18 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-19 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-20 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-21 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-22 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-23 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-24 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-25 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-26 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-27 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-28 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-29 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-30 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-10-31 | 2026 | 2025 | 2025-10-01 | 31 | [23 empty] | 9.21 | 363484.5617 |  | 21.57% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-01 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-02 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-03 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-04 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-05 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-06 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-07 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-08 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-09 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-10 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-11 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-12 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-13 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-14 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-15 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-16 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-17 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-18 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-19 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-20 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-21 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-22 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-23 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-24 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-25 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-26 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-27 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-28 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-29 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-11-30 | 2026 | 2025 | 2025-11-01 | 30 | [23 empty] | 8.33 | 405674.734 |  | 24.08% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-01 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-02 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-03 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-04 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-05 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-06 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-07 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-08 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-09 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-10 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-11 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-12 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-13 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-14 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-15 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-16 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-17 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-18 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-19 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-20 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-21 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-22 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-23 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-24 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-25 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-26 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-27 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-28 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-29 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-30 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2025-12-31 | 2026 | 2025 | 2025-12-01 | 31 | [23 empty] | 6.95 | 574435.4233 |  | 34.1% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-01 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-02 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-03 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-04 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-05 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-06 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-07 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-08 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-09 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-10 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-11 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-12 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-13 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-14 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-15 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-16 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-17 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-18 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-19 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-20 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-21 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-22 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-23 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-24 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-25 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-26 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-27 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-28 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-29 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-30 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-01-31 | 2026 | 2026 | 2026-01-01 | 31 | [23 empty] | 5.57 | 613380.1978 |  | 36.41% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-01 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-02 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-03 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-04 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-05 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-06 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-07 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-08 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-09 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-10 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-11 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-12 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-13 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-14 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-15 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-16 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-17 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-18 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-19 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-20 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-21 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-22 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-23 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-24 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-25 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-26 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-27 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-02-28 | 2026 | 2026 | 2026-02-01 | 28 | [23 empty] | 5.52 | 522509.0574 |  | 31.01% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-01 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-02 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-03 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-04 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-05 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-06 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-07 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-08 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-09 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-10 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-11 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-12 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-13 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-14 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-15 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-16 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-17 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-18 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-19 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-20 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-21 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-22 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-23 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-24 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-25 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-26 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-27 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-28 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-29 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-30 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
2026-03-31 | 2026 | 2026 | 2026-03-01 | 31 | [23 empty] | 6.89 | 629607.1872 |  | 37.37% | 96.03% | 99.5% | [7 empty] | 5% | 5% | 70.2
Formulas:
Month Year = Table13[[#This Row],[Date]]-DAY(Table13[[#This Row],[Date]])+1
Days = DAY(EOMONTH([Date],0))
Date = [Date, row above]+1

## AnnualKPI
Till Date | 2025-06-30 | 2025-06-01
TGPXIIPL Performance Summary-YTD
Year | Days | Estimated WS(m/s) | Measured WS (m/s) | Budgeted Energy (MWh) | Measured Energy (MWh) | Target CUF (%) | Measured CUF (%) | Target GA (%) | Measured GA (%) | Target MA (%) | Measured MA (%) | Target IGA(%) | Measured IGA (%) | Target PA(%) | Measured PA (%) | Expected Energy | Loss (%) | Reactive Power (%)
2026 | 91 | 6.9967 | 6.8459 | 73151.268 | 63931.05 | 47.71% | 41.7% | 99.5% | 100% | 97% | 97% | 99% | 95.61% | 96.03% | 92.74% | 69424.2045 | 3.431% | 0.7953%

## WTG Reactive Power
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
Date | Financial Year | Calendar Year | Month Year | O2_01 (kVArh) | O2_02 (kVArh) | O2_03 (kVArh) | O2_04 (kVArh) | O2_05 (kVArh) | O2_06 (kVArh) | O2_07 (kVArh) | O2_08 (kVArh) | O2_09 (kVArh) | O2_10 (kVArh) | O2_11 (kVArh) | O2_12 (kVArh) | O2_13 (kVArh) | O2_14 (kVArh) | O2_15 (kVArh) | O2_16 (kVArh) | O2_17 (kVArh) | O2_18 (kVArh) | O2_19 (kVArh) | O2_20 (kVArh) | O2_21 (kVArh) | O2_22 (kVArh) | O2_23 (kVArh) | O2_24 (kVArh) | O2_25 (kVArh) | O2_26 (kVArh) | Total Reactive Power (kVArh)
2024-04-01 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-02 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-03 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-04 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-05 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-06 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-07 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-08 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-09 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-10 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-11 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-12 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-13 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-14 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-15 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-16 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-17 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-18 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-19 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-20 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-21 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-22 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-23 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-24 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-25 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-26 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-27 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-28 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-29 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-04-30 | 2025 | 2024 | 2024-04-01 | [26 empty] | 0
2024-05-01 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-02 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-03 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-04 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-05 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-06 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-07 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-08 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-09 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-10 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-11 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-12 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-13 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-14 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-15 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-16 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-17 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-18 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-19 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-20 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-21 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-22 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-23 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-24 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-25 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-26 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-27 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-28 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-29 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-30 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-05-31 | 2025 | 2024 | 2024-05-01 | [26 empty] | 0
2024-06-01 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-02 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-03 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-04 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-05 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-06 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-07 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-08 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-09 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-10 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-11 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-12 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-13 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-14 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-15 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-16 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-17 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-18 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-19 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-20 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-21 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-22 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-23 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-24 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-25 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-26 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-27 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-28 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-29 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-06-30 | 2025 | 2024 | 2024-06-01 | [26 empty] | 0
2024-07-01 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-02 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-03 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-04 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-05 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-06 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-07 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-08 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-09 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-10 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-11 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-12 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-13 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-14 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-15 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-16 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-17 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-18 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-19 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-20 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-21 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-22 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-23 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-24 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-25 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-26 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-27 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-28 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-29 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-30 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-07-31 | 2025 | 2024 | 2024-07-01 | [26 empty] | 0
2024-08-01 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-02 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-03 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-04 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-05 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-06 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-07 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-08 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-09 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-10 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-11 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-12 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-13 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-14 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-15 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-16 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-17 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-18 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-19 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-20 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-21 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-22 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-23 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-24 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-25 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-26 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-27 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-28 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-29 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-30 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-08-31 | 2025 | 2024 | 2024-08-01 | [26 empty] | 0
2024-09-01 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-02 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-03 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-04 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-05 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-06 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-07 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-08 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-09 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-10 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-11 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-12 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-13 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-14 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-15 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-16 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-17 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-18 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-19 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-20 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-21 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-22 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-23 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-24 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-25 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-26 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-27 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-28 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-29 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-09-30 | 2025 | 2024 | 2024-09-01 | [26 empty] | 0
2024-10-01 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-02 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-03 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-04 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-05 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-06 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-07 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-08 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-09 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-10 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-11 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-12 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-13 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-14 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-15 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-16 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-17 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-18 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-19 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-20 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-21 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-22 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-23 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-24 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-25 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-26 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-27 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-28 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-29 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-30 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-10-31 | 2025 | 2024 | 2024-10-01 | [26 empty] | 0
2024-11-01 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-02 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-03 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-04 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-05 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-06 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-07 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-08 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-09 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-10 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-11 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-12 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-13 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-14 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-15 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-16 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-17 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-18 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-19 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-20 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-21 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-22 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-23 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-24 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-25 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-26 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-27 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-28 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-29 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-11-30 | 2025 | 2024 | 2024-11-01 | [26 empty] | 0
2024-12-01 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-02 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-03 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-04 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-05 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-06 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-07 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-08 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-09 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-10 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-11 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-12 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-13 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-14 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-15 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-16 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-17 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-18 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-19 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-20 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-21 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-22 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-23 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-24 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-25 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-26 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-27 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-28 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-29 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-30 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2024-12-31 | 2025 | 2024 | 2024-12-01 | [26 empty] | 0
2025-01-01 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-02 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-03 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-04 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-05 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-06 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-07 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-08 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-09 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-10 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-11 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-12 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-13 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-14 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-15 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-16 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-17 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-18 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-19 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-20 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-21 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-22 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-23 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-24 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-25 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-26 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-27 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-28 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-29 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-30 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-01-31 | 2025 | 2025 | 2025-01-01 | [26 empty] | 0
2025-02-01 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-02 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-03 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-04 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-05 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-06 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-07 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-08 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-09 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-10 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-11 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-12 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-13 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-14 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-15 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-16 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-17 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-18 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-19 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-20 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-21 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-22 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-23 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-24 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-25 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-26 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-27 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-02-28 | 2025 | 2025 | 2025-02-01 | [26 empty] | 0
2025-03-01 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-02 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-03 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-04 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-05 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-06 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-07 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-08 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-09 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-10 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-11 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-12 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-13 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-14 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-15 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-16 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-17 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-18 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-19 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-20 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-21 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-22 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-23 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-24 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-25 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-26 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-27 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-28 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-29 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-30 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-03-31 | 2025 | 2025 | 2025-03-01 | [26 empty] | 0
2025-04-01 | 2026 | 2025 | 2025-04-01 | [26 empty] | 0
2025-04-02 | 2026 | 2025 | 2025-04-01 | [26 empty] | 0
2025-04-03 | 2026 | 2025 | 2025-04-01 | [26 empty] | 0
2025-04-04 | 2026 | 2025 | 2025-04-01 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 50.19 | 1304.94
2025-04-05 | 2026 | 2025 | 2025-04-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-04-06 | 2026 | 2025 | 2025-04-01 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 3149.9
2025-04-07 | 2026 | 2025 | 2025-04-01 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 1228.84 | 31949.84
2025-04-08 | 2026 | 2025 | 2025-04-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-04-09 | 2026 | 2025 | 2025-04-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-04-10 | 2026 | 2025 | 2025-04-01 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 640.38 | 16649.88
2025-04-11 | 2026 | 2025 | 2025-04-01 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 207.69 | 5399.94
2025-04-12 | 2026 | 2025 | 2025-04-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-04-13 | 2026 | 2025 | 2025-04-01 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 2249.78
2025-04-14 | 2026 | 2025 | 2025-04-01 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 15299.96
2025-04-15 | 2026 | 2025 | 2025-04-01 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 709.61 | 18449.86
2025-04-16 | 2026 | 2025 | 2025-04-01 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 1073.07 | 27899.82
2025-04-17 | 2026 | 2025 | 2025-04-01 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 1419.23 | 36899.98
2025-04-18 | 2026 | 2025 | 2025-04-01 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 2249.78
2025-04-19 | 2026 | 2025 | 2025-04-01 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 9899.76
2025-04-20 | 2026 | 2025 | 2025-04-01 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 1349.92
2025-04-21 | 2026 | 2025 | 2025-04-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-04-22 | 2026 | 2025 | 2025-04-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-04-23 | 2026 | 2025 | 2025-04-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-04-24 | 2026 | 2025 | 2025-04-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-04-25 | 2026 | 2025 | 2025-04-01 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 1349.92
2025-04-26 | 2026 | 2025 | 2025-04-01 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 10799.88
2025-04-27 | 2026 | 2025 | 2025-04-01 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 1349.92
2025-04-28 | 2026 | 2025 | 2025-04-01 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 1799.98
2025-04-29 | 2026 | 2025 | 2025-04-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-04-30 | 2026 | 2025 | 2025-04-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-05-01 | 2026 | 2025 | 2025-05-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-05-02 | 2026 | 2025 | 2025-05-01 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 2249.78
2025-05-03 | 2026 | 2025 | 2025-05-01 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 28799.94
2025-05-04 | 2026 | 2025 | 2025-05-01 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 20699.9
2025-05-05 | 2026 | 2025 | 2025-05-01 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 865.38 | 22499.88
2025-05-06 | 2026 | 2025 | 2025-05-01 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 2249.78
2025-05-07 | 2026 | 2025 | 2025-05-01 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 813.46 | 21149.96
2025-05-08 | 2026 | 2025 | 2025-05-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-05-09 | 2026 | 2025 | 2025-05-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-05-10 | 2026 | 2025 | 2025-05-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-05-11 | 2026 | 2025 | 2025-05-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-05-12 | 2026 | 2025 | 2025-05-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-05-13 | 2026 | 2025 | 2025-05-01 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 1349.92
2025-05-14 | 2026 | 2025 | 2025-05-01 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 1349.92
2025-05-15 | 2026 | 2025 | 2025-05-01 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 121.15 | 3149.9
2025-05-16 | 2026 | 2025 | 2025-05-01 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 1194.23 | 31049.98
2025-05-17 | 2026 | 2025 | 2025-05-01 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 796.15 | 20699.9
2025-05-18 | 2026 | 2025 | 2025-05-01 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 51.92 | 1349.92
2025-05-19 | 2026 | 2025 | 2025-05-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-05-20 | 2026 | 2025 | 2025-05-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-05-21 | 2026 | 2025 | 2025-05-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-05-22 | 2026 | 2025 | 2025-05-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-05-23 | 2026 | 2025 | 2025-05-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-05-24 | 2026 | 2025 | 2025-05-01 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 1799.98
2025-05-25 | 2026 | 2025 | 2025-05-01 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 588.46 | 15299.96
2025-05-26 | 2026 | 2025 | 2025-05-01 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 3599.96
2025-05-27 | 2026 | 2025 | 2025-05-01 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 10799.88
2025-05-28 | 2026 | 2025 | 2025-05-01 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 3599.96
2025-05-29 | 2026 | 2025 | 2025-05-01 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 276.92 | 7199.92
2025-05-30 | 2026 | 2025 | 2025-05-01 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 33749.82
2025-05-31 | 2026 | 2025 | 2025-05-01 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 1298.07 | 33749.82
2025-06-01 | 2026 | 2025 | 2025-06-01 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 26999.96
2025-06-02 | 2026 | 2025 | 2025-06-01 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 1038.46 | 26999.96
2025-06-03 | 2026 | 2025 | 2025-06-01 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 4049.76
2025-06-04 | 2026 | 2025 | 2025-06-01 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 2249.78
2025-06-05 | 2026 | 2025 | 2025-06-01 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 9899.76
2025-06-06 | 2026 | 2025 | 2025-06-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-06-07 | 2026 | 2025 | 2025-06-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-06-08 | 2026 | 2025 | 2025-06-01 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 536.53 | 13949.78
2025-06-09 | 2026 | 2025 | 2025-06-01 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 380.76 | 9899.76
2025-06-10 | 2026 | 2025 | 2025-06-01 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 4049.76
2025-06-11 | 2026 | 2025 | 2025-06-01 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 415.38 | 10799.88
2025-06-12 | 2026 | 2025 | 2025-06-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-06-13 | 2026 | 2025 | 2025-06-01 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 2249.78
2025-06-14 | 2026 | 2025 | 2025-06-01 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 1799.98
2025-06-15 | 2026 | 2025 | 2025-06-01 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 34.61 | 899.86
2025-06-16 | 2026 | 2025 | 2025-06-01 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 848.07 | 22049.82
2025-06-17 | 2026 | 2025 | 2025-06-01 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 328.84 | 8549.84
2025-06-18 | 2026 | 2025 | 2025-06-01 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 103.84 | 2699.84
2025-06-19 | 2026 | 2025 | 2025-06-01 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 6749.86
2025-06-20 | 2026 | 2025 | 2025-06-01 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 259.61 | 6749.86
2025-06-21 | 2026 | 2025 | 2025-06-01 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 138.46 | 3599.96
2025-06-22 | 2026 | 2025 | 2025-06-01 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 1799.98
2025-06-23 | 2026 | 2025 | 2025-06-01 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 69.23 | 1799.98
2025-06-24 | 2026 | 2025 | 2025-06-01 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 155.76 | 4049.76
2025-06-25 | 2026 | 2025 | 2025-06-01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025-06-26 | 2026 | 2025 | 2025-06-01 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | 449.8
2025-06-27 | 2026 | 2025 | 2025-06-01 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 86.53 | 2249.78
2025-06-28 | 2026 | 2025 | 2025-06-01 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 986.53 | 25649.78
2025-06-29 | 2026 | 2025 | 2025-06-01 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 1609.61 | 41849.86
2025-06-30 | 2026 | 2025 | 2025-06-01 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 1107.69 | 28799.94
2025-07-01 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-02 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-03 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-04 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-05 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-06 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-07 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-08 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-09 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-10 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-11 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-12 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-13 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-14 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-15 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-16 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-17 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-18 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-19 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-20 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-21 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-22 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-23 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-24 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-25 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-26 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-27 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-28 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-29 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-30 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-07-31 | 2026 | 2025 | 2025-07-01 | [26 empty] | 0
2025-08-01 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-02 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-03 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-04 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-05 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-06 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-07 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-08 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-09 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-10 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-11 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-12 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-13 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-14 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-15 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-16 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-17 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-18 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-19 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-20 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-21 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-22 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-23 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-24 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-25 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-26 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-27 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-28 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-29 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-30 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-08-31 | 2026 | 2025 | 2025-08-01 | [26 empty] | 0
2025-09-01 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-02 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-03 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-04 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-05 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-06 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-07 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-08 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-09 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-10 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-11 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-12 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-13 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-14 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-15 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-16 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-17 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-18 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-19 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-20 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-21 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-22 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-23 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-24 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-25 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-26 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-27 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-28 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-29 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-09-30 | 2026 | 2025 | 2025-09-01 | [26 empty] | 0
2025-10-01 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-02 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-03 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-04 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-05 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-06 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-07 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-08 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-09 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-10 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-11 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-12 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-13 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-14 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-15 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-16 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-17 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-18 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-19 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-20 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-21 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-22 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-23 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-24 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-25 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-26 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-27 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-28 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-29 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-30 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-10-31 | 2026 | 2025 | 2025-10-01 | [26 empty] | 0
2025-11-01 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-02 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-03 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-04 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-05 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-06 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-07 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-08 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-09 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-10 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-11 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-12 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-13 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-14 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-15 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-16 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-17 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-18 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-19 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-20 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-21 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-22 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-23 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-24 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-25 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-26 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-27 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-28 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-29 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-11-30 | 2026 | 2025 | 2025-11-01 | [26 empty] | 0
2025-12-01 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-02 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-03 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-04 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-05 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-06 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-07 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-08 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-09 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-10 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-11 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-12 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-13 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-14 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-15 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-16 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-17 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-18 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-19 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-20 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-21 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-22 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-23 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-24 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-25 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-26 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-27 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-28 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-29 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-30 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2025-12-31 | 2026 | 2025 | 2025-12-01 | [26 empty] | 0
2026-01-01 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-02 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-03 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-04 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-05 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-06 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-07 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-08 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-09 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-10 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-11 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-12 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-13 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-14 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-15 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-16 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-17 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-18 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-19 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-20 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-21 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-22 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-23 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-24 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-25 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-26 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-27 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-28 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-29 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-30 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-01-31 | 2026 | 2026 | 2026-01-01 | [26 empty] | 0
2026-02-01 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-02 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-03 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-04 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-05 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-06 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-07 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-08 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-09 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-10 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-11 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-12 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-13 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-14 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-15 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-16 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-17 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-18 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-19 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-20 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-21 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-22 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-23 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-24 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-25 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-26 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-27 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-02-28 | 2026 | 2026 | 2026-02-01 | [26 empty] | 0
2026-03-01 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-02 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-03 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-04 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-05 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-06 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-07 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-08 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-09 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-10 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-11 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-12 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-13 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-14 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-15 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-16 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-17 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-18 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-19 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-20 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-21 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-22 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-23 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-24 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-25 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-26 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-27 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-28 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-29 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-30 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-03-31 | 2026 | 2026 | 2026-03-01 | [26 empty] | 0
2026-04-01 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-02 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-03 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-04 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-05 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-06 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-07 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-08 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-09 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-10 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-11 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-12 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-13 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-14 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-15 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-16 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-17 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-18 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-19 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-20 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-21 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-22 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-23 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-24 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-25 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-26 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-27 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-28 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-29 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-04-30 | 2027 | 2026 | 2026-04-01 | [26 empty] | 0
2026-05-01 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-02 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-03 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-04 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-05 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-06 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-07 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-08 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-09 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-10 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-11 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-12 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-13 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-14 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-15 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-16 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-17 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-18 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-19 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-20 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-21 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-22 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-23 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-24 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-25 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-26 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-27 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-28 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-29 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-30 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-05-31 | 2027 | 2026 | 2026-05-01 | [26 empty] | 0
2026-06-01 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-02 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-03 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-04 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-05 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-06 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-07 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-08 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-09 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-10 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-11 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-12 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-13 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-14 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-15 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-16 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-17 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-18 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-19 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-20 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-21 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-22 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-23 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-24 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-25 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-26 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-27 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-28 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-29 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-06-30 | 2027 | 2026 | 2026-06-01 | [26 empty] | 0
2026-07-01 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-02 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-03 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-04 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-05 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-06 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-07 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-08 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-09 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-10 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-11 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-12 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-13 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-14 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-15 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-16 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-17 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-18 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-19 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-20 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-21 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-22 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-23 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-24 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-25 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-26 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-27 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-28 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-29 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-30 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-07-31 | 2027 | 2026 | 2026-07-01 | [26 empty] | 0
2026-08-01 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-02 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-03 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-04 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-05 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-06 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-07 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-08 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-09 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-10 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-11 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-12 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-13 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-14 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-15 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-16 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-17 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-18 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-19 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-20 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-21 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-22 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-23 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-24 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-25 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-26 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-27 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-28 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-29 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-30 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-08-31 | 2027 | 2026 | 2026-08-01 | [26 empty] | 0
2026-09-01 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-02 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-03 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-04 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-05 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-06 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-07 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-08 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-09 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-10 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-11 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-12 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-13 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-14 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-15 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-16 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-17 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-18 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-19 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-20 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-21 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-22 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-23 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-24 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-25 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-26 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-27 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-28 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-29 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-09-30 | 2027 | 2026 | 2026-09-01 | [26 empty] | 0
2026-10-01 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-02 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-03 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-04 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-05 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-06 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-07 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-08 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-09 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-10 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-11 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-12 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-13 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-14 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-15 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-16 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-17 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-18 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-19 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-20 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-21 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-22 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-23 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-24 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-25 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-26 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-27 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-28 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-29 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-30 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-10-31 | 2027 | 2026 | 2026-10-01 | [26 empty] | 0
2026-11-01 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-02 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-03 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-04 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-05 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-06 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-07 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-08 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-09 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-10 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-11 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-12 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-13 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-14 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-15 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-16 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-17 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-18 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-19 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-20 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-21 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-22 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-23 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-24 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-25 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-26 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-27 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-28 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-29 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-11-30 | 2027 | 2026 | 2026-11-01 | [26 empty] | 0
2026-12-01 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-02 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-03 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-04 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-05 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-06 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-07 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-08 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-09 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-10 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-11 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-12 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-13 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-14 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-15 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-16 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-17 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-18 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-19 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-20 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-21 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-22 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-23 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-24 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-25 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-26 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-27 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-28 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-29 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-30 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2026-12-31 | 2027 | 2026 | 2026-12-01 | [26 empty] | 0
2027-01-01 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-02 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-03 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-04 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-05 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-06 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-07 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-08 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-09 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-10 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-11 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-12 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-13 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-14 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-15 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-16 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-17 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-18 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-19 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-20 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-21 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-22 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-23 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-24 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-25 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-26 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-27 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-28 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-29 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-30 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-01-31 | 2027 | 2027 | 2027-01-01 | [26 empty] | 0
2027-02-01 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-02 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-03 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-04 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-05 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-06 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-07 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-08 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-09 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-10 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-11 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-12 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-13 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-14 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-15 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-16 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-17 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-18 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-19 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-20 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-21 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-22 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-23 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-24 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-25 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-26 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-27 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-02-28 | 2027 | 2027 | 2027-02-01 | [26 empty] | 0
2027-03-01 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-02 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-03 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-04 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-05 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-06 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-07 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-08 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-09 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-10 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-11 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-12 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-13 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-14 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-15 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-16 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-17 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-18 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-19 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-20 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-21 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-22 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-23 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-24 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-25 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-26 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-27 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-28 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-29 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-30 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-03-31 | 2027 | 2027 | 2027-03-01 | [26 empty] | 0
2027-04-01 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-02 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-03 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-04 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-05 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-06 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-07 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-08 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-09 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-10 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-11 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-12 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-13 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-14 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-15 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-16 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-17 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-18 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-19 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-20 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-21 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-22 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-23 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-24 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-25 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-26 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-27 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-28 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-29 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-04-30 | 2028 | 2027 | 2027-04-01 | [26 empty] | 0
2027-05-01 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-02 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-03 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-04 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-05 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-06 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-07 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-08 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-09 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-10 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-11 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-12 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-13 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-14 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-15 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-16 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-17 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-18 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-19 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-20 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-21 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-22 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-23 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-24 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-25 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-26 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-27 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-28 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-29 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-30 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-05-31 | 2028 | 2027 | 2027-05-01 | [26 empty] | 0
2027-06-01 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-02 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-03 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-04 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-05 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-06 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-07 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-08 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-09 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-10 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-11 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-12 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-13 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-14 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-15 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-16 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-17 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-18 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-19 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-20 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-21 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-22 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-23 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-24 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-25 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-26 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-27 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-28 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-29 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-06-30 | 2028 | 2027 | 2027-06-01 | [26 empty] | 0
2027-07-01 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-02 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-03 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-04 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-05 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-06 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-07 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-08 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-09 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-10 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-11 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-12 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-13 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-14 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-15 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-16 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-17 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-18 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-19 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-20 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-21 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-22 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-23 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-24 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-25 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-26 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-27 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-28 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-29 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-30 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-07-31 | 2028 | 2027 | 2027-07-01 | [26 empty] | 0
2027-08-01 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-02 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-03 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-04 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-05 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-06 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-07 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-08 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-09 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-10 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-11 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-12 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-13 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-14 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-15 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-16 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-17 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-18 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-19 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-20 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-21 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-22 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-23 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-24 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-25 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-26 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-27 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-28 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-29 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-30 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-08-31 | 2028 | 2027 | 2027-08-01 | [26 empty] | 0
2027-09-01 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-02 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-03 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-04 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-05 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-06 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-07 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-08 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-09 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-10 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-11 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-12 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-13 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-14 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-15 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-16 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-17 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-18 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-19 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-20 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-21 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-22 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-23 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-24 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-25 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-26 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-27 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-28 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-29 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-09-30 | 2028 | 2027 | 2027-09-01 | [26 empty] | 0
2027-10-01 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-02 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-03 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-04 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-05 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-06 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-07 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-08 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-09 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-10 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-11 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-12 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-13 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-14 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-15 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-16 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-17 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-18 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-19 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-20 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-21 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-22 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-23 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-24 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-25 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-26 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-27 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-28 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-29 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-30 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-10-31 | 2028 | 2027 | 2027-10-01 | [26 empty] | 0
2027-11-01 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-02 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-03 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-04 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-05 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-06 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-07 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-08 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-09 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-10 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-11 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-12 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-13 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-14 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-15 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-16 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-17 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-18 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-19 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-20 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-21 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-22 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-23 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-24 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-25 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-26 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-27 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-28 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-29 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-11-30 | 2028 | 2027 | 2027-11-01 | [26 empty] | 0
2027-12-01 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-02 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-03 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-04 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-05 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-06 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-07 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-08 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-09 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-10 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-11 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-12 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-13 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-14 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-15 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-16 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-17 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-18 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-19 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-20 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-21 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-22 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-23 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-24 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-25 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-26 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-27 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-28 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-29 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-30 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2027-12-31 | 2028 | 2027 | 2027-12-01 | [26 empty] | 0
2028-01-01 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-02 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-03 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-04 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-05 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-06 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-07 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-08 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-09 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-10 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-11 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-12 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-13 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-14 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-15 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-16 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-17 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-18 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-19 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-20 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-21 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-22 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-23 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-24 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-25 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-26 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-27 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-28 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-29 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-30 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-01-31 | 2028 | 2028 | 2028-01-01 | [26 empty] | 0
2028-02-01 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-02 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-03 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-04 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-05 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-06 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-07 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-08 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-09 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-10 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-11 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-12 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-13 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-14 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-15 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-16 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-17 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-18 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-19 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-20 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-21 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-22 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-23 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-24 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-25 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-26 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-27 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-28 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-02-29 | 2028 | 2028 | 2028-02-01 | [26 empty] | 0
2028-03-01 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-02 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-03 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-04 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-05 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-06 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-07 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-08 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-09 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-10 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-11 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-12 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-13 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-14 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-15 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-16 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-17 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-18 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-19 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-20 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-21 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-22 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-23 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-24 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-25 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-26 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-27 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-28 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-29 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-30 | 2028 | 2028 | 2028-03-01 | [26 empty] | 0
2028-03-31 | 2028 | 2028 | 2028-03-01 | 2411.487 | 891.6197 | 1879.9699 | 874.2626 | 880.4713 | 636.2265 | 372.8833 | 641.519 | 906.0887 | 2260.394 | 383.091 | 377.6865 | 2175.7978 | 1993.9216 | 1758.4657 | 2234.1107 | 1964.6707 | 2190.6098 | 441.9792 | 670.5095 | 1570.8376 | 1180.1707 | 1761.4244 | 0 | 999.7058 | 1757.046 | 33214.9493
Formulas:
Month Year = [Date]-DAY([Date])+1
Date = [Date, row above]+1

## Input_Raw
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! |  | #REF! | #REF! | #REF!
[5 empty] | Energy Generated by individual Turbine | [25 empty] | Wind Speed (M/s) | [30 empty] | Calculated Energy Numbers
Date | Finacial Year | Calendor Year | Month Year | Days | O2_01 | O2_02 | O2_03 | O2_04 | O2_05 | O2_06 | O2_07 | O2_08 | O2_09 | O2_10 | O2_11 | O2_12 | O2_13 | O2_14 | O2_15 | O2_16 | O2_17 | O2_18 | O2_19 | O2_20 | O2_21 | O2_22 | O2_23 | O2_24 | O2_25 | O2_26 | WS_O2_01 | WS_O2_02 | WS_O2_03 | WS_O2_04 | WS_O2_05 | WS_O2_06 | WS_O2_07 | WS_O2_08 | WS_O2_09 | WS_O2_10 | WS_O2_11 | WS_O2_12 | WS_O2_13 | WS_O2_14 | WS_O2_15 | WS_O2_16 | WS_O2_17 | WS_O2_18 | WS_O2_19 | WS_O2_20 | WS_O2_21 | WS_O2_22 | WS_O2_23 | WS_O2_24 | WS_O2_25 | WS_O2_26 | WTG Total Gneration (KWh) | Wind Speed Average cumulative (m/S)2 | Wind Speed Max (m/S) | Rain (mm) | 66 kV_Wind_F1_Export_reading | 66 kV_Wind_F1_Import_reading | 66 kV_Wind_Net_Export (KWh) | 66 kV Line Loss (%) | 66 kV Line Loss (%). | Commissioned Capacity (MW) | Forecasting Penalties (INR) | Expected Power as per power curve. (MWh) | Reactive Energy (MVArH)
2025-03-29 | 2025 | 2025 | 2025-03-01 | 31 | 35421 | 34841 | 35623 | 29136 | 31321 | 28804 | 27095 | 30989 | 35332 | 31185 | 33050 | 33133 | 20694 | 19735 | 33471 | 31121 | 21884 | 33133 | 29914 | 31123 | 29026 | 32797 | 33300 | 28578 | 35313 | 35647 | 7.41 | 7.32 | 7.37 | 6.86 | 7.25 | 6.86 | 6.69 | 6.86 | 7.44 | 7.33 | 7.15 | 7.16 | 6.95 | 7 | 7.29 | 7.15 | 7.16 | 7.14 | 6.93 | 7.09 | 6.97 | 7.35 | 7.25 | 6.95 | 7.37 | 7.34 | 801666 | 7.14 |  |  | 771750 | 0 | 771750 | 29916 | 3.732% | 70.2 | 10730.7503 | 843.5335
2025-03-30 | 2025 | 2025 | 2025-03-01 | 31 | 27637 | 20373 | 26510 | 19936 | 22120 | 15645 | 16384 | 20002 | 27251 | 25559 | 24523 | 24046 | 12208 | 21400 | 24316 | 18394 | 15794 | 22717 | 15830 | 20448 | 14824 | 17472 | 25808 | 23294 | 24269 | 25351 | 6.601 | 5.7503 | 6.2931 | 5.8126 | 6.0321 | 5.3652 | 5.4792 | 5.5716 | 6.4743 | 6.3618 | 6.1913 | 6.2074 | 5.5847 | 6.0429 | 6.276 | 5.7388 | 5.3019 | 5.9562 | 5.3215 | 5.9623 | 5.3554 | 5.6883 | 6.3964 | 6.2215 | 6.2854 | 6.2647 | 552111 | 5.9437 |  |  | 535500 | 0 | 535500 | 16611 | 3.009% | 70.2 | 10615.75 | 562.5916
2025-03-31 | 2025 | 2025 | 2025-03-01 | 31 | 30792 | 23793 | 27249 | 21898 | 29803 | 22412 | 21150 | 28036 | 28127 | 27563 | 26632 | 27244 | 16465 | 23397 | 27726 | 24373 | 27055 | 25496 | 21578 | 25148 | 21585 | 26561 | 26851 | 26200 | 31615 | 28973 | 6.9635 | 6.1958 | 6.6373 | 6.4454 | 6.9128 | 6.2582 | 6.1592 | 6.5843 | 6.7456 | 6.7134 | 6.5781 | 6.543 | 5.6847 | 6.3172 | 6.7261 | 6.4801 | 6.5285 | 6.3689 | 6.1203 | 6.5566 | 6.2088 | 6.6996 | 6.6097 | 6.571 | 7.0082 | 6.7217 | 667722 | 6.513 |  |  | 646650 | 0 | 646650 | 21072 | 3.156% | 70.2 | 6658.3755 | 675.4049
2025-04-01 | 2026 | 2025 | 2025-04-01 | 30 | 24859 | 17522 | 22210 | 18174 | 24626 | 19200 | 16286 | 23133 | 22108 | 18242 | 21579 | 21528 | 16565 | 18906 | 23343 | 20048 | 25148 | 21049 | 16398 | 20464 | 19206 | 22090 | 22657 | 20113 | 25900 | 22764 | 6.4825 | 5.6122 | 6.1156 | 5.7692 | 6.3621 | 5.8644 | 5.5517 | 6.1421 | 6.3004 | 6.3972 | 6.1521 | 6.0389 | 5.5855 | 5.8669 | 6.2559 | 5.8794 | 6.1135 | 5.7826 | 5.4744 | 6.0081 | 5.9768 | 6.161 | 6.234 | 5.9271 | 6.4681 | 6.1781 | 544118 | 6.0269 |  |  | 525600 | 0 | 525600 | 18518 | 3.403% | 70.2 | 6090.625 | 664.4211
2025-04-02 | 2026 | 2025 | 2025-04-01 | 30 | 15390 | 9289 | 11294 | 9155 | 12752 | 10737 | 7398 | 13309 | 13339 | 9359 | 12012 | 11497 | 9164 | 11079 | 13298 | 8978 | 9302 | 10617 | 6666 | 10349 | 9694 | 9405 | 14168 | 10062 | 14691 | 12678 | 4.9065 | 4.2376 | 4.4292 | 4.1886 | 4.667 | 4.4215 | 4.084 | 4.5752 | 4.6524 | 4.4831 | 4.5495 | 4.4724 | 4.2004 | 4.4585 | 4.6362 | 4.3228 | 4.1913 | 4.3113 | 3.8907 | 4.4137 | 4.3231 | 4.4098 | 4.6672 | 4.351 | 4.9297 | 4.6202 | 285682 | 4.4382 |  |  | 275850 | 0 | 275850 | 9832 | 3.442% | 70.2 | 19037.625 | 294.6404
2025-04-03 | 2026 | 2025 | 2025-04-01 | 30 | 13383 | 13133 | 15729 | 11906 | 13760 | 12347 | 9696 | 13829 | 15125 | 15768 | 15119 | 14465 | 12202 | 13740 | 16142 | 12680 | 14651 | 15873 | 10731 | 14473 | 11665 | 13581 | 15118 | 13382 | 15074 | 13667 | 5.0588 | 4.738 | 4.9967 | 4.5332 | 4.8687 | 4.7207 | 4.2519 | 4.7908 | 4.9429 | 5.1479 | 4.9331 | 4.9058 | 4.6674 | 4.8718 | 5.1028 | 5.1621 | 4.8495 | 4.9916 | 4.2991 | 4.9842 | 4.6978 | 4.9978 | 4.8995 | 4.8812 | 5.0099 | 4.7497 | 357239 | 4.8482 |  |  | 346050 | 450 | 345600 | 11189 | 3.132% | 70.2 | 9135.9995 | 371.21
2025-04-04 | 2026 | 2025 | 2025-04-01 | 30 | 9606 | 13454 | 10576 | 13874 | 12870 | 10850 | 10070 | 5950 | 9655 | 9291 | 10519 | 9596 | 9913 | 9746 | 11533 | 10880 | 10328 | 9755 | 9910 | 10901 | 10715 | 11247 | 9751 | 9056 | 12074 | 7143 | 4.1075 | 4.4046 | 4.1697 | 4.5422 | 4.4671 | 4.5188 | 4.2656 | 3.5978 | 4.0915 | 4.2002 | 4.2415 | 4.2454 | 4.2494 | 4.1896 | 4.4556 | 4.5644 | 4.4336 | 4.2047 | 4.2848 | 4.4192 | 4.5513 | 4.681 | 4.1092 | 4.5283 | 4.2424 | 3.6447 | 269263 | 4.285 |  |  | 257400 | 450 | 256950 | 11863 | 4.406% | 70.2 | 11281.3755 | 281.07
2025-04-05 | 2026 | 2025 | 2025-04-01 | 30 | 10770 | 12690 | 8782 | 9733 | 12146 | 6432 | 7205 | 8811 | 10832 | 8037 | 9830 | 9113 | 7542 | 7556 | 8812 | 7842 | 7381 | 8147 | 5738 | 7721 | 6752 | 7069 | 10055 | 3479 | 12113 | 8683 | 4.5263 | 4.7994 | 4.7471 | 4.4608 | 4.8083 | 4.1983 | 4.1056 | 4.2779 | 4.6022 | 4.2916 | 4.4274 | 4.355 | 4.1561 | 4.1406 | 4.387 | 4.3794 | 4.1644 | 4.1692 | 3.7783 | 4.2717 | 4.2272 | 4.3283 | 4.4027 | 4.5231 | 4.7242 | 4.2093 | 223271 | 4.3639 |  |  | 214200 | 0 | 214200 | 9071 | 4.063% | 70.2 | 8341.2508 | 230.95
2025-04-06 | 2026 | 2025 | 2025-04-01 | 30 | 21007 | 29659 | 17733 | 28588 | 27930 | 24449 | 27191 | 18202 | 19159 | 21773 | 21595 | 20692 | 20944 | 20710 | 24021 | 24525 | 36389 | 23303 | 30908 | 21945 | 23865 | 29600 | 21012 | 24582 | 25647 | 14855 | 6.2017 | 6.8914 | 6.069 | 6.902 | 6.8794 | 6.5856 | 6.8617 | 5.6899 | 5.9826 | 6.2822 | 6.2399 | 6.1249 | 6.2119 | 6.1106 | 6.4949 | 6.5378 | 7.2668 | 6.3951 | 6.8189 | 6.5508 | 6.631 | 7.1519 | 6.1025 | 6.6 | 6.4892 | 5.3312 | 620284 | 6.4386 |  |  | 603000 | 0 | 603000 | 17284 | 2.786% | 70.2 |  | 667.03
2025-04-07 | 2026 | 2025 | 2025-04-01 | 30 | 31048 | 39935 | 29201 | 37264 | 38160 | 33948 | 36306 | 29713 | 26172 | 29496 | 28893 | 29862 | 17926 | 24680 | 30580 | 35026 | 42573 | 32649 | 33248 | 28989 | 35533 | 38083 | 29493 | 35825 | 32714 | 27406 | 6.8494 | 7.6928 | 6.7251 | 7.6072 | 7.6881 | 7.1946 | 7.4768 | 6.8182 | 6.7778 | 6.8461 | 6.8254 | 6.8973 | 6.783 | 6.9575 | 6.9858 | 7.4788 | 8.0268 | 6.9819 | 7.2324 | 7.2163 | 7.415 | 7.7592 | 6.8959 | 7.4988 | 7.4038 | 6.501 | 834723 | 7.1744 |  |  | 802800 | 0 | 802800 | 31923 | 3.824% | 70.2 |  | 890.54
2025-04-08 | 2026 | 2025 | 2025-04-01 | 30 | 32931 | 38913 | 30523 | 36527 | 29686 | 31629 | 31884 | 24450 | 23145 | 29213 | 27130 | 32730 | 23942 | 30642 | 33320 | 35024 | 41845 | 29300 | 35384 | 32867 | 32199 | 35456 | 31686 | 34444 | 34312 | 23956 | 7.0247 | 7.503 | 6.8145 | 7.5483 | 7.3112 | 6.937 | 6.9896 | 6.4571 | 7.0619 | 6.8082 | 6.961 | 7.0233 | 6.8967 | 6.8707 | 7.1692 | 7.4628 | 7.7799 | 6.6718 | 7.265 | 7.1443 | 7.1197 | 7.4435 | 7.0236 | 7.2678 | 7.3632 | 6.1385 | 823138 | 7.0791 |  |  | 793800 | 450 | 793350 | 29338 | 3.564% | 70.2 |  | 885.16
2025-04-09 | 2026 | 2025 | 2025-04-01 | 30 | 28683 | 35985 | 29958 | 32935 | 31490 | 28574 | 28440 | 26245 | 28445 | 26608 | 27370 | 29182 | 27038 | 28542 | 28611 | 31225 | 36940 | 29330 | 28437 | 30708 | 28985 | 31056 | 23479 | 32143 | 32309 | 23560 | 7.0392 | 7.6205 | 7.0383 | 7.3772 | 7.6401 | 7.0162 | 6.9249 | 6.6476 | 7.0435 | 6.8212 | 6.9276 | 6.976 | 6.8413 | 6.9871 | 7.0288 | 7.2906 | 7.5616 | 6.9319 | 6.7922 | 7.2261 | 7.124 | 7.2808 | 7.122 | 7.2891 | 7.4078 | 6.3833 | 766278 | 7.09 |  |  | 742500 | 0 | 742500 | 23778 | 3.103% | 70.2 |  | 808
2025-04-10 | 2026 | 2025 | 2025-04-01 | 30 | 37826 | 45183 | 36893 | 42701 | 41567 | 37890 | 42698 | 28587 | 35022 | 35686 | 35407 | 38699 | 34054 | 36725 | 33831 | 40822 | 53780 | 33218 | 46375 | 40773 | 39808 | 44573 | 30874 | 41245 | 41410 | 30495 | 7.9917 | 8.5594 | 7.8494 | 8.5016 | 8.3636 | 8.1974 | 8.6051 | 7.6975 | 7.7553 | 7.8515 | 7.9753 | 8.1052 | 7.7774 | 7.8892 | 8.1558 | 8.6735 | 9.3265 | 7.866 | 9.091 | 8.3635 | 8.351 | 8.7169 | 8.1003 | 8.3699 | 8.2224 | 7.1974 | 1006142 | 8.2136 |  |  | 974700 | 0 | 974700 | 31442 | 3.125% | 70.2 |  | 1103.33
2025-04-11 | 2026 | 2025 | 2025-04-01 | 30 | 41447 | 49347 | 40931 | 44979 | 46056 | 39764 | 38038 | 39635 | 41407 | 40631 | 37304 | 42973 | 36918 | 3872 | 40666 | 40181 | 44076 | 39510 | 42576 | 40190 | 40132 | 39622 | 41157 | 40939 | 47491 | 41874 | 8.3565 | 8.9344 | 8.22 | 8.6743 | 8.8362 | 8.1364 | 8.0317 | 8.2211 | 8.3112 | 8.1988 | 8.1662 | 8.3397 | 7.9668 | 2.4363 | 8.2474 | 8.3751 | 8.3534 | 8.1015 | 8.3621 | 8.2547 | 8.284 | 8.1916 | 8.3781 | 8.2961 | 8.786 | 8.3384 | 1041716 | 8.1076 |  |  | 1004400 | 0 | 1004400 | 37316 | 3.582% | 70.2 |  | 1083.02
2025-04-12 | 2026 | 2025 | 2025-04-01 | 30 | 7035 | 8948 | 7003 | 6732 | 9236 | 6096 | 5753 | 7293 | 7028 | 7345 | 6323 | 7785 | 6299 | 2021 | 7154 | 5854 | 5199 | 5776 | 6293 | 5916 | 6933 | 5641 | 6923 | 7181 | 8783 | 7236 | 5.18 | 5.4 | 5.08 | 4.97 | 5.52 | 4.93 | 4.75 | 5.13 | 5.5 | 5.11 | 5.08 | 5.22 | 4.93 | 3.35 | 5.1 | 4.7 | 4.65 | 4.7 | 4.81 | 4.86 | 5.06 | 4.74 | 5.15 | 5.05 | 5.52 | 5.07 | 173786 | 4.9831 |  |  | 164700 | 0 | 164700 | 9086 | 5.228% | 70.2 |  | 176.01
2025-04-13 | 2026 | 2025 | 2025-04-01 | 30 | 26489 | 28616 | 25705 | 25328 | 26101 | 23521 | 22036 | 10825 | 24188 | 25909 | 23698 | 25190 | 10703 | 23384 | 20653 | 24367 | 23858 | 22828 | 21328 | 24441 | 23356 | 23878 | 25584 | 24224 | 26202 | 25025 | 7.856 | 8.2075 | 7.5842 | 7.5783 | 8.1324 | 7.4854 | 7.1724 | 7.7008 | 7.5091 | 7.9007 | 7.585 | 7.5129 | 7.3763 | 7.4539 | 8.1924 | 7.5736 | 7.3922 | 7.5674 | 6.9816 | 7.5216 | 7.6607 | 7.5939 | 7.603 | 7.8746 | 8.1602 | 7.4845 | 607437 | 7.6408 |  |  | 589950 | 0 | 589950 | 17487 | 2.879% | 70.2 |  | 682.2
2025-04-14 | 2026 | 2025 | 2025-04-01 | 30 | 49494 | 54587 | 26547 | 55152 | 54526 | 43979 | 52855 | 45219 | 45058 | 42261 | 46926 | 44309 | 32069 | 41611 | 35797 | 46276 | 48303 | 42517 | 48676 | 47867 | 43699 | 49144 | 47758 | 48527 | 34863 | 46555 | 9.1019 | 9.6511 | 8.1617 | 9.6955 | 9.7078 | 8.5597 | 9.5655 | 8.9413 | 8.6056 | 8.3949 | 8.8494 | 8.6869 | 8.6396 | 8.4447 | 8.5943 | 8.9833 | 9.5735 | 8.3386 | 9.2369 | 8.9903 | 8.6319 | 9.0699 | 8.865 | 9.1472 | 9.5473 | 8.7862 | 1174575 | 8.9527 |  |  | 1131750 | 0 | 1131750 | 42825 | 3.646% | 70.2 |  | 1310.71
2025-04-15 | 2026 | 2025 | 2025-04-01 | 30 | 46514 | 48545 | 39223 | 47687 | 30448 | 45430 | 44148 | 45573 | 29654 | 39470 | 43359 | 40662 | 40685 | 41368 | 44736 | 36838 | 21163 | 45796 | 44525 | 47068 | 46010 | 50084 | 45181 | 45308 | 43881 | 45361 | 8.6085 | 9.1474 | 7.9455 | 9.1071 | 9.1824 | 8.5749 | 8.7967 | 8.525 | 8.4452 | 8.139 | 8.3094 | 8.1183 | 8.1345 | 8.2362 | 8.4833 | 9.1687 | 9.5176 | 8.4606 | 8.8022 | 8.8149 | 8.7622 | 9.1504 | 8.467 | 8.7845 | 8.7822 | 8.4726 | 1098717 | 8.6514 |  |  | 1060200 | 0 | 1060200 | 38517 | 3.506% | 70.2 |  | 1204.55
2025-04-16 | 2026 | 2025 | 2025-04-01 | 30 | 39687 | 43551 | 33252 | 42754 | 39116 | 41952 | 38923 | 32217 | 37241 | 34029 | 37090 | 34156 | 33570 | 30710 | 38531 | 37845 | 5990 | 33986 | 39068 | 39760 | 41205 | 46060 | 38562 | 36943 | 33701 | 37850 | 7.8429 | 8.2335 | 7.3058 | 8.2092 | 8.2521 | 8.1929 | 7.9235 | 7.8645 | 7.6393 | 7.3693 | 7.6581 | 7.4222 | 7.397 | 7.5144 | 7.7897 | 8.0989 | 8.6369 | 8.0579 | 7.9156 | 8.0108 | 8.152 | 8.6213 | 7.7801 | 7.8828 | 8.0145 | 7.6638 | 947749 | 7.9019 |  |  | 913950 | 0 | 913950 | 33799 | 3.566% | 70.2 |  | 1042.18
2025-04-17 | 2026 | 2025 | 2025-04-01 | 30 | 36843 | 37275 | 31117 | 40506 | 38564 | 34183 | 36587 | 34160 | 34958 | 25644 | 32786 | 27764 | 29488 | 29808 | 32423 | 30737 | 34358 | 33701 | 35632 | 33211 | 29664 | 37507 | 35381 | 32115 | 35469 | 36110 | 7.4667 | 7.8992 | 6.8693 | 7.7908 | 7.9419 | 7.1637 | 7.5519 | 7.2331 | 7.2426 | 6.3555 | 7.1822 | 7.0022 | 6.773 | 6.823 | 6.9757 | 7.0449 | 7.1734 | 7.0146 | 7.2396 | 7.1526 | 6.9462 | 7.5787 | 7.268 | 7.1542 | 7.6756 | 7.2931 | 875991 | 7.2235 |  |  | 845100 | 450 | 844650 | 30891 | 3.526% | 70.2 |  | 924.98
2025-04-18 | 2026 | 2025 | 2025-04-01 | 30 | 34294 | 34912 | 27346 | 45131 | 34316 | 28245 | 45438 | 32009 | 31138 | 26881 | 28371 | 30866 | 28163 | 29384 | 31417 | 34039 | 42599 | 31599 | 40021 | 34801 | 31662 | 36369 | 32033 | 31520 | 28659 | 32826 | 7.6378 | 8.3981 | 6.8683 | 8.6183 | 8.4025 | 7.2827 | 8.6867 | 7.3904 | 7.2176 | 7.0017 | 7.224 | 7.2451 | 7.0875 | 7.1581 | 7.338 | 7.7958 | 8.4907 | 7.244 | 8.1028 | 7.7815 | 7.5028 | 7.9106 | 7.3529 | 7.8792 | 8.1399 | 7.4213 | 864039 | 7.6607 |  |  | 836550 | 0 | 836550 | 27489 | 3.181% | 70.2 |  | 946.76
2025-04-19 | 2026 | 2025 | 2025-04-01 | 30 | 39027 | 53626 | 42200 | 51178 | 48525 | 46454 | 45064 | 39407 | 45465 | 44515 | 45528 | 44692 | 38827 | 42355 | 46436 | 44394 | 46112 | 32014 | 49651 | 46167 | 45633 | 46701 | 45695 | 45796 | 37623 | 45701 | 8.9352 | 9.3668 | 8.5899 | 9.2626 | 9.2918 | 8.9084 | 8.7253 | 8.4041 | 8.7478 | 8.714 | 8.8479 | 8.7184 | 8.2669 | 8.6298 | 8.8724 | 9.0203 | 8.9456 | 9.3124 | 9.1511 | 9.0035 | 8.9362 | 9.0537 | 8.8845 | 8.909 | 9.2601 | 8.7714 | 1158786 | 8.905 |  |  | 1118700 | 0 | 1118700 | 40086 | 3.459% | 70.2 |  | 1285.97
2025-04-20 | 2026 | 2025 | 2025-04-01 | 30 | 24919 | 30555 | 22769 | 30756 | 30469 | 30187 | 26515 | 23102 | 24698 | 25632 | 27364 | 27081 | 22181 | 25432 | 28875 | 27432 | 31607 | 26006 | 30730 | 28383 | 29926 | 28894 | 26129 | 26522 | 30437 | 22337 | 6.8326 | 7.0727 | 6.3584 | 7.1445 | 7.1428 | 7.1265 | 6.7781 | 6.4126 | 6.6051 | 6.5861 | 6.8372 | 6.7898 | 6.4397 | 6.6312 | 6.938 | 7.0153 | 7.2006 | 7.0682 | 7.0188 | 7.0672 | 7.1596 | 7.1419 | 6.7 | 6.8062 | 7.0358 | 6.3572 | 708938 | 6.8564 |  |  | 687150 | 0 | 687150 | 21788 | 3.073% | 70.2 |  | 742.63
2025-04-21 | 2026 | 2025 | 2025-04-01 | 30 | 9337 | 9782 | 9730 | 15664 | 12194 | 11266 | 14994 | 7248 | 11238 | 8551 | 6599 | 9575 | 9644 | 9107 | 9913 | 9599 | 13528 | 11087 | 12704 | 11274 | 9310 | 12120 | 11189 | 11760 | 11595 | 7446 | 5.6226 | 5.7542 | 4.5597 | 5.223 | 6.1471 | 4.8551 | 5.1047 | 5.0916 | 4.8307 | 4.3585 | 4.728 | 4.6615 | 4.5959 | 4.5663 | 4.6028 | 5.0522 | 4.9259 | 4.664 | 4.8502 | 4.854 | 4.4858 | 4.9748 | 4.8434 | 4.9052 | 6.0382 | 5.0628 | 276454 | 4.9753 |  |  | 267300 | 0 | 267300 | 9154 | 3.311% | 70.2 |  | 287.24
2025-04-22 | 2026 | 2025 | 2025-04-01 | 30 | 13330 | 17425 | 13108 | 17013 | 17905 | 10599 | 11872 | 11512 | 13364 | 12763 | 1075 | 12585 | 11275 | 13494 | 14815 | 13908 | 17560 | 12546 | 13070 | 12585 | 9979 | 12902 | 13128 | 14134 | 17975 | 12251 | 5.3521 | 5.482 | 5.0576 | 5.8486 | 5.606 | 4.8199 | 5.1763 | 4.8684 | 5.1595 | 5.1081 | 5.3994 | 5.0492 | 4.9238 | 5.1632 | 5.3535 | 5.3234 | 5.5098 | 4.9449 | 5.2193 | 5.1948 | 4.7258 | 5.2073 | 5.1302 | 5.2645 | 5.6369 | 4.9868 | 342173 | 5.212 |  |  | 332100 | 0 | 332100 | 10073 | 2.944% | 70.2 |  | 353.11
2025-04-23 | 2026 | 2025 | 2025-04-01 | 30 | 16960 | 21906 | 18529 | 21315 | 22924 | 18174 | 18316 | 12455 | 18013 | 16676 | 10518 | 18749 | 17915 | 18765 | 20642 | 20193 | 25074 | 14474 | 20286 | 18572 | 16989 | 19787 | 19115 | 20098 | 20542 | 13113 | 5.4665 | 5.7306 | 5.6083 | 5.7503 | 5.9513 | 5.6327 | 5.451 | 4.8827 | 5.6152 | 5.4492 | 6.0308 | 5.7333 | 5.636 | 5.7173 | 5.8375 | 5.8208 | 6.1108 | 5.5224 | 5.4928 | 5.7317 | 5.6434 | 5.8226 | 5.7935 | 5.8375 | 5.6966 | 4.9992 | 480100 | 5.6525 |  |  | 464400 | 0 | 464400 | 15700 | 3.27% | 70.2 |  | 502.87
2025-04-24 | 2026 | 2025 | 2025-04-01 | 30 | 19242 | 25780 | 15669 | 26930 | 25923 | 18405 | 22688 | 18517 | 17720 | 14637 | 16559 | 17908 | 15286 | 15295 | 16927 | 20003 | 22418 | 15157 | 19991 | 18458 | 18477 | 20201 | 18383 | 19838 | 23888 | 18406 | 5.8056 | 6.2622 | 5.4297 | 6.5066 | 6.3699 | 5.7963 | 6.2158 | 5.7027 | 5.6888 | 5.3344 | 5.6219 | 5.7266 | 5.4587 | 5.4043 | 5.5901 | 5.9983 | 6.4049 | 5.7536 | 5.7161 | 5.8346 | 5.8631 | 5.9811 | 5.7443 | 5.9727 | 6.1442 | 5.7595 | 502706 | 5.8495 |  |  | 488700 | 0 | 488700 | 14006 | 2.786% | 70.2 |  | 510
2025-04-25 | 2026 | 2025 | 2025-04-01 | 30 | 25182 | 30384 | 18648 | 19463 | 24911 | 24475 | 25522 | 21799 | 23355 | 18318 | 20809 | 19079 | 18888 | 19630 | 22699 | 24574 | 27533 | 17366 | 29263 | 19709 | 19854 | 23524 | 20988 | 22510 | 29620 | 24404 | 6.2807 | 6.6538 | 5.8174 | 6.6103 | 6.582 | 6.2724 | 6.3305 | 5.958 | 6.1063 | 5.5885 | 5.9245 | 5.8795 | 5.7399 | 5.8198 | 6.0397 | 6.3219 | 6.4678 | 6.192 | 6.6163 | 6.3278 | 5.8689 | 6.2653 | 5.9163 | 6.128 | 6.591 | 6.1946 | 592507 | 6.1728 |  |  | 573300 | 0 | 573300 | 19207 | 3.242% | 70.2 |  | 628.86
2025-04-26 | 2026 | 2025 | 2025-04-01 | 30 | 23625 | 30087 | 18188 | 32299 | 21016 | 25979 | 32148 | 22049 | 21341 | 18454 | 20631 | 21342 | 18941 | 19393 | 21293 | 26007 | 30680 | 22536 | 26408 | 20947 | 22561 | 28932 | 21099 | 23190 | 21022 | 23193 | 6.1048 | 6.669 | 5.5809 | 7.0202 | 6.7057 | 6.3908 | 7.0044 | 5.8494 | 5.8084 | 5.7265 | 5.8411 | 5.8868 | 5.6961 | 5.6831 | 5.881 | 6.3784 | 6.8857 | 6.0894 | 6.6792 | 6.0615 | 6.1051 | 6.7019 | 5.8595 | 6.1435 | 6.7365 | 6.0563 | 613361 | 6.2133 |  |  | 591750 | 0 | 591750 | 21611 | 3.523% | 70.2 |  | 645.69
2025-04-27 | 2026 | 2025 | 2025-04-01 | 30 | 21657 | 27721 | 15919 | 25863 | 25391 | 21983 | 23298 | 18429 | 17843 | 16452 | 18496 | 19386 | 18292 | 17831 | 19004 | 20954 | 22543 | 21921 | 7065 | 20943 | 17092 | 24160 | 18865 | 20722 | 24769 | 19397 | 5.7472 | 6.1592 | 5.1197 | 6.0952 | 6.1183 | 5.8899 | 5.8613 | 5.3438 | 5.3546 | 5.3179 | 5.4117 | 5.4963 | 5.4688 | 5.3865 | 5.5786 | 5.65 | 5.8974 | 5.7474 | 5.9916 | 5.6647 | 5.384 | 6.1233 | 5.4083 | 5.6394 | 5.9617 | 5.5513 | 525996 | 5.668 |  |  | 507150 | 450 | 506700 | 18846 | 3.583% | 70.2 |  | 546.95
2025-04-28 | 2026 | 2025 | 2025-04-01 | 30 | 25969 | 33725 | 20195 | 35034 | 28941 | 18752 | 34349 | 25046 | 23663 | 17565 | 22680 | 16866 | 21105 | 20172 | 22472 | 26758 | 30758 | 24323 | 33584 | 24463 | 21721 | 28665 | 23637 | 25311 | 30829 | 22931 | 6.5059 | 7.224 | 5.9941 | 7.3876 | 7.4201 | 6.5767 | 7.4235 | 6.456 | 6.2309 | 5.8614 | 6.3037 | 6.2457 | 6.1618 | 6.1025 | 6.2819 | 6.7829 | 7.3135 | 6.2673 | 7.0572 | 6.4876 | 6.3334 | 6.8923 | 6.3927 | 6.669 | 7.1106 | 6.3776 | 659514 | 6.61 |  |  | 638550 | 0 | 638550 | 20964 | 3.179% | 70.2 |  | 695.35
2025-04-29 | 2026 | 2025 | 2025-04-01 | 30 | 39002 | 46987 | 27484 | 47661 | 37871 | 30203 | 47322 | 39218 | 40871 | 33673 | 38381 | 36596 | 34720 | 36243 | 40415 | 41729 | 48820 | 43095 | 45273 | 41925 | 35807 | 41434 | 38719 | 40826 | 27193 | 40476 | 8.2575 | 8.9462 | 7.7198 | 9.1399 | 9.0706 | 8.4182 | 9.3492 | 8.2625 | 8.19 | 7.5788 | 8.0101 | 8.0178 | 7.8329 | 7.8897 | 8.2664 | 8.5734 | 9.0421 | 8.2504 | 8.9583 | 8.3748 | 7.9308 | 8.5792 | 8.1809 | 8.3817 | 8.7624 | 8.3298 | 1021944 | 8.3967 |  |  | 988650 | 0 | 988650 | 33294 | 3.258% | 70.2 |  | 1133.84
2025-04-30 | 2026 | 2025 | 2025-04-01 | 30 | 30766 | 46976 | 35656 | 44874 | 37428 | 40195 | 43595 | 31504 | 39102 | 33815 | 39981 | 32408 | 36204 | 35100 | 39028 | 40390 | 47298 | 40243 | 41700 | 39680 | 34897 | 40527 | 40076 | 39729 | 39918 | 38333 | 8.194 | 8.65 | 7.6236 | 8.8325 | 8.841 | 8.0705 | 8.6465 | 8.0776 | 8.0356 | 7.6161 | 8.0497 | 7.8434 | 7.8399 | 7.7305 | 8.0103 | 8.2765 | 8.6799 | 7.9736 | 8.4427 | 8.1253 | 7.8634 | 8.3185 | 8.1649 | 8.2602 | 8.5589 | 7.9543 | 1009423 | 8.18 |  |  | 975600 | 0 | 975600 | 33823 | 3.351% | 70.2 |  | 1088.32
2025-05-01 | 2026 | 2025 | 2025-05-01 | 31 | 44015 | 49670 | 35787 | 49041 | 47609 | 46547 | 45834 | 40949 | 42067 | 34234 | 40516 | 37980 | 36887 | 38537 | 42682 | 45078 | 48276 | 46077 | 47537 | 43931 | 38412 | 47524 | 41723 | 41385 | 45723 | 44674 | 8.4306 | 8.8271 | 7.7422 | 9.0086 | 8.9183 | 8.6306 | 8.9895 | 8.3082 | 8.2972 | 7.6025 | 8.0794 | 8.0581 | 7.9119 | 7.9996 | 8.2834 | 8.7056 | 8.7574 | 8.5746 | 9.1475 | 8.5126 | 8.146 | 8.9812 | 8.2779 | 8.5276 | 8.4943 | 8.4674 | 1122695 | 8.4492 |  |  | 1082700 | 0 | 1082700 | 39995 | 3.562% | 70.2 |  | 1190.71
2025-05-02 | 2026 | 2025 | 2025-05-01 | 31 | 29702 | 32978 | 24447 | 31464 | 33306 | 29048 | 26581 | 23768 | 27074 | 27547 | 26607 | 25954 | 22606 | 25514 | 27055 | 29106 | 34884 | 32010 | 27520 | 27553 | 23738 | 28813 | 28402 | 27823 | 33472 | 25628 | 6.922 | 7.1906 | 6.3539 | 7.1813 | 7.2628 | 6.856 | 6.7724 | 6.3506 | 6.6205 | 6.6928 | 6.5622 | 6.5078 | 6.2274 | 6.4798 | 6.6526 | 6.9531 | 7.408 | 7.0756 | 6.6686 | 6.7272 | 7.2083 | 7.0424 | 6.7051 | 6.7346 | 7.2115 | 6.4764 | 732600 | 6.8017 |  |  | 681750 | 0 | 681750 | 50850 | 6.941% | 70.2 |  | 781.68
2025-05-03 | 2026 | 2025 | 2025-05-01 | 31 | 29084 | 50749 | 38653 | 45482 | 50589 | 39457 | 42306 | 24327 | 40568 | 43941 | 41617 | 43049 | 33999 | 39854 | 42149 | 47857 | 52503 | 42004 | 45398 | 44438 | 47180 | 46189 | 43594 | 20716 | 45983 | 43445 | 8.5129 | 9.066 | 8.0985 | 8.8032 | 9.1381 | 8.6614 | 8.4251 | 8.132 | 8.3519 | 8.6158 | 8.3835 | 8.4734 | 7.8183 | 8.2897 | 8.4081 | 9.0144 | 9.3542 | 8.9001 | 8.8603 | 8.6981 | 8.9399 | 8.967 | 8.6199 | 9.0589 | 8.9481 | 8.5372 | 1085131 | 8.6568 |  |  | 1074150 | 0 | 1074150 | 10981 | 1.012% | 70.2 |  | 1224.47
2025-05-04 | 2026 | 2025 | 2025-05-01 | 31 | 17974 | 29174 | 25699 | 27656 | 29142 | 28832 | 23702 | 17190 | 28449 | 29343 | 28037 | 29548 | 25159 | 26738 | 27808 | 28968 | 30672 | 30284 | 28628 | 26654 | 30867 | 28077 | 29011 | 28077 | 25433 | 30825 | 6.6283 | 6.7307 | 6.5555 | 6.7367 | 6.8492 | 6.7621 | 6.2467 | 6.54 | 6.7583 | 6.9048 | 6.8124 | 6.8777 | 6.5328 | 6.6881 | 6.7801 | 7.0407 | 7.0868 | 6.8567 | 6.82 | 6.5917 | 6.9838 | 6.7583 | 6.8653 | 6.6847 | 6.8663 | 6.9374 | 711947 | 6.7652 |  |  | 685800 | 450 | 685350 | 26147 | 3.673% | 70.2 |  | 773.86
2025-05-05 | 2026 | 2025 | 2025-05-01 | 31 | 18835 | 31559 | 29715 | 30722 | 30948 | 30904 | 28268 | 27202 | 31886 | 31922 | 20276 | 31332 | 28547 | 29701 | 31905 | 30318 | 28089 | 33937 | 30708 | 29830 | 31289 | 25892 | 32518 | 30515 | 29760 | 31214 | 7.3475 | 7.3099 | 7.1846 | 7.2253 | 7.3093 | 7.2811 | 6.9722 | 7.1834 | 7.403 | 7.442 | 7.3674 | 7.37 | 7.1776 | 7.2469 | 7.3885 | 7.3498 | 7.2903 | 7.5298 | 7.2362 | 7.2922 | 7.3964 | 6.8903 | 7.4494 | 7.2444 | 7.1503 | 7.371 | 767792 | 7.2849 |  |  | 741600 | 0 | 741600 | 26192 | 3.411% | 70.2 |  | 837.33
2025-05-06 | 2026 | 2025 | 2025-05-01 | 31 | 10165 | 15091 | 15302 | 15082 | 14339 | 23291 | 18793 | 11190 | 15245 | 18504 | 16459 | 15671 | 14458 | 16788 | 17961 | 177 | 24296 | 25931 | 26460 | 24540 | 23651 | 21281 | 15228 | 87 | 14231 | 10926 | 7.0833 | 6.6335 | 6.8706 | 6.3598 | 6.7275 | 6.9846 | 6.1776 | 6.7678 | 6.8908 | 7.1291 | 6.9965 | 6.9837 | 6.8513 | 6.9905 | 7.1088 | 7.1132 | 7.2666 | 7.1202 | 6.9017 | 6.8773 | 6.9616 | 6.8491 | 6.8998 | 7.1285 | 6.467 | 6.9039 | 425147 | 6.8863 |  |  | 412650 | 0 | 412650 | 12497 | 2.939% | 70.2 |  | 541.99
2025-05-07 | 2026 | 2025 | 2025-05-01 | 31 | 11319 | 16965 | 1852 | 19556 | 16886 | 19918 | 16111 | 11676 | 15126 | 14677 | 14545 | 11445 | 15086 | 14856 | 14641 | 1279 | 19367 | 21456 | 20272 | 19397 | 21725 | 19485 | 12584 | 10416 | 15407 | 15166 | 5.7432 | 5.8574 | 5.5645 | 5.6083 | 5.9282 | 6.034 | 5.3851 | 5.6519 | 5.6113 | 5.6851 | 5.7726 | 5.8937 | 5.8009 | 5.7049 | 5.6932 | 5.7809 | 6.1783 | 6.1342 | 5.7728 | 6.1547 | 6.0544 | 5.9905 | 5.79 | 6.1613 | 6.0004 | 5.7176 | 391213 | 5.8334 |  |  | 377100 | 0 | 377100 | 14113 | 3.607% | 70.2 |  | 371.67
2025-05-08 | 2026 | 2025 | 2025-05-01 | 31 | 7575 | 10183 | 6151 | 9882 | 9278 | 7917 | 7381 | 6257 | 6464 | 6233 | 7094 | 6716 | 6390 | 6051 | 7149 | 7733 | 7908 | 8265 | 8140 | 6207 | 7764 | 7733 | 5173 | 9370 | 8720 | 6869 | 4.2821 | 4.4326 | 3.9808 | 4.3882 | 4.4838 | 4.251 | 4.0774 | 3.8574 | 3.9506 | 4.0057 | 4.1706 | 4.0232 | 3.9824 | 3.9163 | 4.0494 | 4.1438 | 4.2416 | 4.1926 | 4.1282 | 4.3726 | 4.0258 | 4.1732 | 3.9137 | 4.3362 | 4.322 | 4.0434 | 194603 | 4.144 |  |  | 187200 | 450 | 186750 | 7403 | 3.804% | 70.2 |  | 194.403
2025-05-09 | 2026 | 2025 | 2025-05-01 | 31 | 9128 | 12509 | 9207 | 5316 | 11663 | 6891 | 4777 | 9913 | 8780 | 9374 | 9372 | 10322 | 10508 | 10289 | 10040 | 6386 | 6518 | 6914 | 4077 | 6597 | 5387 | 7622 | 9232 | 7052 | 11182 | 9743 | 4.35 | 4.66 | 4.13 | 4 | 4.67 | 4.13 | 3.94 | 4.25 | 4.14 | 4.17 | 4.31 | 4.34 | 4.31 | 4.36 | 4.29 | 4.06 | 4.33 | 3.93 | 3.79 | 4.1 | 3.76 | 4.26 | 4.26 | 4.14 | 4.55 | 4.29 | 218799 | 4.2123 |  |  | 210150 | 0 | 210150 | 8649 | 3.953% | 70.2 |  | 215.78
2025-05-10 | 2026 | 2025 | 2025-05-01 | 31 | 14837 | 21132 | 12290 | 17359 | 19838 | 12904 | 13014 | 12886 | 13132 | 11294 | 13194 | 13400 | 12510 | 12935 | 13423 | 13663 | 15113 | 11997 | 0 | 12177 | 11514 | 15068 | 11818 | 12570 | 20756 | 14169 | 5.074 | 5.6715 | 4.8213 | 5.5293 | 5.6067 | 5.1672 | 4.9639 | 5.0511 | 4.8701 | 4.719 | 4.9156 | 4.9999 | 4.8692 | 4.9765 | 4.9662 | 5.21 | 5.9097 | 4.9219 | 0 | 5.004 | 4.856 | 5.7399 | 4.9135 | 4.9545 | 5.5285 | 4.9138 | 352993 | 4.929 |  |  | 341550 | 900 | 340650 | 11443 | 3.242% | 70.2 |  | 361.29
2025-05-11 | 2026 | 2025 | 2025-05-01 | 31 | 11784 | 18152 | 10710 | 14944 | 16638 | 12050 | 12314 | 12976 | 11136 | 9042 | 10160 | 7229 | 10619 | 10415 | 11894 | 10970 | 13086 | 10907 | 9508 | 9816 | 9404 | 13232 | 10858 | 10039 | 17651 | 10027 | 4.94 | 5.32 | 4.51 | 5.05 | 5.31 | 4.9 | 4.65 | 4.77 | 4.58 | 4.33 | 4.5 | 4.53 | 4.5 | 4.54 | 4.7 | 4.6 | 5.08 | 4.6 | 4.58 | 4.5 | 4.35 | 5.04 | 4.55 | 4.46 | 5.37 | 4.62 | 305561 | 4.7262 |  |  | 296550 | 450 | 296100 | 9011 | 2.949% | 70.2 |  | 313.28
2025-05-12 | 2026 | 2025 | 2025-05-01 | 31 | 13179 | 18885 | 12004 | 15005 | 16569 | 11228 | 10674 | 12686 | 12783 | 10350 | 11071 | 9535 | 10103 | 11238 | 11575 | 10406 | 12451 | 11034 | 9396 | 9383 | 9631 | 11832 | 12422 | 10435 | 17749 | 13322 | 5.2 | 5.56 | 4.87 | 5.29 | 5.43 | 5.14 | 4.58 | 4.9 | 4.99 | 4.59 | 4.8 | 4.76 | 4.61 | 4.79 | 4.81 | 4.73 | 5.14 | 4.81 | 4.66 | 4.56 | 4.6 | 5.18 | 4.91 | 4.65 | 5.62 | 5 | 314946 | 4.93 |  |  | 306000 | 0 | 306000 | 8946 | 2.84% | 70.2 |  | 314.91
2025-05-13 | 2026 | 2025 | 2025-05-01 | 31 | 15857 | 18876 | 15776 | 17095 | 17236 | 17663 | 12778 | 15814 | 16473 | 13813 | 14778 | 15300 | 13332 | 15553 | 14487 | 14790 | 16970 | 17995 | 15025 | 15229 | 16195 | 18584 | 16842 | 15551 | 17764 | 15898 | 5.4114 | 5.4339 | 5.0701 | 5.3212 | 5.3029 | 5.6258 | 4.8813 | 5.1025 | 5.188 | 4.8715 | 5.069 | 5.0838 | 4.9722 | 5.1481 | 5.0597 | 5.1417 | 5.5261 | 5.3897 | 5.0406 | 5.1537 | 5.1899 | 5.8051 | 5.2141 | 5.1444 | 5.479 | 5.1699 | 415674 | 5.2229 |  |  | 400950 | 0 | 400950 | 14724 | 3.542% | 70.2 |  | 410.17
2025-05-14 | 2026 | 2025 | 2025-05-01 | 31 | 16319 | 18583 | 14080 | 17417 | 15099 | 17720 | 11697 | 15283 | 15322 | 15415 | 14181 | 15302 | 13452 | 14700 | 15173 | 15303 | 18475 | 17089 | 16326 | 15624 | 16085 | 19544 | 14410 | 16242 | 16100 | 15454 | 5.0697 | 5.2797 | 5.0058 | 5.2352 | 5.3367 | 5.4969 | 4.6087 | 4.9868 | 5.0221 | 5.1212 | 4.961 | 5.0131 | 4.8338 | 5.0288 | 5.0728 | 5.1335 | 5.5705 | 5.2769 | 5.0337 | 5.0945 | 5.1835 | 5.7272 | 5.0189 | 5.0988 | 5.3312 | 5.0005 | 410395 | 5.1362 |  |  | 396450 | 450 | 396000 | 13945 | 3.398% | 70.2 |  | 415.16
2025-05-15 | 2026 | 2025 | 2025-05-01 | 31 | 10977 | 13755 | 10870 | 10727 | 12109 | 10080 | 3143 | 9579 | 10970 | 9261 | 9679 | 10295 | 9066 | 10110 | 10258 | 9560 | 7809 | 9672 | 9583 | 8813 | 8783 | 9938 | 8838 | 9045 | 14292 | 11056 | 4.6133 | 4.6857 | 4.5751 | 4.4538 | 4.7587 | 4.6811 | 4.0416 | 4.3451 | 4.6019 | 4.4359 | 4.4327 | 4.5008 | 4.2769 | 4.5788 | 4.5176 | 4.471 | 4.5255 | 4.4989 | 4.3186 | 4.4651 | 4.3518 | 4.8256 | 4.4764 | 4.3887 | 4.8763 | 4.4816 | 258268 | 4.5069 |  |  | 248850 | 450 | 248400 | 9418 | 3.647% | 70.2 |  | 270.48
2025-05-16 | 2026 | 2025 | 2025-05-01 | 31 | 15323 | 18473 | 17202 | 13328 | 17636 | 15436 | 0 | 17474 | 4818 | 15439 | 17201 | 16669 | 15204 | 17755 | 16720 | 13381 | 17700 | 16087 | 17687 | 13373 | 16523 | 14989 | 15167 | 15031 | 17672 | 17902 | 5.5061 | 5.6145 | 5.4803 | 5.2666 | 5.6366 | 5.5567 | 5.2729 | 5.519 | 5.3178 | 5.2531 | 5.5726 | 5.5027 | 5.364 | 5.5334 | 5.3435 | 5.2426 | 5.9712 | 5.4459 | 5.6102 | 5.2698 | 5.4586 | 5.5388 | 5.2906 | 5.391 | 5.6255 | 5.584 | 394190 | 5.468 |  |  | 380700 | 0 | 380700 | 13490 | 3.422% | 70.2 |  | 429.76
2025-05-17 | 2026 | 2025 | 2025-05-01 | 31 | 12936 | 13841 | 13636 | 14208 | 13981 | 15568 | 6613 | 13646 | 0 | 12377 | 12651 | 12234 | 12639 | 13588 | 11589 | 13521 | 16123 | 16373 | 16562 | 14646 | 15887 | 15871 | 12728 | 14583 | 14600 | 12529 | 4.9874 | 5.0358 | 5.0377 | 5.0835 | 5.1158 | 5.5332 | 5.1147 | 5.0208 | 5.0653 | 4.9758 | 5.0733 | 4.9411 | 5.0442 | 5.1525 | 4.9208 | 5.1012 | 5.6313 | 5.4148 | 5.4194 | 5.3 | 5.4234 | 5.6298 | 4.9781 | 5.252 | 5.1213 | 4.916 | 342930 | 5.165 |  |  | 332550 | 0 | 332550 | 10380 | 3.027% | 70.2 |  | 357.08
2025-05-18 | 2026 | 2025 | 2025-05-01 | 31 | 11946 | 13720 | 12694 | 13552 | 13489 | 14126 | 12289 | 12152 | 10459 | 13272 | 12398 | 12617 | 11059 | 11662 | 11511 | 13018 | 14762 | 14428 | 14526 | 11805 | 13482 | 13318 | 12401 | 13791 | 14092 | 12416 | 5.0464 | 5.1148 | 5.0215 | 4.996 | 5.1639 | 5.3816 | 4.9451 | 4.9598 | 5.1681 | 5.1108 | 5.0665 | 5.0718 | 4.9145 | 4.9747 | 4.8935 | 5.0484 | 5.4293 | 5.2307 | 5.1165 | 4.977 | 5.0487 | 5.3208 | 4.956 | 5.1421 | 5.1714 | 4.9966 | 334985 | 5.0872 |  |  | 324900 | 0 | 324900 | 10085 | 3.011% | 70.2 |  | 337.37
2025-05-19 | 2026 | 2025 | 2025-05-01 | 31 | 15558 | 18002 | 13334 | 16163 | 16621 | 15698 | 15577 | 13643 | 15728 | 14496 | 12657 | 13600 | 13181 | 14141 | 13808 | 14766 | 16170 | 16444 | 15562 | 13464 | 14918 | 15617 | 14305 | 14413 | 18378 | 14378 | 5.2353 | 5.3892 | 4.931 | 5.1551 | 5.3842 | 5.4276 | 5.1708 | 4.8988 | 5.2003 | 5.0985 | 4.9034 | 4.9524 | 4.9085 | 5.0753 | 4.9822 | 5.2071 | 5.5333 | 5.2873 | 5.1228 | 4.9801 | 5.1851 | 5.3824 | 5.0476 | 5.0416 | 5.4908 | 5.0735 | 390622 | 5.1563 |  |  | 377550 | 0 | 377550 | 13072 | 3.346% | 70.2 |  | 390.56
2025-05-20 | 2026 | 2025 | 2025-05-01 | 31 | 13354 | 14878 | 13186 | 14713 | 13341 | 17635 | 12687 | 11853 | 13578 | 11868 | 12633 | 12059 | 13608 | 13779 | 14995 | 15196 | 16025 | 16145 | 14966 | 13323 | 13934 | 19816 | 13677 | 13270 | 11901 | 14103 | 5.1534 | 5.165 | 5.1111 | 5.335 | 5.0268 | 5.9038 | 5.0603 | 5.2739 | 5.193 | 4.9713 | 5.1108 | 5.0332 | 5.1621 | 5.2392 | 5.2847 | 5.468 | 5.6389 | 5.571 | 5.2465 | 5.266 | 5.3048 | 5.9965 | 5.2114 | 5.168 | 5.2221 | 5.1612 | 366523 | 5.2799 |  |  | 354150 | 450 | 353700 | 12373 | 3.376% | 70.2 |  | 390.19
2025-05-21 | 2026 | 2025 | 2025-05-01 | 31 | 5803 | 6870 | 4988 | 8746 | 6797 | 12064 | 8259 | 5500 | 5730 | 4705 | 4932 | 5048 | 5506 | 4919 | 6055 | 9269 | 12347 | 10658 | 9074 | 7738 | 9422 | 13881 | 5134 | 7917 | 6874 | 5324 | 4.4813 | 4.6071 | 4.2281 | 4.4625 | 4.6091 | 5.2309 | 4.3908 | 4.3136 | 4.3978 | 4.1453 | 4.1941 | 4.2658 | 4.2231 | 4.2792 | 4.4517 | 4.6978 | 5.031 | 4.9651 | 4.5521 | 4.3837 | 4.7536 | 5.3845 | 4.2631 | 4.4425 | 4.6387 | 4.4501 | 193560 | 4.5324 |  |  | 186750 | 0 | 186750 | 6810 | 3.518% | 70.2 |  | 202.65
2025-05-22 | 2026 | 2025 | 2025-05-01 | 31 | 5325 | 4261 | 2693 | 5901 | 5814 | 7702 | 5581 | 3597 | 4651 | 4928 | 4947 | 3211 | 4996 | 4869 | 5244 | 7051 | 7589 | 7942 | 5630 | 6725 | 6408 | 7766 | 2985 | 6850 | 3810 | 3271 | 4.1618 | 4.1426 | 3.9926 | 3.2892 | 4.2083 | 3.7441 | 3.2205 | 3.7531 | 3.9939 | 3.4765 | 4.0462 | 4.0371 | 3.4254 | 4.0648 | 3.5271 | 3.5917 | 3.8218 | 3.6434 | 3.3441 | 3.5103 | 3.3944 | 3.7944 | 4.0029 | 3.5227 | 4.2637 | 3.8773 | 139747 | 3.7635 |  |  | 134100 | 1350 | 132750 | 5647 | 4.041% | 70.2 |  | 158.54
2025-05-23 | 2026 | 2025 | 2025-05-01 | 31 | 13668 | 14033 | 15582 | 13541 | 13606 | 14664 | 12284 | 12198 | 13305 | 12638 | 15506 | 12864 | 12326 | 13110 | 13871 | 14234 | 13106 | 14776 | 12232 | 13537 | 12398 | 14801 | 15126 | 12086 | 12387 | 12236 | 4.8401 | 4.7564 | 5.1458 | 4.727 | 4.8064 | 5.301 | 4.534 | 4.7815 | 4.9097 | 4.901 | 5.1875 | 4.8191 | 4.7542 | 4.966 | 4.9407 | 5.018 | 4.8984 | 5.1885 | 4.5148 | 4.9509 | 4.8264 | 5.2289 | 5.1031 | 4.7422 | 4.8134 | 4.6903 | 350115 | 4.8979 |  |  | 337950 | 0 | 337950 | 12165 | 3.475% | 70.2 |  | 371.21
2025-05-24 | 2026 | 2025 | 2025-05-01 | 31 | 27867 | 31651 | 27965 | 37041 | 32935 | 34792 | 37142 | 16489 | 27378 | 28918 | 28336 | 14646 | 29021 | 28337 | 27961 | 36391 | 43558 | 34099 | 37403 | 35369 | 36290 | 39991 | 28932 | 36419 | 29481 | 25631 | 8.5741 | 9.3281 | 6.7629 | 7.3269 | 9.2793 | 7.164 | 7.2506 | 8.749 | 8.543 | 6.8704 | 6.8695 | 6.7288 | 6.8412 | 6.8389 | 6.8011 | 7.326 | 8.011 | 6.9788 | 7.2006 | 7.0827 | 7.1904 | 7.7211 | 6.8802 | 7.1317 | 8.7937 | 8.5232 | 814043 | 7.568 |  |  | 785250 | 0 | 785250 | 28793 | 3.537% | 70.2 |  | 847.72
2025-05-25 | 2026 | 2025 | 2025-05-01 | 31 | 31523 | 31804 | 32524 | 35537 | 30576 | 37549 | 32089 | 13402 | 32584 | 30599 | 32802 | 29518 | 33578 | 34055 | 34662 | 37245 | 36698 | 36409 | 34792 | 36870 | 19043 | 39460 | 33513 | 36629 | 24177 | 33380 | 7.39 | 8.54 | 7.42 | 7.44 | 8.41 | 7.81 | 7.1 | 7.66 | 7.5 | 7.36 | 7.55 | 7.49 | 7.53 | 7.64 | 7.72 | 7.75 | 7.77 | 7.61 | 7.37 | 7.68 | 7.9 | 8.09 | 7.57 | 7.6 | 8.27 | 7.56 | 841018 | 7.6819 |  |  | 812250 | 0 | 812250 | 28768 | 3.421% | 70.2 |  | 893.8
2025-05-26 | 2026 | 2025 | 2025-05-01 | 31 | 30294 | 31689 | 28918 | 30880 | 29206 | 30683 | 29635 | 26348 | 30386 | 26076 | 29120 | 27828 | 27161 | 28114 | 26878 | 28386 | 31939 | 31288 | 28966 | 26825 | 27558 | 31331 | 30243 | 28117 | 27468 | 29985 | 7.26 | 7.51 | 6.95 | 7.26 | 7.45 | 7.23 | 7.14 | 7.21 | 7.18 | 6.69 | 7.06 | 6.95 | 6.86 | 6.97 | 6.79 | 6.98 | 7.38 | 7.15 | 6.93 | 6.81 | 7.15 | 7.45 | 7.14 | 6.94 | 7.29 | 7.39 | 755322 | 7.12 |  |  | 731700 | 0 | 731700 | 23622 | 3.127% | 70.2 |  | 797.2
2025-05-27 | 2026 | 2025 | 2025-05-01 | 31 | 45298 | 48703 | 30098 | 55945 | 44273 | 54646 | 50912 | 10998 | 43632 | 44057 | 43495 | 44780 | 44658 | 45661 | 45816 | 53730 | 55315 | 55192 | 55584 | 52891 | 53312 | 54059 | 44797 | 54974 | 24864 | 45417 | 9.3 | 9.71 | 8.98 | 9.82 | 9.44 | 9.5 | 9.72 | 9.58 | 9.19 | 9.29 | 9.21 | 9.31 | 9.22 | 9.36 | 9.43 | 9.59 | 9.86 | 9.48 | 9.78 | 9.47 | 9.43 | 9.83 | 9.33 | 9.53 | 9.65 | 9.43 | 1203107 | 9.4785 |  |  | 1159200 | 0 | 1159200 | 43907 | 3.649% | 70.2 |  | 1294.88
2025-05-28 | 2026 | 2025 | 2025-05-01 | 31 | 36145 | 38104 | 36941 | 36974 | 37270 | 38856 | 38555 | 28269 | 35976 | 40745 | 37551 | 39371 | 36909 | 39144 | 38829 | 38163 | 42635 | 39115 | 41216 | 35547 | 38234 | 39494 | 40262 | 37785 | 29365 | 30364 | 8.29 | 8.39 | 7.92 | 8.51 | 8.3 | 8.62 | 8.62 | 8.51 | 8.26 | 8.29 | 8.08 | 8.19 | 8.04 | 8.18 | 8.18 | 8.63 | 9.12 | 8.56 | 8.88 | 8.35 | 8.51 | 8.86 | 8.3 | 8.46 | 8.39 | 8.48 | 971819 | 8.42 |  |  | 940050 | 0 | 940050 | 31769 | 3.269% | 70.2 |  | 1024.62
2025-05-29 | 2026 | 2025 | 2025-05-01 | 31 | 34991 | 35336 | 34454 | 27457 | 34066 | 38069 | 36624 | 36586 | 35770 | 35884 | 35836 | 35861 | 34932 | 36054 | 35776 | 34759 | 40825 | 38317 | 35573 | 33065 | 38437 | 38478 | 36437 | 36704 | 36147 | 36092 | 7.31 | 7.48 | 7.19 | 7.46 | 7.41 | 7.75 | 7.54 | 7.41 | 7.34 | 7.39 | 7.49 | 7.42 | 7.29 | 7.4 | 7.39 | 7.36 | 7.97 | 7.64 | 7.4 | 7.17 | 7.7 | 7.86 | 7.49 | 7.43 | 7.38 | 7.46 | 932530 | 7.4665 |  |  | 901800 | 450 | 901350 | 30730 | 3.295% | 70.2 |  | 986.68
2025-05-30 | 2026 | 2025 | 2025-05-01 | 31 | 54422 | 56778 | 55357 | 51855 | 54055 | 55099 | 52504 | 54379 | 53124 | 54576 | 55825 | 54494 | 54331 | 55074 | 55209 | 53676 | 48430 | 54614 | 54160 | 53978 | 57017 | 57090 | 56047 | 56687 | 57270 | 56413 | 9.9 | 10.18 | 9.76 | 9.77 | 10.13 | 9.69 | 9.71 | 10.04 | 9.74 | 9.86 | 9.98 | 9.98 | 9.82 | 9.76 | 9.86 | 9.88 | 9.77 | 9.82 | 9.85 | 9.64 | 9.92 | 10.04 | 10 | 9.95 | 10.09 | 10.06 | 1422464 | 9.8923 |  |  | 1370700 | 0 | 1370700 | 51764 | 3.639% | 70.2 |  | 1505.57
2025-05-31 | 2026 | 2025 | 2025-05-01 | 31 | 54328 | 59812 | 55547 | 48432 | 57780 | 47521 | 50547 | 51528 | 52803 | 45951 | 54037 | 53252 | 50292 | 52651 | 52780 | 45969 | 51878 | 48505 | 48391 | 47567 | 47315 | 50992 | 54330 | 47157 | 60528 | 51268 | 9.89 | 10.23 | 9.62 | 9.86 | 10.1 | 9.17 | 9.72 | 9.64 | 9.68 | 9.25 | 9.65 | 9.55 | 9.65 | 9.55 | 9.53 | 9.31 | 9.65 | 9.28 | 9.41 | 9.34 | 9.37 | 9.71 | 9.65 | 9.42 | 10.27 | 9.72 | 1341161 | 9.6238 |  |  | 1292850 | 0 | 1292850 | 48311 | 3.602% | 70.2 |  | 1438.1
2025-06-01 | 2026 | 2025 | 2025-06-01 | 30 | 51452 | 51968 | 49583 | 54729 | 51526 | 52898 | 52421 | 50512 | 46509 | 49419 | 52508 | 50282 | 53279 | 50629 | 55744 | 52351 | 53866 | 55945 | 53972 | 54727 | 53202 | 56693 | 50635 | 54417 | 52009 | 51125 | 9.59 | 9.56 | 9.25 | 9.8 | 9.61 | 9.83 | 9.67 | 9.51 | 9.19 | 9.32 | 9.66 | 9.43 | 9.68 | 9.53 | 9.69 | 9.74 | 10.12 | 9.94 | 9.94 | 9.85 | 9.88 | 10.26 | 9.4 | 9.71 | 9.56 | 9.59 | 1362401 | 9.6658 |  |  | 1315800 | 0 | 1315800 | 46601 | 3.421% | 70.2 |  | 1430.08
2025-06-02 | 2026 | 2025 | 2025-06-01 | 30 | 45136 | 43458 | 43320 | 43885 | 37935 | 47284 | 43351 | 40665 | 43095 | 42160 | 43507 | 42074 | 42757 | 42499 | 43008 | 42883 | 49276 | 48790 | 47122 | 44390 | 47930 | 51083 | 42240 | 45499 | 45713 | 44306 | 8.84 | 8.67 | 8.95 | 8.84 | 8.61 | 9.11 | 8.72 | 8.67 | 8.59 | 8.53 | 8.71 | 8.55 | 8.68 | 8.68 | 8.71 | 8.62 | 9.54 | 9.1 | 9.09 | 8.82 | 9.17 | 9.6 | 8.61 | 8.84 | 8.74 | 8.82 | 1153366 | 8.8388 |  |  | 1115550 | 0 | 1115550 | 37816 | 3.279% | 70.2 |  | 1231.2
2025-06-03 | 2026 | 2025 | 2025-06-01 | 30 | 40925 | 42209 | 38087 | 42047 | 36685 | 45651 | 40929 | 42705 | 38850 | 41700 | 40451 | 41874 | 43273 | 42846 | 42470 | 42266 | 44084 | 49499 | 42974 | 43980 | 45569 | 49028 | 39881 | 43980 | 40698 | 40020 | 8.3613 | 8.3293 | 7.9692 | 8.4647 | 8.2582 | 8.8278 | 8.2866 | 8.3554 | 8.095 | 8.3624 | 8.3172 | 8.3362 | 8.463 | 8.4297 | 8.4471 | 8.4174 | 8.7751 | 8.9645 | 8.5001 | 8.5967 | 8.7317 | 9.2119 | 8.2733 | 8.5872 | 8.1648 | 8.3165 | 1102681 | 8.4555 |  |  | 1066950 | 0 | 1066950 | 35731 | 3.24% | 70.2 |  | 1108.56
2025-06-04 | 2026 | 2025 | 2025-06-01 | 30 | 24898 | 25759 | 26108 | 25763 | 24508 | 27140 | 24286 | 27126 | 25943 | 25043 | 25689 | 27206 | 25486 | 26571 | 25789 | 25548 | 27895 | 27513 | 26102 | 25085 | 26598 | 27739 | 27511 | 27210 | 26511 | 26960 | 6.4133 | 6.38 | 6.3997 | 6.5212 | 6.316 | 6.8666 | 6.3282 | 6.5191 | 6.4479 | 6.4703 | 6.5357 | 6.5948 | 6.4676 | 6.5564 | 6.4814 | 6.5065 | 6.9206 | 6.6987 | 6.5718 | 6.4744 | 6.6208 | 6.9825 | 6.616 | 6.6071 | 6.3789 | 6.5644 | 681987 | 6.5477 |  |  | 661950 | 0 | 661950 | 20037 | 2.938% | 70.2 |  | 27.04
2025-06-05 | 2026 | 2025 | 2025-06-01 | 30 | 13550 | 16125 | 13730 | 13586 | 16515 | 16771 | 12137 | 14453 | 13444 | 15036 | 14184 | 14072 | 11586 | 13691 | 13908 | 15393 | 17046 | 16278 | 13284 | 13474 | 14863 | 17240 | 13874 | 14133 | 16460 | 14824 | 5.0131 | 5.2413 | 5.0058 | 5.089 | 5.35 | 5.5488 | 4.7424 | 4.9908 | 4.9435 | 5.2642 | 5.141 | 5.079 | 4.7873 | 5.0693 | 5.0746 | 5.1963 | 5.4158 | 5.3292 | 4.7405 | 5.0078 | 5.1641 | 5.5613 | 5.0563 | 5.0798 | 5.202 | 5.0755 | 379657 | 5.1219 |  |  | 367200 | 450 | 366750 | 12457 | 3.281% | 70.2 |  | 385.8
2025-06-06 | 2026 | 2025 | 2025-06-01 | 30 | 23542 | 28011 | 21461 | 25991 | 25186 | 21010 | 24124 | 23491 | 22922 | 19049 | 21231 | 21248 | 15424 | 21157 | 21726 | 21529 | 21983 | 20504 | 24299 | 21713 | 17959 | 22267 | 20887 | 22271 | 27512 | 23651 | 6.396 | 6.5941 | 6.1098 | 6.4729 | 6.5211 | 6.0505 | 6.2222 | 6.1627 | 6.3328 | 5.79 | 6.0825 | 6.013 | 5.6119 | 6.0167 | 6.0845 | 5.9181 | 6.0956 | 5.8436 | 6.1321 | 5.9603 | 5.674 | 6.1553 | 6.2453 | 6.0592 | 6.5124 | 6.2502 | 580148 | 6.1272 |  |  | 562950 | 0 | 562950 | 17198 | 2.964% | 70.2 |  | 593.58
2025-06-07 | 2026 | 2025 | 2025-06-01 | 30 | 36444 | 39249 | 34508 | 37281 | 35981 | 35598 | 29552 | 35543 | 35377 | 27739 | 32412 | 32626 | 30645 | 31718 | 32828 | 34805 | 36795 | 33687 | 34286 | 33556 | 30481 | 36261 | 33585 | 33319 | 36168 | 36341 | 7.7685 | 7.8717 | 7.4576 | 8.0349 | 7.7258 | 7.6244 | 7.9135 | 7.6635 | 7.6497 | 6.8254 | 7.3806 | 7.3603 | 7.1381 | 7.2479 | 7.2614 | 7.4703 | 7.7663 | 7.3792 | 7.4387 | 7.3408 | 7.1207 | 7.8234 | 7.6009 | 7.3147 | 7.5799 | 7.7582 | 886785 | 7.5199 |  |  | 860400 | 0 | 860400 | 26385 | 2.975% | 70.2 |  | 899.42
2025-06-08 | 2026 | 2025 | 2025-06-01 | 30 | 32831 | 38753 | 28801 | 31181 | 35576 | 34796 | 27380 | 32471 | 32169 | 21370 | 27931 | 28514 | 29599 | 29807 | 29849 | 27769 | 37806 | 34026 | 32013 | 31913 | 29442 | 37250 | 30447 | 31586 | 36044 | 31644 | 7.4015 | 7.7237 | 6.9159 | 7.5828 | 7.5312 | 7.4843 | 8.5573 | 7.2618 | 7.364 | 6.7678 | 6.9065 | 6.9401 | 7.0048 | 7.0737 | 7.0331 | 7.2335 | 7.7298 | 7.2961 | 7.1389 | 7.1742 | 6.9294 | 7.8553 | 7.1547 | 7.1456 | 7.4145 | 7.267 | 820968 | 7.3034 |  |  | 796950 | 0 | 796950 | 24018 | 2.926% | 70.2 |  | 846.28
2025-06-09 | 2026 | 2025 | 2025-06-01 | 30 | 38655 | 43809 | 35879 | 43999 | 40683 | 40911 | 42416 | 40286 | 37517 | 33817 | 35565 | 36462 | 36617 | 36339 | 38249 | 35416 | 43247 | 39577 | 43313 | 39588 | 36821 | 41992 | 38136 | 39136 | 41879 | 38713 | 7.9085 | 8.2609 | 7.5985 | 8.3585 | 8.0426 | 8.0916 | 8.1931 | 7.98 | 7.8343 | 7.4884 | 7.7117 | 7.7317 | 7.7314 | 7.7606 | 7.8296 | 7.9069 | 8.2959 | 7.9583 | 8.2128 | 7.9706 | 7.7406 | 8.3485 | 7.9217 | 7.9288 | 8.0008 | 7.9617 | 1019022 | 7.9526 |  |  | 986400 | 0 | 986400 | 32622 | 3.201% | 70.2 |  | 1032.83
2025-06-10 | 2026 | 2025 | 2025-06-01 | 30 | 31902 | 48133 | 38820 | 45191 | 45509 | 45918 | 44939 | 41406 | 40203 | 24662 | 39174 | 38012 | 38340 | 40587 | 39946 | 36929 | 47784 | 45025 | 45854 | 41819 | 39222 | 47621 | 41629 | 42452 | 44148 | 40326 | 7.9992 | 8.5849 | 7.7553 | 8.7191 | 8.443 | 8.4359 | 8.9128 | 8.1028 | 7.9328 | 7.2729 | 7.9554 | 7.786 | 7.8585 | 8.0126 | 7.9769 | 8.1076 | 8.687 | 8.3174 | 8.5791 | 8.0747 | 7.8759 | 8.8274 | 8.1328 | 8.126 | 8.1667 | 8.0076 | 1075551 | 8.1789 |  |  | 1039950 | 0 | 1039950 | 35601 | 3.31% | 70.2 |  | 1108.35
2025-06-11 | 2026 | 2025 | 2025-06-01 | 30 | 9734 | 36977 | 29844 | 39436 | 36794 | 40136 | 37443 | 32554 | 31584 | 29395 | 30425 | 29594 | 30667 | 31516 | 33467 | 31802 | 43028 | 38012 | 38995 | 36328 | 32780 | 42577 | 32660 | 32861 | 34949 | 31821 | 7.0827 | 7.3478 | 6.831 | 7.7086 | 7.4348 | 7.7985 | 7.5848 | 7.161 | 7.0099 | 6.8957 | 6.9265 | 6.8606 | 6.9643 | 7.0266 | 7.2197 | 7.3999 | 8.0123 | 7.5483 | 7.5444 | 7.3913 | 7.1442 | 8.2019 | 7.1577 | 7.1294 | 7.1596 | 7.0726 | 875379 | 7.2928 |  |  | 847350 | 0 | 847350 | 28029 | 3.202% | 70.2 |  | 911.21
2025-06-12 | 2026 | 2025 | 2025-06-01 | 30 | 34477 | 39052 | 34841 | 38026 | 39640 | 38942 | 35495 | 35425 | 34158 | 32656 | 35464 | 35020 | 36239 | 33546 | 34042 | 33459 | 38207 | 38826 | 31298 | 36557 | 36826 | 38525 | 34706 | 35891 | 39349 | 34057 | 7.534 | 7.9267 | 7.3833 | 7.9136 | 8.0057 | 7.9624 | 7.6539 | 7.5212 | 7.4208 | 7.3535 | 7.5994 | 7.5747 | 7.6447 | 7.4271 | 7.4801 | 7.7637 | 8.1265 | 7.858 | 7.1226 | 7.7411 | 7.7533 | 8.1178 | 7.5441 | 7.6124 | 7.741 | 7.4847 | 934724 | 7.6641 |  |  | 904050 | 0 | 904050 | 30674 | 3.282% | 70.2 |  | 956.64
2025-06-13 | 2026 | 2025 | 2025-06-01 | 30 | 32934 | 36638 | 25663 | 36067 | 36849 | 39258 | 36104 | 34334 | 33994 | 34029 | 32527 | 34595 | 33442 | 34593 | 34646 | 37642 | 39839 | 38863 | 37802 | 35544 | 36906 | 38130 | 34730 | 36590 | 37779 | 35207 | 7.4089 | 7.695 | 7.1972 | 7.6815 | 7.7423 | 7.8989 | 7.6507 | 7.4099 | 7.4381 | 7.4326 | 7.3402 | 7.4908 | 7.4001 | 7.4993 | 7.4936 | 7.7504 | 8.0449 | 7.8056 | 7.7017 | 7.5676 | 7.653 | 7.9468 | 7.5196 | 7.6124 | 7.6494 | 7.5599 | 924705 | 7.5996 |  |  | 917550 | 0 | 917550 | 7155 | 0.7738% | 70.2 |  | 974.61
2025-06-14 | 2026 | 2025 | 2025-06-01 | 30 | 19047 | 22274 | 13499 | 19604 | 21920 | 17769 | 17345 | 16297 | 17985 | 16628 | 17271 | 18334 | 18635 | 18138 | 17305 | 17419 | 18673 | 15821 | 17165 | 16544 | 15053 | 18674 | 18024 | 16943 | 22054 | 14946 | 5.5226 | 5.77 | 5.4419 | 5.6206 | 5.7987 | 5.541 | 5.391 | 5.2151 | 5.4499 | 5.2749 | 5.4329 | 5.3913 | 5.4374 | 5.4235 | 5.6494 | 5.4108 | 5.6649 | 5.2827 | 5.2842 | 5.3307 | 5.1783 | 5.6629 | 5.446 | 5.3007 | 5.7179 | 5.2453 | 463367 | 5.4571 |  |  | 429300 | 450 | 428850 | 34067 | 7.352% | 70.2 |  | 487.83
2025-06-15 | 2026 | 2025 | 2025-06-01 | 30 | 6873 | 7405 | 6039 | 7279 | 7628 | 6453 | 6199 | 6049 | 6230 | 5616 | 5733 | 6246 | 5738 | 5678 | 6379 | 6661 | 7576 | 6368 | 6397 | 6037 | 6617 | 7684 | 6606 | 6770 | 7091 | 6614 | 3.4516 | 3.5476 | 3.3484 | 3.5663 | 3.62 | 3.7085 | 3.3538 | 3.3355 | 3.2887 | 3.471 | 3.3755 | 3.5653 | 3.4454 | 3.4983 | 3.5603 | 3.647 | 3.9024 | 3.5278 | 3.4488 | 3.558 | 3.5866 | 3.8319 | 3.4724 | 3.5779 | 3.5811 | 3.4431 | 169966 | 3.5274 |  |  | 162900 | 1800 | 161100 | 7066 | 4.157% | 70.2 |  | 170.73
2025-06-16 | 2026 | 2025 | 2025-06-01 | 30 | 39130 | 42568 | 38565 | 36994 | 40178 | 31287 | 35642 | 32516 | 37258 | 39353 | 39549 | 9859 | 39723 | 41004 | 40211 | 34356 | 38744 | 30414 | 34847 | 27510 | 32444 | 35130 | 38850 | 35934 | 41655 | 30609 | 8.16 | 8.51 | 8.05 | 8.54 | 8.36 | 7.97 | 8.45 | 7.81 | 7.9 | 8.17 | 8.32 | 8.02 | 8.23 | 8.45 | 8.37 | 8.21 | 8.9 | 7.81 | 8.17 | 8.05 | 8.01 | 8.47 | 8.19 | 8.1 | 8.35 | 7.76 | 924330 | 8.205 |  |  | 899100 | 0 | 899100 | 25230 | 2.73% | 70.2 |  | 988.32
2025-06-17 | 2026 | 2025 | 2025-06-01 | 30 | 37729 | 42080 | 35379 | 41258 | 38415 | 36528 | 41267 | 38538 | 35719 | 35315 | 36162 | 0 | 37389 | 38123 | 36756 | 35950 | 36964 | 37972 | 42584 | 37144 | 38228 | 38185 | 36578 | 39219 | 39729 | 37582 | 7.88 | 8.19 | 7.45 | 8.13 | 8.14 | 7.74 | 8.14 | 7.77 | 7.61 | 7.4 | 7.71 | 7.68 | 7.69 | 7.74 | 7.62 | 7.6 | 8.11 | 7.73 | 8.3 | 7.65 | 7.83 | 7.91 | 7.6 | 7.79 | 8.05 | 7.75 | 950793 | 7.8158 |  |  | 919350 | 450 | 918900 | 31443 | 3.307% | 70.2 |  | 991.84
2025-06-18 | 2026 | 2025 | 2025-06-01 | 30 | 44447 | 46395 | 44523 | 46220 | 44448 | 46246 | 45647 | 35384 | 43011 | 43123 | 44761 | 0 | 42752 | 45291 | 47505 | 45385 | 47491 | 46030 | 46597 | 45114 | 43476 | 45732 | 45536 | 45654 | 46792 | 46495 | 8.41 | 8.62 | 8.26 | 8.6 | 8.43 | 8.78 | 8.53 | 8.37 | 8.27 | 8.17 | 8.42 | 8.64 | 8.2 | 8.43 | 8.53 | 8.69 | 9.04 | 8.61 | 8.8 | 8.54 | 8.46 | 8.86 | 8.44 | 8.48 | 8.49 | 8.46 | 1124055 | 8.5204 |  |  | 1089450 | 0 | 1089450 | 34605 | 3.079% | 70.2 |  | 1202.27
2025-06-19 | 2026 | 2025 | 2025-06-01 | 30 | 60392 | 61807 | 60544 | 60132 | 58668 | 63667 | 58782 | 58864 | 61695 | 62876 | 59212 | 1 | 60450 | 62218 | 61780 | 63183 | 56889 | 63849 | 61676 | 61808 | 64593 | 61067 | 63255 | 63198 | 61713 | 61863 | 10.18 | 10.5 | 10.06 | 10.49 | 10.41 | 10.57 | 10.44 | 10.56 | 10.3 | 10.43 | 10.22 | 10.3 | 10.3 | 10.42 | 10.49 | 10.75 | 10.79 | 10.49 | 10.74 | 10.47 | 10.68 | 10.65 | 10.45 | 10.57 | 10.32 | 10.41 | 1534182 | 10.4612 |  |  | 1476900 | 0 | 1476900 | 57282 | 3.734% | 70.2 |  | 1596.54
2025-06-20 | 2026 | 2025 | 2025-06-01 | 30 | 53793 | 54625 | 53938 | 28462 | 54458 | 25348 | 26899 | 26779 | 55200 | 51226 | 52720 | 2 | 52599 | 53088 | 48939 | 23998 | 30663 | 26196 | 22014 | 28404 | 26386 | 26278 | 54129 | 30076 | 56557 | 26295 | 9.5837 | 9.7622 | 9.5528 | 8.364 | 9.5912 | 8.0911 | 8.1708 | 8.6714 | 9.7222 | 9.4076 | 9.5963 | 9.5979 | 9.5624 | 9.5958 | 9.2876 | 7.6072 | 8.4266 | 8.0541 | 7.8662 | 8.0893 | 8.1819 | 7.9512 | 9.7455 | 8.2486 | 9.6965 | 8.558 | 989072 | 8.8839 |  |  | 956250 | 0 | 956250 | 32822 | 3.318% | 70.2 |  | 1078.22
2025-06-21 | 2026 | 2025 | 2025-06-01 | 30 | 48915 | 52214 | 49894 | 46630 | 51899 | 43979 | 48182 | 50739 | 52017 | 50278 | 47808 | 3 | 49448 | 48944 | 45933 | 42701 | 49013 | 44036 | 40849 | 45324 | 45389 | 40673 | 51283 | 50597 | 54700 | 52790 | 8.98 | 9.25 | 8.88 | 8.81 | 9.26 | 8.45 | 8.94 | 9.01 | 9.24 | 8.92 | 8.9 | 8.75 | 8.92 | 8.88 | 8.81 | 8.29 | 8.76 | 8.34 | 8.44 | 8.65 | 8.46 | 8.07 | 9.25 | 8.93 | 9.3 | 9.24 | 1204238 | 8.8358 |  |  | 1165500 | 0 | 1165500 | 38738 | 3.217% | 70.2 |  | 1261.16
2025-06-22 | 2026 | 2025 | 2025-06-01 | 30 | 29608 | 32913 | 33071 | 28909 | 33162 | 28395 | 25670 | 33659 | 32328 | 29827 | 29493 | 1 | 30075 | 31473 | 26706 | 26754 | 30399 | 29382 | 26158 | 27533 | 30069 | 24705 | 32944 | 30198 | 35011 | 31309 | 7.15 | 7.3 | 7.28 | 6.95 | 7.4 | 7.1 | 6.57 | 7.25 | 7.32 | 7.03 | 7.11 | 7.51 | 7.07 | 7.21 | 6.77 | 6.76 | 7.21 | 7.02 | 6.84 | 6.86 | 7.06 | 6.61 | 7.32 | 6.98 | 7.4 | 7.21 | 749752 | 7.0881 |  |  | 729900 | 0 | 729900 | 19852 | 2.648% | 70.2 |  | 790.8
2025-06-23 | 2026 | 2025 | 2025-06-01 | 30 | 32259 | 36662 | 33725 | 28913 | 33535 | 32886 | 30932 | 33205 | 35738 | 33998 | 33536 | 0 | 34442 | 35000 | 33852 | 32991 | 35432 | 33258 | 34347 | 30969 | 32231 | 28383 | 36008 | 33852 | 38693 | 35736 | 7.43 | 7.67 | 7.6 | 7.05 | 7.64 | 7.68 | 7.18 | 7.45 | 7.78 | 7.57 | 7.67 | 8.97 | 7.57 | 7.66 | 7.54 | 7.58 | 7.84 | 7.52 | 7.63 | 7.31 | 7.45 | 7.07 | 7.76 | 7.43 | 7.78 | 7.68 | 840583 | 7.5965 |  |  | 820350 | 0 | 820350 | 20233 | 2.407% | 70.2 |  | 894.97
2025-06-24 | 2026 | 2025 | 2025-06-01 | 30 | 43504 | 46613 | 43680 | 42991 | 46848 | 42185 | 44567 | 39645 | 44922 | 41740 | 43228 | 0 | 43455 | 43210 | 40798 | 38965 | 45630 | 41810 | 48279 | 41972 | 44172 | 40585 | 44719 | 43964 | 49046 | 45247 | 8.31 | 8.58 | 8.2 | 8.34 | 8.7 | 8.23 | 8.35 | 8.36 | 8.44 | 8.03 | 8.29 | 9.76 | 8.23 | 8.23 | 8.01 | 7.85 | 8.53 | 8.08 | 8.59 | 8.14 | 8.25 | 8.08 | 8.35 | 8.19 | 8.61 | 8.41 | 1091775 | 8.3515 |  |  | 1056600 | 0 | 1056600 | 35175 | 3.222% | 70.2 |  | 1165.22
2025-06-25 | 2026 | 2025 | 2025-06-01 | 30 | 9881 | 9958 | 9307 | 10703 | 10550 | 13541 | 10134 | 9903 | 9690 | 8295 | 10093 | 0 | 8970 | 8612 | 8951 | 10180 | 15934 | 12551 | 13990 | 10246 | 13211 | 14081 | 9260 | 11296 | 11852 | 9536 | 4.89 | 4.76 | 4.66 | 4.85 | 4.84 | 5.7 | 4.78 | 4.66 | 4.75 | 4.53 | 4.88 | 5.4 | 4.69 | 4.61 | 4.59 | 4.84 | 5.87 | 5.25 | 5.34 | 4.9 | 5.31 | 5.48 | 4.63 | 4.97 | 4.97 | 4.7 | 270725 | 4.9558 |  |  | 263250 | 0 | 263250 | 7475 | 2.761% | 70.2 |  | 286.3
2025-06-26 | 2026 | 2025 | 2025-06-01 | 30 | 5982 | 6461 | 5250 | 6918 | 6206 | 7570 | 6102 | 6987 | 5838 | 5654 | 6362 | 0 | 7100 | 6657 | 6563 | 5760 | 9140 | 7687 | 7434 | 6217 | 7106 | 7623 | 5808 | 6764 | 6817 | 6401 | 3.92 | 3.9 | 3.67 | 3.89 | 3.93 | 4.61 | 3.73 | 3.83 | 3.78 | 3.73 | 3.95 | 2.72 | 3.94 | 3.96 | 3.85 | 3.72 | 4.55 | 4.09 | 3.99 | 3.93 | 4.13 | 4.19 | 3.76 | 3.97 | 3.98 | 3.85 | 166407 | 3.9065 |  |  | 161100 | 900 | 160200 | 5307 | 3.189% | 70.2 |  | 172.06
2025-06-27 | 2026 | 2025 | 2025-06-01 | 30 | 29710 | 29694 | 30983 | 29532 | 28858 | 35928 | 27937 | 31893 | 31282 | 31871 | 32970 | 0 | 25886 | 32706 | 33647 | 33184 | 35884 | 35848 | 32324 | 29446 | 32170 | 37800 | 29380 | 32878 | 30869 | 31562 | 6.9103 | 6.8455 | 6.8801 | 6.8813 | 6.8433 | 7.6981 | 6.7058 | 6.9772 | 7.0094 | 7.0302 | 7.2204 | 0 | 7.1978 | 7.1072 | 7.1797 | 7.136 | 7.7324 | 7.3765 | 7.1459 | 6.9877 | 7.1735 | 7.7765 | 6.8871 | 7.154 | 6.8993 | 7.0189 | 794242 | 6.8375 |  |  | 772650 | 0 | 772650 | 21592 | 2.719% | 70.2 |  | 807.27
2025-06-28 | 2026 | 2025 | 2025-06-01 | 30 | 56204 | 55284 | 54660 | 53600 | 54703 | 58092 | 53572 | 42838 | 56209 | 54705 | 56457 | 0 | 56738 | 56319 | 58053 | 55682 | 56104 | 58276 | 57627 | 52311 | 56225 | 58011 | 53851 | 54860 | 56866 | 55344 | 9.8894 | 9.8825 | 9.6035 | 9.6678 | 9.7336 | 10.1486 | 9.5979 | 9.7179 | 9.8218 | 9.616 | 9.9553 | 5.8128 | 9.8643 | 9.7319 | 9.9236 | 9.908 | 10.3196 | 9.9668 | 10.1456 | 9.5035 | 10.0352 | 10.3418 | 9.751 | 9.6994 | 9.8126 | 9.729 | 1382591 | 9.6992 |  |  | 1334250 | 0 | 1334250 | 48341 | 3.496% | 70.2 |  | 1434.41
2025-06-29 | 2026 | 2025 | 2025-06-01 | 30 | 54692 | 56261 | 53336 | 58716 | 53004 | 62725 | 57606 | 46179 | 45425 | 55795 | 57284 | 0 | 57422 | 58023 | 56720 | 58947 | 61742 | 63546 | 62375 | 60462 | 62347 | 63422 | 53083 | 60695 | 55475 | 55208 | 9.73 | 9.94 | 9.48 | 10.12 | 9.74 | 10.8 | 10.09 | 9.86 | 9.53 | 9.88 | 10.01 | 10.9 | 9.96 | 10.04 | 9.96 | 10.28 | 11.07 | 10.65 | 10.77 | 10.29 | 10.64 | 11.09 | 9.6 | 10.22 | 9.64 | 9.79 | 1430490 | 10.1569 |  |  | 1379250 | 0 | 1379250 | 51240 | 3.582% | 70.2 |  | 1508.13
2025-06-30 | 2026 | 2025 | 2025-06-01 | 30 | 53426 | 53878 | 52369 | 55594 | 52759 | 57647 | 55087 | 38128 | 44861 | 49805 | 54194 | 0 | 53550 | 53754 | 51323 | 51935 | 59127 | 58437 | 59722 | 55431 | 59418 | 58811 | 53587 | 55787 | 56331 | 53074 | 9.3383 | 9.4256 | 9.1933 | 9.5111 | 9.4017 | 9.9126 | 9.5431 | 9.3522 | 9.3042 | 9.1195 | 9.449 | 10.4606 | 9.3082 | 9.2949 | 9.1255 | 9.3399 | 10.2606 | 9.7431 | 10.0963 | 9.5286 | 9.9464 | 10.0696 | 9.3122 | 9.5404 | 9.4933 | 9.3251 | 1348035 | 9.5537 |  |  | 1301850 | 0 | 1301850 | 46185 | 3.426% | 70.2 |  | 1451.83
Formulas:
Month Year = [Date]-DAY([Date])+1
Days = DAY(EOMONTH(Input_Raw[[#This Row],[Date]],0))
Date = [Date, row above]+1

## WTG_BD
Sr. No. | Financial Year | Calendar Year | Operating Year | Month | Date | Affected WTG | SPV | Consumer | Plant Equivalent Weightage | Error Code | Error Text | Breakdown Description | Stoppage Type | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Paired WTG for Enegy based MA | Paired WTG Generation for loss calculation | Estimated Energy Loss (kWh) | Special Remarks | PTW No. | Job Card No.
1 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-01 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 5:17 | 5:17 | 5:21 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-05 | 24626 | 68.4056
2 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-01 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 18:42 | 18:42 | 18:54 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-05 | 24626 | 205.2167
3 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-01 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Break down |  | 14:18 | 14:18 | 14:32 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & started WTG. | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-07 | 16286 | 158.3361
4 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-01 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Break down |  | 15:25 | 15:30 | 15:51 | 0.083333 | 0.35 | 0.43333 | Attend and check error related ckt than found Yaw MPCB Feedback connection loose so tight it than reset and started WTG. | Close | 0.016667 | WTG Unscheduled Maintenance | O2-07 | 16286 | 294.0528
5 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-01 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 9:23 | 9:23 | 18:00 | 0 | 8.6167 | 8.6167 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.33141 | WTG Scheduled Maintenance | O2-15 | 23343 | 8380.7854
6 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-01 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 7:05 | 7:05 | 7:07 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-11 | 21579 | 29.9708
7 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-01 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 21:10 | 21:10 | 21:12 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-06 | 19200 | 26.6667
8 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 12:04 | 12:04 | 12:10 | 0 | 0.1 | 0.1 | Check Event log and check Data log after Reset and started wtg | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 12678 | 52.825
9 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 11:45 | 11:45 | 11:50 | 0 | 0.083333 | 0.083333 | Check Event and check Converter Data log after Reset and started wtg | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-05 | 12752 | 44.2778
10 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 17:51 | 17:51 | 17:54 | 0 | 0.05 | 0.05 | check event log after check voltage and current data after so ok then reset and started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-05 | 12752 | 26.5667
11 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 17:51 | 17:51 | 17:53 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-07 | 7398 | 10.275
12 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset |  | 11:42 | 11:42 | 11:45 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-02 | 9289 | 19.3521
13 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset |  | 15:31 | 15:31 | 15:34 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-02 | 9289 | 19.3521
14 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 8:24 | 8:24 | 8:48 | 0 | 0.4 | 0.4 | Check Event log and check Nacelle Hydralic Presure value and apply flushing mode on after check value after reset and started wtg | Close | 0.015385 | WTG Unscheduled Maintenance | O2-26 | 12678 | 211.3
15 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_10 | TQGXIIPL | GEDA | 3.846% | 656 | Error pitch converter 1 | Break down |  | 7:45 | 7:45 | 8:13 | 0 | 0.46667 | 0.46667 | check Event log and check pitch converter 1 Data check snapshot and open hub and check Motor current value so ok after reset and started wtg. | Close | 0.017949 | WTG Unscheduled Maintenance | O2-15 | 13298 | 258.5722
16 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 9:36 | 9:36 | 15:30 | 0 | 5.9 | 5.9 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.22692 | WTG Scheduled Maintenance | O2-15 | 13298 | 3269.0917
17 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 7:23 | 7:23 | 7:29 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 12012 | 50.05
18 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset |  | 4:03 | 4:03 | 4:05 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-22 | 9405 | 13.0625
19 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 17:51 | 17:51 | 17:56 | 0 | 0.083333 | 0.083333 | Check Event and check Converter Data log after Reset and started wtg | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-06 | 10737 | 37.2812
20 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 17:51 | 17:51 | 17:53 | 0 | 0.033333 | 0.033333 | Check Event and check Converter Data log after Reset and started wtg | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-11 | 12012 | 16.6833
21 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Break down |  | 13:38 | 14:36 | 15:24 | 0.96667 | 0.8 | 1.7667 | Attend and wtg check MPCB Check Motor and check all connection so found MPCB Connection loose after then all connection tight after tack trail all candion ok then reset and started wtg. | Close | 0.067949 | WTG Unscheduled Maintenance | O2-01 | 15390 | 1132.875
22 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-02 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 17:51 | 17:51 | 17:56 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-01 | 15390 | 53.4375
23 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-03 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 9:09 | 9:09 | 18:40 | 0 | 9.5167 | 9.5167 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.36603 | WTG Scheduled Maintenance | O2-26 | 13667 | 5419.3451
24 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-03 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 12:00 | 12:00 | 12:04 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-04 | 11906 | 33.0722
25 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-03 | O2_08 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down |  | 22:35 | 22:35 | 22:58 | 0 | 0.38333 | 0.38333 | Check Data log and all Perameter check and Nacell angle check and check Angle of twist after Removed cable twist after trail so ok then started wtg. | Close | 0.014744 | WTG Unscheduled Maintenance | O2-26 | 13667 | 218.2924
26 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-03 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset |  | 11:01 | 11:01 | 11:02 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-15 | 16142 | 11.2097
27 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-03 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset |  | 11:13 | 11:13 | 11:14 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-15 | 16142 | 11.2097
28 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-03 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 12:40 | 12:40 | 12:53 | 0 | 0.21667 | 0.21667 | check Data log and converter Data check after so ok then reset and started wtg. | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-12 | 14465 | 130.5868
29 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-03 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 10:45 | 10:45 | 15:52 | 0 | 5.1167 | 5.1167 | Attend and check related ckt so found QA 7.1 Grid filter contactor burnout and 2 nos fuse faulty after Replaced all cable between contactor to fuse and contactor to capacitor . Then we taken all capacitor value found all normal . Then we have replaced both QA7.1 And QA7.2 Contactor and all 6 nos cable between contactor to fuse and fuse to capacitor and 2 nos fuse after complete all cable rooting properly we have perform a precharge , grid filter and GSC Test found all values normal so we started the turbine. | Close | 0.19679 | WTG Unscheduled Maintenance | O2-21 | 11665 | 2486.9132
30 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-04 | O2_01 | TQGXIIPL | GEDA | 3.846% | 5550 | Low hydraulic oil level | Break down |  | 4:06 | 4:06 | 6:18 | 0 | 2.2 | 2.2 | Attend and wtg check releted circuit and check all valve and after oil top up after trail so ok then reset and started wtg. | Close | 0.084615 | WTG Unscheduled Maintenance | O2-26 | 7143 | 654.775
31 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-04 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 9:50 | 9:50 | 15:23 | 0 | 5.55 | 5.55 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.21346 | WTG Scheduled Maintenance | O2-26 | 7143 | 1651.8188
32 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-04 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset |  | 5:05 | 5:05 | 5:08 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-02 | 13454 | 28.0292
33 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-04 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset |  | 1:30 | 1:30 | 1:41 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-26 | 7143 | 54.5646
34 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-04 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down |  | 2:16 | 2:16 | 2:41 | 0 | 0.41667 | 0.41667 | Checked related error data log then reset & started WTG. | Close | 0.016026 | WTG Unscheduled Maintenance | O2-26 | 7143 | 124.0104
35 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-04 | O2_08 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down |  | 22:54 | 22:54 | 24:00 | 0 | 1.1 | 1.1 | Check Data log and all Perameter check and Nacell angle check and check Angle of twist after Removed cable twist after trail so ok then started wtg. | Close | 0.042308 | WTG Unscheduled Maintenance | O2-26 | 7143 | 327.3875
36 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-04 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down |  | 4:36 | 4:36 | 8:15 | 0 | 3.65 | 3.65 | Attend and wtg check Hydraulic Pump 9.1 Valve and Hydraulic oil top up after check all pipe and flushing mode on and check pressure so ok after trail then reset and started wtg. | Close | 0.14038 | WTG Unscheduled Maintenance | O2-14 | 9746 | 1482.2042
37 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-04 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset |  | 11:43 | 11:43 | 11:45 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-20 | 10901 | 15.1403
38 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-04 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down |  | 19:35 | 19:35 | 24:00 | 0 | 4.4167 | 4.4167 | Attend and wtg check Hydraulic unit valve and check pressure and check all valv after replace 9.1 valv and top up hydraulic oil wtg working pogress | open | 0.16987 | WTG Unscheduled Maintenance | O2-20 | 10901 | 2006.0868
39 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-05 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 6:14 | 6:14 | 14:54 | 0 | 8.6667 | 8.6667 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.33333 | WTG Scheduled Maintenance | O2-09 | 10832 | 3911.5556
40 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-05 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 22:10 | 22:10 | 22:44 | 0 | 0.56667 | 0.56667 | Check Data log and all Perameter check and Nacell angle check and check Angle of twist after Removed cable twist after trail so ok then started wtg. | Close | 0.021795 | WTG Unscheduled Maintenance | O2-04 | 9733 | 229.8069
41 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-05 | O2_08 | TQGXIIPL | GEDA | 3.846% | 153 | SLC SF max. cable winding | Break down |  | 0:00 | 0:00 | 1:29 | 0 | 1.4833 | 1.4833 | Check Data log and all Perameter check and Nacell angle check and check Angle of twist after Removed cable twist after trail so ok then started wtg. | Close | 0.057051 | WTG Unscheduled Maintenance | O2-26 | 8683 | 536.6576
42 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-05 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Auto reset |  | 7:07 | 7:07 | 7:08 | 0 | 0.016667 | 0.016667 | auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-12 | 9113 | 6.3285
43 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-05 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset |  | 8:57 | 8:57 | 9:00 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-11 | 9830 | 20.4792
44 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-05 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Major BD |  | 0:00 | 0:00 | 16:45 | 0 | 16.75 | 16.75 | Attend and check than hydraulic oil level than found ok than check 9.1 Valve than check pressure value devuation in SAM than found pressure is suddenly drop so replace 9.1 valve and fluxing but same error occureded so check all other valve than check Accumulator than set rotor pressure proper than take trail than nothing abnormal so reset and start turbine. | Close | 0.64423 | WTG Unscheduled Maintenance | O2-20 | 7721 | 5388.6146
45 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-05 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset |  | 8:57 | 8:57 | 9:00 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-01 | 10770 | 22.4375
46 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset |  | 6:56 | 6:56 | 7:07 | 0 | 0.18333 | 0.18333 | Auto Reset | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-26 | 14855 | 113.4757
47 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset |  | 9:00 | 9:00 | 9:11 | 0 | 0.18333 | 0.18333 | Auto Reset | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-26 | 14855 | 113.4757
48 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 9:40 | 9:40 | 15:12 | 0 | 5.5333 | 5.5333 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.21282 | WTG Scheduled Maintenance | O2-09 | 19159 | 4417.2139
49 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down |  | 13:40 | 13:40 | 14:11 | 0 | 0.51667 | 0.51667 | Check Data log and check hydraulic pressure check by sam and apply Manually oil flushing after Manual Yawing CW Check pressure ok after reset and started WTG. | Close | 0.019872 | WTG Unscheduled Maintenance | O2-07 | 27191 | 585.3618
50 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down |  | 17:41 | 17:41 | 18:16 | 0 | 0.58333 | 0.58333 | Check Data log and check hydraulic pressure check by sam and apply Manually oil flushing after Manual Yawing CW Check pressure ok after reset and started WTG. | Close | 0.022436 | WTG Unscheduled Maintenance | O2-07 | 27191 | 660.8924
51 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 10:21 | 10:21 | 10:27 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 23865 | 99.4375
52 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 10:36 | 10:36 | 11:02 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & started WTG. | Close | 0.016667 | WTG Unscheduled Maintenance | O2-04 | 28588 | 516.1722
53 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset |  | 6:12 | 6:12 | 6:23 | 0 | 0.18333 | 0.18333 | Auto Reset | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-26 | 14855 | 113.4757
54 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 2:28 | 2:28 | 2:32 | 0 | 0.066667 | 0.066667 | Auto Reset | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-15 | 24021 | 66.725
55 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_12 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 2:52 | 2:52 | 2:58 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-14 | 20710 | 86.2917
56 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 10:20 | 10:20 | 11:38 | 0 | 1.3 | 1.3 | Wtg Manual Stop for slip ring inspection work after reset and started wtg | Close | 0.05 | WTG Breakdown Maintenance | O2-11 | 21595 | 1169.7292
57 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_17 | TQGXIIPL | GEDA | 3.846% | 657 | Error pitch converter 2 | Auto reset |  | 11:58 | 11:58 | 12:00 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-22 | 29600 | 41.1111
58 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 19:14 | 19:14 | 19:29 | 0 | 0.25 | 0.25 | Check event log and check converter Data after trail so ok then reset and started wtg | Close | 0.0096154 | WTG Unscheduled Maintenance | O2-06 | 24449 | 254.6771
59 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 19:43 | 19:43 | 20:31 | 0 | 0.8 | 0.8 | Check Event log and Converter Data check after SO FOUND coolant Temp High after Temp Normal and started wtg | Close | 0.030769 | WTG Unscheduled Maintenance | O2-24 | 24582 | 819.4
60 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_21 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down |  | 9:20 | 9:20 | 9:46 | 0 | 0.43333 | 0.43333 | Check Event LOG And Hub Event check after Reboot and trail so ok then reset and started wtg | Close | 0.016667 | WTG Unscheduled Maintenance | O2-06 | 24449 | 441.4403
61 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:38 | 12:38 | 12:44 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 24449 | 101.8708
62 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:33 | 15:33 | 15:44 | 0 | 0.18333 | 0.18333 | Auto Reset | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-06 | 24449 | 186.7632
63 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-06 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset |  | 19:07 | 19:07 | 19:09 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-11 | 21595 | 29.9931
64 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 3:53 | 3:53 | 7:45 | 0 | 3.8667 | 3.8667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.14872 | WTG Unscheduled Maintenance | O2-11 | 28893 | 4654.9833
65 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 4:49 | 4:49 | 6:29 | 0 | 1.6667 | 1.6667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.064103 | WTG Unscheduled Maintenance | O2-12 | 29862 | 2073.75
66 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 7:06 | 7:06 | 7:45 | 0 | 0.65 | 0.65 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.025 | WTG Unscheduled Maintenance | O2-12 | 29862 | 808.7625
67 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:34 | 19:34 | 20:24 | 0 | 0.83333 | 0.83333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.032051 | WTG Unscheduled Maintenance | O2-11 | 28893 | 1003.2292
68 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 20:34 | 20:34 | 21:01 | 0 | 0.45 | 0.45 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.017308 | WTG Breakdown Maintenance | O2-01 | 31048 | 582.15
69 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_03 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Auto reset |  | 5:10 | 5:10 | 5:13 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-09 | 26172 | 54.525
70 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down |  | 13:27 | 13:27 | 13:51 | 0 | 0.4 | 0.4 | Check event log and check hydraulic pressure after flushing mode on after check and trail so ok then reset and start wtg. | Close | 0.015385 | WTG Unscheduled Maintenance | O2-07 | 36306 | 605.1
71 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Auto reset |  | 16:33 | 16:33 | 16:36 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-07 | 36306 | 75.6375
72 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down |  | 18:49 | 18:49 | 19:05 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-07 | 36306 | 403.4
73 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_05 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down |  | 7:48 | 7:48 | 8:08 | 0 | 0.33333 | 0.33333 | After grid resume time error occurred check event log then reset and started wtg. | Close | 0.012821 | WTG Unscheduled Maintenance | O2-02 | 39935 | 554.6528
74 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_05 | TQGXIIPL | GEDA | 3.846% | 2521 | Gen.sp.analog <<>> gearb.sp. | Auto reset |  | 17:44 | 17:44 | 17:46 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-02 | 39935 | 55.4653
75 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 11:12 | 11:12 | 17:18 | 0 | 6.1 | 6.1 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.23462 | WTG Scheduled Maintenance | O2-03 | 29201 | 7421.9208
76 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_11 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down |  | 7:48 | 7:48 | 7:53 | 0 | 0.083333 | 0.083333 | After grid resume time error occurred check event log then reset and started wtg. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-12 | 29862 | 103.6875
77 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset |  | 13:20 | 13:20 | 13:22 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-10 | 29496 | 40.9667
78 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset |  | 14:40 | 14:40 | 14:42 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-10 | 29496 | 40.9667
79 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset |  | 7:25 | 7:25 | 7:30 | 0 | 0.083333 | 0.083333 | Auto Reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-21 | 35533 | 123.3785
80 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 19:16 | 19:16 | 19:26 | 0 | 0.16667 | 0.16667 | Check event log and check converter Data after trail so ok then reset and started wtg | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-06 | 33948 | 235.75
81 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset |  | 3:31 | 3:31 | 3:38 | 0 | 0.11667 | 0.11667 | Auto Reset | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-24 | 35825 | 174.1493
82 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 6:25 | 6:25 | 6:31 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-24 | 35825 | 149.2708
83 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 12:00 | 12:00 | 12:35 | 0 | 0.58333 | 0.58333 | Attend and WTG Check temp sensor , fan conditions and connection Replace Panel filter then started Turbine. | Close | 0.022436 | WTG Breakdown Maintenance | O2-24 | 35825 | 870.7465
84 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:26 | 11:26 | 11:32 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 33948 | 141.45
85 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_25 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down |  | 19:46 | 19:46 | 20:08 | 0 | 0.36667 | 0.36667 | Checked related error data log then reset & started WTG. | Close | 0.014103 | WTG Unscheduled Maintenance | O2-01 | 31048 | 474.3444
86 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-07 | O2_25 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down |  | 20:48 | 20:48 | 21:01 | 0 | 0.21667 | 0.21667 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-01 | 31048 | 280.2944
87 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 9:01 | 9:01 | 9:06 | 0 | 0.083333 | 0.083333 | Check event log and check converter Data after trail so ok then reset and started wtg | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-05 | 29686 | 103.0764
88 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_03 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down |  | 7:05 | 7:05 | 7:20 | 0 | 0.25 | 0.25 | Check event log and check Hub event and check current motor so ok after reset and started wtg | Close | 0.0096154 | WTG Unscheduled Maintenance | O2-09 | 23145 | 241.0938
89 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down |  | 13:10 | 13:10 | 13:20 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & started WTG. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-07 | 31884 | 221.4167
90 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6300 | Yaw error | Auto reset |  | 15:36 | 15:36 | 15:37 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-07 | 31884 | 22.1417
91 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down |  | 17:45 | 17:47 | 18:35 | 0.033333 | 0.8 | 0.83333 | We Have attened turbine and check in hydraulic system oil level system pressure 9.1 valv conditions found all normal after we check 9.8 valve pressure with gauge found deviation. So correct its and taken trail then started turbine. | Close | 0.032051 | WTG Unscheduled Maintenance | O2-07 | 31884 | 1107.0833
92 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset |  | 3:16 | 3:16 | 3:19 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-02 | 38913 | 81.0688
93 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 4:15 | 4:15 | 5:45 | 0 | 1.5 | 1.5 | Attend and wtg check filter and clean after check converter fan condition check so ok after temp sensor connection check and tight then reset and start wtg | Close | 0.057692 | WTG Unscheduled Maintenance | O2-02 | 38913 | 2432.0625
94 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 11:30 | 11:30 | 13:20 | 0 | 1.8333 | 1.8333 | we have attend turbine and check in converter temp sensor value , sensor connection and conditions after taken trail of turbine found temp in noirmal range so started turbine. | Close | 0.070513 | WTG Unscheduled Maintenance | O2-02 | 38913 | 2972.5208
95 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset |  | 6:43 | 6:43 | 6:54 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-26 | 23956 | 182.9972
96 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 20:53 | 20:53 | 20:56 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-26 | 23956 | 49.9083
97 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 21:50 | 22:35 | 23:50 | 0.75 | 1.25 | 2 | Attend wtg check related circuit than check overvoltage protaction circuit than check surge arrestor and connection than found 24V feedback connection was loose so retight properly than reset and start wtg | Close | 0.076923 | WTG Unscheduled Maintenance | O2-12 | 32730 | 2727.5
98 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 20:11 | 20:11 | 20:17 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 32199 | 134.1625
99 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_18 | TQGXIIPL | GEDA | 3.846% | 2521 | Gen.sp.analog <<>> gearb.sp. | Break down |  | 19:36 | 19:36 | 19:48 | 0 | 0.2 | 0.2 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-06 | 31629 | 263.575
100 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 14:30 | 14:30 | 14:44 | 0 | 0.23333 | 0.23333 | Check event log and check converter Data after trail so ok then reset and started wtg | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-24 | 34444 | 334.8722
101 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset |  | 9:01 | 9:01 | 9:04 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-11 | 27130 | 56.5208
102 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 2:35 | 2:35 | 2:48 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & started WTG. | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-01 | 32931 | 297.2937
103 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_26 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset |  | 2:28 | 2:28 | 2:39 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-01 | 32931 | 251.5563
104 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset |  | 9:01 | 9:01 | 9:04 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-01 | 32931 | 68.6062
105 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 2:54 | 2:54 | 3:23 | 0 | 0.48333 | 0.48333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.01859 | WTG Breakdown Maintenance | O2-11 | 27130 | 546.3681
106 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 2:55 | 2:55 | 3:13 | 0 | 0.3 | 0.3 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.011538 | WTG Breakdown Maintenance | O2-01 | 32931 | 411.6375
107 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 7:00 | 7:00 | 13:00 | 0 | 6 | 6 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.23077 | WTG Scheduled Maintenance | O2-03 | 30523 | 7630.75
108 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:09 | 19:09 | 21:00 | 0 | 1.85 | 1.85 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.071154 | WTG Breakdown Maintenance | O2-11 | 27130 | 2091.2708
109 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-08 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:44 | 19:44 | 20:30 | 0 | 0.76667 | 0.76667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.029487 | WTG Breakdown Maintenance | O2-26 | 23956 | 765.2611
110 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-09 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset |  | 1:42 | 1:42 | 1:53 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-26 | 23560 | 179.9722
111 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-09 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset |  | 14:34 | 14:34 | 14:37 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-07 | 28440 | 59.25
112 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-09 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 7:30 | 8:50 | 9:38 | 1.3333 | 0.8 | 2.1333 | Attend wtg check inductor cell temp increase so cannibalize temp sensor connection wid another temp sensor ( Now turbine running under observation ) | Close | 0.082051 | WTG Unscheduled Maintenance | O2-02 | 35985 | 3198.6667
113 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-09 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:25 | 16:25 | 16:31 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 28985 | 120.7708
114 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-09 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3065 | Conv. emerg.off type F | Break down |  | 14:30 | 14:30 | 14:49 | 0 | 0.31667 | 0.31667 | Check event log and check converter Data after trail so ok then reset and started wtg | Close | 0.012179 | WTG Unscheduled Maintenance | O2-21 | 28985 | 382.441
115 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-09 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset |  | 15:34 | 15:34 | 15:37 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-06 | 28574 | 59.5292
116 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-09 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset |  | 15:36 | 15:36 | 15:38 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-24 | 32143 | 44.6431
117 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-09 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:19 | 15:19 | 15:25 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 28574 | 119.0583
118 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-09 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down |  | 19:30 | 20:00 | 24:00 | 0.5 | 4 | 4.5 | Attend And check related circuit found MPCB Trip so we check motor winding connection and found Motor Bearing jam after arrange motor for Mahuva site WIP | open | 0.17308 | WTG Unscheduled Maintenance | O2-11 | 27370 | 5131.875
119 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-09 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 3:40 | 3:40 | 3:47 | 0 | 0.11667 | 0.11667 | Check event log and check converter Data after trail so ok then reset and started wtg | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-01 | 28683 | 139.4312
120 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 15:13 | 15:13 | 15:17 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-05 | 41567 | 115.4639
121 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_04 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 18:19 | 18:19 | 18:27 | 0 | 0.13333 | 0.13333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-05 | 41567 | 230.9278
122 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 12:48 | 12:48 | 12:50 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-02 | 45183 | 62.7542
123 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 13:43 | 13:43 | 13:52 | 0 | 0.15 | 0.15 | Checked related error data log then reset & started WTG. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-18 | 33218 | 207.6125
124 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_06 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 19:05 | 19:05 | 19:34 | 0 | 0.48333 | 0.48333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.01859 | WTG Unscheduled Maintenance | O2-18 | 33218 | 668.9736
125 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_07 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 3:26 | 3:26 | 3:32 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-19 | 46375 | 193.2292
126 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down |  | 3:27 | 3:27 | 3:38 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & started WTG. | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-01 | 37826 | 288.9486
127 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down |  | 9:34 | 9:34 | 9:45 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & started WTG. | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-01 | 37826 | 288.9486
128 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 17:23 | 17:23 | 19:30 | 0 | 2.1167 | 2.1167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.08141 | WTG Breakdown Maintenance | O2-01 | 37826 | 3336.0431
129 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 13:51 | 13:51 | 13:57 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-12 | 38699 | 161.2458
130 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 19:07 | 19:07 | 19:24 | 0 | 0.28333 | 0.28333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-11 | 35407 | 417.9993
131 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:02 | 14:02 | 14:08 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-14 | 36725 | 153.0208
132 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 15:50 | 15:50 | 16:12 | 0 | 0.36667 | 0.36667 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.014103 | WTG Unscheduled Maintenance | O2-14 | 36725 | 561.0764
133 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 17:04 | 17:04 | 17:16 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-10 | 35686 | 297.3833
134 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 17:36 | 17:36 | 18:56 | 0 | 1.3333 | 1.3333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.051282 | WTG Breakdown Maintenance | O2-10 | 35686 | 1982.5556
135 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 16:05 | 16:05 | 16:14 | 0 | 0.15 | 0.15 | Checked related error data log then reset & started WTG. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-20 | 40773 | 254.8313
136 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 16:42 | 16:42 | 17:01 | 0 | 0.31667 | 0.31667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.012179 | WTG Unscheduled Maintenance | O2-20 | 40773 | 537.9771
137 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 17:37 | 17:37 | 17:46 | 0 | 0.15 | 0.15 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-20 | 40773 | 254.8313
138 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 18:14 | 18:14 | 18:35 | 0 | 0.35 | 0.35 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.013462 | WTG Unscheduled Maintenance | O2-20 | 40773 | 594.6063
139 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 9:04 | 9:04 | 9:09 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-06 | 37890 | 131.5625
140 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 18:14 | 18:14 | 18:34 | 0 | 0.33333 | 0.33333 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.012821 | WTG Unscheduled Maintenance | O2-06 | 37890 | 526.25
141 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 18:43 | 18:43 | 19:39 | 0 | 0.93333 | 0.93333 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.035897 | WTG Unscheduled Maintenance | O2-06 | 37890 | 1473.5
142 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 16:06 | 16:06 | 16:15 | 0 | 0.15 | 0.15 | Checked related error data log then reset & started WTG. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-07 | 42698 | 266.8625
143 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 18:12 | 18:12 | 18:25 | 0 | 0.21667 | 0.21667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-07 | 42698 | 385.4681
144 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:21 | 19:21 | 19:28 | 0 | 0.11667 | 0.11667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-07 | 42698 | 207.5597
145 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:35 | 14:35 | 14:41 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-18 | 33218 | 138.4083
146 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down |  | 0:00 | 0:00 | 4:19 | 0 | 4.3167 | 4.3167 | Attend And check related circuit found MPCB Trip so we check motor winding connection and found Motor Bearing jam after arrange motor and replace Motor than started WTG. | Close | 0.16603 | WTG Breakdown Maintenance | O2-08 | 28587 | 5141.6896
147 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-10 | O2_26 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down |  | 4:01 | 4:01 | 4:13 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-08 | 28587 | 238.225
148 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:55 | 12:55 | 13:01 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 41874 | 174.475
149 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:16 | 14:16 | 14:30 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & started WTG. | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-26 | 41874 | 407.1083
150 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:00 | 15:00 | 15:06 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-02 | 49347 | 205.6125
151 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 21:45 | 21:45 | 21:53 | 0 | 0.13333 | 0.13333 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-02 | 49347 | 274.15
152 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 10:12 | 10:12 | 10:39 | 0 | 0.45 | 0.45 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.017308 | WTG Unscheduled Maintenance | O2-26 | 41874 | 785.1375
153 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 17:19 | 17:19 | 17:25 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 41874 | 174.475
154 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:26 | 13:26 | 13:32 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-15 | 40666 | 169.4417
155 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset |  | 13:42 | 13:42 | 13:45 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-11 | 37304 | 77.7167
156 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:40 | 14:40 | 14:46 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 37304 | 155.4333
157 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Major BD |  | 1:05 | 2:30 | 7:47 | 1.4167 | 5.2833 | 6.7 | Attend and check error related ckt than found Slipring cable short with the Ground than we use temparory Earthing cable for restore the Turbine and plan for the further rectification work in day Shift. | Close | 0.25769 | WTG Unscheduled Maintenance | O2-12 | 42973 | 11996.6292
158 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR |  | 10:42 | 10:42 | 24:00 | 0 | 13.3 | 13.3 | Turbine stop for Slipring 646 WTR Work WIP, | Close | 0.51154 | WTG Scheduled Maintenance | O2-12 | 42973 | 23814.2042
159 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 16:44 | 16:44 | 16:50 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 40132 | 167.2167
160 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 18:48 | 18:48 | 19:06 | 0 | 0.3 | 0.3 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.011538 | WTG Unscheduled Maintenance | O2-21 | 40132 | 501.65
161 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 13:17 | 13:17 | 13:20 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-22 | 39622 | 82.5458
162 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 1:25 | 1:25 | 1:37 | 0 | 0.2 | 0.2 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-06 | 39764 | 331.3667
163 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 15:07 | 15:07 | 15:10 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-06 | 39764 | 82.8417
164 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_18 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:33 | 15:33 | 15:39 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 39764 | 165.6833
165 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:38 | 13:38 | 13:44 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 37304 | 155.4333
166 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_23 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down |  | 15:21 | 15:21 | 15:28 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-11 | 37304 | 181.3389
167 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:50 | 13:50 | 13:56 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-20 | 40190 | 167.4583
168 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-11 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:35 | 11:35 | 11:41 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-01 | 41447 | 172.6958
169 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-12 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 10:38 | 10:38 | 11:30 | 0 | 0.86667 | 0.86667 | Turbine stop for Software Update Work. | Close | 0.033333 | WTG Unscheduled Maintenance | O2-08 | 7028 | 253.7889
170 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-12 | O2_03 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Break down |  | 7:32 | 7:32 | 8:24 | 0 | 0.86667 | 0.86667 | check event log and check all data after reboot and check so ok then reset and started wtg | Close | 0.033333 | WTG Unscheduled Maintenance | O2-09 | 7345 | 265.2361
171 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-12 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 11:35 | 11:35 | 11:47 | 0 | 0.2 | 0.2 | Turbine stop for Software Update Work. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-02 | 8948 | 74.5667
172 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-12 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR |  | 0:00 | 0:00 | 4:50 | 0 | 4.8333 | 4.8333 | After done Slipring WTR 646 than reset and started WTG. | Close | 0.1859 | WTG Scheduled Maintenance | O2-12 | 7785 | 1567.8125
173 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 21:51 | 21:51 | 22:00 | 0 | 0.15 | 0.15 | Checked related error data log then reset & started WTG. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-02 | 28616 | 178.85
174 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 22:49 | 22:49 | 22:53 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-02 | 28616 | 79.4889
175 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_06 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down |  | 7:32 | 7:32 | 7:43 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-21 | 23356 | 178.4139
176 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down |  | 15:13 | 15:13 | 15:16 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-21 | 23356 | 48.6583
177 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset |  | 8:12 | 8:12 | 8:23 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-26 | 25025 | 191.1632
178 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:35 | 18:35 | 21:24 | 0 | 2.8167 | 2.8167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.10833 | WTG Breakdown Maintenance | O2-26 | 25025 | 2936.9618
179 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 21:23 | 21:23 | 24:00 | 0 | 2.6167 | 2.6167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.10064 | WTG Breakdown Maintenance | O2-26 | 25025 | 2728.4201
180 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:40 | 15:40 | 15:52 | 0 | 0.2 | 0.2 | WTG Manual stop for Software Updated Work. | Close | 0.0076923 | WTG Breakdown Maintenance | O2-03 | 25705 | 214.2083
181 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_10 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Auto reset |  | 7:48 | 7:48 | 7:59 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-15 | 20653 | 157.766
182 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 7:28 | 7:28 | 7:31 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-12 | 25190 | 52.4792
183 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 7:36 | 7:36 | 7:41 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-12 | 25190 | 87.4653
184 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 7:50 | 7:50 | 7:58 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-12 | 25190 | 139.9444
185 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:08 | 16:08 | 16:39 | 0 | 0.51667 | 0.51667 | WTG Manual stop for Software Updated Work. | Close | 0.019872 | WTG Breakdown Maintenance | O2-12 | 25190 | 542.2847
186 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 7:31 | 7:31 | 7:35 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-11 | 23698 | 65.8278
187 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_13 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 7:41 | 7:41 | 7:45 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-11 | 23698 | 65.8278
188 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 16:44 | 16:44 | 16:50 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 23698 | 98.7417
189 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:27 | 18:27 | 19:21 | 0 | 0.9 | 0.9 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.034615 | WTG Breakdown Maintenance | O2-11 | 23698 | 888.675
190 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 20:13 | 20:13 | 24:00 | 0 | 3.7833 | 3.7833 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.14551 | WTG Breakdown Maintenance | O2-11 | 23698 | 3735.7264
191 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 7:31 | 7:31 | 7:36 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-12 | 25190 | 87.4653
192 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_14 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 7:40 | 7:40 | 7:49 | 0 | 0.15 | 0.15 | Checked related error data log then reset & started WTG. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-12 | 25190 | 157.4375
193 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:19 | 15:19 | 15:46 | 0 | 0.45 | 0.45 | WTG Manual stop for Software Updated Work. | Close | 0.017308 | WTG Breakdown Maintenance | O2-12 | 25190 | 472.3125
194 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 8:01 | 8:01 | 15:07 | 0 | 7.1 | 7.1 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.27308 | WTG Scheduled Maintenance | O2-10 | 25909 | 7664.7458
195 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 21:55 | 21:55 | 22:04 | 0 | 0.15 | 0.15 | Checked related error data log then reset & started WTG. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-22 | 23878 | 149.2375
196 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_18 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down |  | 7:19 | 7:19 | 7:23 | 0 | 0.066667 | 0.066667 | after grid resume error is occurs so Checked related error data log then reset & started WTG. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-06 | 23521 | 65.3361
197 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 20:33 | 20:33 | 20:41 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-06 | 23521 | 130.6722
198 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 21:09 | 21:09 | 21:36 | 0 | 0.45 | 0.45 | Checked related error data log then reset & started WTG. | Close | 0.017308 | WTG Unscheduled Maintenance | O2-06 | 23521 | 441.0188
199 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_18 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 23:21 | 23:21 | 23:27 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 23521 | 98.0042
200 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 7:27 | 7:27 | 7:51 | 0 | 0.4 | 0.4 | after grid resume error is occurs so Checked related error data log then reset & started WTG. | Close | 0.015385 | WTG Unscheduled Maintenance | O2-07 | 22036 | 367.2667
201 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 7:51 | 9:15 | 10:43 | 1.4 | 1.4667 | 2.8667 | WTG Manual stop for Software Updated Work. | Close | 0.11026 | WTG Breakdown Maintenance | O2-07 | 22036 | 2632.0778
202 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_19 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Break down |  | 15:51 | 15:51 | 15:54 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-07 | 22036 | 45.9083
203 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 7:04 | 7:04 | 8:42 | 0 | 1.6333 | 1.6333 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.062821 | WTG Unscheduled Maintenance | O2-06 | 23521 | 1600.7347
204 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_24 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 7:24 | 7:58 | 9:15 | 0.56667 | 1.2833 | 1.85 | Attend and check ckt than found FA01 Surge arrestor feedback connection loose so tight it than started Turbine. | Close | 0.071154 | WTG Unscheduled Maintenance | O2-20 | 24441 | 1883.9938
205 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 22:00 | 22:00 | 22:06 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-01 | 26489 | 110.3708
206 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-13 | O2_25 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down |  | 23:35 | 23:35 | 23:37 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-01 | 26489 | 36.7903
207 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 8:12 | 8:12 | 8:18 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-05 | 54526 | 227.1917
208 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 12:06 | 12:06 | 12:14 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-05 | 54526 | 302.9222
209 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Connectivity issue |  | 3:59 | 3:59 | 4:55 | 0 | 0.93333 | 0.93333 | Checked related error data log then reset & started WTG.lat reset due to all WTGs is not cannected in feetpro because internet connectivity breakdown. | Close | 0.035897 | WTG Unscheduled Maintenance | O2-09 | 45058 | 1752.2556
210 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 16:42 | 16:42 | 18:59 | 0 | 2.2833 | 2.2833 | attend and check all releted circuit. Check sensor cable laying is ok. check break pad 2 temp sensor found loose cannections so tight it then start WTG. | Close | 0.087821 | WTG Unscheduled Maintenance | O2-09 | 45058 | 4286.7681
211 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_04 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 18:48 | 18:48 | 18:58 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & started WTG. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-07 | 52855 | 367.0486
212 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 11:59 | 11:59 | 12:05 | 0 | 0.1 | 0.1 | Checked related error data log then apply manual DO found all condition is ok then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-02 | 54587 | 227.4458
213 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_07 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 8:06 | 8:06 | 8:09 | 0 | 0.05 | 0.05 | Checked related error data log then apply manual DO found all condition is ok then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-04 | 55152 | 114.9
214 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 0:00 | 0:00 | 1:07 | 0 | 1.1167 | 1.1167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.042949 | WTG Breakdown Maintenance | O2-26 | 46555 | 2166.1007
215 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 11:43 | 11:43 | 11:59 | 0 | 0.26667 | 0.26667 | Checked related error data log then apply manual DO found all condition is ok then reset & started WTG. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-26 | 46555 | 517.2778
216 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 17:52 | 17:52 | 18:08 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-14 | 41611 | 462.3444
217 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 0:00 | 0:00 | 0:38 | 0 | 0.63333 | 0.63333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.024359 | WTG Breakdown Maintenance | O2-11 | 46926 | 1238.325
218 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:06 | 19:06 | 22:54 | 0 | 3.8 | 3.8 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.14615 | WTG Breakdown Maintenance | O2-11 | 46926 | 7429.95
219 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_14 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down |  | 13:29 | 13:29 | 13:45 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-12 | 44309 | 492.3222
220 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 6:56 | 7:06 | 12:03 | 0.16667 | 4.95 | 5.1167 | WTG stop for YPM day-2 activity and software updated than started WTG. | Close | 0.19679 | WTG Scheduled Maintenance | O2-10 | 42261 | 9009.8104
221 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 12:29 | 12:29 | 12:35 | 0 | 0.1 | 0.1 | Checked related error data log then apply manual DO found all condition is ok then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 43699 | 182.0792
222 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_17 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down |  | 3:24 | 3:24 | 3:44 | 0 | 0.33333 | 0.33333 | Checked related error data log then reset & started WTG. | Close | 0.012821 | WTG Unscheduled Maintenance | O2-22 | 49144 | 682.5556
223 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 4:11 | 4:11 | 4:17 | 0 | 0.1 | 0.1 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0038462 | WTG Breakdown Maintenance | O2-22 | 49144 | 204.7667
224 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 17:01 | 17:01 | 18:10 | 0 | 1.15 | 1.15 | Checked related error data log then check wind direction and wind difference data apply DO yawing and check difference is ok so reset & started WTG.now wtg under observation | Close | 0.044231 | WTG Unscheduled Maintenance | O2-22 | 49144 | 2354.8167
225 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_18 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 15:03 | 15:03 | 15:09 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 43979 | 183.2458
226 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 17:32 | 17:32 | 18:13 | 0 | 0.68333 | 0.68333 | Checked related error data log then apply manual DO cooling pump then reset & started WTG. | Close | 0.026282 | WTG Unscheduled Maintenance | O2-07 | 52855 | 1504.8993
227 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 12:48 | 12:48 | 12:54 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 43979 | 183.2458
228 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 15:46 | 15:46 | 15:50 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-20 | 47867 | 132.9639
229 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_25 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down |  | 0:14 | 0:14 | 0:26 | 0 | 0.2 | 0.2 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-01 | 49494 | 412.45
230 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 10:00 | 10:00 | 10:26 | 0 | 0.43333 | 0.43333 | WTG Manual stop for Software Updated Work. | Close | 0.016667 | WTG Breakdown Maintenance | O2-01 | 49494 | 893.6417
231 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_25 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 16:57 | 16:57 | 18:03 | 0 | 1.1 | 1.1 | Checked related error data log then apply manual DO cooling pump then reset & started WTG. | Close | 0.042308 | WTG Unscheduled Maintenance | O2-01 | 49494 | 2268.475
232 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-14 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:25 | 18:25 | 23:07 | 0 | 4.7 | 4.7 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.18077 | WTG Breakdown Maintenance | O2-01 | 49494 | 9692.575
233 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 2:41 | 2:41 | 2:49 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-02 | 48545 | 269.6944
234 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down |  | 2:55 | 2:55 | 3:07 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-02 | 48545 | 404.5417
235 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 3:30 | 3:30 | 8:23 | 0 | 4.8833 | 4.8833 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.18782 | WTG Breakdown Maintenance | O2-02 | 48545 | 9877.559
236 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 8:47 | 8:47 | 8:53 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 46010 | 191.7083
237 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 3:08 | 3:08 | 8:18 | 0 | 5.1667 | 5.1667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.19872 | WTG Breakdown Maintenance | O2-03 | 39223 | 8443.8403
238 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 12:56 | 12:56 | 13:28 | 0 | 0.53333 | 0.53333 | attend and Check rotor brake pads temp sensor condition,cable layout, measure temp value and found loose connection in TB.So re tight and started turbine. | Close | 0.020513 | WTG Breakdown Maintenance | O2-15 | 44736 | 994.1333
239 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 16:04 | 16:04 | 16:09 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-15 | 44736 | 155.3333
240 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:04 | 14:04 | 14:10 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-12 | 40662 | 169.425
241 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 7:02 | 7:13 | 12:48 | 0.18333 | 5.5833 | 5.7667 | WTG stop for YPM day-1 activity and software updated than started WTG. | Close | 0.22179 | WTG Scheduled Maintenance | O2-21 | 46010 | 11055.1806
242 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_16 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 15:07 | 15:07 | 15:13 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 46010 | 191.7083
243 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 4:24 | 4:24 | 4:41 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & started WTG. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-22 | 50084 | 591.2694
244 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 8:32 | 8:56 | 24:00 | 0.4 | 15.0667 | 15.4667 | WTG manual stop for Blade repairing work.today skylift installing work and damage area surface Measuring and grinding work done and first layer removing work complated and new paste apply & cuting. | open | 0.59487 | WTG Breakdown Maintenance | O2-22 | 50084 | 32276.3556
245 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 19:10 | 19:10 | 19:23 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & started WTG. | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-07 | 44148 | 398.5583
246 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_24 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Break down |  | 14:58 | 14:58 | 15:01 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-20 | 47068 | 98.0583
247 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 23:44 | 23:44 | 24:00 | 0 | 0.26667 | 0.26667 | attend for generator slipring earthing brush replacement work wip. | open | 0.010256 | WTG Breakdown Maintenance | O2-20 | 47068 | 522.9778
248 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-15 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6012 | Overload yaw motors group 2 | Break down |  | 14:19 | 15:15 | 17:45 | 0.93333 | 2.5 | 3.4333 | attend and check all releted circuit check all yaw motor winding is ok check all yaw motor break is ok so check and found yaw motor contactor on loose cannection so tight it and started wtg. Now wtg under observations. | Close | 0.13205 | WTG Unscheduled Maintenance | O2-01 | 46514 | 6654.0861
249 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:45 | 18:45 | 19:29 | 0 | 0.73333 | 0.73333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.028205 | WTG Breakdown Maintenance | O2-02 | 43551 | 1330.725
250 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 20:34 | 20:34 | 20:46 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-02 | 43551 | 362.925
251 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 23:41 | 23:41 | 23:49 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-02 | 43551 | 241.95
252 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_06 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Auto reset |  | 18:10 | 18:10 | 18:14 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-21 | 41205 | 114.4583
253 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 11:31 | 11:31 | 16:12 | 0 | 4.6833 | 4.6833 | We have attended turbine for Rep converter temp and Nacelle coolant pressure low check and fill up coolant, Nacelle radiator cleaning with water and Converter in top up coolant,Fan filter replaced, check fan working condition, it's temp sensor circuit then start wtg under observation. | Close | 0.18013 | WTG Breakdown Maintenance | O2-26 | 37850 | 7386.0069
254 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:56 | 16:56 | 18:03 | 0 | 1.1167 | 1.1167 | then bottom radiator clean with water, check it's working condition.Then reset and started turbine. | Close | 0.042949 | WTG Breakdown Maintenance | O2-26 | 37850 | 1761.0764
255 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Auto reset |  | 19:07 | 19:07 | 19:18 | 0 | 0.18333 | 0.18333 | Auto reset | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-14 | 30710 | 234.5903
256 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:51 | 15:51 | 16:52 | 0 | 1.0167 | 1.0167 | WTG Manual stop for blade inspection work. | Close | 0.039103 | WTG Breakdown Maintenance | O2-11 | 37090 | 1571.1736
257 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 17:45 | 17:45 | 18:23 | 0 | 0.63333 | 0.63333 | WTG Manual stop for blade inspection work. | Close | 0.024359 | WTG Breakdown Maintenance | O2-12 | 34156 | 901.3389
258 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:23 | 18:23 | 19:09 | 0 | 0.76667 | 0.76667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.029487 | WTG Breakdown Maintenance | O2-12 | 34156 | 1091.0944
259 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 0:00 | 0:00 | 21:40 | 0 | 21.6667 | 21.6667 | WTG manual stop for Blade repairing work.today we work in blade on Pest leaving and grinding champaring and lamination and curing and heating then putty apply and putty sending work completed then last paint apply then start wtg. | Close | 0.83333 | WTG Breakdown Maintenance | O2-22 | 46060 | 41581.9444
260 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 11:24 | 11:24 | 17:20 | 0 | 5.9333 | 5.9333 | Repeated Conv error (rotor leckage current and encoder error) ocuured so plan to inspection Turbine , Check and visual inspection of Hopewind converter panel components and connection but nothing found abnormal so check Generator slip ring at that time found earthing carbon brush fully wear out and some hot spot mark on Power brush track so clean Power and earthing brush track and do smooth it as well as replace earthing brush and Generator RPM encoder connector loose at yaw platform so correct it the reset and start turbine. | Close | 0.22821 | WTG Breakdown Maintenance | O2-06 | 41952 | 10371.4667
261 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 0:00 | 0:00 | 1:02 | 0 | 1.0333 | 1.0333 | attend for generator slipring earthing brush replacement work done then started wtg. | Close | 0.039744 | WTG Breakdown Maintenance | O2-20 | 39760 | 1711.8889
262 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_25 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 19:03 | 19:03 | 19:20 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & started WTG. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-01 | 39687 | 468.5271
263 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 19:50 | 19:50 | 20:07 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & started WTG. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-01 | 39687 | 468.5271
264 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 20:55 | 20:55 | 21:07 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-01 | 39687 | 330.725
265 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-16 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 21:16 | 21:16 | 23:14 | 0 | 1.9667 | 1.9667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.075641 | WTG Breakdown Maintenance | O2-01 | 39687 | 3252.1292
266 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 14:50 | 14:50 | 14:59 | 0 | 0.15 | 0.15 | WTG Manual stop for Software Updated Work. | Close | 0.0057692 | WTG Breakdown Maintenance | O2-26 | 36110 | 225.6875
267 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_02 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down |  | 4:34 | 4:34 | 4:36 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-05 | 38564 | 53.5611
268 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 6:54 | 6:58 | 13:54 | 0.066667 | 6.9333 | 7 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.26923 | WTG Scheduled Maintenance | O2-05 | 38564 | 11247.8333
269 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 19:35 | 19:35 | 19:44 | 0 | 0.15 | 0.15 | WTG Manual stop for Software Updated Work. | Close | 0.0057692 | WTG Breakdown Maintenance | O2-05 | 38564 | 241.025
270 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 18:41 | 18:41 | 18:53 | 0 | 0.2 | 0.2 | WTG Manual stop for Software Updated Work. | Close | 0.0076923 | WTG Breakdown Maintenance | O2-07 | 36587 | 304.8917
271 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 3:38 | 3:38 | 3:48 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & started WTG. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-02 | 37275 | 258.8542
272 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 4:24 | 4:24 | 4:43 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & started WTG. | Close | 0.012179 | WTG Unscheduled Maintenance | O2-02 | 37275 | 491.8229
273 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 11:03 | 11:03 | 12:14 | 0 | 1.1833 | 1.1833 | Checked related error data log then found temp sensor malfunctioning so reboot PLC then reset & started WTG. | Close | 0.045513 | WTG Unscheduled Maintenance | O2-02 | 37275 | 1837.8646
274 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 18:51 | 18:51 | 19:02 | 0 | 0.18333 | 0.18333 | WTG Manual stop for Software Updated Work. | Close | 0.0070513 | WTG Breakdown Maintenance | O2-04 | 40506 | 309.4208
275 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset |  | 15:03 | 15:03 | 15:06 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-26 | 36110 | 75.2292
276 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 18:00 | 18:00 | 18:10 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Software Updated Work. | Close | 0.0064103 | WTG Breakdown Maintenance | O2-26 | 36110 | 250.7639
277 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset |  | 13:51 | 13:51 | 13:53 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-15 | 32423 | 45.0319
278 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 17:22 | 17:22 | 17:30 | 0 | 0.13333 | 0.13333 | WTG Manual stop for Software Updated Work. | Close | 0.0051282 | WTG Breakdown Maintenance | O2-15 | 32423 | 180.1278
279 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 7:22 | 7:22 | 7:34 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-12 | 27764 | 231.3667
280 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 14:22 | 14:22 | 14:40 | 0 | 0.3 | 0.3 | Checked related error data log then reset & started WTG. | Close | 0.011538 | WTG Unscheduled Maintenance | O2-12 | 27764 | 347.05
281 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:47 | 19:47 | 21:23 | 0 | 1.6 | 1.6 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.061538 | WTG Breakdown Maintenance | O2-14 | 29808 | 1987.2
282 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:01 | 14:01 | 14:07 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 32786 | 136.6083
283 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 19:01 | 19:01 | 19:13 | 0 | 0.2 | 0.2 | WTG Manual stop for Software Updated Work. | Close | 0.0076923 | WTG Breakdown Maintenance | O2-11 | 32786 | 273.2167
284 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_14 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 15:33 | 15:33 | 15:59 | 0 | 0.43333 | 0.43333 | Checked related error data log then reset & started WTG. | Close | 0.016667 | WTG Unscheduled Maintenance | O2-12 | 27764 | 501.2944
285 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 19:14 | 19:14 | 19:22 | 0 | 0.13333 | 0.13333 | WTG Manual stop for Software Updated Work. | Close | 0.0051282 | WTG Breakdown Maintenance | O2-10 | 25644 | 142.4667
286 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 14:51 | 14:51 | 14:53 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-22 | 37507 | 52.0931
287 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 19:11 | 19:11 | 19:21 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Software Updated Work. | Close | 0.0064103 | WTG Breakdown Maintenance | O2-22 | 37507 | 260.4653
288 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:30 | 16:30 | 16:37 | 0 | 0.11667 | 0.11667 | WTG Manual stop for Software Updated Work. | Close | 0.0044872 | WTG Breakdown Maintenance | O2-07 | 36587 | 177.8535
289 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 19:20 | 19:20 | 19:29 | 0 | 0.15 | 0.15 | WTG Manual stop for Software Updated Work. | Close | 0.0057692 | WTG Breakdown Maintenance | O2-24 | 32115 | 200.7187
290 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_21 | TQGXIIPL | GEDA | 3.846% | 4520 | Tower oscillation X level 1 | Break down |  | 4:48 | 4:48 | 4:59 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & started WTG. | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-06 | 34183 | 261.1201
291 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 19:46 | 19:46 | 19:55 | 0 | 0.15 | 0.15 | WTG Manual stop for Software Updated Work. | Close | 0.0057692 | WTG Breakdown Maintenance | O2-06 | 34183 | 213.6438
292 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 18:46 | 18:46 | 18:55 | 0 | 0.15 | 0.15 | WTG Manual stop for Software Updated Work. | Close | 0.0057692 | WTG Breakdown Maintenance | O2-06 | 34183 | 213.6437
293 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 18:23 | 18:23 | 18:46 | 0 | 0.38333 | 0.38333 | WTG Manual stop for Software Updated Work. | Close | 0.014744 | WTG Breakdown Maintenance | O2-20 | 33211 | 530.4535
294 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 23:13 | 23:13 | 24:00 | 0 | 0.78333 | 0.78333 | attend for generator slipring earthing brush replacement work wip. | open | 0.030128 | WTG Breakdown Maintenance | O2-20 | 33211 | 1083.9701
295 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 3:59 | 3:59 | 4:27 | 0 | 0.46667 | 0.46667 | Checked related error data log then reset & started WTG. | Close | 0.017949 | WTG Unscheduled Maintenance | O2-01 | 36843 | 716.3917
296 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 18:29 | 18:29 | 18:36 | 0 | 0.11667 | 0.11667 | WTG Manual stop for Software Updated Work. | Close | 0.0044872 | WTG Breakdown Maintenance | O2-01 | 36843 | 179.0979
297 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-17 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 20:49 | 20:49 | 21:50 | 0 | 1.0167 | 1.0167 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.039103 | WTG Breakdown Maintenance | O2-01 | 36843 | 1560.7104
298 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 6:31 | 6:38 | 12:21 | 0.11667 | 5.7167 | 5.8333 | WTG stop for YPM day-2 activity and software updated than started WTG. | Close | 0.22436 | WTG Scheduled Maintenance | O2-05 | 34316 | 8340.6944
299 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_03 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 13:15 | 13:15 | 13:31 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-09 | 31138 | 345.9778
300 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_04 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 16:32 | 16:32 | 16:48 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-07 | 45438 | 504.8667
301 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 3:41 | 3:41 | 3:47 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-02 | 34912 | 145.4667
302 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 4:00 | 4:00 | 4:48 | 0 | 0.8 | 0.8 | Checked related error data log then found high temp ambient upper converter error the temp sensor malfunction so then reset & started WTG. | Close | 0.030769 | WTG Unscheduled Maintenance | O2-02 | 34912 | 1163.7333
303 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 9:54 | 10:03 | 11:09 | 0.15 | 1.1 | 1.25 | attend and check all related circuit and found temp ambient upper converter sensor on loose cannectinon so tight it then software updated started WTG. | Close | 0.048077 | WTG Unscheduled Maintenance | O2-02 | 34912 | 1818.3333
304 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:26 | 18:26 | 20:02 | 0 | 1.6 | 1.6 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.061538 | WTG Breakdown Maintenance | O2-02 | 34912 | 2327.4667
305 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:58 | 16:58 | 17:28 | 0 | 0.5 | 0.5 | WTG Manual stop for Software Updated Work. | Close | 0.019231 | WTG Breakdown Maintenance | O2-21 | 31662 | 659.625
306 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 0:02 | 0:02 | 0:38 | 0 | 0.6 | 0.6 | Checked related error data log then reset & started WTG. | Close | 0.023077 | WTG Unscheduled Maintenance | O2-12 | 30866 | 771.65
307 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 14:03 | 14:03 | 15:04 | 0 | 1.0167 | 1.0167 | Checked related error data log then found PPD pitch angle is diff so apply reboot then reset & started WTG. | Close | 0.039103 | WTG Unscheduled Maintenance | O2-12 | 30866 | 1307.5181
308 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 11:10 | 11:10 | 12:01 | 0 | 0.85 | 0.85 | Checked related error data log then reset & started WTG. | Close | 0.032692 | WTG Unscheduled Maintenance | O2-22 | 36369 | 1288.0687
309 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_18 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:36 | 14:36 | 14:42 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 28245 | 117.6875
310 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_19 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 7:58 | 7:58 | 8:14 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-07 | 45438 | 504.8667
311 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_19 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 8:43 | 8:43 | 8:49 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 45438 | 189.325
312 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:35 | 14:35 | 14:41 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 28245 | 117.6875
313 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 15:17 | 15:17 | 15:35 | 0 | 0.3 | 0.3 | Checked related error data log then reset & started WTG. | Close | 0.011538 | WTG Unscheduled Maintenance | O2-06 | 28245 | 353.0625
314 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 0:00 | 0:00 | 3:45 | 0 | 3.75 | 3.75 | attend and check generator slipring and found earthing brush are wear out so clean earthing track and measure by dial gauge take reading and replace brush then start wtg now turbine running under observation | Close | 0.14423 | WTG Unscheduled Maintenance | O2-20 | 34801 | 5437.6562
315 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 17:38 | 17:38 | 17:56 | 0 | 0.3 | 0.3 | Checked related error data log then reset & started WTG. | Close | 0.011538 | WTG Unscheduled Maintenance | O2-01 | 34294 | 428.675
316 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:12 | 18:12 | 20:46 | 0 | 2.5667 | 2.5667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.098718 | WTG Breakdown Maintenance | O2-01 | 34294 | 3667.5528
317 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-18 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 21:39 | 21:39 | 22:30 | 0 | 0.85 | 0.85 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.032692 | WTG Breakdown Maintenance | O2-01 | 34294 | 1214.5792
318 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 17:12 | 17:12 | 17:33 | 0 | 0.35 | 0.35 | Checked related error data log then reset & started WTG. | Close | 0.013462 | WTG Unscheduled Maintenance | O2-26 | 45701 | 666.4729
319 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:11 | 18:11 | 20:39 | 0 | 2.4667 | 2.4667 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.094872 | WTG Breakdown Maintenance | O2-26 | 45701 | 4697.0472
320 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 17:25 | 17:25 | 17:39 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & started WTG. | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-02 | 53626 | 521.3639
321 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:00 | 18:00 | 18:42 | 0 | 0.7 | 0.7 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.026923 | WTG Breakdown Maintenance | O2-02 | 53626 | 1564.0917
322 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_06 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 17:08 | 17:08 | 17:11 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-21 | 45633 | 95.0687
323 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_07 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 12:24 | 12:24 | 12:40 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-04 | 51178 | 568.6444
324 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 16:23 | 16:23 | 16:39 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-26 | 45701 | 507.7889
325 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:29 | 14:29 | 14:35 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-12 | 44692 | 186.2167
326 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 16:51 | 16:51 | 16:54 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-14 | 42355 | 88.2396
327 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_14 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 12:36 | 12:36 | 12:47 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & started WTG. | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-12 | 44692 | 341.3972
328 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 6:54 | 6:54 | 15:37 | 0 | 8.7167 | 8.7167 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.33526 | WTG Scheduled Maintenance | O2-06 | 46454 | 16871.8347
329 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_20 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 12:59 | 12:59 | 13:15 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-24 | 45796 | 508.8444
330 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 10:36 | 10:36 | 10:42 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 46454 | 193.5583
331 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_23 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 14:49 | 14:49 | 15:05 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-11 | 45528 | 505.8667
332 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 10:30 | 10:30 | 11:09 | 0 | 0.65 | 0.65 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.025 | WTG Breakdown Maintenance | O2-01 | 39027 | 1056.9813
333 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-19 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 16:55 | 16:55 | 21:10 | 0 | 4.25 | 4.25 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.16346 | WTG Breakdown Maintenance | O2-01 | 39027 | 6911.0312
334 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 22:23 | 23:28 | 24:00 | 1.0833 | 0.53306 | 1.6164 | wtg manual stop for converter coolant temp high wip. | open | 0.062169 | WTG Unscheduled Maintenance | O2-26 | 22337 | 1504.3866
335 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:25 | 15:25 | 15:31 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 26515 | 110.4792
336 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_07 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:27 | 14:27 | 14:34 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-04 | 30756 | 149.5083
337 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:03 | 16:03 | 16:10 | 0 | 0.11667 | 0.11667 | WTG Manual stop for Software Updated Work. | Close | 0.0044872 | WTG Breakdown Maintenance | O2-26 | 22337 | 108.5826
338 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 14:48 | 14:48 | 15:00 | 0 | 0.2 | 0.2 | WTG Manual stop for Software Updated Work. | Close | 0.0076923 | WTG Breakdown Maintenance | O2-03 | 22769 | 189.7417
339 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:24 | 16:24 | 16:31 | 0 | 0.11667 | 0.11667 | WTG Manual stop for Software Updated Work. | Close | 0.0044872 | WTG Breakdown Maintenance | O2-12 | 27081 | 131.6437
340 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 17:33 | 17:33 | 17:58 | 0 | 0.41667 | 0.41667 | WTG Manual stop for Software Updated Work. | Close | 0.016026 | WTG Breakdown Maintenance | O2-14 | 25432 | 441.5278
341 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 13:57 | 13:57 | 14:03 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 27364 | 114.0167
342 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:38 | 15:38 | 15:55 | 0 | 0.28333 | 0.28333 | WTG Manual stop for Software Updated Work. | Close | 0.010897 | WTG Breakdown Maintenance | O2-11 | 27364 | 323.0472
343 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:14 | 16:14 | 16:20 | 0 | 0.1 | 0.1 | WTG Manual stop for Software Updated Work. | Close | 0.0038462 | WTG Breakdown Maintenance | O2-12 | 27081 | 112.8375
344 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 14:53 | 14:53 | 15:02 | 0 | 0.15 | 0.15 | WTG Manual stop for Software Updated Work. | Close | 0.0057692 | WTG Breakdown Maintenance | O2-21 | 29926 | 187.0375
345 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 11:51 | 11:51 | 12:02 | 0 | 0.18333 | 0.18333 | WTG Manual stop for Software Updated Work. | Close | 0.0070513 | WTG Breakdown Maintenance | O2-22 | 28894 | 220.7181
346 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 13:44 | 13:44 | 13:52 | 0 | 0.13333 | 0.13333 | WTG Manual stop for Software Updated Work. | Close | 0.0051282 | WTG Breakdown Maintenance | O2-22 | 28894 | 160.5222
347 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 6:41 | 6:49 | 13:03 | 0.13333 | 6.2333 | 6.3667 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.24487 | WTG Scheduled Maintenance | O2-06 | 30187 | 8007.9403
348 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 12:53 | 12:53 | 13:03 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Software Updated Work. | Close | 0.0064103 | WTG Breakdown Maintenance | O2-06 | 30187 | 209.6319
349 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 17:25 | 17:25 | 17:31 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 30187 | 125.7792
350 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_24 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 9:00 | 9:00 | 9:19 | 0 | 0.31667 | 0.31667 | Checked related error data log then reset & started WTG. | Close | 0.012179 | WTG Unscheduled Maintenance | O2-20 | 28383 | 374.4979
351 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-20 | O2_26 | TQGXIIPL | GEDA | 3.846% | 658 | Error pitch converter 3 | Break down |  | 7:29 | 7:29 | 7:46 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & started WTG. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-01 | 24919 | 294.1826
352 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-21 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 0:00 | 0:00 | 0:14 | 0 | 0.23333 | 0.23333 | wtg manual stop for converter coolant temp high so check and found coolanr MPCB trip and cable cut by mouse so correct it then started wtg. | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-26 | 7446 | 72.3917
353 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-21 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:10 | 19:10 | 19:56 | 0 | 0.76667 | 0.76667 | After grid Resume time Converter RFO Single Note so after so and Reset and start wtg | Close | 0.029487 | WTG Unscheduled Maintenance | O2-05 | 12194 | 389.5306
354 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-21 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 16:58 | 16:58 | 17:05 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-21 | 9310 | 45.2569
355 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-21 | O2_11 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down |  | 19:10 | 19:10 | 19:59 | 0 | 0.81667 | 0.81667 | Checked related error data log then apply softreboot then reset & started WTG. | Close | 0.03141 | WTG Unscheduled Maintenance | O2-12 | 9575 | 325.816
356 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-21 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 20:36 | 22:30 | 24:00 | 1.9 | 1.4997 | 3.3997 | attend check all related circuit and found Hub panel entry point len cable is damage so replace it and take Wtg trial 30 mini after error it occurs so check all 3 axis len cable entry point found no any abnormality so discuss with commissioning team,wtg restoration wip | open | 0.13076 | WTG Unscheduled Maintenance | O2-12 | 9575 | 1356.3475
357 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-21 | O2_12 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down |  | 9:31 | 10:40 | 12:30 | 1.15 | 1.8333 | 2.9833 | after grid resume error is occurs so attend check all all 3 axis blade calibration is ok so check pitch encode A and B and found pitch encoder connector loose so tight it then started wtg. | Close | 0.11474 | WTG Unscheduled Maintenance | O2-14 | 9107 | 1132.0507
358 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-21 | O2_14 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 19:10 | 19:10 | 19:44 | 0 | 0.56667 | 0.56667 | Checked related error data log then apply softreboot then reset & started WTG. | Close | 0.021795 | WTG Unscheduled Maintenance | O2-12 | 9575 | 226.0764
359 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-21 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 6:52 | 7:01 | 13:10 | 0.15 | 6.15 | 6.3 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.24231 | WTG Scheduled Maintenance | O2-21 | 9310 | 2443.875
360 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-22 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 15:48 | 15:48 | 16:02 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & started WTG. | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-26 | 12251 | 119.1069
361 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-22 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 18:09 | 18:50 | 19:23 | 0.68333 | 0.55 | 1.2333 | attend and check and found coverter cooling fan MPCB trip so check all releted circuit no any abnormality so interchange MPCB then start wtg. Now wtg under observation. | Close | 0.047436 | WTG Unscheduled Maintenance | O2-26 | 12251 | 629.5653
362 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-22 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 0:00 | 0:00 | 0:31 | 0 | 0.51667 | 0.51667 | attend and check releted circuit check Hub panel entry point len cable is damage so replace it take Wtg trial | Close | 0.019872 | WTG Unscheduled Maintenance | O2-12 | 12585 | 270.9271
363 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-22 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 1:01 | 1:01 | 5:06 | 0 | 4.0833 | 4.0833 | 30 mini after error it occurs so check all 3 axis len cable entry point found no any abnormality so take Wtg trial | Close | 0.15705 | WTG Unscheduled Maintenance | O2-12 | 12585 | 2141.1979
364 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-22 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Major BD |  | 6:00 | 6:00 | 24:00 | 0 | 17.9997 | 17.9997 | after error it occurs so discuss with commissioning team and check and found all 3 axis len cable is not connected as per wtg wiring diagram so correct it WIP | OPEN | 0.6923 | WTG Unscheduled Maintenance | O2-12 | 12585 | 9438.6043
365 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-22 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:08 | 13:08 | 13:14 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 10599 | 44.1625
366 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-23 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 4:28 | 4:28 | 4:44 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & started WTG. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-26 | 13113 | 145.7
367 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-23 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Auto reset |  | 5:25 | 5:25 | 5:41 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-26 | 13113 | 145.7
368 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-23 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 0:00 | 0:00 | 5:35 | 0 | 5.5833 | 5.5833 | Attend and check all Communication Cables and replace and also Check FO cable and connection and than take trial but same error occured so reprogramming of HUb module MX220 and interchange PPD between blade 1&3 than recalibration of all 3 blades than reset and start turbine(Now Turbine under observation). | Close | 0.21474 | WTG Unscheduled Maintenance | O2-12 | 18749 | 4361.7465
369 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-23 | O2_11 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 10:30 | 11:37 | 15:35 | 1.1167 | 3.9667 | 5.0833 | We have check In SAM Event found Pitch communication loss to 1,2 and 3 also check in Snap and found Encode value deviation.So We have Attend turbine and check all Communication Cables Connector and clean properly and refixed and Further We have interchage Communication module to Mx220 module cable with BLS and Replace MX220 Module with new one and Install new Base package.After Programming Complete We Calibration all 3 blade and properly all cable laying complete we have Taken trail turbine.After No any abnormal absorb so started WTG. | Close | 0.19551 | WTG Unscheduled Maintenance | O2-12 | 18749 | 3971.1424
370 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-23 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 9:42 | 9:42 | 18:21 | 0 | 8.65 | 8.65 | WTG Manual stop for Blade-3 VG installation work done than started wtg. | Close | 0.33269 | WTG Breakdown Maintenance | O2-06 | 18174 | 6550.2125
371 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-24 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 11:20 | 11:20 | 18:38 | 0 | 7.3 | 7.3 | Wtg manual stop for wtg Lift FTU work. | Close | 0.28077 | WTG Breakdown Maintenance | O2-22 | 20201 | 6144.4708
372 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-24 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 9:14 | 9:14 | 16:34 | 0 | 7.3333 | 7.3333 | WTG Manual stop for Blade-2 VG installation work done than started wtg. | Close | 0.28205 | WTG Breakdown Maintenance | O2-06 | 18405 | 5623.75
373 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-24 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 16:43 | 16:43 | 16:46 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-11 | 16559 | 34.4979
374 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-24 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:48 | 13:48 | 13:54 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-20 | 18458 | 76.9083
375 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 18:49 | 18:49 | 19:26 | 0 | 0.61667 | 0.61667 | Checked related error data log then check parameter then apply soft reboot then reset & started WTG. | Close | 0.023718 | WTG Unscheduled Maintenance | O2-09 | 23355 | 600.0938
376 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_04 | TQGXIIPL | GEDA | 3.846% | 630 | Overload fan pitch motor | Break down |  | 0:28 | 1:42 | 3:00 | 1.2333 | 1.3 | 2.5333 | attend and check all related circuit and found axis1 pitch motor cooling MPCB FC002 trip so check and found cooling fan cannection bolt is loose so tight it then start wtg. | Close | 0.097436 | WTG Unscheduled Maintenance | O2-07 | 25522 | 2693.9889
377 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3250 | No power | Auto reset |  | 4:18 | 4:18 | 4:19 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-07 | 25522 | 17.7236
378 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 5:13 | 5:13 | 5:17 | 0 | 0.066667 | 0.066667 | attend and check and found converter cooling fan MPCB triped so check no any abnormality so stert MPCB then started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-07 | 25522 | 70.8944
379 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3010 | Conv. comm.error | Break down |  | 3:53 | 4:36 | 5:04 | 0.71667 | 0.46667 | 1.1833 | attend and check all related circuit and check CAND cable all related cable no any abnormality so apply hard reboot then started wtg. | Close | 0.045513 | WTG Unscheduled Maintenance | O2-02 | 30384 | 1498.1
380 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_05 | TQGXIIPL | GEDA | 3.846% | 7017 | Parameter outside limits stop | Break down |  | 19:25 | 19:25 | 20:07 | 0 | 0.7 | 0.7 | Checked related error data log then check parameter no any abnormality apply soft reboot then reset & started WTG. | Close | 0.026923 | WTG Unscheduled Maintenance | O2-02 | 30384 | 886.2
381 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 20:28 | 20:28 | 21:01 | 0 | 0.55 | 0.55 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.021154 | WTG Breakdown Maintenance | O2-14 | 19630 | 449.8542
382 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 15:18 | 15:18 | 15:24 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 20809 | 86.7042
383 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:43 | 15:58 | 17:05 | 0.25 | 1.1167 | 1.3667 | Wtg manual stop for wtg Lift FTU work. | Close | 0.052564 | WTG Breakdown Maintenance | O2-12 | 19079 | 1086.4431
384 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 9:02 | 9:02 | 17:21 | 0 | 8.3167 | 8.3167 | WTG Manual stop for Blade-1 VG installation work done than started wtg. | Close | 0.31987 | WTG Breakdown Maintenance | O2-06 | 24475 | 8481.2674
385 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 19:56 | 19:56 | 19:59 | 0 | 0.05 | 0.05 | Wtg manual stop for parameter check then start wtg | Close | 0.0019231 | WTG Breakdown Maintenance | O2-06 | 24475 | 50.9896
386 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_18 | TQGXIIPL | GEDA | 3.846% | 60 | Wind > power | Break down |  | 20:21 | 20:21 | 20:29 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-06 | 24475 | 135.9722
387 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_18 | TQGXIIPL | GEDA | 3.846% | 60 | Wind > power | Break down |  | 20:52 | 20:52 | 21:09 | 0 | 0.28333 | 0.28333 | Checked related error data log check parameter by L2 team then reset & started WTG. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-06 | 24475 | 288.941
388 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_18 | TQGXIIPL | GEDA | 3.846% | 60 | Wind > power | Break down |  | 21:32 | 21:32 | 21:58 | 0 | 0.43333 | 0.43333 | Checked related error data log check parameter by L2 team then reset & started WTG. | Close | 0.016667 | WTG Unscheduled Maintenance | O2-06 | 24475 | 441.9097
389 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 22:02 | 22:02 | 22:13 | 0 | 0.18333 | 0.18333 | WTG Manual stop for Turbine Manual stop for PPC parameter checking work | Close | 0.0070513 | WTG Breakdown Maintenance | O2-06 | 24475 | 186.9618
390 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-25 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 7:23 | 7:23 | 15:00 | 0 | 7.6167 | 7.6167 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.29295 | WTG Scheduled Maintenance | O2-24 | 22510 | 7143.7986
391 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_03 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 11:03 | 11:03 | 11:13 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & started WTG. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-09 | 21341 | 148.2014
392 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 16:11 | 16:11 | 16:17 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 32148 | 133.95
393 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:11 | 19:11 | 21:43 | 0 | 2.5333 | 2.5333 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.097436 | WTG Breakdown Maintenance | O2-02 | 30087 | 3175.85
394 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:33 | 16:33 | 17:55 | 0 | 1.3667 | 1.3667 | Wtg manual stop for wtg Lift FTU work. | Close | 0.052564 | WTG Breakdown Maintenance | O2-15 | 21293 | 1212.5181
395 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 14:46 | 14:46 | 16:00 | 0 | 1.2333 | 1.2333 | Wtg manual stop for wtg Lift FTU work. | Close | 0.047436 | WTG Breakdown Maintenance | O2-12 | 21342 | 1096.7417
396 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 10:48 | 10:48 | 12:00 | 0 | 1.2 | 1.2 | Wtg manual stop for wtg Lift FTU work. | Close | 0.046154 | WTG Breakdown Maintenance | O2-11 | 20631 | 1031.55
397 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 12:00 | 12:00 | 13:15 | 0 | 1.25 | 1.25 | WTG stop for Customer Audit work. | Close | 0.048077 | WTG Breakdown Maintenance | O2-11 | 20631 | 1074.5313
398 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 13:36 | 13:36 | 14:24 | 0 | 0.8 | 0.8 | WTG stop for Customer Audit work. | Close | 0.030769 | WTG Breakdown Maintenance | O2-11 | 20631 | 687.7
399 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 9:24 | 9:24 | 16:12 | 0 | 6.8 | 6.8 | WTG Manual stop for Blade-3 VG installation work done than started wtg. | Close | 0.26154 | WTG Breakdown Maintenance | O2-22 | 28932 | 8197.4
400 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 13:59 | 13:59 | 14:08 | 0 | 0.15 | 0.15 | Wtg manual stop for parameter check then apply soft reboot then reset & started WTG. | Close | 0.0057692 | WTG Breakdown Maintenance | O2-06 | 25979 | 162.3687
401 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_18 | TQGXIIPL | GEDA | 3.846% | 60 | Wind > power | Break down |  | 17:59 | 17:59 | 18:26 | 0 | 0.45 | 0.45 | Checked related error data log check parameterthen reset & started WTG. | Close | 0.017308 | WTG Unscheduled Maintenance | O2-06 | 25979 | 487.1063
402 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Auto reset |  | 21:35 | 21:35 | 21:37 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-07 | 32148 | 44.65
403 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Break down |  | 21:45 | 23:59 | 24:00 | 2.2333 | 0.016389 | 2.2497 | attend and found bottom power panel ACB trip and 1 nos 500A fuse is faulty. So this fault is machine side fault so check generator stator and rotor carbon brush and slipring is all condition is ok so check IR value ACB and ingeteam person traubleshooting WIP. | Close | 0.086528 | WTG Unscheduled Maintenance | O2-07 | 32148 | 3013.5029
404 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 6:22 | 6:22 | 11:38 | 0 | 5.2667 | 5.2667 | WTG stop for YPM day-1 activity complate than started WTG. | Close | 0.20256 | WTG Scheduled Maintenance | O2-24 | 23190 | 5088.9167
405 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_20 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down |  | 11:55 | 11:55 | 11:58 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-24 | 23190 | 48.3125
406 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:20 | 12:20 | 12:26 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 20631 | 85.9625
407 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-26 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:10 | 18:10 | 21:15 | 0 | 3.0833 | 3.0833 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.11859 | WTG Breakdown Maintenance | O2-01 | 23625 | 3035.1562
408 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-27 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3210 | Frequency converter load rejection | Break down |  | 5:32 | 5:32 | 5:35 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-02 | 27721 | 57.7521
409 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-27 | O2_07 | TQGXIIPL | GEDA | 3.846% | 6300 | Yaw error | Break down |  | 19:24 | 19:24 | 19:31 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-04 | 25863 | 125.7229
410 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-27 | O2_12 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down |  | 11:59 | 11:59 | 12:11 | 0 | 0.2 | 0.2 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-14 | 17831 | 148.5917
411 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-27 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 7:36 | 7:36 | 14:58 | 0 | 7.3667 | 7.3667 | WTG Manual stop for Blade-1 VG installation work done than started wtg. | Close | 0.28333 | WTG Breakdown Maintenance | O2-22 | 24160 | 7415.7778
412 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-27 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Major BD |  | 0:00 | 3:44 | 14:34 | 3.7333 | 10.8333 | 14.5667 | attend for WTG stop in Grid loss error(Circuit breaker(Grid loss without grid loss auxiliary power) so we attend turbine and check Sam data and also check physically and check converter panel and found ACB was trip so check Busbar and its connections and also check power cable and stator and rotor and Also take Busbar IR but nothing found abnormalities so now we check ACB and its setting with our technical team and supplier and set ACB settings and also re-tight all connection than reset and take trial than nothing found abnormal so start WTG.(now turbine under observation). | Close | 0.56026 | WTG Unscheduled Maintenance | O2-07 | 23298 | 14140.5917
413 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-27 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 17:02 | 17:02 | 17:34 | 0 | 0.53333 | 0.53333 | attend wtg for power panel inspection work. | Close | 0.020513 | WTG Breakdown Maintenance | O2-07 | 23298 | 517.7333
414 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-27 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 9:09 | 9:09 | 9:12 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-11 | 18496 | 38.5333
415 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-27 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 9:09 | 9:09 | 9:12 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-01 | 21657 | 45.1188
416 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:22 | 11:22 | 11:28 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-05 | 28941 | 120.5875
417 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_03 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 18:36 | 18:36 | 18:43 | 0 | 0.11667 | 0.11667 | After Grid error occurred so Checked related error data log then apply soft reboot & started WTG. | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-09 | 23663 | 115.0285
418 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 11:23 | 11:23 | 11:26 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-02 | 33725 | 70.2604
419 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 17:58 | 17:58 | 18:04 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-02 | 33725 | 140.5208
420 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 20:35 | 20:35 | 22:14 | 0 | 1.65 | 1.65 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.063462 | WTG Breakdown Maintenance | O2-02 | 33725 | 2318.5938
421 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 6:50 | 6:50 | 14:36 | 0 | 7.7667 | 7.7667 | WTG stop for YPM day-1 activity complate and Lift FTU work done than started WTG. | Close | 0.29872 | WTG Scheduled Maintenance | O2-21 | 21721 | 7029.1569
422 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down |  | 15:53 | 15:53 | 15:55 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-21 | 21721 | 30.1681
423 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:53 | 18:53 | 20:10 | 0 | 1.2833 | 1.2833 | WTG Manual stop for load shedding due to feeder-01 overloading issue + Lift FTU work done than start WTG. | Close | 0.049359 | WTG Breakdown Maintenance | O2-14 | 20172 | 1078.6417
424 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:45 | 16:45 | 17:27 | 0 | 0.7 | 0.7 | Wtg manual stop for wtg Lift FTU work. | Close | 0.026923 | WTG Breakdown Maintenance | O2-21 | 21721 | 633.5292
425 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_17 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down |  | 6:03 | 6:03 | 6:08 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-22 | 28665 | 99.5312
426 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 8:28 | 8:28 | 16:35 | 0 | 8.1167 | 8.1167 | WTG Manual stop for Blade-2 VG installation work done than started wtg. | Close | 0.31218 | WTG Breakdown Maintenance | O2-22 | 28665 | 9694.3437
427 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 21:04 | 21:04 | 21:06 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-22 | 28665 | 39.8125
428 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_20 | TQGXIIPL | GEDA | 3.846% | 7017 | Parameter outside limits stop | Break down |  | 18:51 | 18:51 | 19:03 | 0 | 0.2 | 0.2 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-24 | 25311 | 210.925
429 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:06 | 15:06 | 15:58 | 0 | 0.86667 | 0.86667 | Wtg manual stop for wtg Lift FTU work. | Close | 0.033333 | WTG Breakdown Maintenance | O2-06 | 18752 | 677.1556
430 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 11:05 | 11:05 | 12:05 | 0 | 1 | 1 | WTG stop for Customer Audit work than WIP, | Close | 0.038462 | WTG Breakdown Maintenance | O2-06 | 18752 | 781.3333
431 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 12:05 | 12:05 | 12:53 | 0 | 0.8 | 0.8 | Wtg manual stop for wtg Lift FTU work. | Close | 0.030769 | WTG Breakdown Maintenance | O2-06 | 18752 | 625.0667
432 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_23 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down |  | 18:23 | 18:23 | 18:32 | 0 | 0.15 | 0.15 | After Grid error occurred so Checked related error data log then apply soft reboot & started WTG. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-11 | 22680 | 141.75
433 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-28 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:10 | 16:10 | 16:16 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-20 | 24463 | 101.9292
434 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 14:05 | 14:05 | 14:31 | 0 | 0.43333 | 0.43333 | Wtg manual stop for wtg Lift FTU work. | Close | 0.016667 | WTG Breakdown Maintenance | O2-26 | 40476 | 730.8167
435 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_01 | TQGXIIPL | GEDA | 3.846% | 159 | SLC SF emergency stop | Break down |  | 23:10 | 23:10 | 24:00 | 0 | 0.83333 | 0.83333 | WTG disconnect from Scada so Attend and check error related ckt than found UPS supply output MCB tripped so wip, | Close | 0.032051 | WTG Unscheduled Maintenance | O2-26 | 40476 | 1405.4167
436 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 17:03 | 17:03 | 17:39 | 0 | 0.6 | 0.6 | Wtg manual stop for wtg Lift FTU work. | Close | 0.023077 | WTG Breakdown Maintenance | O2-05 | 37871 | 946.775
437 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_03 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 12:00 | 12:00 | 16:10 | 0 | 4.1667 | 4.1667 | Attend and check event in SAM found pitch error also check in snap and found Encoder value deviation so we have attend turbine and check QA001 contector manually oparate found L2 and L3 cable loose so check All NO/NC auxiliry switch and found one nos NC switch not working properly and check voltage found normal then we have taken trial turbine after no any abnormality so started Turbine. | Close | 0.16026 | WTG Breakdown Maintenance | O2-09 | 40871 | 7095.6597
438 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:00 | 16:00 | 16:34 | 0 | 0.56667 | 0.56667 | Wtg manual stop for wtg Lift FTU work. | Close | 0.021795 | WTG Breakdown Maintenance | O2-07 | 47322 | 1117.325
439 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_04 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 18:03 | 18:03 | 18:10 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-07 | 47322 | 230.0375
440 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 20:45 | 20:45 | 24:00 | 0 | 3.25 | 3.25 | WTG Manual stop for load shedding due to feeder-01 overloading issue | Close | 0.125 | WTG Breakdown Maintenance | O2-02 | 46987 | 6362.8229
441 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 6:56 | 6:56 | 13:54 | 0 | 6.9667 | 6.9667 | WTG stop for YPM day-2 activity complate than started WTG. | Close | 0.26795 | WTG Scheduled Maintenance | O2-21 | 35807 | 10393.9764
442 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 14:39 | 14:39 | 14:46 | 0 | 0.11667 | 0.11667 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-21 | 35807 | 174.0618
443 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_07 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 7:50 | 7:50 | 7:56 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-04 | 47661 | 198.5875
444 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 17:57 | 17:57 | 18:45 | 0 | 0.8 | 0.8 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.030769 | WTG Unscheduled Maintenance | O2-04 | 47661 | 1588.7
445 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:16 | 13:16 | 13:22 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 40476 | 168.65
446 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:39 | 14:39 | 14:50 | 0 | 0.18333 | 0.18333 | Checked related error data log then reset & started WTG. | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-26 | 40476 | 309.1917
447 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:36 | 12:36 | 12:42 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-15 | 40415 | 168.3958
448 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 12:12 | 12:12 | 12:28 | 0 | 0.26667 | 0.26667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-14 | 36243 | 402.7
449 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:02 | 11:02 | 11:08 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 38381 | 159.9208
450 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 11:32 | 11:32 | 11:53 | 0 | 0.35 | 0.35 | Checked related error data log then reset & started WTG. | Close | 0.013462 | WTG Unscheduled Maintenance | O2-11 | 38381 | 559.7229
451 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 12:24 | 12:24 | 12:29 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-12 | 36596 | 127.0694
452 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 8:37 | 8:37 | 8:43 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-10 | 33673 | 140.3042
453 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 16:34 | 16:34 | 16:58 | 0 | 0.4 | 0.4 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.015385 | WTG Unscheduled Maintenance | O2-10 | 33673 | 561.2167
454 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 15:34 | 15:34 | 15:42 | 0 | 0.13333 | 0.13333 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-21 | 35807 | 198.9278
455 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 16:09 | 16:09 | 16:15 | 0 | 0.1 | 0.1 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 35807 | 149.1958
456 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:41 | 16:41 | 16:47 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 35807 | 149.1958
457 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 14:57 | 14:57 | 14:59 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-22 | 41434 | 57.5472
458 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:31 | 15:31 | 15:37 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-22 | 41434 | 172.6417
459 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 17:53 | 17:53 | 18:32 | 0 | 0.65 | 0.65 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.025 | WTG Unscheduled Maintenance | O2-22 | 41434 | 1122.1708
460 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 12:17 | 12:17 | 12:25 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-07 | 47322 | 262.9
461 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 17:33 | 17:33 | 17:56 | 0 | 0.38333 | 0.38333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.014744 | WTG Unscheduled Maintenance | O2-07 | 47322 | 755.8375
462 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:44 | 14:44 | 14:50 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 30203 | 125.8458
463 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_22 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 20:09 | 20:09 | 20:33 | 0 | 0.4 | 0.4 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.015385 | WTG Unscheduled Maintenance | O2-06 | 30203 | 503.3833
464 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 18:28 | 18:28 | 18:52 | 0 | 0.4 | 0.4 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.015385 | WTG Unscheduled Maintenance | O2-11 | 38381 | 639.6833
465 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down |  | 13:42 | 13:42 | 13:45 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-20 | 41925 | 87.3437
466 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:10 | 18:10 | 24:00 | 0 | 5.8333 | 5.8333 | WTG Manual stop for load shedding due to feeder-01 overloading issue + Lift FTU work done than start WTG. | Close | 0.22436 | WTG Breakdown Maintenance | O2-01 | 39002 | 9479.6528
467 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down |  | 15:38 | 15:38 | 16:01 | 0 | 0.38333 | 0.38333 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.014744 | WTG Unscheduled Maintenance | O2-01 | 39002 | 622.9486
468 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-29 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:12 | 16:12 | 16:18 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-01 | 39002 | 162.5083
469 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_01 | TQGXIIPL | GEDA | 3.846% | 159 | SLC SF emergency stop | Break down |  | 0:00 | 0:00 | 2:40 | 0 | 2.6667 | 2.6667 | WTG disconnect from Scada so Attend and check error related ckt than found UPS supply output MCB tripped so check all connection in panel found ok than reset and started WTG. | Close | 0.10256 | WTG Unscheduled Maintenance | O2-26 | 38333 | 4259.2222
470 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_01 | TQGXIIPL | GEDA | 3.846% | 159 | SLC SF emergency stop | Break down |  | 3:30 | 3:30 | 4:30 | 0 | 1 | 1 | WTG disconnect from Scada so Attend and check error related ckt than found UPS supply output MCB tripped so check all connection in panel found ok than reset and started WTG. | Close | 0.038462 | WTG Unscheduled Maintenance | O2-26 | 38333 | 1597.2083
471 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 21:36 | 21:36 | 22:50 | 0 | 1.2333 | 1.2333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.047436 | WTG Breakdown Maintenance | O2-26 | 38333 | 1969.8903
472 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 13:48 | 13:48 | 13:50 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-05 | 37428 | 51.9833
473 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 8:22 | 8:22 | 8:28 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 43595 | 181.6458
474 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 9:09 | 9:09 | 9:11 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-07 | 43595 | 60.5486
475 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:56 | 11:56 | 12:02 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 43595 | 181.6458
476 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_04 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 18:18 | 18:18 | 18:44 | 0 | 0.43333 | 0.43333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.016667 | WTG Unscheduled Maintenance | O2-07 | 43595 | 787.1319
477 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 0:00 | 0:00 | 0:55 | 0 | 0.91667 | 0.91667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.035256 | WTG Breakdown Maintenance | O2-02 | 46976 | 1794.2222
478 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 18:43 | 18:43 | 18:49 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-02 | 46976 | 195.7333
479 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 21:28 | 21:28 | 23:20 | 0 | 1.8667 | 1.8667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.071795 | WTG Breakdown Maintenance | O2-02 | 46976 | 3653.6889
480 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down |  | 14:37 | 14:37 | 14:40 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-21 | 34897 | 72.7021
481 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 10:40 | 10:40 | 11:25 | 0 | 0.75 | 0.75 | Wtg manual stop for wtg Lift FTU work. | Close | 0.028846 | WTG Breakdown Maintenance | O2-26 | 38333 | 1197.9062
482 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:24 | 16:24 | 16:30 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 38333 | 159.7208
483 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:10 | 18:10 | 20:23 | 0 | 2.2167 | 2.2167 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.085256 | WTG Unscheduled Maintenance | O2-26 | 38333 | 3540.4785
484 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:38 | 16:38 | 17:19 | 0 | 0.68333 | 0.68333 | Wtg manual stop for wtg Lift FTU work. | Close | 0.026282 | WTG Breakdown Maintenance | O2-03 | 35656 | 1015.2056
485 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:57 | 16:57 | 17:03 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-15 | 39028 | 162.6167
486 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_12 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down |  | 10:56 | 10:56 | 13:45 | 0 | 2.8167 | 2.8167 | Attend WTG for repeated error Sim angle 3 so check all related ckt and found QA001 contactor auxiliary 23 and 24 on loose connection so tight it and apply manually Pitching no any abnormality so reset and started WTG. | Close | 0.10833 | WTG Breakdown Maintenance | O2-14 | 35100 | 4119.375
487 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 14:27 | 14:27 | 15:00 | 0 | 0.55 | 0.55 | Wtg manual stop for wtg Lift FTU work. | Close | 0.021154 | WTG Breakdown Maintenance | O2-10 | 33815 | 774.9271
488 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 15:35 | 15:35 | 15:45 | 0 | 0.16667 | 0.16667 | Checked related error data log then reset & started WTG. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-22 | 40527 | 281.4375
489 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_17 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 17:36 | 17:36 | 17:39 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-22 | 40527 | 84.4313
490 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_18 | TQGXIIPL | GEDA | 3.846% | 2355 | Temp. rot.br.pad high | Break down |  | 1:44 | 1:44 | 1:50 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 40195 | 167.4792
491 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_18 | TQGXIIPL | GEDA | 3.846% | 2355 | Temp. rot.br.pad high | Break down |  | 22:41 | 22:41 | 22:54 | 0 | 0.21667 | 0.21667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-06 | 40195 | 362.8715
492 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:57 | 15:57 | 16:03 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 40195 | 167.4792
493 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:44 | 12:44 | 12:50 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 40195 | 167.4792
494 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:46 | 14:46 | 14:49 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-06 | 40195 | 83.7396
495 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:39 | 15:39 | 16:15 | 0 | 0.6 | 0.6 | Wtg manual stop for wtg Lift FTU work. | Close | 0.023077 | WTG Breakdown Maintenance | O2-11 | 39981 | 999.525
496 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 0:00 | 0:00 | 0:24 | 0 | 0.4 | 0.4 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.015385 | WTG Breakdown Maintenance | O2-01 | 30766 | 512.7667
497 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 17:52 | 17:52 | 19:31 | 0 | 1.65 | 1.65 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.063462 | WTG Breakdown Maintenance | O2-01 | 30766 | 2115.1625
498 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 11:57 | 11:57 | 12:17 | 0 | 0.33333 | 0.33333 | Wtg manual stop for wtg Lift FTU work. | Close | 0.012821 | WTG Breakdown Maintenance | O2-01 | 30766 | 427.3056
499 | 2026 | 2025 | Year_2 | 2025-04-01 | 2025-04-30 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 13:34 | 13:34 | 13:46 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-01 | 30766 | 256.3833
500 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:36 | 14:36 | 14:42 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 45834 | 190.975
501 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 10:41 | 10:41 | 11:25 | 0 | 0.73333 | 0.73333 | Wtg manual stop for wtg Lift FTU work. | Close | 0.028205 | WTG Breakdown Maintenance | O2-02 | 49670 | 1517.6944
502 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:52 | 14:52 | 14:54 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-02 | 49670 | 68.9861
503 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:25 | 14:25 | 14:31 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 44674 | 186.1417
504 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 14:40 | 14:40 | 14:43 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-26 | 44674 | 93.0708
505 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_12 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 15:15 | 15:15 | 15:17 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & started WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-14 | 38537 | 53.5236
506 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 18:48 | 18:48 | 19:10 | 0 | 0.36667 | 0.36667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.014103 | WTG Unscheduled Maintenance | O2-14 | 38537 | 588.7597
507 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 10:11 | 10:11 | 13:45 | 0 | 3.5667 | 3.5667 | Attend for WTG Repeated error (Wind dire.diff.level 2) so check wind vane connection after wind vane 1 & 2 alignment properly after trail so ok then reset and start WTG. | Close | 0.13718 | WTG Breakdown Maintenance | O2-22 | 47524 | 7062.5944
508 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_18 | TQGXIIPL | GEDA | 3.846% | 2355 | Temp. rot.br.pad high | Break down |  | 3:28 | 3:28 | 4:02 | 0 | 0.56667 | 0.56667 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.021795 | WTG Unscheduled Maintenance | O2-06 | 46547 | 1099.0264
509 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_19 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 13:44 | 13:44 | 13:49 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-07 | 45834 | 159.1458
510 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 17:07 | 17:07 | 17:30 | 0 | 0.38333 | 0.38333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.014744 | WTG Unscheduled Maintenance | O2-07 | 45834 | 732.0708
511 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 19:47 | 19:47 | 20:16 | 0 | 0.48333 | 0.48333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.01859 | WTG Unscheduled Maintenance | O2-07 | 45834 | 923.0458
512 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:49 | 12:49 | 12:55 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-24 | 41385 | 172.4375
513 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:08 | 14:08 | 14:21 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & started WTG. | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-24 | 41385 | 373.6146
514 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 7:31 | 7:31 | 7:37 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 46547 | 193.9458
515 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 10:37 | 10:37 | 10:43 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 40516 | 168.8167
516 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-01 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:32 | 15:32 | 16:28 | 0 | 0.93333 | 0.93333 | Wtg manual stop for wtg Lift FTU work. | Close | 0.035897 | WTG Breakdown Maintenance | O2-20 | 43931 | 1708.4278
517 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-02 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:20 | 16:20 | 16:26 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 26581 | 110.7542
518 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-02 | O2_08 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Break down |  | 14:05 | 14:05 | 14:08 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-26 | 25628 | 53.3917
519 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-02 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:31 | 13:31 | 13:37 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 25628 | 106.7833
520 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-02 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 14:42 | 14:42 | 15:04 | 0 | 0.36667 | 0.36667 | In turbine error occurred during bettry test Rotor br. Buff.volt too low so check related error data log and all perameter then apply soft reboot than started Turbine. | Close | 0.014103 | WTG Unscheduled Maintenance | O2-26 | 25628 | 391.5389
521 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-02 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:34 | 12:34 | 12:40 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-12 | 25954 | 108.1417
522 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-02 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down |  | 15:52 | 15:52 | 15:55 | 0 | 0.05 | 0.05 | Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-11 | 26607 | 55.4312
523 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-02 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 11:38 | 11:38 | 11:40 | 0 | 0.033333 | 0.033333 | After Software Update work done than start WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-22 | 28813 | 40.0181
524 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-02 | O2_18 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down |  | 1:43 | 1:43 | 2:06 | 0 | 0.38333 | 0.38333 | Checked related error data log then apply soft reboot then reset & started WTG. | Close | 0.014744 | WTG Unscheduled Maintenance | O2-06 | 29048 | 463.9611
525 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-02 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 11:42 | 11:42 | 11:45 | 0 | 0.05 | 0.05 | After Software Update work done than start WTG. | Close | 0.0019231 | WTG Breakdown Maintenance | O2-06 | 29048 | 60.5167
526 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-02 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 7:26 | 7:26 | 16:30 | 0 | 9.0667 | 9.0667 | WTG stop for YPM activity and replace axis 1 (1.7 ohm)Flat resistor then work complated than started WTG. | Close | 0.34872 | WTG Scheduled Maintenance | O2-06 | 29048 | 10973.6889
527 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-02 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 15:00 | 15:00 | 15:06 | 0 | 0.1 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-01 | 29702 | 123.7583
528 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-02 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 17:38 | 17:38 | 17:52 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & started WTG. | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-01 | 29702 | 288.7694
529 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_01 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down |  | 4:00 | 4:00 | 4:07 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-26 | 43445 | 211.191
530 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:01 | 18:01 | 22:00 | 0 | 3.9833 | 3.9833 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.15321 | WTG Breakdown Maintenance | O2-26 | 43445 | 7210.6632
531 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_02 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Auto reset |  | 4:13 | 4:13 | 4:16 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-05 | 50589 | 105.3938
532 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_06 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 14:36 | 14:36 | 14:54 | 0 | 0.3 | 0.3 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.011538 | WTG Unscheduled Maintenance | O2-21 | 47180 | 589.75
533 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_06 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 16:14 | 16:34 | 17:10 | 0.33333 | 0.6 | 0.93333 | Attend turbine check connection of rotor brake pad 01 sensor its ohmic value , then remove sensor from pad check physical condition then refixed properly . Then check the temp value found normal so take the trail of the turbine and started . | Close | 0.035897 | WTG Breakdown Maintenance | O2-21 | 47180 | 1834.7778
534 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 8:37 | 8:37 | 8:42 | 0 | 0.083333 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-26 | 43445 | 150.8507
535 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 16:14 | 16:14 | 16:21 | 0 | 0.11667 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-26 | 43445 | 211.191
536 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 23:52 | 23:52 | 23:57 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-26 | 43445 | 150.8507
537 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:00 | 15:00 | 15:06 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-12 | 43049 | 179.3708
538 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:01 | 16:01 | 16:05 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-11 | 41617 | 115.6028
539 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_18 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Auto reset |  | 15:10 | 15:10 | 15:22 | 0 | 0.2 | 0.2 | Auto reset | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-06 | 39457 | 328.8083
540 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_18 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 18:40 | 18:40 | 20:14 | 0 | 1.5667 | 1.5667 | Attend and check error related ckt than clean rotor Brake pad and also check brake pad thickness and rotor brake pad temp.sensor connection check found ok than reset and start WTG. | Close | 0.060256 | WTG Breakdown Maintenance | O2-06 | 39457 | 2575.6653
541 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 16:24 | 16:24 | 16:44 | 0 | 0.33333 | 0.33333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.012821 | WTG Unscheduled Maintenance | O2-07 | 42306 | 587.5833
542 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 16:45 | 16:45 | 21:36 | 0 | 4.85 | 4.85 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.18654 | WTG Breakdown Maintenance | O2-26 | 43445 | 8779.5104
543 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 16:21 | 16:21 | 16:28 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-11 | 41617 | 202.3049
544 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 7:17 | 7:17 | 20:35 | 0 | 13.3 | 13.3 | WTG stop for YPM activity complated than started WTG. | Close | 0.51154 | WTG Scheduled Maintenance | O2-20 | 44438 | 24626.0583
545 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_25 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down |  | 2:21 | 2:21 | 2:39 | 0 | 0.3 | 0.3 | Checked related error data log then reset & started WTG. | Close | 0.011538 | WTG Breakdown Maintenance | O2-01 | 29084 | 363.55
546 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:31 | 16:31 | 16:37 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-01 | 29084 | 121.1833
547 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-03 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 16:57 | 16:57 | 18:00 | 0 | 1.05 | 1.05 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.040385 | WTG Breakdown Maintenance | O2-01 | 29084 | 1272.425
548 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Auto reset |  | 11:00 | 11:00 | 11:07 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-09 | 28449 | 138.2938
549 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:34 | 16:34 | 16:40 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 23702 | 98.7583
550 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset |  | 16:44 | 16:44 | 16:46 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-02 | 29174 | 40.5194
551 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset |  | 14:46 | 14:46 | 14:48 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-21 | 30867 | 42.8708
552 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 0:16 | 0:16 | 0:19 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-26 | 30825 | 64.2187
553 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 17:27 | 17:27 | 20:30 | 0 | 3.05 | 3.05 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.11731 | WTG Breakdown Maintenance | O2-26 | 30825 | 3917.3437
554 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 17:05 | 17:05 | 17:11 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-15 | 27808 | 115.8667
555 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:12 | 13:12 | 13:14 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-12 | 29548 | 41.0389
556 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 17:41 | 17:41 | 17:47 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-12 | 29548 | 123.1167
557 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 5:40 | 6:46 | 9:35 | 1.1 | 2.8167 | 3.9167 | Attend for WTG stop in Circuit breaker Error (Grid loss without grid loss auxiliary power) so we attend turbine and check Sam data and also check physically and check converter panel and found ACB was trip so check Busbar and its connections and also check power cable and stator and rotor and Also take Busbar but nothing found abnormalities so now we check ACB and its setting with our technical team and set ACB setting also re-tight all connection than reset and take trial than nothing found abnormal so start WTG.(now turbine under observation). | Close | 0.15064 | WTG Breakdown Maintenance | O2-21 | 30867 | 5037.3229
558 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_16 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 10:07 | 10:07 | 10:20 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & started WTG. | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-21 | 30867 | 278.6604
559 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 17:19 | 17:19 | 17:39 | 0 | 0.33333 | 0.33333 | After Temp. down check all perameter than reset and Started Turbine. | Close | 0.012821 | WTG Unscheduled Maintenance | O2-22 | 28077 | 389.9583
560 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:11 | 15:11 | 15:17 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 28832 | 120.1333
561 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:57 | 16:57 | 17:03 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 28037 | 116.8208
562 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Schedule WTG PM |  | 7:24 | 7:24 | 17:41 | 0 | 10.2833 | 10.2833 | WTG stop for YPM activity complated than started WTG. | Close | 0.39551 | WTG Scheduled Maintenance | O2-01 | 17974 | 7701.3597
563 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 17:21 | 17:21 | 20:43 | 0 | 3.3667 | 3.3667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.12949 | WTG Breakdown Maintenance | O2-26 | 30825 | 4324.0625
564 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-04 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset |  | 22:55 | 22:55 | 22:58 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-02 | 29174 | 60.7792
565 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 15:22 | 15:22 | 18:00 | 0 | 2.6333 | 2.6333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.10128 | WTG Breakdown Maintenance | O2-26 | 31214 | 3424.8694
566 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:51 | 18:51 | 20:55 | 0 | 2.0667 | 2.0667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.079487 | WTG Breakdown Maintenance | O2-26 | 31214 | 2687.8722
567 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset |  | 15:26 | 15:26 | 15:28 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-02 | 31559 | 43.8319
568 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:53 | 14:53 | 14:59 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 31214 | 130.0583
569 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:19 | 16:19 | 16:22 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-26 | 31214 | 65.0292
570 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 17:22 | 17:22 | 17:28 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 31214 | 130.0583
571 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 15:28 | 15:28 | 17:57 | 0 | 2.4833 | 2.4833 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.095513 | WTG Breakdown Maintenance | O2-12 | 31332 | 3241.9917
572 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:07 | 19:07 | 20:44 | 0 | 1.6167 | 1.6167 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.062179 | WTG Breakdown Maintenance | O2-12 | 31332 | 2110.5583
573 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_12 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:09 | 15:09 | 15:15 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-14 | 29701 | 123.7542
574 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_17 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Auto reset |  | 15:27 | 15:27 | 15:32 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-22 | 25892 | 89.9028
575 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 18:35 | 18:35 | 18:52 | 0 | 0.28333 | 0.28333 | Checked related error data log then reset & started WTG. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-22 | 25892 | 305.6694
576 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:43 | 16:43 | 16:49 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-24 | 30515 | 127.1458
577 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_22 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 13:06 | 13:06 | 13:18 | 0 | 0.2 | 0.2 | Checked related error data log then reset & started WTG. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-06 | 30904 | 257.5333
578 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-05 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:21 | 14:21 | 14:26 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-01 | 18835 | 65.3993
579 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_01 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Environment |  | 0:09 | 0:09 | 0:27 | 0 | 0.3 | 0.3 | Auto reset | Close | 0.011538 | WTG Unscheduled Maintenance | O2-26 | 10926 | 136.575
580 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 7:43 | 7:43 | 7:58 | 0 | 0.25 | 0.25 | Checked related error data log then reset & started WTG. | Close | 0.0096154 | WTG Breakdown Maintenance | O2-26 | 10926 | 113.8125
581 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_03 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Environment |  | 15:29 | 15:29 | 15:54 | 0 | 0.41667 | 0.41667 | Auto reset | Close | 0.016026 | WTG Unscheduled Maintenance | O2-09 | 15245 | 264.6701
582 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5550 | Low hydraulic oil level | Break down |  | 14:33 | 14:33 | 15:31 | 0 | 0.96667 | 0.96667 | wtg wip | Close | 0.037179 | WTG Breakdown Maintenance | O2-07 | 18793 | 756.9403
583 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5550 | Low hydraulic oil level | Break down |  | 17:51 | 17:51 | 21:27 | 0 | 3.6 | 3.6 | Attend and wtg oil top then reset and started wtg | Close | 0.13846 | WTG Breakdown Maintenance | O2-07 | 18793 | 2818.95
584 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_05 | TQGXIIPL | GEDA | 3.846% | 567 | Pitch too slow BP52 | Break down |  | 0:28 | 0:28 | 0:38 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-02 | 15091 | 104.7986
585 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_05 | TQGXIIPL | GEDA | 3.846% | 2520 | Gen.speed analog<>gear.speed | Break down |  | 15:50 | 15:50 | 15:52 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-02 | 15091 | 20.9597
586 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 22:01 | 22:01 | 22:02 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-04 | 15082 | 10.4736
587 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 0:38 | 0:38 | 1:10 | 0 | 0.53333 | 0.53333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.020513 | WTG Breakdown Maintenance | O2-26 | 10926 | 242.8
588 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6007 | Overload yaw motors group 1 | Auto reset |  | 1:15 | 1:34 | 2:04 | 0.31667 | 0.5 | 0.81667 | Attend and wtg check Releted circuit so found Yaw MPCB TRIP Connection loose after all connection tight then reset and start wtg. | Close | 0.03141 | WTG Breakdown Maintenance | O2-26 | 10926 | 371.7875
589 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:16 | 13:16 | 13:22 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 10926 | 45.525
590 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:33 | 15:33 | 15:54 | 0 | 0.35 | 0.35 | Auto reset | Close | 0.013462 | WTG Unscheduled Maintenance | O2-26 | 10926 | 159.3375
591 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_09 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Environment |  | 15:09 | 15:09 | 15:11 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-03 | 15302 | 21.2528
592 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_10 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Environment |  | 15:13 | 15:13 | 15:19 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-15 | 17961 | 74.8375
593 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:36 | 15:36 | 15:42 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-15 | 17961 | 74.8375
594 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_11 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Environment |  | 15:00 | 15:00 | 15:14 | 0 | 0.23333 | 0.23333 | Auto reset | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-12 | 15671 | 152.3569
595 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_12 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Environment |  | 15:06 | 15:06 | 15:26 | 0 | 0.33333 | 0.33333 | Auto reset | Close | 0.012821 | WTG Unscheduled Maintenance | O2-14 | 16788 | 233.1667
596 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:27 | 11:27 | 11:33 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 16459 | 68.5792
597 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset |  | 15:20 | 15:20 | 15:23 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-10 | 18504 | 38.55
598 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD |  | 1:06 | 1:06 | 15:31 | 0 | 14.4167 | 14.4167 | Attend And check releated circuit so found ACB Tripped so we check all cable check stator and rotor connection check and all fuse check,CT Check troubleshooting WIP | Close | 0.55449 | WTG Breakdown Maintenance | O2-21 | 23651 | 14207.0243
599 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Road issue |  | 20:49 | 20:49 | 24:00 | 0 | 3.1833 | 3.1833 | WTG Road approached issue | OPEN | 0.12244 | WTG Unscheduled Maintenance | O2-21 | 23651 | 3137.0424
600 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_17 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Auto reset |  | 15:21 | 15:21 | 15:26 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-22 | 21281 | 73.8924
601 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_23 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Auto reset |  | 0:12 | 0:12 | 0:15 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-11 | 16459 | 34.2896
602 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_23 | TQGXIIPL | GEDA | 3.846% | 64 | Max. wind speed | Auto reset |  | 15:07 | 15:07 | 15:09 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-11 | 16459 | 22.8597
603 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:32 | 15:32 | 15:38 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 16459 | 68.5792
604 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Major BD |  | 1:03 | 1:03 | 15:31 | 0 | 14.4667 | 14.4667 | Rotor Break Pressure High so attend Turbine and check Related circuit Check HPU all valve and check all Valve setting also check Hydrolic Unit oil level is ok Found than taken trail but same error occurred so Disccusion with Enginnering team and found Accumulator Pressure low so Further reffilling. | Close | 0.55641 | WTG Breakdown Maintenance | O2-20 | 24540 | 14792.1667
605 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Major BD |  | 17:51 | 17:51 | 24:00 | 0 | 6.15 | 6.15 | Rotor Break Pressure High so attend Turbine and check Related circuit Check HPU all valve and check all Valve setting also check Hydrolic Unit oil level is ok Found than taken trail but same error occurred so Disccusion with Enginnering team and found Accumulator Pressure low so Further reffilling. | OPEN | 0.23654 | WTG Breakdown Maintenance | O2-20 | 24540 | 6288.375
606 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_25 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset |  | 14:55 | 14:55 | 15:00 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-01 | 10165 | 35.2951
607 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6012 | Overload yaw motors group 2 | Break down |  | 0:40 | 2:23 | 2:48 | 1.7167 | 0.41667 | 2.1333 | Attend and wtg check Releted circuit so found Yaw MPCB TRIP After on MPCB after all connection tight then reset and start wtg. | Close | 0.082051 | WTG Breakdown Maintenance | O2-01 | 10165 | 903.5556
608 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-06 | O2_26 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down |  | 7:15 | 7:15 | 8:37 | 0 | 1.3667 | 1.3667 | Checked related error data log then reset & started WTG. | Close | 0.052564 | WTG Unscheduled Maintenance | O2-01 | 10165 | 578.8403
609 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_01 | TQGXIIPL | GEDA | 3.846% | 2390 | Brake due to sudden sys.failure | Break down |  | 2:09 | 2:09 | 3:18 | 0 | 1.15 | 1.15 | Let start wtg Due to wtg Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) | Close | 0.044231 | WTG Unscheduled Maintenance | O2-26 | 15166 | 726.7042
610 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 12:20 | 12:20 | 14:18 | 0 | 1.9667 | 1.9667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.075641 | WTG Unscheduled Maintenance | O2-26 | 15166 | 1242.7694
611 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 2:10 | 2:10 | 3:19 | 0 | 1.15 | 1.15 | Late start wtg due to disconnect to scada O2-25 VCB Tripped after charge VCB And connect wtg reset and start wtg | Close | 0.044231 | WTG Unscheduled Maintenance | O2-05 | 16886 | 809.1208
612 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_03 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Major BD |  | 4:50 | 4:50 | 14:55 | 0 | 10.0833 | 10.0833 | We have check in sam Found pitch error also chech in snap and check QA001 CONTACTOR all connection and retight it than check ALL NO/NC Auxiliary switch and found NC &NO switch not working properly so replace all switch and check then have trail taken by turbine after no any abnormal absorb so started wtg. | Close | 0.38782 | WTG Breakdown Maintenance | O2-09 | 15126 | 6355.0208
613 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 2:29 | 2:29 | 3:40 | 0 | 1.1833 | 1.1833 | Late start wtg due to disconnect to scada O2-25 VCB Tripped after charge VCB And connect wtg reset and start wtg | Close | 0.045513 | WTG Unscheduled Maintenance | O2-02 | 16965 | 836.4688
614 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 2:10 | 2:10 | 3:22 | 0 | 1.2 | 1.2 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.046154 | WTG Unscheduled Maintenance | O2-26 | 15166 | 758.3
615 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 2:10 | 2:10 | 3:24 | 0 | 1.2333 | 1.2333 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.047436 | WTG Unscheduled Maintenance | O2-03 | 1852 | 95.1722
616 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 2:10 | 2:10 | 3:28 | 0 | 1.3 | 1.3 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.05 | WTG Unscheduled Maintenance | O2-15 | 14641 | 793.0542
617 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 2:10 | 2:10 | 2:13 | 0 | 0.05 | 0.05 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-12 | 11445 | 23.8438
618 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_11 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 16:58 | 16:58 | 17:28 | 0 | 0.5 | 0.5 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.019231 | WTG Unscheduled Maintenance | O2-12 | 11445 | 238.4375
619 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 2:10 | 2:10 | 2:20 | 0 | 0.16667 | 0.16667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-14 | 14856 | 103.1667
620 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5516 | Rot.br. press. low | Break down |  | 3:43 | 3:43 | 8:40 | 0 | 4.95 | 4.95 | WTG Road approached issue | Close | 0.19038 | WTG Unscheduled Maintenance | O2-14 | 14856 | 3064.05
621 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5516 | Rot.br. press. low | Break down |  | 8:40 | 8:40 | 9:02 | 0 | 0.36667 | 0.36667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) Attend wtg apply hard reboot after check hydrolic presure so ok after trail so ok then reset and started wtg. | Close | 0.014103 | WTG Unscheduled Maintenance | O2-14 | 14856 | 226.9667
622 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_12 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 2:20 | 2:20 | 2:46 | 0 | 0.43333 | 0.43333 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.016667 | WTG Unscheduled Maintenance | O2-14 | 14856 | 268.2333
623 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_12 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 16:58 | 16:58 | 17:29 | 0 | 0.51667 | 0.51667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.019872 | WTG Unscheduled Maintenance | O2-14 | 14856 | 319.8167
624 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5516 | Rot.br. press. low | Break down |  | 17:29 | 17:29 | 17:32 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-14 | 14856 | 30.95
625 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 2:23 | 2:23 | 3:30 | 0 | 1.1167 | 1.1167 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.042949 | WTG Unscheduled Maintenance | O2-11 | 14545 | 676.7465
626 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 16:58 | 16:58 | 17:29 | 0 | 0.51667 | 0.51667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.019872 | WTG Unscheduled Maintenance | O2-11 | 14545 | 313.1215
627 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 2:32 | 2:32 | 3:31 | 0 | 0.98333 | 0.98333 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.037821 | WTG Unscheduled Maintenance | O2-12 | 11445 | 468.9271
628 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_14 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Break down |  | 16:58 | 16:58 | 17:30 | 0 | 0.53333 | 0.53333 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) wip | Close | 0.020513 | WTG Unscheduled Maintenance | O2-12 | 11445 | 254.3333
629 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_14 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Break down |  | 17:30 | 17:30 | 17:57 | 0 | 0.45 | 0.45 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.017308 | WTG Unscheduled Maintenance | O2-12 | 11445 | 214.5938
630 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_15 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 2:10 | 2:10 | 3:29 | 0 | 1.3167 | 1.3167 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.050641 | WTG Unscheduled Maintenance | O2-10 | 14677 | 805.1965
631 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_15 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 16:58 | 16:58 | 17:31 | 0 | 0.55 | 0.55 | Due to WTG Disconnect to SCADA (Heavy rain and lighting at site and multiple activity at site) wip | Close | 0.021154 | WTG Unscheduled Maintenance | O2-10 | 14677 | 336.3479
632 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_15 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Break down |  | 17:35 | 17:35 | 19:13 | 0 | 1.6333 | 1.6333 | Checked related error data log then apply shoft reboot then reset & started WTG. | Close | 0.062821 | WTG Unscheduled Maintenance | O2-10 | 14677 | 998.8514
633 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_16 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD |  | 0:00 | 0:00 | 17:45 | 0 | 17.75 | 17.75 | attend turbine check converter panel in ACB feedback ckt, ACB physical condition, check main Contactor and it's working condition, check further power cable all joints, junction box all joints and taken all power cable IR value, check stator and rotor box and it's connection also taken generator IR value but nothing found abnormal.So taken trail but again error occured.So discuss with our L2 team and Supplier check in converter panel MSC and GSC stack and perform all test and all test pass successful. So after as per supply suggested we have interchange ACB control card with other turbine and Error shift in other turbine. So now O2.16 Started and O2.20 Stop now material arranging work in progress. | Close | 0.68269 | WTG Breakdown Maintenance | O2-21 | 21725 | 16067.4479
634 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 19:26 | 19:26 | 22:35 | 0 | 3.15 | 3.15 | Late wtg start Due to WTG Disconnect to SCADA after Checked related error data log then reset & started WTG. | Close | 0.12115 | WTG Unscheduled Maintenance | O2-22 | 19485 | 2557.4062
635 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 17:15 | 17:15 | 23:29 | 0 | 6.2414 | 6.2414 | wtg manual stop for component testing work wip | open | 0.24005 | WTG Breakdown Maintenance | O2-24 | 10416 | 2708.7628
636 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 2:10 | 2:10 | 3:25 | 0 | 1.25 | 1.25 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.048077 | WTG Unscheduled Maintenance | O2-11 | 14545 | 757.5521
637 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_23 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down |  | 6:28 | 6:28 | 9:01 | 0 | 2.55 | 2.55 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) | Close | 0.098077 | WTG Unscheduled Maintenance | O2-11 | 14545 | 1545.4062
638 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_23 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 16:58 | 16:58 | 17:35 | 0 | 0.61667 | 0.61667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.023718 | WTG Unscheduled Maintenance | O2-11 | 14545 | 373.7257
639 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_24 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Major BD |  | 0:00 | 0:00 | 11:11 | 0 | 11.1833 | 11.1833 | Disccusion with Engineering team and found Accumulator Pressure low so arrange material for anothar side and replace Accumulato then start wtg. | Close | 0.43013 | WTG Unscheduled Maintenance | O2-20 | 19397 | 9038.4632
640 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 16:58 | 16:58 | 17:38 | 0 | 0.66667 | 0.66667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.025641 | WTG Unscheduled Maintenance | O2-01 | 11319 | 314.4167
641 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_25 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down |  | 3:10 | 3:10 | 3:35 | 0 | 0.41667 | 0.41667 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.016026 | WTG Unscheduled Maintenance | O2-01 | 11319 | 196.5104
642 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 12:25 | 12:25 | 12:51 | 0 | 0.43333 | 0.43333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.016667 | WTG Unscheduled Maintenance | O2-01 | 11319 | 204.3708
643 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-07 | O2_26 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down |  | 16:58 | 16:58 | 17:39 | 0 | 0.68333 | 0.68333 | Late wtg start Due to WTG Disconnect to SCADA(Heavy rain and lighting at site and multiple activity at site) after Checked related error data log then reset & started WTG. | Close | 0.026282 | WTG Unscheduled Maintenance | O2-01 | 11319 | 322.2771
644 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-08 | O2_03 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Auto reset |  | 19:00 | 19:00 | 19:03 | 0 | 0.05 | 0.05 | Auto reset. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-09 | 6464 | 13.4667
645 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-08 | O2_13 | TQGXIIPL | GEDA | 3.846% | 578 | Pitch set point slow hold time BP75 | Auto reset |  | 20:11 | 20:11 | 20:13 | 0 | 0.033333 | 0.033333 | Auto reset. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-11 | 7094 | 9.8528
646 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-08 | O2_14 | TQGXIIPL | GEDA | 3.846% | 72 | Outdoor temperature high | Break down |  | 20:13 | 20:13 | 20:34 | 0 | 0.35 | 0.35 | Check temperature value, after temperature normlize started WTG. | Close | 0.013462 | WTG Unscheduled Maintenance | O2-12 | 6716 | 97.9417
647 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-08 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:45 | 15:45 | 16:14 | 0 | 0.48333 | 0.48333 | WTG stopped for material cannibalize work. | Close | 0.01859 | WTG Breakdown Maintenance | O2-21 | 7764 | 156.3583
648 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-08 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset |  | 12:04 | 12:04 | 12:07 | 0 | 0.05 | 0.05 | Auto reset. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-22 | 7733 | 16.1104
649 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-08 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 0:00 | 0:00 | 3:44 | 0 | 3.7333 | 3.7333 | Arrange material than replaced trip unit card and trial takken and started WTG. | Close | 0.14359 | WTG Breakdown Maintenance | O2-24 | 9370 | 1457.5556
650 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-08 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:20 | 15:20 | 16:46 | 0 | 1.4333 | 1.4333 | WTG stopped for material cannibalize work. | Close | 0.055128 | WTG Breakdown Maintenance | O2-24 | 9370 | 559.5972
651 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-08 | O2_23 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down |  | 19:00 | 21:47 | 23:14 | 2.7833 | 1.45 | 4.2333 | Attend wtg check releted circuit so found Blade no 1 1.7 ohm Flat resistor faulty after replace then reset and started wtg. | Close | 0.16282 | WTG Breakdown Maintenance | O2-11 | 7094 | 1251.3028
652 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-08 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Auto reset |  | 18:58 | 18:58 | 19:02 | 0 | 0.066667 | 0.066667 | Auto reset. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-01 | 7575 | 21.0417
653 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 14:21 | 14:21 | 14:23 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-05 | 11663 | 16.1986
654 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 14:25 | 14:25 | 14:27 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-09 | 8780 | 12.1944
655 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 14:38 | 14:38 | 14:41 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | WTG Breakdown Maintenance | O2-07 | 4777 | 9.9521
656 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 14:53 | 14:53 | 14:55 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-02 | 12509 | 17.3736
657 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 14:30 | 14:30 | 14:32 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-21 | 5387 | 7.4819
658 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:12 | 15:12 | 15:25 | 0 | 0.21667 | 0.21667 | WTG Manual stop for Software Updated Work. | Close | 0.0083333 | WTG Breakdown Maintenance | O2-04 | 5316 | 47.9917
659 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:31 | 15:31 | 15:33 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-26 | 9743 | 13.5319
660 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 14:03 | 14:03 | 14:05 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-26 | 9743 | 13.5319
661 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:35 | 15:35 | 15:37 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-03 | 9207 | 12.7875
662 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:38 | 15:38 | 15:51 | 0 | 0.21667 | 0.21667 | WTG Manual stop for Software Updated Work. | Close | 0.0083333 | WTG Breakdown Maintenance | O2-15 | 10040 | 90.6389
663 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_11 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Auto reset |  | 11:11 | 11:11 | 11:16 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-12 | 10322 | 35.8403
664 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:50 | 15:50 | 15:53 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | WTG Breakdown Maintenance | O2-12 | 10322 | 21.5042
665 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:54 | 15:54 | 15:57 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | WTG Breakdown Maintenance | O2-14 | 10289 | 21.4354
666 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:58 | 15:58 | 16:01 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | WTG Breakdown Maintenance | O2-11 | 9372 | 19.525
667 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:02 | 16:02 | 16:06 | 0 | 0.066667 | 0.066667 | WTG Manual stop for Software Updated Work. | Close | 0.0025641 | WTG Breakdown Maintenance | O2-12 | 10322 | 28.6722
668 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:07 | 16:07 | 16:11 | 0 | 0.066667 | 0.066667 | WTG Manual stop for Software Updated Work. | Close | 0.0025641 | WTG Breakdown Maintenance | O2-10 | 9374 | 26.0389
669 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:12 | 16:12 | 16:15 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | WTG Breakdown Maintenance | O2-21 | 5387 | 11.2229
670 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:15 | 16:15 | 16:20 | 0 | 0.083333 | 0.083333 | WTG Manual stop for Software Updated Work. | Close | 0.0032051 | WTG Breakdown Maintenance | O2-07 | 4777 | 16.5868
671 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:16 | 16:16 | 16:29 | 0 | 0.21667 | 0.21667 | WTG Manual stop for Software Updated Work. | Close | 0.0083333 | WTG Breakdown Maintenance | O2-24 | 7052 | 63.6639
672 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:44 | 16:44 | 16:46 | 0 | 0.033333 | 0.033333 | WTG Manual stop for Software Updated Work. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-06 | 6891 | 9.5708
673 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:53 | 16:53 | 16:56 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | WTG Breakdown Maintenance | O2-06 | 6891 | 14.3562
674 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Auto reset |  | 13:12 | 13:12 | 13:15 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Breakdown Maintenance | O2-11 | 9372 | 19.525
675 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:30 | 16:30 | 16:33 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-11 | 9372 | 19.525
676 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_24 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:31 | 16:31 | 16:34 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | WTG Breakdown Maintenance | O2-20 | 6597 | 13.7437
677 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:34 | 16:34 | 16:37 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | WTG Breakdown Maintenance | O2-01 | 9128 | 19.0167
678 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-09 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:34 | 16:34 | 16:37 | 0 | 0.05 | 0.05 | WTG Manual stop for Software Updated Work. | Close | 0.0019231 | WTG Breakdown Maintenance | O2-01 | 9128 | 19.0167
679 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-10 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6210 | Max. cable twistangle | Break down |  | 4:31 | 4:31 | 5:54 | 0 | 1.3833 | 1.3833 | Checked related error data log then apply shoft reboot and removed cable twist then reset & started WTG. | Close | 0.053205 | WTG Breakdown Maintenance | O2-26 | 14169 | 816.6854
680 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-10 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 11:08 | 11:08 | 14:45 | 0 | 3.6167 | 3.6167 | Attend and wtg Nacell Position Sensor fault warning and repeated error (wind Dir.diff.Level 1) so check and found wind sensor alignment not proper so wind sensor aligment properly done and also check axis 1 flat resistor faulty so replace it and check yaw releted repeated error, check and found yaw sensor switch setting is not proper so correct it then reset and started wtg. | Close | 0.1391 | WTG Breakdown Maintenance | O2-26 | 14169 | 2135.1896
681 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-10 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 12:04 | 12:04 | 13:00 | 0 | 0.93333 | 0.93333 | Attend and check ckt then blade axis 2 chopper resistor found faulty so replacement work WIP | Close | 0.035897 | WTG Breakdown Maintenance | O2-22 | 15068 | 585.9778
682 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-10 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:39 | 16:39 | 17:15 | 0 | 0.6 | 0.6 | After grid time replace chopper resistor work done after trail then reset and started wtg | Close | 0.023077 | WTG Breakdown Maintenance | O2-22 | 15068 | 376.7
683 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-10 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down |  | 3:05 | 3:42 | 5:10 | 0.61667 | 1.4667 | 2.0833 | Attend and wtg check hydraulic oil so ok after replace 9.1 valve after check hydraulic pressure values so ok then reset and started wtg. | Close | 0.080128 | WTG Breakdown Maintenance | O2-11 | 13194 | 1145.3125
684 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-11 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 16:43 | 16:43 | 17:16 | 0 | 0.55 | 0.55 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.021154 | WTG Unscheduled Maintenance | O2-26 | 10027 | 229.7854
685 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-11 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others |  | 17:26 | 17:26 | 17:42 | 0 | 0.26667 | 0.26667 | Late start wtg dut to BOP Suggestions after reset and started wtg | Close | 0.010256 | WTG Breakdown Maintenance | O2-07 | 12314 | 136.8222
686 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-11 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others |  | 17:26 | 17:26 | 17:38 | 0 | 0.2 | 0.2 | Late start wtg dut to BOP Suggestions after reset and started wtg | Close | 0.0076923 | WTG Breakdown Maintenance | O2-21 | 9404 | 78.3667
687 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-11 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others |  | 17:26 | 17:26 | 17:41 | 0 | 0.25 | 0.25 | Late start wtg dut to BOP Suggestions after reset and started wtg | Close | 0.0096154 | WTG Breakdown Maintenance | O2-04 | 14944 | 155.6667
688 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-11 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Break down |  | 18:23 | 18:23 | 24:00 | 0 | 5.6167 | 5.6167 | Attend wtg check hydralic unit and check all valve so ok after check accumulator both so found accumulator Pressure low so wtg WIP | OPEN | 0.21603 | WTG Breakdown Maintenance | O2-14 | 10415 | 2437.3993
689 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-11 | O2_16 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down |  | 17:26 | 17:26 | 18:15 | 0 | 0.81667 | 0.81667 | Attend wtg check Pitch data AND Check all blade angle so ok After trail so ok then reset and started wtg. | Close | 0.03141 | WTG Breakdown Maintenance | O2-21 | 9404 | 319.9972
690 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-11 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Others |  | 17:26 | 17:26 | 18:01 | 0 | 0.58333 | 0.58333 | Late start wtg dut to BOP Suggestions after reset and started wtg | Close | 0.022436 | WTG Breakdown Maintenance | O2-06 | 12050 | 292.8819
691 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-11 | O2_19 | TQGXIIPL | GEDA | 3.846% | 660 | Limit switches error 91° | Break down |  | 19:21 | 19:21 | 21:58 | 0 | 2.6167 | 2.6167 | Check Data in SCADA so found blade 1 91 limit switch connection loose so tight it then reset and started wtg. | Close | 0.10064 | WTG Breakdown Maintenance | O2-07 | 12314 | 1342.5681
692 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-11 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others |  | 17:26 | 17:26 | 17:40 | 0 | 0.23333 | 0.23333 | Late start wtg dut to BOP Suggestions after reset and started wtg | Close | 0.0089744 | WTG Breakdown Maintenance | O2-24 | 10039 | 97.6014
693 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-11 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Others |  | 17:26 | 17:26 | 18:00 | 0 | 0.56667 | 0.56667 | Late start wtg dut to BOP Suggestions after reset and started wtg | Close | 0.021795 | WTG Breakdown Maintenance | O2-06 | 12050 | 284.5139
694 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-11 | O2_23 | TQGXIIPL | GEDA | 3.846% | 159 | SLC SF emergency stop | Break down |  | 14:07 | 14:07 | 15:54 | 0 | 1.7833 | 1.7833 | Check error related CKT Found Bottom Emergency button connection found loose in BOB FS2 Panel so correct it then reset and started wtg | Close | 0.06859 | WTG Breakdown Maintenance | O2-11 | 10160 | 754.9444
695 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-11 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 16:44 | 16:44 | 17:15 | 0 | 0.51667 | 0.51667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.019872 | WTG Breakdown Maintenance | O2-01 | 11784 | 253.6833
696 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-12 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 15:41 | 15:41 | 15:56 | 0 | 0.25 | 0.25 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.0096154 | WTG Breakdown Maintenance | O2-26 | 13322 | 138.7708
697 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-12 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:10 | 16:10 | 16:16 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 13322 | 55.5083
698 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-12 | O2_12 | TQGXIIPL | GEDA | 3.846% | 5506 | Rot.br. press. high | Break down |  | 0:00 | 0:00 | 2:53 | 0 | 2.8833 | 2.8833 | After Filling Nitrogen accumulator pressure set than trail taken and started wtg | Close | 0.1109 | WTG Breakdown Maintenance | O2-14 | 11238 | 1350.1208
699 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-12 | O2_20 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset |  | 10:43 | 10:43 | 10:45 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-24 | 10435 | 14.4931
700 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-12 | O2_22 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Auto reset |  | 17:42 | 17:42 | 17:45 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-06 | 11228 | 23.3917
701 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-12 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 15:42 | 15:42 | 15:56 | 0 | 0.23333 | 0.23333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.0089744 | WTG Breakdown Maintenance | O2-01 | 13179 | 128.1292
702 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-13 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR |  | 9:04 | 9:04 | 18:00 | 0 | 8.9333 | 8.9333 | WTG manual stop for Slipring WTR 646,658,629,633 work. | Close | 0.34359 | WTG Breakdown Maintenance | O2-26 | 15898 | 5917.5889
703 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-13 | O2_05 | TQGXIIPL | GEDA | 3.846% | 2521 | Gen.sp.analog <<>> gearb.sp. | Auto reset |  | 14:58 | 14:58 | 15:01 | 0 | 0.05 | 0.05 | AUTO Reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-02 | 18876 | 39.325
704 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-13 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 20:28 | 20:28 | 20:55 | 0 | 0.45 | 0.45 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.017308 | WTG Unscheduled Maintenance | O2-01 | 15857 | 297.3188
705 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-14 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR |  | 17:01 | 17:27 | 17:57 | 0.43333 | 0.5 | 0.93333 | WTG Manual stop for WTR 656 work. | Close | 0.035897 | WTG Unscheduled Maintenance | O2-26 | 15454 | 600.9889
706 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-14 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Auto reset |  | 8:21 | 8:21 | 8:25 | 0 | 0.066667 | 0.066667 | AUTO Reset | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-02 | 18583 | 51.6194
707 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-14 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:16 | 19:16 | 20:25 | 0 | 1.15 | 1.15 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.044231 | WTG Unscheduled Maintenance | O2-02 | 18583 | 890.4354
708 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-14 | O2_09 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Auto reset |  | 15:42 | 15:42 | 15:45 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-03 | 14080 | 29.3333
709 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-14 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6690 | Icing (stop) | Auto reset |  | 15:48 | 15:48 | 15:52 | 0 | 0.066667 | 0.066667 | Auto Reset | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-03 | 14080 | 39.1111
710 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-14 | O2_09 | TQGXIIPL | GEDA | 3.846% | 88 | Outs.temp. nacelle implaus. | Break down |  | 16:18 | 16:18 | 17:05 | 0 | 0.78333 | 0.78333 | Checked related error data log then reset & start WTG. | Close | 0.030128 | WTG Unscheduled Maintenance | O2-03 | 14080 | 459.5556
711 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-14 | O2_10 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down |  | 19:03 | 19:03 | 19:16 | 0 | 0.21667 | 0.21667 | Checked related error data log then reset & start WTG. | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-15 | 15173 | 136.9785
712 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-14 | O2_12 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 10:37 | 10:37 | 10:38 | 0 | 0.016667 | 0.016667 | Auto Reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-14 | 14700 | 10.2083
713 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-14 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR |  | 14:55 | 14:55 | 16:37 | 0 | 1.7 | 1.7 | WTG Manual stop for WTR 629,658,656 work. | Close | 0.065385 | WTG Unscheduled Maintenance | O2-11 | 14181 | 1004.4875
714 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-14 | O2_23 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down |  | 19:00 | 19:00 | 19:15 | 0 | 0.25 | 0.25 | Checked related error data log then reset & start WTG. | Close | 0.0096154 | WTG Unscheduled Maintenance | O2-11 | 14181 | 147.7188
715 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-14 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:01 | 19:01 | 19:17 | 0 | 0.26667 | 0.26667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-01 | 16319 | 181.3222
716 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-14 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:24 | 19:24 | 20:00 | 0 | 0.6 | 0.6 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.023077 | WTG Unscheduled Maintenance | O2-01 | 16319 | 407.975
717 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-15 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 18:27 | 18:27 | 18:33 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 11056 | 46.0667
718 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-15 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 3:03 | 3:03 | 3:36 | 0 | 0.55 | 0.55 | Checked related error data log then reset & start WTG. | Close | 0.021154 | WTG Unscheduled Maintenance | O2-02 | 13755 | 315.2188
719 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-15 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR |  | 10:59 | 10:59 | 18:34 | 0 | 7.5833 | 7.5833 | WTG Manual stop for WTR 646,633,656,658,629 work. | Close | 0.29167 | WTG Breakdown Maintenance | O2-02 | 13755 | 4346.1979
720 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-15 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Major BD |  | 2:47 | 2:47 | 12:54 | 0 | 10.1167 | 10.1167 | attend and check data in Sam and also conver data and default restore than check physicaly ACB and it's settings and than check CT connection and take it's Ohm value than value found ok so check ACB setting and set them and also control card relay supply check and rebooted and reset as per Engineering team instruction than reset and start wtg.Now Turbine under observation. | Close | 0.3891 | WTG Breakdown Maintenance | O2-04 | 10727 | 4521.7285
721 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-15 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Break down |  | 22:20 | 22:20 | 24:00 | 0 | 1.6664 | 1.6664 | atten WTG and found ACB smart trip unit is malfunctioning so we interchange for O2-20 WIP. | Close | 0.064092 | WTG Breakdown Maintenance | O2-04 | 10727 | 744.8064
722 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-15 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:50 | 19:50 | 20:12 | 0 | 0.36667 | 0.36667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.014103 | WTG Unscheduled Maintenance | O2-26 | 11056 | 168.9111
723 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-15 | O2_15 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Break down |  | 17:03 | 17:03 | 17:06 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-10 | 9261 | 19.2937
724 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-15 | O2_16 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down |  | 18:36 | 18:36 | 18:39 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-21 | 8783 | 18.2979
725 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-15 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:43 | 19:43 | 20:18 | 0 | 0.58333 | 0.58333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.022436 | WTG Unscheduled Maintenance | O2-11 | 9679 | 235.2535
726 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 17:03 | 17:03 | 17:06 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-26 | 17902 | 37.2958
727 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:24 | 18:24 | 19:00 | 0 | 0.6 | 0.6 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.023077 | WTG Unscheduled Maintenance | O2-26 | 17902 | 447.55
728 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_02 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 16:47 | 16:47 | 17:03 | 0 | 0.26667 | 0.26667 | Checked related error data log then reset & start WTG. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-05 | 17636 | 195.9556
729 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_05 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 17:09 | 17:09 | 17:15 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-02 | 18473 | 76.9708
730 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 17:56 | 17:56 | 17:58 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-02 | 18473 | 25.6569
731 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Major BD |  | 0:00 | 0:00 | 16:40 | 0 | 16.6667 | 16.6667 | ACB smart trip unit Material arrangement for another site WIP | OPEN | 0.64103 | WTG Breakdown Maintenance | O2-04 | 13328 | 9255.5556
732 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Major BD |  | 19:11 | 19:11 | 24:00 | 0 | 4.8164 | 4.8164 | ACB smart trip unit Material arrangement for another site WIP | OPEN | 0.18525 | WTG Breakdown Maintenance | O2-04 | 13328 | 2674.7013
733 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6690 | Icing (stop) | Major BD |  | 15:17 | 15:17 | 24:00 | 0 | 8.7164 | 8.7164 | Turbine stop in icing (Stop) Error Occurred.But at that time turbine running shown in Fleetpro and status as online but physical in breakdown.Due to data freeze from the server so turbine stop. | Close | 0.33525 | WTG Unscheduled Maintenance | O2-03 | 17202 | 6247.4717
734 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_11 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Auto reset |  | 16:48 | 16:48 | 16:50 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-12 | 16669 | 23.1514
735 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_11 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 18:00 | 18:00 | 18:08 | 0 | 0.13333 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-12 | 16669 | 92.6056
736 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR |  | 10:53 | 10:53 | 13:08 | 0 | 2.25 | 2.25 | WTG Manual stop for WTR 633,656,658,629 work. | Close | 0.086538 | WTG Scheduled Maintenance | O2-11 | 17201 | 1612.5938
737 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_13 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Auto reset |  | 16:44 | 16:44 | 16:46 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-11 | 17201 | 23.8903
738 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:23 | 18:23 | 18:27 | 0 | 0.066667 | 0.066667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-11 | 17201 | 47.7806
739 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 0:57 | 0:57 | 1:44 | 0 | 0.78333 | 0.78333 | wtg manual stop for material cannibalize work | Close | 0.030128 | WTG Breakdown Maintenance | O2-24 | 15031 | 490.5951
740 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_20 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down |  | 18:41 | 18:41 | 18:42 | 0 | 0.016667 | 0.016667 | after grid resume error occurs so Checked related error data log then reset & start WTG. | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-24 | 15031 | 10.4382
741 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1731 | Oil temperature gearbox input high | Break down |  | 4:39 | 4:39 | 4:50 | 0 | 0.18333 | 0.18333 | Checked related error data log then found sensor is malfunctioning so apply shoft reboot then reset & start WTG. | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-11 | 17201 | 131.3965
742 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_23 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset |  | 17:53 | 17:53 | 17:54 | 0 | 0.016667 | 0.016667 | Auto Reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-11 | 17201 | 11.9451
743 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-16 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 18:34 | 18:34 | 19:01 | 0 | 0.45 | 0.45 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.017308 | WTG Unscheduled Maintenance | O2-01 | 15323 | 287.3062
744 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-17 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 9:28 | 9:28 | 9:31 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-02 | 13841 | 28.8354
745 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-17 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Major BD |  | 0:00 | 0:00 | 6:44 | 0 | 6.7333 | 6.7333 | ACB smart trip unit Material arrangement for another site WIP | Close | 0.25897 | WTG Breakdown Maintenance | O2-04 | 14208 | 3986.1333
746 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-17 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3800 | Circuit breaker | Major BD |  | 6:57 | 6:57 | 17:50 | 0 | 10.8833 | 10.8833 | ACB smart trip unit Material arrangement for another site then replace it then start wtg. | Close | 0.41859 | WTG Breakdown Maintenance | O2-04 | 14208 | 6442.9333
747 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-17 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 13:19 | 13:19 | 13:25 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 12529 | 52.2042
748 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-17 | O2_11 | TQGXIIPL | GEDA | 3.846% | 7002 | Task runtime failure 5ms | Break down |  | 19:00 | 19:00 | 19:14 | 0 | 0.23333 | 0.23333 | Checked related error data log then reset & start WTG. | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-12 | 12234 | 118.9417
749 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-17 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR |  | 15:21 | 15:21 | 16:16 | 0 | 0.91667 | 0.91667 | WTG Manual stop for WTR 633,656,658,629 work. | Close | 0.035256 | WTG Breakdown Maintenance | O2-07 | 6613 | 252.5799
750 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-17 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6690 | Icing (stop) | Major BD |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | Turbine stop in icing (Stop) Error Occurred.But at that time turbine running shown in Fleetpro and status as online but physical in breakdown.Due to data freeze from the server so turbine stop. | Close | 0.92307 | WTG Unscheduled Maintenance | O2-03 | 13636 | 13635.8422
751 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-18 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 21:00 | 21:00 | 21:02 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-04 | 13552 | 18.8222
752 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-18 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6690 | Icing (stop) | Major BD |  | 0:00 | 0:00 | 7:34 | 0 | 7.5667 | 7.5667 | Turbine stop in icing (Stop) Error Occurred.But at that time turbine running shown in Fleetpro and status as online but physical in breakdown.Due to data freeze from the server so turbine stop. So cannected wtg (Farm) reset then start WTG. | Close | 0.29103 | WTG Unscheduled Maintenance | O2-03 | 12694 | 4002.1361
753 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-18 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1130 | Acceleration detector drivetrain | Auto reset |  | 2:36 | 2:36 | 2:38 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-14 | 11662 | 16.1972
754 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-18 | O2_15 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Break down |  | 12:26 | 13:33 | 13:56 | 1.1167 | 0.38333 | 1.5 | after grid resume error is occurs so We have check in SAM error related data then attend turbine check blade 02 in converter side connection and found loose connection so re tight properly then started Turbine. | Close | 0.057692 | WTG Breakdown Maintenance | O2-10 | 13272 | 829.5
755 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-18 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 13:09 | 13:09 | 13:15 | 0 | 0.1 | 0.1 | Checked related error data log then reset & start WTG. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 14126 | 58.8583
756 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-18 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:47 | 15:47 | 15:48 | 0 | 0.016667 | 0.016667 | Auto Reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-11 | 12398 | 8.6097
757 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-26 | 14378 | 99.8472
758 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-05 | 16621 | 115.4236
759 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-09 | 15728 | 109.2222
760 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-02 | 18002 | 125.0139
761 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 1:45 | 1:45 | 1:47 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-04 | 16163 | 22.4486
762 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-26 | 14378 | 99.8472
763 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-03 | 13334 | 92.5972
764 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-15 | 13808 | 95.8889
765 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-12 | 13600 | 94.4444
766 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-14 | 14141 | 98.2014
767 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-11 | 12657 | 87.8958
768 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-12 | 13600 | 94.4444
769 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_15 | TQGXIIPL | GEDA | 3.846% | 4555 | Tower accel. difference | Auto reset |  | 3:05 | 3:05 | 3:11 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-10 | 14496 | 60.4
770 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-10 | 14496 | 100.6667
771 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 12:42 | 12:42 | 15:00 | 0 | 2.3 | 2.3 | Attend Wtg and Anomaly related work like Blade calibration and ultrasonic value found deviation so alignment done than occurred error Battery under voltage/over voltage so check and found axis 3 flat resistor faulty so arrenge it and replace. | Close | 0.088462 | WTG Breakdown Maintenance | O2-06 | 15698 | 1504.3917
772 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR |  | 15:00 | 15:00 | 18:05 | 0 | 3.0833 | 3.0833 | WTR 656,658,629 and 633 performing work done then start wtg. | Close | 0.11859 | WTG Breakdown Maintenance | O2-06 | 15698 | 2016.7569
773 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-11 | 12657 | 87.8958
774 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-01 | 15558 | 108.0417
775 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-19 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 17:30 | 17:30 | 17:40 | 0 | 0.16667 | 0.16667 | WTG Manual stop for Feeder#1 Shutdown taking by BOP team but Feeder#1 Shutdown postponed due to ROW issue. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-01 | 15558 | 108.0417
776 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-20 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 17:02 | 17:02 | 17:11 | 0 | 0.15 | 0.15 | Checked related error data log then reset & start WTG. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-07 | 12687 | 79.2937
777 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-20 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:01 | 13:01 | 13:07 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 13934 | 58.0583
778 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-20 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 17:13 | 17:13 | 18:15 | 0 | 1.0333 | 1.0333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.039744 | WTG Unscheduled Maintenance | O2-26 | 14103 | 607.2125
779 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-20 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 17:35 | 17:35 | 17:41 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-15 | 14995 | 62.4792
780 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-20 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 8:54 | 8:54 | 11:00 | 0 | 2.1 | 2.1 | Attend and Wtg check Converter 230 V AC Supply check UPS connection check Feedback connection check all connection tight after trail so ok then Reset and started Wtg. | Close | 0.080769 | WTG Breakdown Maintenance | O2-14 | 13779 | 1205.6625
781 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-20 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | WTR |  | 11:32 | 11:32 | 13:11 | 0 | 1.65 | 1.65 | WTG Manual stop for WTR 656,658,633 and 629 Performing and started Wtg. | Close | 0.063462 | WTG Breakdown Maintenance | O2-14 | 13779 | 947.3063
782 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-20 | O2_13 | TQGXIIPL | GEDA | 3.846% | 1510 | Low gearbox oil pressure | Break down |  | 21:29 | 21:29 | 21:32 | 0 | 0.05 | 0.05 | Checked related error data log then reset & start WTG. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-11 | 12633 | 26.3187
783 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-20 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 15:55 | 15:55 | 15:57 | 0 | 0.033333 | 0.033333 | Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-22 | 19816 | 27.5222
784 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-20 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 17:16 | 17:16 | 18:10 | 0 | 0.9 | 0.9 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.034615 | WTG Unscheduled Maintenance | O2-01 | 13354 | 500.775
785 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-20 | O2_26 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 8:54 | 8:54 | 9:11 | 0 | 0.28333 | 0.28333 | after grid resume error is occurs so Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-01 | 13354 | 157.6514
786 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_01 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down |  | 19:16 | 19:16 | 19:37 | 0 | 0.35 | 0.35 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.013462 | WTG Unscheduled Maintenance | O2-26 | 5324 | 77.6417
787 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:16 | 19:16 | 20:00 | 0 | 0.73333 | 0.73333 | After Grid charge RFO signal coming than Start WTG. | Close | 0.028205 | WTG Unscheduled Maintenance | O2-05 | 6797 | 207.6861
788 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:16 | 19:16 | 19:56 | 0 | 0.66667 | 0.66667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.025641 | WTG Unscheduled Maintenance | O2-09 | 5730 | 159.1667
789 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 19:10 | 19:10 | 20:30 | 0 | 1.3333 | 1.3333 | after grid resume error is occurs so Checked related error data log then reset & start WTG. | Close | 0.051282 | WTG Unscheduled Maintenance | O2-07 | 8259 | 458.8333
790 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 19:16 | 19:16 | 20:03 | 0 | 0.78333 | 0.78333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.030128 | WTG Unscheduled Maintenance | O2-02 | 6870 | 224.2292
791 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:10 | 19:10 | 19:58 | 0 | 0.8 | 0.8 | After Grid charge RFO signal coming than Start WTG. | Close | 0.030769 | WTG Unscheduled Maintenance | O2-21 | 9422 | 314.0667
792 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_07 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down |  | 19:10 | 19:10 | 20:31 | 0 | 1.35 | 1.35 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.051923 | WTG Unscheduled Maintenance | O2-04 | 8746 | 491.9625
793 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 19:16 | 19:16 | 19:40 | 0 | 0.4 | 0.4 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.015385 | WTG Unscheduled Maintenance | O2-26 | 5324 | 88.7333
794 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 19:16 | 19:16 | 19:42 | 0 | 0.43333 | 0.43333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.016667 | WTG Unscheduled Maintenance | O2-03 | 4988 | 90.0611
795 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 19:16 | 19:16 | 19:42 | 0 | 0.43333 | 0.43333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.016667 | WTG Unscheduled Maintenance | O2-15 | 6055 | 109.3264
796 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_11 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down |  | 19:16 | 19:16 | 19:43 | 0 | 0.45 | 0.45 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.017308 | WTG Unscheduled Maintenance | O2-12 | 5048 | 94.65
797 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:16 | 19:16 | 19:59 | 0 | 0.71667 | 0.71667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.027564 | WTG Unscheduled Maintenance | O2-14 | 4919 | 146.8868
798 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_14 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down |  | 19:16 | 19:16 | 19:45 | 0 | 0.48333 | 0.48333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.01859 | WTG Unscheduled Maintenance | O2-12 | 5048 | 101.6611
799 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 19:16 | 19:16 | 19:45 | 0 | 0.48333 | 0.48333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.01859 | WTG Unscheduled Maintenance | O2-10 | 4705 | 94.7535
800 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_16 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down |  | 19:10 | 20:25 | 20:45 | 1.25 | 0.33333 | 1.5833 | after grid resume error is occurs so attend Checked related error data log then apply hard reboot then reset & start WTG | Close | 0.060897 | WTG Breakdown Maintenance | O2-21 | 9422 | 621.5903
801 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_17 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down |  | 19:10 | 19:10 | 19:46 | 0 | 0.6 | 0.6 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.023077 | WTG Unscheduled Maintenance | O2-22 | 13881 | 347.025
802 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 19:10 | 21:11 | 21:26 | 2.0167 | 0.25 | 2.2667 | after grid resume error is occurs so attend Checked related error data log then apply hard reboot then reset & start WTG | Close | 0.087179 | WTG Breakdown Maintenance | O2-06 | 12064 | 1139.3778
803 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 19:10 | 19:10 | 20:32 | 0 | 1.3667 | 1.3667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.052564 | WTG Unscheduled Maintenance | O2-07 | 8259 | 470.3042
804 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_20 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down |  | 19:10 | 19:10 | 19:48 | 0 | 0.63333 | 0.63333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.024359 | WTG Unscheduled Maintenance | O2-24 | 7917 | 208.9208
805 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:10 | 19:10 | 20:51 | 0 | 1.6833 | 1.6833 | After Grid charge RFO signal coming than Start WTG. | Close | 0.064744 | WTG Unscheduled Maintenance | O2-06 | 12064 | 846.1556
806 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 19:10 | 19:10 | 20:17 | 0 | 1.1167 | 1.1167 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.042949 | WTG Unscheduled Maintenance | O2-06 | 12064 | 561.3111
807 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:16 | 19:16 | 19:57 | 0 | 0.68333 | 0.68333 | After Grid charge RFO signal coming than Start WTG. | Close | 0.026282 | WTG Unscheduled Maintenance | O2-11 | 4932 | 140.425
808 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_24 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down |  | 19:10 | 19:10 | 19:50 | 0 | 0.66667 | 0.66667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.025641 | WTG Unscheduled Maintenance | O2-20 | 7738 | 214.9444
809 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 19:16 | 19:16 | 19:51 | 0 | 0.58333 | 0.58333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.022436 | WTG Unscheduled Maintenance | O2-01 | 5803 | 141.0451
810 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-21 | O2_26 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down |  | 19:16 | 19:16 | 20:02 | 0 | 0.76667 | 0.76667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.029487 | WTG Unscheduled Maintenance | O2-01 | 5803 | 185.3736
811 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-22 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:01 | 19:01 | 19:42 | 0 | 0.68333 | 0.68333 | After Grid charge RFO signal coming than Start WTG. | Close | 0.026282 | WTG Unscheduled Maintenance | O2-05 | 5814 | 165.5375
812 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-22 | O2_03 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:01 | 19:01 | 19:40 | 0 | 0.65 | 0.65 | After Grid charge RFO signal coming than Start WTG. | Close | 0.025 | WTG Unscheduled Maintenance | O2-09 | 4651 | 125.9646
813 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-22 | O2_03 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 19:43 | 19:43 | 20:07 | 0 | 0.4 | 0.4 | Checked related error data log then apply shoft reboot then reset & start WTG | Close | 0.015385 | WTG Unscheduled Maintenance | O2-09 | 4651 | 77.5167
814 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-22 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 19:01 | 19:01 | 19:23 | 0 | 0.36667 | 0.36667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.014103 | WTG Unscheduled Maintenance | O2-02 | 4261 | 65.0986
815 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-22 | O2_08 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down |  | 19:01 | 19:01 | 19:32 | 0 | 0.51667 | 0.51667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.019872 | WTG Unscheduled Maintenance | O2-26 | 3271 | 70.4174
816 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-22 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 11:23 | 11:23 | 11:49 | 0 | 0.43333 | 0.43333 | after grid resume error is occurs so Checked related error data log then reset & start WTG(Late start due to disconnected from scada due to jumer open at O2 14 ) | Close | 0.016667 | WTG Unscheduled Maintenance | O2-15 | 5244 | 94.6833
817 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-22 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:01 | 19:01 | 19:42 | 0 | 0.68333 | 0.68333 | After Grid charge RFO signal coming than Start WTG. | Close | 0.026282 | WTG Unscheduled Maintenance | O2-14 | 4869 | 138.6313
818 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-22 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 11:23 | 11:23 | 11:49 | 0 | 0.43333 | 0.43333 | after grid resume error is occurs so Checked related error data log then reset & start WTG(Late start due to disconnected from scada due to jumer open at O2 14 ) | Close | 0.016667 | WTG Unscheduled Maintenance | O2-10 | 4928 | 88.9778
819 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-22 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:01 | 19:01 | 19:47 | 0 | 0.76667 | 0.76667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.029487 | WTG Unscheduled Maintenance | O2-11 | 4947 | 158.0292
820 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-22 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 19:01 | 19:01 | 19:55 | 0 | 0.9 | 0.9 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.034615 | WTG Unscheduled Maintenance | O2-01 | 5325 | 199.6875
821 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-22 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:01 | 19:01 | 19:41 | 0 | 0.66667 | 0.66667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.025641 | WTG Unscheduled Maintenance | O2-01 | 5325 | 147.9167
822 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_03 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Auto reset |  | 17:23 | 17:23 | 17:26 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-09 | 13305 | 27.7187
823 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3555 | Current asymmetry | Auto reset |  | 9:24 | 9:24 | 9:35 | 0 | 0.18333 | 0.18333 | Auto Reset | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-26 | 12236 | 93.4694
824 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 17:40 | 17:40 | 17:57 | 0 | 0.28333 | 0.28333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-26 | 12236 | 144.4528
825 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:22 | 19:22 | 19:43 | 0 | 0.35 | 0.35 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.013462 | WTG Unscheduled Maintenance | O2-26 | 12236 | 178.4417
826 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_10 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Auto reset |  | 17:23 | 17:23 | 17:24 | 0 | 0.016667 | 0.016667 | Auto Reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-15 | 13871 | 9.6326
827 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 19:50 | 19:50 | 19:52 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-11 | 15506 | 21.5361
828 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3532 | Min. voltage cut in | Auto reset |  | 7:11 | 7:11 | 7:12 | 0 | 0.016667 | 0.016667 | Auto Reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-10 | 12638 | 8.7764
829 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 19:42 | 19:42 | 19:46 | 0 | 0.066667 | 0.066667 | Checked related error data log then reset & start WTG. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-21 | 12398 | 34.4389
830 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 20:19 | 20:19 | 20:21 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-22 | 14801 | 20.5569
831 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_18 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset |  | 17:08 | 17:08 | 17:10 | 0 | 0.033333 | 0.033333 | Auto Reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-06 | 14664 | 20.3667
832 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_19 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Auto reset |  | 19:47 | 19:47 | 19:50 | 0 | 0.05 | 0.05 | Auto Reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-07 | 12284 | 25.5917
833 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 17:32 | 17:32 | 17:34 | 0 | 0.033333 | 0.033333 | Checked related error data log then reset & start WTG. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-06 | 14664 | 20.3667
834 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 17:39 | 17:39 | 17:57 | 0 | 0.3 | 0.3 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.011538 | WTG Unscheduled Maintenance | O2-01 | 13668 | 170.85
835 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-23 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:20 | 19:20 | 19:44 | 0 | 0.4 | 0.4 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.015385 | WTG Unscheduled Maintenance | O2-01 | 13668 | 227.8
836 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-24 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 18:28 | 18:28 | 19:08 | 0 | 0.66667 | 0.66667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.025641 | WTG Unscheduled Maintenance | O2-05 | 32935 | 914.8611
837 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-24 | O2_03 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down |  | 10:35 | 10:35 | 10:52 | 0 | 0.28333 | 0.28333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.010897 | WTG Unscheduled Maintenance | O2-09 | 27378 | 323.2125
838 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-24 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:14 | 19:14 | 24:00 | 0 | 4.7664 | 4.7664 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | open | 0.18332 | WTG Unscheduled Maintenance | O2-26 | 25631 | 5090.3047
839 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-24 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:56 | 14:56 | 15:01 | 0 | 0.083333 | 0.083333 | Auto Reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-12 | 14646 | 50.8542
840 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-24 | O2_12 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 18:46 | 18:46 | 19:18 | 0 | 0.53333 | 0.53333 | after grid resume error is occurs so attend Checked related error data log then apply hard reboot then reset & start WTG | Close | 0.020513 | WTG Breakdown Maintenance | O2-14 | 28337 | 629.7111
841 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-24 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:23 | 19:23 | 22:27 | 0 | 3.0667 | 3.0667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.11795 | WTG Unscheduled Maintenance | O2-14 | 28337 | 3620.8389
842 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-24 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 22:48 | 22:48 | 24:00 | 0 | 1.1997 | 1.1997 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | open | 0.046143 | WTG Unscheduled Maintenance | O2-14 | 28337 | 1416.522
843 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-24 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:27 | 16:27 | 16:33 | 0 | 0.1 | 0.1 | Auto Reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-12 | 14646 | 61.025
844 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-24 | O2_15 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Break down |  | 18:28 | 18:28 | 18:49 | 0 | 0.35 | 0.35 | after grid resume error is occurs so attend Checked related error data log then apply shoft reboot then reset & start WTG | Close | 0.013462 | WTG Unscheduled Maintenance | O2-10 | 28918 | 421.7208
845 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-24 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1731 | Oil temperature gearbox input high | Break down |  | 11:24 | 11:24 | 11:41 | 0 | 0.28333 | 0.28333 | Checked related error data log then apply shoft reboot then reset & start WTG. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-11 | 28336 | 334.5222
846 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-24 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 7:34 | 7:34 | 7:58 | 0 | 0.4 | 0.4 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.015385 | WTG Unscheduled Maintenance | O2-01 | 27867 | 464.45
847 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-24 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 18:28 | 18:28 | 19:08 | 0 | 0.66667 | 0.66667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.025641 | WTG Unscheduled Maintenance | O2-01 | 27867 | 774.0833
848 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-25 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 8:22 | 8:23 | 8:23 | 0.016667 | 0 | 0.016667 | Auto Reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-26 | 33380 | 23.1806
849 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-25 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 16:57 | 17:40 | 17:40 | 0.71667 | 0 | 0.71667 | After Grid charge RFO signal coming than Start WTG. | Close | 0.027564 | WTG Breakdown Maintenance | O2-05 | 30576 | 913.0333
850 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-25 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:37 | 15:54 | 15:54 | 0.28333 | 0 | 0.28333 | WTG stopped for material cannibalize work. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-21 | 19043 | 224.8132
851 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-25 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 0:00 | 3:28 | 3:28 | 3.4667 | 0 | 3.4667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.13333 | WTG Unscheduled Maintenance | O2-26 | 33380 | 4821.5556
852 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-25 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 7:33 | 8:40 | 8:40 | 1.1167 | 0 | 1.1167 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.042949 | WTG Unscheduled Maintenance | O2-26 | 33380 | 1553.0972
853 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-25 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 4:17 | 4:23 | 4:23 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 33380 | 139.0833
854 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-25 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:37 | 23:08 | 23:08 | 3.5167 | 0 | 3.5167 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.13526 | WTG Unscheduled Maintenance | O2-26 | 33380 | 4891.0972
855 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-25 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 0:00 | 1:20 | 1:20 | 1.3333 | 0 | 1.3333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.051282 | WTG Unscheduled Maintenance | O2-14 | 34055 | 1891.9444
856 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-25 | O2_12 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Auto reset |  | 1:21 | 1:26 | 1:26 | 0.083333 | 0 | 0.083333 | Auto Reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-14 | 34055 | 118.2465
857 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-25 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Major BD |  | 14:11 | 15:45 | 23:56 | 1.5667 | 8.1833 | 9.75 | Attend and wtg check related circuit check Converter cable check Power panel check control panel after check Stator cable rotor cable and check slipring so found Rotor cable minor Damage after arranging material 3M Tap apply and after trail so ok then reset and started wtg. | Close | 0.375 | WTG Breakdown Maintenance | O2-06 | 37549 | 15254.2812
858 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-25 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 19:51 | 22:24 | 22:24 | 2.55 | 0 | 2.55 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.098077 | WTG Unscheduled Maintenance | O2-01 | 31523 | 3349.3188
859 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_01 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset |  | 0:09 | 0:12 | 0:12 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-26 | 29985 | 62.4687
860 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_02 | TQGXIIPL | GEDA | 3.846% | 565 | Max. windspeed bladeangle | Environment |  | 0:07 | 0:09 | 0:09 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-05 | 29206 | 40.5639
861 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_03 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Auto reset |  | 0:14 | 0:17 | 0:17 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-09 | 30386 | 63.3042
862 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_03 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down |  | 0:51 | 1:01 | 1:01 | 0.16667 | 0 | 0.16667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.0064103 | WTG Breakdown Maintenance | O2-09 | 30386 | 211.0139
863 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 0:52 | 1:01 | 1:01 | 0.15 | 0 | 0.15 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.0057692 | WTG Breakdown Maintenance | O2-07 | 29635 | 185.2188
864 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 4:42 | 4:48 | 4:48 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 29635 | 123.4792
865 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_05 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Auto reset |  | 0:23 | 0:25 | 0:25 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-02 | 31689 | 44.0125
866 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 0:51 | 1:21 | 1:21 | 0.5 | 0 | 0.5 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.019231 | WTG Breakdown Maintenance | O2-02 | 31689 | 660.1875
867 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 1:35 | 2:40 | 2:40 | 1.0833 | 0 | 1.0833 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.041667 | WTG Breakdown Maintenance | O2-02 | 31689 | 1430.4062
868 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_05 | TQGXIIPL | GEDA | 3.846% | 2521 | Gen.sp.analog <<>> gearb.sp. | Break down |  | 14:14 | 14:22 | 14:22 | 0.13333 | 0 | 0.13333 | Checked related error data log then reset & start WTG. | Close | 0.0051282 | WTG Breakdown Maintenance | O2-02 | 31689 | 176.05
869 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_08 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset |  | 0:09 | 0:12 | 0:12 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-26 | 29985 | 62.4687
870 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_08 | TQGXIIPL | GEDA | 3.846% | 2390 | Brake due to sudden sys.failure | Break down |  | 0:51 | 1:05 | 1:05 | 0.23333 | 0 | 0.23333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.0089744 | WTG Breakdown Maintenance | O2-26 | 29985 | 291.5208
871 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 4:16 | 5:04 | 5:04 | 0.8 | 0 | 0.8 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.030769 | WTG Unscheduled Maintenance | O2-26 | 29985 | 999.5
872 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 5:14 | 6:10 | 6:10 | 0.93333 | 0 | 0.93333 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.035897 | WTG Unscheduled Maintenance | O2-26 | 29985 | 1166.0833
873 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 23:47 | 24:00 | 24:00 | 0.21667 | 0 | 0.21667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-26 | 29985 | 270.6979
874 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_09 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset |  | 0:12 | 0:15 | 0:15 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-03 | 28918 | 60.2458
875 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_09 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down |  | 0:51 | 1:06 | 1:06 | 0.25 | 0 | 0.25 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.0096154 | WTG Breakdown Maintenance | O2-03 | 28918 | 301.2292
876 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_10 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down |  | 0:51 | 1:07 | 1:07 | 0.26667 | 0 | 0.26667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.010256 | WTG Breakdown Maintenance | O2-15 | 26878 | 298.6444
877 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_12 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down |  | 0:51 | 1:08 | 1:08 | 0.28333 | 0 | 0.28333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.010897 | WTG Breakdown Maintenance | O2-14 | 28114 | 331.9014
878 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 0:51 | 1:09 | 1:09 | 0.3 | 0 | 0.3 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.011538 | WTG Breakdown Maintenance | O2-12 | 27828 | 347.85
879 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_15 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 0:51 | 1:10 | 1:10 | 0.31667 | 0 | 0.31667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.012179 | WTG Breakdown Maintenance | O2-10 | 26076 | 344.0583
880 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_16 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down |  | 0:52 | 1:11 | 1:11 | 0.31667 | 0 | 0.31667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.012179 | WTG Breakdown Maintenance | O2-21 | 27558 | 363.6125
881 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_17 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 0:52 | 1:11 | 1:11 | 0.31667 | 0 | 0.31667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.012179 | WTG Breakdown Maintenance | O2-22 | 31331 | 413.3951
882 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 0:52 | 1:12 | 1:12 | 0.33333 | 0 | 0.33333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.012821 | WTG Breakdown Maintenance | O2-06 | 30683 | 426.1528
883 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_19 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 0:52 | 1:13 | 1:13 | 0.35 | 0 | 0.35 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.013462 | WTG Breakdown Maintenance | O2-07 | 29635 | 432.1771
884 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_20 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down |  | 0:52 | 1:11 | 1:11 | 0.31667 | 0 | 0.31667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.012179 | WTG Breakdown Maintenance | O2-24 | 28117 | 370.9882
885 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 1:11 | 1:52 | 1:52 | 0.68333 | 0 | 0.68333 | Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.026282 | WTG Breakdown Maintenance | O2-06 | 30683 | 873.6132
886 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_21 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:55 | 18:11 | 18:11 | 1.2667 | 0 | 1.2667 | Wtg manual stop for bottom panel inspection work after started wtg | Close | 0.048718 | WTG Breakdown Maintenance | O2-06 | 30683 | 1619.3806
887 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_22 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down |  | 1:21 | 1:41 | 1:41 | 0.33333 | 0 | 0.33333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.012821 | WTG Breakdown Maintenance | O2-06 | 30683 | 426.1528
888 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_23 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset |  | 0:12 | 0:15 | 0:15 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-11 | 29120 | 60.6667
889 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_23 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 0:51 | 1:15 | 1:15 | 0.4 | 0 | 0.4 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.015385 | WTG Breakdown Maintenance | O2-11 | 29120 | 485.3333
890 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_24 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down |  | 0:52 | 1:16 | 1:16 | 0.4 | 0 | 0.4 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.015385 | WTG Breakdown Maintenance | O2-20 | 26825 | 447.0833
891 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_25 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset |  | 0:05 | 0:08 | 0:08 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-01 | 30294 | 63.1125
892 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Break down |  | 0:51 | 1:15 | 1:15 | 0.4 | 0 | 0.4 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.015385 | WTG Breakdown Maintenance | O2-01 | 30294 | 504.9
893 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 4:17 | 5:05 | 5:05 | 0.8 | 0 | 0.8 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.030769 | WTG Unscheduled Maintenance | O2-01 | 30294 | 1009.8
894 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 5:14 | 6:19 | 6:19 | 1.0833 | 0 | 1.0833 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.041667 | WTG Unscheduled Maintenance | O2-01 | 30294 | 1367.4375
895 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-26 | O2_26 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down |  | 0:51 | 1:16 | 1:16 | 0.41667 | 0 | 0.41667 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.016026 | WTG Breakdown Maintenance | O2-01 | 30294 | 525.9375
896 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-27 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 0:23 | 6:28 | 6:28 | 6.0833 | 0 | 6.0833 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.23397 | WTG Unscheduled Maintenance | O2-09 | 43632 | 11059.5
897 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-27 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 6:39 | 6:50 | 6:50 | 0.18333 | 0 | 0.18333 | Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.0070513 | WTG Breakdown Maintenance | O2-02 | 48703 | 372.0368
898 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-27 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 21:12 | 21:34 | 21:34 | 0.36667 | 0 | 0.36667 | Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.014103 | WTG Breakdown Maintenance | O2-02 | 48703 | 744.0736
899 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-27 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 5:32 | 5:43 | 5:43 | 0.18333 | 0 | 0.18333 | Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.0070513 | WTG Breakdown Maintenance | O2-04 | 55945 | 427.3576
900 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-27 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 6:19 | 7:04 | 8:28 | 0.75 | 1.4 | 2.15 | Attend and wtg check MPCB Motor and coolant so found QA008 MPCB Tripped after check voltage and fidbac connection tight after fan on temperature normal coolant fill up then reset and started wtg. | Close | 0.082692 | WTG Breakdown Maintenance | O2-04 | 55945 | 5011.7396
901 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-27 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 0:00 | 5:04 | 5:04 | 5.0667 | 0 | 5.0667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.19487 | WTG Unscheduled Maintenance | O2-26 | 45417 | 9588.0333
902 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-27 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 13:48 | 22:11 | 22:11 | 8.3833 | 0 | 8.3833 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.32244 | WTG Unscheduled Maintenance | O2-26 | 45417 | 15864.4104
903 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-27 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 5:12 | 5:19 | 5:19 | 0.11667 | 0 | 0.11667 | Checked related error data log then reset & start WTG. | Close | 0.0044872 | WTG Breakdown Maintenance | O2-22 | 54059 | 262.7868
904 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-27 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 5:45 | 5:57 | 5:57 | 0.2 | 0 | 0.2 | Checked related error data log apply shoft reboot then reset & start WTG. | Close | 0.0076923 | WTG Breakdown Maintenance | O2-22 | 54059 | 450.4917
905 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-27 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 13:48 | 21:45 | 21:45 | 7.95 | 0 | 7.95 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.30577 | WTG Unscheduled Maintenance | O2-01 | 45298 | 15004.9625
906 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-28 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 21:21 | 21:23 | 21:23 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-07 | 38555 | 53.5486
907 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-28 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 3:43 | 4:56 | 4:56 | 1.2167 | 0 | 1.2167 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.046795 | WTG Unscheduled Maintenance | O2-26 | 30364 | 1539.2861
908 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-28 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 3:20 | 3:26 | 3:26 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 37551 | 156.4625
909 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-28 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:02 | 15:08 | 15:08 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 37551 | 156.4625
910 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-28 | O2_15 | TQGXIIPL | GEDA | 3.846% | 642 | Sim.angle E enc. <> act.angle 2 | Break down |  | 9:41 | 9:55 | 9:55 | 0.23333 | 0 | 0.23333 | Checked related error data log then reset & started WTG. | Close | 0.0089744 | WTG Breakdown Maintenance | O2-10 | 40745 | 396.1319
911 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-28 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 3:55 | 3:59 | 3:59 | 0.066667 | 0 | 0.066667 | Checked related error data log then reset & started WTG. | Close | 0.0025641 | WTG Breakdown Maintenance | O2-22 | 39494 | 109.7056
912 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-28 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 4:19 | 4:25 | 4:25 | 0.1 | 0 | 0.1 | Checked related error data log then reset & started WTG. | Close | 0.0038462 | WTG Breakdown Maintenance | O2-22 | 39494 | 164.5583
913 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-28 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Auto reset |  | 9:34 | 9:36 | 9:36 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-06 | 38856 | 53.9667
914 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-28 | O2_25 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Load Shedding |  | 3:46 | 4:56 | 4:56 | 1.1667 | 0 | 1.1667 | WTG Manual stop for load shedding due to feeder-01 overloading issue. | Close | 0.044872 | WTG Unscheduled Maintenance | O2-01 | 36145 | 1757.0486
915 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-28 | O2_25 | TQGXIIPL | GEDA | 3.846% | 172 | SLC MF torque protection | Break down |  | 16:49 | 19:17 | 19:17 | 2.4667 | 0 | 2.4667 | Attend and wtg check Rotor brake pad Temp Sensor check and all connection check and tight after trail then reset and started wtg. | Close | 0.094872 | WTG Breakdown Maintenance | O2-01 | 36145 | 3714.9028
916 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work |  | 10:15 | 11:40 | 11:40 | 1.4167 | 0 | 1.4167 | Jumper open for Project Pending Work | Close | 0.054487 | WTG Breakdown Maintenance | O2-05 | 34066 | 2010.8403
917 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work |  | 10:15 | 11:40 | 11:40 | 1.4167 | 0 | 1.4167 | Jumper open for Project Pending Work | Close | 0.054487 | WTG Breakdown Maintenance | O2-02 | 35336 | 2085.8056
918 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Project pending work |  | 10:15 | 11:40 | 11:40 | 1.4167 | 0 | 1.4167 | Jumper open for Project Pending Work | Close | 0.054487 | WTG Breakdown Maintenance | O2-01 | 34991 | 2065.441
919 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_03 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset |  | 12:43 | 12:47 | 12:47 | 0.066667 | 0 | 0.066667 | Auto reset | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-09 | 35770 | 99.3611
920 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:51 | 14:52 | 14:52 | 0.016667 | 0 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-07 | 36624 | 25.4333
921 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 17:20 | 17:26 | 17:26 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 36624 | 152.6
922 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5550 | Low hydraulic oil level | Break down |  | 20:27 | 21:54 | 24:00 | 1.45 | 2.1 | 3.55 | Attend wtg check related circuit so check all valve and check oil level so found oil level low after check all yaw calliper and check all pipe check oil leakage WTG WIP | Close | 0.13654 | WTG Breakdown Maintenance | O2-07 | 36624 | 5417.3
923 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset |  | 14:51 | 14:58 | 14:58 | 0.11667 | 0 | 0.11667 | Auto reset | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-02 | 35336 | 171.7722
924 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Auto reset |  | 17:37 | 17:38 | 17:38 | 0.016667 | 0 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-26 | 36092 | 25.0639
925 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:42 | 15:48 | 15:48 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-12 | 35861 | 149.4208
926 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 16:17 | 16:22 | 16:22 | 0.083333 | 0 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | WTG Breakdown Maintenance | O2-14 | 36054 | 125.1875
927 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_19 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset |  | 15:10 | 15:11 | 15:11 | 0.016667 | 0 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-07 | 36624 | 25.4333
928 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:25 | 14:26 | 14:26 | 0.016667 | 0 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-24 | 36704 | 25.4889
929 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1731 | Oil temperature gearbox input high | Auto reset |  | 17:38 | 17:40 | 17:40 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-11 | 35836 | 49.7722
930 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-29 | O2_23 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Auto reset |  | 17:47 | 17:50 | 17:50 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-11 | 35836 | 74.6583
931 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_01 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 11:52 | 12:00 | 12:00 | 0.13333 | 0 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | WTG Breakdown Maintenance | O2-26 | 56413 | 313.4056
932 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:23 | 15:29 | 15:29 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Breakdown Maintenance | O2-26 | 56413 | 235.0542
933 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_04 | TQGXIIPL | GEDA | 3.846% | 5550 | Low hydraulic oil level | Break down |  | 0:00 | 0:18 | 0:18 | 0.3 | 0 | 0.3 | Check All Pipe after fill up oil after trail then reset and started wtg. | Close | 0.011538 | WTG Breakdown Maintenance | O2-07 | 52504 | 656.3
934 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 10:27 | 10:35 | 10:35 | 0.13333 | 0 | 0.13333 | Auto reset | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-07 | 52504 | 291.6889
935 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 19:08 | 19:39 | 19:39 | 0.51667 | 0 | 0.51667 | WTG Manual stop for PPC Software Updating work Done . | Close | 0.019872 | WTG Breakdown Maintenance | O2-07 | 52504 | 1130.2944
936 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 2:13 | 2:20 | 2:20 | 0.11667 | 0 | 0.11667 | Checked related error data log then reset & started WTG. | Close | 0.0044872 | WTG Breakdown Maintenance | O2-02 | 56778 | 276.0042
937 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 14:44 | 15:20 | 15:20 | 0.6 | 0 | 0.6 | Check Related Error Data log after PPC Software Updating Work Donethen reset and started wtg | Close | 0.023077 | WTG Breakdown Maintenance | O2-02 | 56778 | 1419.45
938 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 17:00 | 17:05 | 17:05 | 0.083333 | 0 | 0.083333 | Auto reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-02 | 56778 | 197.1458
939 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 19:08 | 19:39 | 19:39 | 0.51667 | 0 | 0.51667 | WTG Manual stop for PPC Software Updating work Done . | Close | 0.019872 | WTG Breakdown Maintenance | O2-04 | 51855 | 1116.3229
940 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 7:41 | 7:46 | 7:46 | 0.083333 | 0 | 0.083333 | Checked related error data log then reset & started WTG. | Close | 0.0032051 | WTG Breakdown Maintenance | O2-26 | 56413 | 195.8785
941 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset |  | 8:37 | 8:41 | 8:41 | 0.066667 | 0 | 0.066667 | Auto reset | Close | 0.0025641 | WTG Breakdown Maintenance | O2-26 | 56413 | 156.7028
942 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 12:19 | 12:27 | 12:27 | 0.13333 | 0 | 0.13333 | Checked related error data log then reset & started WTG. | Close | 0.0051282 | WTG Breakdown Maintenance | O2-26 | 56413 | 313.4056
943 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 21:16 | 21:29 | 21:29 | 0.21667 | 0 | 0.21667 | check Event And Data log then reset & started wtg. | Close | 0.0083333 | WTG Breakdown Maintenance | O2-26 | 56413 | 509.284
944 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_09 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 19:09 | 19:36 | 19:36 | 0.45 | 0 | 0.45 | WTG Manual stop for PPC Software Updating work Done . | Close | 0.017308 | WTG Breakdown Maintenance | O2-03 | 55357 | 1037.9437
945 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_10 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 19:09 | 19:35 | 19:35 | 0.43333 | 0 | 0.43333 | WTG Manual stop for PPC Software Updating work Done . | Close | 0.016667 | WTG Breakdown Maintenance | O2-15 | 55209 | 996.8292
946 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset |  | 19:49 | 19:51 | 19:51 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-15 | 55209 | 76.6792
947 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Auto reset |  | 16:08 | 16:11 | 16:11 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-14 | 55074 | 114.7375
948 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_12 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 18:13 | 18:29 | 18:29 | 0.26667 | 0 | 0.26667 | check Event And Data log then reset & started wtg. | Close | 0.010256 | WTG Breakdown Maintenance | O2-14 | 55074 | 611.9333
949 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 19:11 | 19:32 | 19:32 | 0.35 | 0 | 0.35 | WTG Manual stop for PPC Software Updating work Done . | Close | 0.013462 | WTG Breakdown Maintenance | O2-14 | 55074 | 803.1625
950 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_14 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 19:11 | 19:29 | 19:29 | 0.3 | 0 | 0.3 | WTG Manual stop for PPC Software Updating work Done . | Close | 0.011538 | WTG Breakdown Maintenance | O2-12 | 54494 | 681.175
951 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 1:07 | 2:41 | 3:40 | 1.5667 | 0.98333 | 2.55 | Attend and wtg check converter panel check PT100 Sensor , Replace All filter and clean Radiator after trail then reset and started wtg. | Close | 0.098077 | WTG Breakdown Maintenance | O2-22 | 57090 | 6065.8125
952 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_17 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 11:54 | 11:58 | 11:58 | 0.066667 | 0 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Breakdown Maintenance | O2-22 | 57090 | 158.5833
953 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 17:22 | 17:40 | 17:40 | 0.3 | 0 | 0.3 | check Event And Data log then reset & started wtg. | Close | 0.011538 | WTG Breakdown Maintenance | O2-22 | 57090 | 713.625
954 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_18 | TQGXIIPL | GEDA | 3.846% | 696 | Indiv. setp.pitch ang. offset incorr. | Break down |  | 15:25 | 15:37 | 15:37 | 0.2 | 0 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | WTG Breakdown Maintenance | O2-06 | 55099 | 459.1583
955 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_19 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset |  | 13:15 | 13:16 | 13:16 | 0.016667 | 0 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-07 | 52504 | 36.4611
956 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Auto reset |  | 15:38 | 15:40 | 15:40 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-07 | 52504 | 72.9222
957 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_19 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 18:12 | 18:29 | 18:29 | 0.28333 | 0 | 0.28333 | check Event And Data log check temp then reset & started wtg. | Close | 0.010897 | WTG Breakdown Maintenance | O2-07 | 52504 | 619.8389
958 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1731 | Oil temperature gearbox input high | Break down |  | 13:38 | 13:48 | 13:48 | 0.16667 | 0 | 0.16667 | check Event And Data log check temp then reset & started wtg. | Close | 0.0064103 | WTG Breakdown Maintenance | O2-11 | 55825 | 387.6736
959 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1731 | Oil temperature gearbox input high | Break down |  | 14:26 | 14:42 | 14:42 | 0.26667 | 0 | 0.26667 | check Event And Data log check temp then reset & started wtg. | Close | 0.010256 | WTG Breakdown Maintenance | O2-11 | 55825 | 620.2778
960 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 10:09 | 10:15 | 10:15 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-20 | 53978 | 224.9083
961 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_25 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 17:25 | 17:36 | 17:36 | 0.18333 | 0 | 0.18333 | check Event And Data log check temp then reset & started wtg. | Close | 0.0070513 | WTG Breakdown Maintenance | O2-01 | 54422 | 415.7236
962 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-30 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:16 | 12:22 | 12:22 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-01 | 54422 | 226.7583
963 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 13:16 | 14:07 | 14:07 | 0.85 | 0 | 0.85 | Check event log and check hydraulic yaw brake pressure After Flushing mode on check pressure , both side Yawing manually and check cable twist after trail then reset and started wtg. | Close | 0.032692 | WTG Breakdown Maintenance | O2-26 | 51268 | 1815.7417
964 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:11 | 15:17 | 15:17 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 51268 | 213.6167
965 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 7:06 | 7:10 | 7:10 | 0.066667 | 0 | 0.066667 | Auto reset | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-07 | 50547 | 140.4083
966 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 12:33 | 13:03 | 13:03 | 0.5 | 0 | 0.5 | Check event log and check hydraulic yaw brake pressure After trail then reset started wtg. | Close | 0.019231 | WTG Breakdown Maintenance | O2-07 | 50547 | 1053.0625
967 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:38 | 14:44 | 14:44 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 50547 | 210.6125
968 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3420 | UPS buffer time too short | Connectivity issue |  | 16:01 | 17:07 | 17:07 | 1.1 | 0 | 1.1 | AFTER Feeder shutdown clear than wtg in Disconnected due to O2 07 VCB tripped so After charge than reset and start WTG. | Close | 0.042308 | WTG Breakdown Maintenance | O2-07 | 50547 | 2316.7375
969 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_08 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Auto reset |  | 18:54 | 18:56 | 18:56 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-26 | 51268 | 71.2056
970 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_09 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:49 | 12:55 | 12:55 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-03 | 55547 | 231.4458
971 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset |  | 16:54 | 16:56 | 16:56 | 0.033333 | 0 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-15 | 52780 | 73.3056
972 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset |  | 17:25 | 17:27 | 17:27 | 0.033333 | 0 | 0.033333 | Auto resert | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-15 | 52780 | 73.3056
973 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down |  | 19:49 | 19:54 | 19:54 | 0.083333 | 0 | 0.083333 | check Event And Data log check temp then reset & started wtg. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-15 | 52780 | 183.2639
974 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:10 | 12:16 | 12:16 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 54037 | 225.1542
975 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 12:36 | 13:03 | 13:03 | 0.45 | 0 | 0.45 | Check event log and check hydraulic yaw brake pressure and check cable twist removed After trail then reset started wtg. | Close | 0.017308 | WTG Breakdown Maintenance | O2-11 | 54037 | 1013.1937
976 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_13 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down |  | 17:30 | 17:38 | 17:38 | 0.13333 | 0 | 0.13333 | check Event And Data log check temp then reset & started wtg. | Close | 0.0051282 | WTG Breakdown Maintenance | O2-11 | 54037 | 300.2056
977 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_16 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down |  | 17:19 | 17:32 | 17:32 | 0.21667 | 0 | 0.21667 | check Event And Data log check temp then reset & started wtg. | Close | 0.0083333 | WTG Breakdown Maintenance | O2-21 | 47315 | 427.1493
978 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_18 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:41 | 13:48 | 13:48 | 0.11667 | 0 | 0.11667 | Auto reset | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-06 | 47521 | 231.0049
979 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:54 | 12:00 | 12:00 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-24 | 47157 | 196.4875
980 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:26 | 12:32 | 12:32 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 54037 | 225.1542
981 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_24 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Auto reset |  | 17:13 | 17:16 | 17:16 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-20 | 47567 | 99.0979
982 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_25 | TQGXIIPL | GEDA | 3.846% | 1700 | High temp. gear bearing 1 | Break down |  | 16:31 | 16:46 | 16:46 | 0.25 | 0 | 0.25 | check Event And Data log check temp then reset & started wtg. | Close | 0.0096154 | WTG Breakdown Maintenance | O2-01 | 54328 | 565.9167
983 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:32 | 12:35 | 12:35 | 0.05 | 0 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-01 | 54328 | 113.1833
984 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:44 | 13:50 | 13:50 | 0.1 | 0 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-15 | 52780 | 219.9167
985 | 2026 | 2025 | Year_2 | 2025-05-01 | 2025-05-31 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:55 | 14:56 | 14:56 | 0.016667 | 0 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-15 | 52780 | 36.6528
986 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 17:48 | 17:48 | 17:54 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 50608.8333 | 210.8701
987 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:24 | 11:24 | 11:28 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-07 | 51412.6667 | 142.813
988 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:53 | 11:53 | 11:59 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 51412.6667 | 214.2194
989 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_06 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset |  | 12:25 | 12:25 | 12:42 | 0 | 0.28333 | 0.28333 | Auto reset | Close | 0.010897 | WTG Unscheduled Maintenance | O2-21 | 52837.5 | 623.776
990 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_09 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 16:46 | 16:46 | 17:01 | 0 | 0.25 | 0.25 | Auto reset | Close | 0.0096154 | WTG Unscheduled Maintenance | O2-03 | 48703.3333 | 507.3264
991 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:17 | 12:17 | 12:23 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-15 | 54464.8333 | 226.9368
992 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:08 | 16:08 | 16:13 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-12 | 49060.8333 | 170.3501
993 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_12 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset |  | 15:16 | 15:16 | 15:30 | 0 | 0.23333 | 0.23333 | Auto reset | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-14 | 49854.5 | 484.6965
994 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:08 | 11:08 | 11:13 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-11 | 51597 | 179.1563
995 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:14 | 13:14 | 13:20 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-12 | 49060.8333 | 204.4201
996 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:30 | 13:30 | 13:38 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-12 | 49060.8333 | 272.5602
997 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_14 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 16:18 | 16:18 | 16:37 | 0 | 0.31667 | 0.31667 | Auto reset | Close | 0.012179 | WTG Unscheduled Maintenance | O2-12 | 49060.8333 | 647.3304
998 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 12:54 | 12:54 | 13:10 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-21 | 52837.5 | 587.0833
999 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 14:00 | 14:00 | 15:00 | 0 | 1 | 1 | check Event and Data log Temp high then temp is normalize then apply shoft reboot then reset & started wtg. | Close | 0.038462 | WTG Unscheduled Maintenance | O2-22 | 56229 | 2342.875
1000 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_19 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 12:50 | 12:50 | 13:05 | 0 | 0.25 | 0.25 | Auto reset | Close | 0.0096154 | WTG Unscheduled Maintenance | O2-07 | 51412.6667 | 535.5486
1001 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:23 | 12:23 | 12:31 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-24 | 53390.8333 | 296.6157
1002 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_21 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 13:34 | 13:34 | 13:50 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-06 | 52292.1667 | 581.0241
1003 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:44 | 11:44 | 11:46 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-11 | 51597 | 71.6625
1004 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:32 | 12:32 | 12:38 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-20 | 53693 | 223.7208
1005 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 2:49 | 2:49 | 2:57 | 0 | 0.13333 | 0.13333 | check Event and Data log then reset & started wtg. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-01 | 50690.1667 | 281.612
1006 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:09 | 15:09 | 15:15 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-01 | 50690.1667 | 211.209
1007 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-01 | O2_26 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 16:55 | 16:55 | 17:05 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-01 | 50690.1667 | 352.015
1008 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:16 | 12:16 | 12:18 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-26 | 44649.8333 | 62.0137
1009 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:34 | 12:34 | 12:40 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 43345.3333 | 180.6056
1010 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 16:15 | 16:15 | 17:13 | 0 | 0.96667 | 0.96667 | check Event and Data log Temp high them temp is normalize then apply shoft reboot then reset & started wtg. | Close | 0.037179 | WTG Unscheduled Maintenance | O2-02 | 43828.3333 | 1765.3079
1011 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_05 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Auto reset |  | 18:14 | 18:14 | 18:30 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-02 | 43828.3333 | 486.9815
1012 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 21:47 | 21:47 | 22:01 | 0 | 0.23333 | 0.23333 | check Event and Data log then apply shoft reboot then reset & started wtg. | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-02 | 43828.3333 | 426.1088
1013 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 18:40 | 18:40 | 18:46 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 48023.3333 | 200.0972
1014 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset |  | 13:43 | 13:43 | 13:44 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-26 | 44649.8333 | 31.0068
1015 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:22 | 15:22 | 15:28 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 44649.8333 | 186.041
1016 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset |  | 16:07 | 16:07 | 16:09 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-26 | 44649.8333 | 62.0137
1017 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 16:35 | 16:35 | 16:51 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-26 | 44649.8333 | 496.1093
1018 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 21:42 | 21:42 | 21:48 | 0 | 0.1 | 0.1 | check Event and Data log reset & started wtg. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 44649.8333 | 186.041
1019 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:52 | 16:52 | 16:58 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 44131.3333 | 183.8806
1020 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:07 | 14:07 | 14:13 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-12 | 42844.3333 | 178.5181
1021 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 17:36 | 17:36 | 17:39 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-10 | 43054.6667 | 89.6972
1022 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Auto reset |  | 10:04 | 10:04 | 10:10 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 48023.3333 | 200.0972
1023 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:41 | 11:41 | 11:47 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 48023.3333 | 200.0972
1024 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:30 | 19:30 | 19:59 | 0 | 0.48333 | 0.48333 | check Event and Data log Temp high then temp is normalize then apply shoft reboot then reset & started wtg. | Close | 0.01859 | WTG Unscheduled Maintenance | O2-22 | 51023 | 1027.5465
1025 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:41 | 13:41 | 13:47 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-24 | 46021.3333 | 191.7556
1026 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:25 | 13:25 | 13:30 | 0 | 0.083333 | 0.083333 | Auto reset | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-06 | 47731 | 165.7326
1027 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-02 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Auto reset |  | 14:23 | 14:23 | 14:42 | 0 | 0.31667 | 0.31667 | Auto reset | Close | 0.012179 | WTG Unscheduled Maintenance | O2-11 | 44131.3333 | 582.2884
1028 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:52 | 13:52 | 13:58 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 38729.76 | 161.374
1029 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 16:00 | 16:00 | 16:02 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-26 | 38729.76 | 53.7913
1030 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 12:56 | 12:56 | 13:05 | 0 | 0.15 | 0.15 | check Event And Data log then reset & started wtg. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-07 | 39912.24 | 249.4515
1031 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_04 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down |  | 13:07 | 13:07 | 13:09 | 0 | 0.033333 | 0.033333 | During Battery test occurred error so check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-07 | 39912.24 | 55.4337
1032 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:00 | 15:00 | 15:06 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 39912.24 | 166.301
1033 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 11:00 | 11:00 | 11:04 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-02 | 40819.68 | 113.388
1034 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 15:25 | 15:25 | 15:27 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-02 | 40819.68 | 56.694
1035 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 17:10 | 17:15 | 18:30 | 0.083333 | 1.25 | 1.3333 | Attend and check Convertor in found Ambient control Temp. high so check in convertor panel PT100 value and found loose connection in TB so tightly properly and started Turbine. | Close | 0.051282 | WTG Breakdown Maintenance | O2-02 | 40819.68 | 2267.76
1036 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_06 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 14:20 | 14:20 | 14:36 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-21 | 43956.24 | 488.4027
1037 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 10:43 | 10:43 | 10:49 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-15 | 40892.64 | 170.386
1038 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 12:46 | 12:46 | 13:02 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-12 | 40312.8 | 447.92
1039 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_15 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 15:15 | 15:15 | 15:31 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-10 | 40083.36 | 445.3707
1040 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 17:16 | 17:16 | 17:53 | 0 | 0.61667 | 0.61667 | check Event and Data log Temp high then temp is normalize then apply shoft reboot then reset & started wtg. | Close | 0.023718 | WTG Unscheduled Maintenance | O2-22 | 47631.36 | 1223.8613
1041 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_19 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 15:08 | 15:08 | 15:16 | 0 | 0.13333 | 0.13333 | check Event And Data log then reset & started wtg. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-07 | 39912.24 | 221.7347
1042 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:15 | 15:15 | 15:21 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-24 | 42707.04 | 177.946
1043 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 9:26 | 9:26 | 9:32 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 39065.04 | 162.771
1044 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down |  | 11:17 | 11:17 | 11:22 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-11 | 39065.04 | 135.6425
1045 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_24 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 15:37 | 15:37 | 15:53 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-20 | 42388.08 | 470.9787
1046 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_25 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:15 | 13:15 | 13:21 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-01 | 39300.48 | 163.752
1047 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_26 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 11:20 | 11:20 | 11:36 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-01 | 39300.48 | 436.672
1048 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-03 | O2_26 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:10 | 14:10 | 14:16 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-01 | 39300.48 | 163.752
1049 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-04 | O2_04 | TQGXIIPL | GEDA | 3.846% | 177 | SLC MF blade regulation control | Break down |  | 9:15 | 9:15 | 9:18 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-07 | 24286 | 50.5958
1050 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-04 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:35 | 14:35 | 14:36 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-07 | 24286 | 16.8653
1051 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-04 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:44 | 12:44 | 12:50 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-02 | 25759 | 107.3292
1052 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-04 | O2_06 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 14:28 | 14:28 | 14:44 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-21 | 26598 | 295.5333
1053 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-04 | O2_06 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:29 | 15:29 | 15:38 | 0 | 0.15 | 0.15 | Bottom Panel Inspection work done than started Turbine. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-21 | 26598 | 166.2375
1054 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-04 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:27 | 13:27 | 13:33 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 26960 | 112.3333
1055 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-04 | O2_10 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 11:09 | 11:09 | 11:25 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-15 | 25789 | 286.5444
1056 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-04 | O2_10 | TQGXIIPL | GEDA | 3.846% | 6601 | Wind.dir. diff. level 1 | Break down |  | 11:25 | 11:25 | 11:27 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-15 | 25789 | 35.8181
1057 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-04 | O2_15 | TQGXIIPL | GEDA | 3.846% | 780 | Error bridging start-up | Break down |  | 12:11 | 12:11 | 12:15 | 0 | 0.066667 | 0.066667 | During Battery test occurred error so check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-10 | 25043 | 69.5639
1058 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-04 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 15:30 | 15:30 | 15:34 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-24 | 27210 | 75.5833
1059 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-05 | O2_02 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 11:04 | 11:04 | 11:18 | 0 | 0.23333 | 0.23333 | check Event And Data log then reset & started wtg. | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-05 | 16515 | 160.5625
1060 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-05 | O2_02 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 11:34 | 11:34 | 11:40 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-05 | 16515 | 68.8125
1061 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-05 | O2_04 | TQGXIIPL | GEDA | 3.846% | 177 | SLC MF blade regulation control | Break down |  | 8:52 | 8:52 | 9:09 | 0 | 0.28333 | 0.28333 | check Event And Data log then reset & started wtg. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-07 | 12137 | 143.284
1062 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-05 | O2_04 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down |  | 11:25 | 11:25 | 11:44 | 0 | 0.31667 | 0.31667 | check Event And Data log then reset & started wtg. | Close | 0.012179 | WTG Unscheduled Maintenance | O2-07 | 12137 | 160.141
1063 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-05 | O2_04 | TQGXIIPL | GEDA | 3.846% | 588 | Target >< act. coll. pitch angle | Break down |  | 12:19 | 13:18 | 16:50 | 0.98333 | 3.5333 | 4.5167 | Attend and wtg check Axis No 3 so found Pitch Encoder cable connection loose after tight and Repeated error occurred check found Axis no 1 flat resistor failure found after replace then trail so ok after winch load test completed then reset and started wtg. | Close | 0.17372 | WTG Unscheduled Maintenance | O2-07 | 12137 | 2284.116
1064 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-05 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Auto reset |  | 20:06 | 20:06 | 20:07 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-15 | 13908 | 9.6583
1065 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-05 | O2_13 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Auto reset |  | 19:53 | 19:53 | 19:55 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-11 | 14184 | 19.7
1066 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-05 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset |  | 18:19 | 18:19 | 18:20 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-06 | 16771 | 11.6465
1067 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-05 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset |  | 18:24 | 18:24 | 18:30 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 16771 | 69.8792
1068 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-05 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset |  | 17:57 | 17:57 | 17:59 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-07 | 12137 | 16.8569
1069 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_01 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 19:21 | 19:21 | 19:37 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-26 | 23651 | 262.7889
1070 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_03 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 11:53 | 13:50 | 17:42 | 1.95 | 3.8667 | 5.8167 | Attend and WTG check event log and snap found encoder value deviation Axis No.1 so we have check QA001 contactor manually operate but not pickup after check all connection check rectifier fuse and Diode and QA001 Contactor NO/NC Auxiliry switch check so found NO switch not proper working after all connection check and tight then we have take trail turbine after No any abnormality so started WTG. | Close | 0.22372 | WTG Breakdown Maintenance | O2-09 | 22922 | 5555.4014
1071 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 19:04 | 19:04 | 19:10 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 24124 | 100.5167
1072 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_05 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 18:44 | 18:44 | 19:00 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-02 | 28011 | 311.2333
1073 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 13:30 | 13:30 | 14:03 | 0 | 0.55 | 0.55 | check Event and Data log also check error related Perameter then apply shoft reboot then reset & started wtg. | Close | 0.021154 | WTG Unscheduled Maintenance | O2-04 | 25991 | 595.6271
1074 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_09 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset |  | 19:15 | 19:15 | 19:31 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-03 | 21461 | 238.4556
1075 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_13 | TQGXIIPL | GEDA | 3.846% | 687 | Power failure pitch | Break down |  | 16:38 | 17:00 | 19:30 | 0.36667 | 2.5 | 2.8667 | Check error related ckt tha found Hub supply 400V MCB tripped so check before and after related ckt nothing found abnormal so charge MCB and reset and started Turbine. | Close | 0.11026 | WTG Breakdown Maintenance | O2-11 | 21231 | 2535.925
1076 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_17 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 17:57 | 17:57 | 18:13 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-22 | 22267 | 247.4111
1077 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_21 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down |  | 18:18 | 18:18 | 18:31 | 0 | 0.21667 | 0.21667 | check Event And Data log then reset & started wtg. | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-06 | 21010 | 189.6736
1078 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down |  | 12:24 | 12:24 | 12:35 | 0 | 0.18333 | 0.18333 | check Event And Data log then reset & started wtg. | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-11 | 21231 | 162.1812
1079 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down |  | 13:53 | 13:53 | 14:04 | 0 | 0.18333 | 0.18333 | check Event and Data log also check error related Perameter then apply shoft reboot then reset & started wtg. | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-11 | 21231 | 162.1812
1080 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down |  | 17:49 | 17:49 | 18:07 | 0 | 0.3 | 0.3 | check Event and Data log also check error related Perameter then apply shoft reboot then reset & started wtg. | Close | 0.011538 | WTG Unscheduled Maintenance | O2-11 | 21231 | 265.3875
1081 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6300 | Yaw error | Break down |  | 18:48 | 18:48 | 18:50 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-11 | 21231 | 29.4875
1082 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-06 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down |  | 23:24 | 23:24 | 24:00 | 0 | 0.6 | 0.6 | Attend and check HPU Unit 9.1 and 9.7 Valve also check yaw System Pressure than wip, | Close | 0.023077 | WTG Breakdown Maintenance | O2-11 | 21231 | 530.775
1083 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:33 | 14:33 | 14:39 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 36341 | 151.4208
1084 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 10:22 | 10:22 | 11:34 | 0 | 1.2 | 1.2 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.046154 | WTG Breakdown Maintenance | O2-07 | 29552 | 1477.6
1085 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 12:28 | 12:28 | 12:51 | 0 | 0.38333 | 0.38333 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.014744 | WTG Breakdown Maintenance | O2-07 | 29552 | 472.0111
1086 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 16:52 | 16:52 | 17:14 | 0 | 0.36667 | 0.36667 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.014103 | WTG Breakdown Maintenance | O2-07 | 29552 | 451.4889
1087 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 17:48 | 17:48 | 17:54 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-02 | 39249 | 163.5375
1088 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 21:54 | 21:54 | 22:04 | 0 | 0.16667 | 0.16667 | check Event And Data log then reset & started wtg. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-02 | 39249 | 272.5625
1089 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 10:22 | 10:22 | 11:34 | 0 | 1.2 | 1.2 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.046154 | WTG Breakdown Maintenance | O2-04 | 37281 | 1864.05
1090 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 12:28 | 12:28 | 17:16 | 0 | 4.8 | 4.8 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.18462 | WTG Breakdown Maintenance | O2-04 | 37281 | 7456.2
1091 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:43 | 13:43 | 13:49 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 36341 | 151.4208
1092 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_08 | TQGXIIPL | GEDA | 3.846% | 53 | Wind dir.dev. level 1 | Break down |  | 14:42 | 14:42 | 14:43 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-26 | 36341 | 25.2368
1093 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:56 | 14:56 | 15:03 | 0 | 0.11667 | 0.11667 | check Event And Data log then reset & started wtg. | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-26 | 36341 | 176.6576
1094 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6056 | High yaw load | Break down |  | 14:01 | 14:01 | 14:04 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-12 | 32626 | 67.9708
1095 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:31 | 14:31 | 14:37 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-12 | 32626 | 135.9417
1096 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 10:22 | 10:22 | 11:34 | 0 | 1.2 | 1.2 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.046154 | WTG Breakdown Maintenance | O2-07 | 29552 | 1477.6
1097 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 12:28 | 12:28 | 12:49 | 0 | 0.35 | 0.35 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.013462 | WTG Breakdown Maintenance | O2-07 | 29552 | 430.9667
1098 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 16:52 | 16:52 | 17:14 | 0 | 0.36667 | 0.36667 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.014103 | WTG Breakdown Maintenance | O2-07 | 29552 | 451.4889
1099 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_19 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down |  | 18:39 | 18:39 | 18:48 | 0 | 0.15 | 0.15 | check Event And Data log then reset & started wtg. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-07 | 29552 | 184.7
1100 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:40 | 14:40 | 14:46 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 35598 | 148.325
1101 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:26 | 14:26 | 14:32 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 35598 | 148.325
1102 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_23 | TQGXIIPL | GEDA | 3.846% | 5700 | Max. operation time hydraulic | Break down |  | 0:00 | 0:00 | 0:20 | 0 | 0.33333 | 0.33333 | Attend and check HPU Unit 9.1 and 9.7 Valve also check yaw System Pressure than take trail and started WTG. | Close | 0.012821 | WTG Unscheduled Maintenance | O2-11 | 32412 | 450.1667
1103 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-07 | O2_25 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset |  | 18:31 | 18:31 | 18:46 | 0 | 0.25 | 0.25 | Auto reset | Close | 0.0096154 | WTG Unscheduled Maintenance | O2-01 | 36444 | 379.625
1104 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 8:04 | 8:04 | 8:10 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 27380 | 114.0833
1105 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 8:56 | 8:56 | 10:37 | 0 | 1.6833 | 1.6833 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.064744 | WTG Breakdown Maintenance | O2-07 | 27380 | 1920.4028
1106 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 18:25 | 18:25 | 18:57 | 0 | 0.53333 | 0.53333 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.020513 | WTG Breakdown Maintenance | O2-07 | 27380 | 608.4444
1107 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 22:26 | 22:26 | 23:20 | 0 | 0.9 | 0.9 | check Event And Data log then reset & started wtg. | Close | 0.034615 | WTG Unscheduled Maintenance | O2-07 | 27380 | 1026.75
1108 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_06 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down |  | 12:22 | 12:22 | 12:25 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-21 | 29442 | 61.3375
1109 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 8:55 | 8:55 | 18:56 | 0 | 10.0167 | 10.0167 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.38526 | WTG Breakdown Maintenance | O2-04 | 31181 | 13013.7368
1110 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 11:34 | 11:34 | 11:57 | 0 | 0.38333 | 0.38333 | check Event And Data log then reset & started wtg. | Close | 0.014744 | WTG Unscheduled Maintenance | O2-26 | 31644 | 505.425
1111 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 20:14 | 20:14 | 20:20 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-15 | 29849 | 124.3708
1112 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 20:49 | 20:49 | 21:30 | 0 | 0.68333 | 0.68333 | after temp reduse then reset & started wtg. | Close | 0.026282 | WTG Unscheduled Maintenance | O2-15 | 29849 | 849.8674
1113 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 21:40 | 22:20 | 23:13 | 0.66667 | 0.88333 | 1.55 | Attend and wtg check MPCB Motor and coolant so found QA008 MPCB Tripped after check voltage and fidbac connection tight after fan on temperature normal then reset and started wtg. | Close | 0.059615 | WTG Breakdown Maintenance | O2-15 | 29849 | 1927.7479
1114 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_16 | TQGXIIPL | GEDA | 3.846% | 558 | Pitch deviation Pitch Back | Major BD |  | 10:19 | 11:00 | 17:03 | 0.68333 | 6.05 | 6.7333 | WTG attend then check related CKT check Axis no 1 battery box found battery lug broken so replace battery then start wtg also winch load test completed. | Close | 0.25897 | WTG Breakdown Maintenance | O2-21 | 29442 | 8260.1167
1115 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 8:55 | 8:55 | 10:24 | 0 | 1.4833 | 1.4833 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.057051 | WTG Breakdown Maintenance | O2-07 | 27380 | 1692.2361
1116 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 18:23 | 18:23 | 18:55 | 0 | 0.53333 | 0.53333 | Shutdown taken by GETCO Team for GETCO Tower line Dismentaling Work. | Close | 0.020513 | WTG Breakdown Maintenance | O2-07 | 27380 | 608.4444
1117 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-08 | O2_24 | TQGXIIPL | GEDA | 3.846% | 700 | Batt. undervoltage/overvoltage | Break down |  | 10:32 | 10:32 | 10:44 | 0 | 0.2 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-20 | 31913 | 265.9417
1118 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-09 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:29 | 14:29 | 14:35 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-12 | 36462 | 151.925
1119 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-09 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 14:24 | 14:24 | 14:30 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 35565 | 148.1875
1120 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-09 | O2_14 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 15:04 | 15:04 | 15:20 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-12 | 36462 | 405.1333
1121 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-09 | O2_18 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:53 | 11:53 | 11:59 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-06 | 40911 | 170.4625
1122 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-09 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down |  | 9:44 | 9:44 | 9:49 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-01 | 38655 | 134.2187
1123 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_01 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down |  | 8:00 | 8:00 | 8:06 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 40326 | 168.025
1124 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_01 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down |  | 20:19 | 21:50 | 24:00 | 1.5167 | 2.1667 | 3.6833 | Turbine Attend for Sim angle E enc.<> act.angle 3 so check error related ckt than check QA001 contactor and it's connection tightness also check all auxillary NO-NC connection than check Motor Encoder connector and connection of Encoder cable than WIP, | Close | 0.14167 | WTG Breakdown Maintenance | O2-26 | 40326 | 6188.9208
1125 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 9:28 | 9:28 | 9:34 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 44939 | 187.2458
1126 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 10:29 | 10:29 | 11:28 | 0 | 0.98333 | 0.98333 | WTG Stop for GETCO line work Shutdown. | Close | 0.037821 | WTG Breakdown Maintenance | O2-07 | 44939 | 1841.2507
1127 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_04 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 12:18 | 12:18 | 12:43 | 0 | 0.41667 | 0.41667 | WTG Stop for GETCO line work Shutdown. | Close | 0.016026 | WTG Breakdown Maintenance | O2-07 | 44939 | 780.191
1128 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 18:56 | 18:56 | 18:59 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-07 | 44939 | 93.6229
1129 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_05 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 12:05 | 12:05 | 12:08 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-02 | 48133 | 100.2771
1130 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:21 | 14:21 | 14:22 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-02 | 48133 | 33.4257
1131 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_06 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 11:55 | 11:55 | 11:56 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-21 | 39222 | 27.2375
1132 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_07 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 10:29 | 10:29 | 12:44 | 0 | 2.25 | 2.25 | WTG Stop for GETCO line work Shutdown. | Close | 0.086538 | WTG Breakdown Maintenance | O2-04 | 45191 | 4236.6562
1133 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 2:45 | 2:45 | 2:51 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 40326 | 168.025
1134 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 7:40 | 7:40 | 7:50 | 0 | 0.16667 | 0.16667 | check Event And Data log then reset & started wtg. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-26 | 40326 | 280.0417
1135 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 7:02 | 7:02 | 7:12 | 0 | 0.16667 | 0.16667 | check Event and Data log then apply shoft reboot then reset & started wtg. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-15 | 39946 | 277.4028
1136 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3395 | Pump cooling sys. overload | Break down |  | 7:16 | 8:30 | 12:58 | 1.2333 | 4.4667 | 5.7 | Attend and check error related ckt than found QA008 MPCB was tripped so check connection also check current setting and check voltage but voltage is cut in one phase so check and remove relay and refix then found MPCB one contect was loose inside than tight and take trail and started Turbine. | Close | 0.21923 | WTG Breakdown Maintenance | O2-15 | 39946 | 9487.175
1137 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 11:08 | 11:08 | 11:11 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-12 | 38012 | 79.1917
1138 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 16:03 | 16:03 | 16:04 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-12 | 38012 | 26.3972
1139 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_15 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:21 | 13:21 | 13:27 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-10 | 24662 | 102.7583
1140 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_17 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Auto reset |  | 10:31 | 10:31 | 10:47 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-22 | 47621 | 529.1222
1141 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 10:29 | 10:29 | 11:03 | 0 | 0.56667 | 0.56667 | WTG Stop for GETCO line work Shutdown. | Close | 0.021795 | WTG Breakdown Maintenance | O2-07 | 44939 | 1061.0597
1142 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 12:18 | 12:18 | 12:43 | 0 | 0.41667 | 0.41667 | WTG Stop for GETCO line work Shutdown. | Close | 0.016026 | WTG Breakdown Maintenance | O2-07 | 44939 | 780.191
1143 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 16:46 | 16:46 | 16:50 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-20 | 41819 | 116.1639
1144 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-10 | O2_25 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Auto reset |  | 19:59 | 19:59 | 20:15 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-01 | 31902 | 354.4667
1145 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_01 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Major BD |  | 0:00 | 0:00 | 13:13 | 0 | 13.2167 | 13.2167 | Turbine Attend for Sim angle E enc.<> act.angle 3 so check error related ckt than check QA001 contactor and it's connection tightness also check all auxillary NO-NC connection than check Motor Encoder connector and connection of Encoder cable than interchange motor Encoder with onther blade than error shifted so found Motor Encoder faulty so arrenge from other site and replace with new one than done blade -3 calibration done and also winch load capacity testing done than started Turbine. | Close | 0.50833 | WTG Breakdown Maintenance | O2-26 | 31821 | 17523.6479
1146 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_01 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:44 | 15:44 | 15:50 | 0 | 0.1 | 0.1 | WTG Stop for PPC parameter Update Work. | Close | 0.0038462 | WTG Breakdown Maintenance | O2-26 | 31821 | 132.5875
1147 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:24 | 15:24 | 15:38 | 0 | 0.23333 | 0.23333 | WTG Stop for PPC parameter Update Work. | Close | 0.0089744 | WTG Breakdown Maintenance | O2-05 | 36794 | 357.7194
1148 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_03 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down |  | 6:46 | 6:46 | 6:50 | 0 | 0.066667 | 0.066667 | check Event and all axis current in Sam than Data log check reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-09 | 31584 | 87.7333
1149 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 15:11 | 15:11 | 15:17 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-02 | 36977 | 154.0708
1150 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 3:06 | 3:06 | 3:19 | 0 | 0.21667 | 0.21667 | check Event And Data log then reset & started wtg. | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-26 | 31821 | 287.2729
1151 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 4:06 | 4:06 | 4:21 | 0 | 0.25 | 0.25 | check Event And Data log then reset & started wtg. | Close | 0.0096154 | WTG Unscheduled Maintenance | O2-26 | 31821 | 331.4687
1152 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_11 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:22 | 15:22 | 15:30 | 0 | 0.13333 | 0.13333 | WTG Stop for PPC parameter Update Work. | Close | 0.0051282 | WTG Breakdown Maintenance | O2-12 | 29594 | 164.4111
1153 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_13 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 2:54 | 2:54 | 2:57 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-11 | 30425 | 63.3854
1154 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:18 | 15:18 | 15:27 | 0 | 0.15 | 0.15 | WTG Stop for PPC parameter Update Work. | Close | 0.0057692 | WTG Breakdown Maintenance | O2-11 | 30425 | 190.1563
1155 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:40 | 15:40 | 15:46 | 0 | 0.1 | 0.1 | WTG Stop for PPC parameter Update Work. | Close | 0.0038462 | WTG Breakdown Maintenance | O2-22 | 42577 | 177.4042
1156 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_24 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 8:51 | 8:51 | 8:55 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-20 | 36328 | 100.9111
1157 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_25 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down |  | 6:20 | 6:20 | 6:32 | 0 | 0.2 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-01 | 9734 | 81.1167
1158 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-11 | O2_26 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 10:19 | 10:19 | 10:28 | 0 | 0.15 | 0.15 | WTG Stop for PPC parameter Update Work. | Close | 0.0057692 | WTG Breakdown Maintenance | O2-01 | 9734 | 60.8375
1159 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-12 | O2_16 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 13:46 | 13:46 | 14:46 | 0 | 1 | 1 | Attend and WTG Check BLS Warning releted ckt found BLS FOS4X module Communication connection loose so retight it start WTG. | Close | 0.038462 | WTG Breakdown Maintenance | O2-21 | 36826 | 1534.4167
1160 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-12 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 2:15 | 2:15 | 2:29 | 0 | 0.23333 | 0.23333 | After temp reduce then reset & started wtg. | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-22 | 38525 | 374.5486
1161 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-12 | O2_23 | TQGXIIPL | GEDA | 3.846% | 72 | Outdoor temperature high | Break down |  | 16:18 | 16:18 | 16:30 | 0 | 0.2 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-11 | 35464 | 295.5333
1162 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-12 | O2_19 | TQGXIIPL | GEDA | 3.846% | 6601 | Wind.dir. diff. level 1 | Break down |  | 18:01 | 18:01 | 18:04 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-06 | 38942 | 81.1292
1163 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-13 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 12:39 | 12:39 | 12:45 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 35207 | 146.6958
1164 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-13 | O2_01 | TQGXIIPL | GEDA | 3.846% | 650 | Pitch controller communication error | Break down |  | 12:46 | 12:46 | 12:49 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-26 | 35207 | 73.3479
1165 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-13 | O2_03 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down |  | 12:37 | 12:37 | 12:47 | 0 | 0.16667 | 0.16667 | check Event And Data log then reset & started wtg. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-09 | 33994 | 236.0694
1166 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-13 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 15:30 | 15:30 | 19:24 | 0 | 3.9 | 3.9 | Blade Bearing inner seal inspection work along with suppiler and found axis 3 inner seal open in one end so refix and apply manually DO then nathing found abnormal so reset and start WTG. | Close | 0.15 | WTG Breakdown Maintenance | O2-09 | 33994 | 5524.025
1167 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-13 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:46 | 11:46 | 11:52 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-07 | 36104 | 150.4333
1168 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-13 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 12:09 | 12:09 | 12:11 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-26 | 35207 | 48.8986
1169 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-13 | O2_11 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 15:15 | 15:15 | 15:22 | 0 | 0.11667 | 0.11667 | check Event and Data log then apply shoft reboot then reset & started wtg. | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-12 | 34595 | 168.1701
1170 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-13 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 2:12 | 2:12 | 2:27 | 0 | 0.25 | 0.25 | check Event and Data log then apply shoft reboot then reset & started wtg. | Close | 0.0096154 | WTG Unscheduled Maintenance | O2-22 | 38130 | 397.1875
1171 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-14 | O2_02 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 17:21 | 17:21 | 17:24 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-05 | 21920 | 45.6667
1172 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-14 | O2_03 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 16:39 | 16:39 | 19:40 | 0 | 3.0167 | 3.0167 | Attend for Blade Bearing Inner seal inspection work along with supplier and found Axis-1 Blade bearing inner seal damage so replace by supplier and apply manually pitching then nothing abnormal so reset and start WTG. | Close | 0.11603 | WTG Breakdown Maintenance | O2-09 | 17985 | 2260.6146
1173 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-14 | O2_08 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 23:28 | 23:28 | 23:34 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 14946 | 62.275
1174 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-14 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 10:39 | 10:39 | 18:18 | 0 | 7.65 | 7.65 | WTG stop for Blade Bearing outer seal Inspection work then after refir the outer seal and apply manual greasing DO than nothing found abnormal so reset than take generation trail at that time PITCH ERROR (Sim angle encoder 2) error was occurred so We check QA001 contector and check Auxilary than found 2 nos Auxilary malfunction so replace it with new one than take trial than reset and start WTG. | Close | 0.29423 | WTG Breakdown Maintenance | O2-10 | 16628 | 5300.175
1175 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-14 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 11:04 | 11:04 | 11:07 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-22 | 18674 | 38.9042
1176 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-14 | O2_20 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down |  | 11:34 | 11:34 | 11:36 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-24 | 16943 | 23.5319
1177 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-14 | O2_20 | TQGXIIPL | GEDA | 3.846% | 178 | SLC MF safe operation speed limit | Break down |  | 20:10 | 20:10 | 20:28 | 0 | 0.3 | 0.3 | check Event and Data log then apply shoft reboot then reset & started wtg. | Close | 0.011538 | WTG Unscheduled Maintenance | O2-24 | 16943 | 211.7875
1178 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-14 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue |  | 19:13 | 19:13 | 19:59 | 0 | 0.76667 | 0.76667 | After Feeder-2 charge than Turbine disconnected from scada. | Close | 0.029487 | WTG Unscheduled Maintenance | O2-06 | 17769 | 567.6208
1179 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-14 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3500 | Grid loss | Connectivity issue |  | 20:10 | 20:10 | 20:35 | 0 | 0.41667 | 0.41667 | After Feeder-2 charge than Turbine disconnected from scada than restore connectivity reset and started WTG. | Close | 0.016026 | WTG Unscheduled Maintenance | O2-06 | 17769 | 308.4896
1180 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-14 | O2_07 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 22:03 | 22:03 | 22:08 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-04 | 19604 | 68.0694
1181 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-14 | O2_26 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down |  | 20:10 | 20:10 | 20:30 | 0 | 0.33333 | 0.33333 | check Event and Data log then apply shoft reboot then reset & started wtg. | Close | 0.012821 | WTG Unscheduled Maintenance | O2-01 | 19047 | 264.5417
1182 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-14 | O2_26 | TQGXIIPL | GEDA | 3.846% | 5510 | Low hydraulic pressure | Break down |  | 20:30 | 20:30 | 20:41 | 0 | 0.18333 | 0.18333 | check Event And Data log then reset & started wtg. | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-01 | 19047 | 145.4979
1183 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-15 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 11:22 | 11:22 | 11:24 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-07 | 6199 | 8.6097
1184 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-15 | O2_04 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 13:05 | 13:05 | 13:07 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-07 | 6199 | 8.6097
1185 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-15 | O2_14 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 18:55 | 18:55 | 19:01 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-12 | 6246 | 26.025
1186 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-15 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 11:43 | 11:43 | 11:44 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-06 | 6453 | 4.4812
1187 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-15 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 13:26 | 13:26 | 13:30 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-06 | 6453 | 17.925
1188 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-15 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 11:49 | 11:49 | 11:50 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-06 | 6453 | 4.4812
1189 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-15 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 13:32 | 13:32 | 13:37 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-06 | 6453 | 22.4062
1190 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-15 | O2_22 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Break down |  | 19:06 | 19:06 | 19:10 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-06 | 6453 | 17.925
1191 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-16 | O2_04 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Customer |  | 14:24 | 14:24 | 15:02 | 0 | 0.63333 | 0.63333 | check Event And Data log then reset & started wtg.( lat reset due to O2-08 VCB trip so wtg discannected from SCADA) | Close | 0.024359 | WTG Unscheduled Maintenance | O2-07 | 35642 | 940.5528
1192 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-16 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 23:40 | 23:40 | 23:48 | 0 | 0.13333 | 0.13333 | check Event And Data log then reset & started wtg. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-02 | 42568 | 236.4889
1193 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-16 | O2_06 | TQGXIIPL | GEDA | 3.846% | 58 | Wind dir.dev. level 2 | Auto reset |  | 19:45 | 19:45 | 19:48 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-21 | 32444 | 67.5917
1194 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-16 | O2_07 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Customer |  | 14:24 | 14:24 | 15:06 | 0 | 0.7 | 0.7 | check Event And Data log then reset & started wtg.( lat reset due to O2-08 VCB trip so wtg discannected from SCADA) | Close | 0.026923 | WTG Unscheduled Maintenance | O2-04 | 36994 | 1078.9917
1195 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-16 | O2_12 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Major BD |  | 10:18 | 10:18 | 24:00 | 0 | 13.6997 | 13.6997 | attend turbine and check error related ckt so found blade 1 QA001 NO contact connection loose so tight it then take take tral time we found blade 2 Root crack so now wtg in breakdown and blade repairing and material shifting work wip. | open | 0.52691 | WTG Breakdown Maintenance | O2-14 | 41004 | 23405.9754
1196 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-16 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 10:14 | 10:14 | 10:26 | 0 | 0.2 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-12 | 9859 | 82.1583
1197 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-16 | O2_17 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 23:27 | 23:27 | 23:44 | 0 | 0.28333 | 0.28333 | check Event And Data log then reset & started wtg. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-22 | 35130 | 414.7292
1198 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-16 | O2_20 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Environment |  | 14:24 | 14:24 | 16:06 | 0 | 1.7 | 1.7 | turbine delay attend due to bad weather conditions like lighting , heavy rain and high wind | Close | 0.065385 | WTG Unscheduled Maintenance | O2-24 | 35934 | 2545.325
1199 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-16 | O2_20 | TQGXIIPL | GEDA | 3.846% | 643 | Sim.angle E enc. <> act.angle 3 | Break down |  | 16:06 | 16:06 | 17:11 | 0 | 1.0833 | 1.0833 | attend turbine and check error related ckt so found blade 3 QA001 NO contact connection loose so tight it then reset and start turbine (turbine delay attend due to bad weather conditions like lighting , heavy rain and high wind) | Close | 0.041667 | WTG Breakdown Maintenance | O2-24 | 35934 | 1622.0208
1200 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-16 | O2_23 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 17:58 | 17:58 | 18:00 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-11 | 39549 | 54.9292
1201 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-16 | O2_23 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Auto reset |  | 23:03 | 23:03 | 23:06 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-11 | 39549 | 82.3937
1202 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-16 | O2_26 | TQGXIIPL | GEDA | 3.846% | 675 | Pitch measuring system 1><2 | Break down |  | 8:09 | 8:09 | 8:23 | 0 | 0.23333 | 0.23333 | after grid resume error is occurs so Checked related error data log then reset & start WTG | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-01 | 39130 | 380.4306
1203 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-17 | O2_01 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 4:04 | 4:04 | 4:13 | 0 | 0.15 | 0.15 | check Event And Data log then reset & started wtg. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-26 | 37582 | 234.8875
1204 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-17 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 0:45 | 0:45 | 1:01 | 0 | 0.26667 | 0.26667 | check Event And Data log then reset & started wtg. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-02 | 42080 | 467.5556
1205 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-17 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 1:45 | 1:45 | 1:57 | 0 | 0.2 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-02 | 42080 | 350.6667
1206 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-17 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 4:41 | 4:41 | 4:45 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-02 | 42080 | 116.8889
1207 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-17 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down |  | 2:57 | 2:57 | 3:13 | 0 | 0.26667 | 0.26667 | check Event And Data log then reset & started wtg. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-13 | 37389 | 415.4333
1208 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-17 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | Attend and check by blade team inspect Root area and remove paint defected area approx. 0.1mtr and another related work WIP. | open | 0.92307 | WTG Breakdown Maintenance | O2-14 | 38123 | 38122.5588
1209 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-17 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 1:05 | 1:05 | 1:22 | 0 | 0.28333 | 0.28333 | check Event And Data log then reset & started wtg. | Close | 0.010897 | WTG Unscheduled Maintenance | O2-22 | 38185 | 450.7951
1210 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-17 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 4:05 | 4:05 | 4:21 | 0 | 0.26667 | 0.26667 | check Event And Data log then reset & started wtg. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-22 | 38185 | 424.2778
1211 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-17 | O2_23 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down |  | 6:55 | 6:55 | 6:59 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-11 | 36162 | 100.45
1212 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-17 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 0:22 | 0:22 | 0:43 | 0 | 0.35 | 0.35 | check Event And Data log then reset & started wtg. | Close | 0.013462 | WTG Unscheduled Maintenance | O2-01 | 37729 | 550.2146
1213 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-17 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 2:08 | 2:08 | 2:19 | 0 | 0.18333 | 0.18333 | check Event And Data log then reset & started wtg. | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-01 | 37729 | 288.2076
1214 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-18 | O2_03 | TQGXIIPL | GEDA | 3.846% | 520 | Overload axis 1 | Break down |  | 0:55 | 0:55 | 1:04 | 0 | 0.15 | 0.15 | check Event And Data log then reset & started wtg. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-09 | 43011 | 268.8187
1215 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-18 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 18:39 | 18:39 | 19:33 | 0 | 0.9 | 0.9 | check Event And Data log then apply shoft reboot then reset & started wtg. | Close | 0.034615 | WTG Unscheduled Maintenance | O2-26 | 46495 | 1743.5625
1216 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-18 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 21:04 | 21:50 | 23:28 | 0.76667 | 1.6333 | 2.4 | attend turbine and check error related ckt so found blade 1 QA001 NO contact connection loose so tight it then reset and start turbine. | Close | 0.092308 | WTG Breakdown Maintenance | O2-26 | 46495 | 4649.5
1217 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-18 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | sky lift installation work complate and inspection not done due to whether condition was not ok rain and wind is very high so further plane tomorrow | open | 0.92307 | WTG Environmental | O2-14 | 45291 | 45290.4758
1218 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-18 | O2_23 | TQGXIIPL | GEDA | 3.846% | 4093 | Rel. air hum. tower base inside too high (in operation) | Break down |  | 7:35 | 7:35 | 7:36 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-11 | 44761 | 31.084
1219 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 10:26 | 10:26 | 10:29 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-26 | 61863 | 128.8812
1220 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 2:38 | 2:38 | 2:49 | 0 | 0.18333 | 0.18333 | check Event And Data log then found grid voltage is high (712v)so reset & started wtg. | Close | 0.0070513 | WTG Unscheduled Maintenance | O2-02 | 61807 | 472.1368
1221 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 3:35 | 3:35 | 3:40 | 0 | 0.083333 | 0.083333 | check Event And Data log then found grid voltage is high (711v)so reset & started wtg. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-02 | 61807 | 214.6076
1222 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 4:44 | 4:44 | 4:48 | 0 | 0.066667 | 0.066667 | check Event And Data log then found grid voltage is high (715v)so reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-02 | 61807 | 171.6861
1223 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 6:06 | 6:06 | 6:11 | 0 | 0.083333 | 0.083333 | check Event And Data log then found grid voltage is high (714v)so reset & started wtg. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-02 | 61807 | 214.6076
1224 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 13:39 | 13:39 | 13:42 | 0 | 0.05 | 0.05 | check Event And Data log then found grid voltage is high (714v)so reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-02 | 61807 | 128.7646
1225 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 16:51 | 16:51 | 16:59 | 0 | 0.13333 | 0.13333 | check Event And Data log then reset & started wtg. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-26 | 61863 | 343.6833
1226 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 21:10 | 21:10 | 21:25 | 0 | 0.25 | 0.25 | check Event And Data log then reset & started wtg. | Close | 0.0096154 | WTG Unscheduled Maintenance | O2-26 | 61863 | 644.4063
1227 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | sky lift installation work complate and inspection not done due to whether condition was not ok rain and wind is very high so further plane tomorrow | open | 0.92307 | WTG Environmental | O2-14 | 62218 | 62217.2799
1228 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 0:12 | 0:12 | 0:22 | 0 | 0.16667 | 0.16667 | check Event And Data log then found grid voltage is high (715v)so reset & started wtg. | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-22 | 61067 | 424.0764
1229 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 2:31 | 2:31 | 2:51 | 0 | 0.33333 | 0.33333 | check Event And Data log then found grid voltage is high (713v)so reset & started wtg. | Close | 0.012821 | WTG Unscheduled Maintenance | O2-22 | 61067 | 848.1528
1230 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 3:44 | 3:44 | 3:48 | 0 | 0.066667 | 0.066667 | check Event And Data log then found grid voltage is high (713v)so reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-22 | 61067 | 169.6306
1231 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 4:23 | 4:23 | 4:26 | 0 | 0.05 | 0.05 | check Event And Data log then found grid voltage is high (718v)so reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-22 | 61067 | 127.2229
1232 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 5:49 | 5:49 | 5:52 | 0 | 0.05 | 0.05 | check Event And Data log then found grid voltage is high (711v)so reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-22 | 61067 | 127.2229
1233 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 6:22 | 6:22 | 6:25 | 0 | 0.05 | 0.05 | check Event And Data log then found grid voltage is high (715v)so reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-22 | 61067 | 127.2229
1234 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 12:52 | 12:52 | 12:55 | 0 | 0.05 | 0.05 | check Event And Data log then found grid voltage is high (718v)so reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-22 | 61067 | 127.2229
1235 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 13:21 | 13:21 | 13:25 | 0 | 0.066667 | 0.066667 | check Event And Data log then found grid voltage is high (724v)so reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-22 | 61067 | 169.6306
1236 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 13:55 | 13:55 | 13:58 | 0 | 0.05 | 0.05 | check Event And Data log then found grid voltage is high (718v)so reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-22 | 61067 | 127.2229
1237 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 14:08 | 14:08 | 14:12 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-24 | 63198 | 175.55
1238 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-19 | O2_25 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 3:57 | 3:57 | 4:03 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-01 | 60392 | 251.6333
1239 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_02 | TQGXIIPL | GEDA | 3.846% | 4960 | Tower oscillation YF | Break down |  | 12:18 | 12:18 | 12:22 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-05 | 54458 | 151.2722
1240 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_03 | TQGXIIPL | GEDA | 3.846% | 520 | Overload axis 1 | Break down |  | 3:07 | 3:07 | 3:25 | 0 | 0.3 | 0.3 | check Event And Data log then reset & started wtg. | Close | 0.011538 | WTG Unscheduled Maintenance | O2-09 | 55200 | 690
1241 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 10:33 | 10:33 | 10:34 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-07 | 26899 | 18.6799
1242 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_04 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down |  | 19:50 | 19:50 | 20:38 | 0 | 0.8 | 0.8 | After grid resume check Event And Data log then reset & started wtg.( lat reset due to O2-07 VCB trip so wtg discannected from SCADA) | Close | 0.030769 | WTG Unscheduled Maintenance | O2-07 | 26899 | 896.6333
1243 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 23:40 | 23:40 | 23:47 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-07 | 26899 | 130.759
1244 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_06 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:50 | 19:50 | 20:36 | 0 | 0.76667 | 0.76667 | After grid resume Converter RFO (CAN) singnal not available After single available then reset and start wtg | Close | 0.029487 | WTG Unscheduled Maintenance | O2-21 | 26386 | 842.8861
1245 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_07 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down |  | 12:07 | 12:07 | 12:13 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-04 | 28462 | 118.5917
1246 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 0:53 | 0:53 | 0:56 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-26 | 26295 | 54.7812
1247 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_08 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 2:35 | 2:35 | 5:09 | 0 | 2.5667 | 2.5667 | attend and found axis 1 encoder cable lag broken so rectification done then reset start WTG now WTG under observation. | Close | 0.098718 | WTG Breakdown Maintenance | O2-26 | 26295 | 2812.1042
1248 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 9:42 | 9:42 | 9:49 | 0 | 0.11667 | 0.11667 | check Event And Data log then reset & started wtg. | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-26 | 26295 | 127.8229
1249 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 22:22 | 22:22 | 22:30 | 0 | 0.13333 | 0.13333 | check Event And Data log then reset & started wtg. | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-26 | 26295 | 146.0833
1250 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 23:08 | 23:08 | 23:17 | 0 | 0.15 | 0.15 | check Event And Data log then reset & started wtg. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-26 | 26295 | 164.3437
1251 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_10 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Auto reset |  | 15:33 | 15:33 | 15:34 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-15 | 48939 | 33.9854
1252 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | sky lift installation work complate and inspection not done due to whether condition was not ok rain and wind is very high so further plane tomorrow | open | 0.92307 | WTG Environmental | O2-14 | 53088 | 53087.3856
1253 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_18 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:50 | 19:50 | 20:33 | 0 | 0.71667 | 0.71667 | After grid resume Converter RFO (CAN) singnal not available After single available then reset and start wtg | Close | 0.027564 | WTG Unscheduled Maintenance | O2-06 | 25348 | 756.9194
1254 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_19 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 19:50 | 21:24 | 22:54 | 1.5667 | 1.5 | 3.0667 | After grid resume error is occurs so Checked related circuit and found FC008 MCB out put not come so all MCB trip and check proper mechanism is working then cherge all MCB then reset & start WTG | Close | 0.11795 | WTG Breakdown Maintenance | O2-07 | 26899 | 3437.0944
1255 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_21 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 19:50 | 19:50 | 21:14 | 0 | 1.4 | 1.4 | After grid resume Converter RFO (CAN) singnal not available After single available then reset and start wtg | Close | 0.053846 | WTG Unscheduled Maintenance | O2-06 | 25348 | 1478.6333
1256 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1732 | Max. oil temperature gearbox input | Break down |  | 1:24 | 1:24 | 1:26 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-11 | 52720 | 73.2222
1257 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1732 | Max. oil temperature gearbox input | Break down |  | 1:50 | 1:50 | 2:04 | 0 | 0.23333 | 0.23333 | check Event And Data log then found temp sensor malfunction apply shoft reboot then reset & started wtg. | Close | 0.0089744 | WTG Unscheduled Maintenance | O2-11 | 52720 | 512.5556
1258 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-20 | O2_26 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 21:01 | 21:01 | 22:08 | 0 | 1.1167 | 1.1167 | After grid resume Converter RFO (CAN) singnal not available After single available then reset and start wtg | Close | 0.042949 | WTG Unscheduled Maintenance | O2-01 | 53793 | 2502.8688
1259 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-21 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 4:58 | 4:58 | 4:59 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-07 | 48182 | 33.4597
1260 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-21 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 5:47 | 5:47 | 5:50 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-07 | 48182 | 100.3792
1261 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-21 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:50 | 11:50 | 11:52 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-07 | 48182 | 66.9194
1262 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-21 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 16:31 | 16:31 | 16:33 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-07 | 48182 | 66.9194
1263 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-21 | O2_05 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 12:00 | 12:00 | 12:02 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-02 | 52214 | 72.5194
1264 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-21 | O2_07 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down |  | 5:47 | 5:47 | 6:03 | 0 | 0.26667 | 0.26667 | check Event And Data log then reset & started wtg. | Close | 0.010256 | WTG Unscheduled Maintenance | O2-04 | 46630 | 518.1111
1265 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-21 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 23:38 | 23:38 | 23:47 | 0 | 0.15 | 0.15 | check Event And Data log then reset & started wtg. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-26 | 52790 | 329.9375
1266 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-21 | O2_09 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down |  | 15:01 | 15:01 | 15:07 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-03 | 49894 | 207.8917
1267 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-21 | O2_11 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down |  | 22:15 | 22:15 | 22:22 | 0 | 0.11667 | 0.11667 | check Event And Data log then reset & started wtg. | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-13 | 49448 | 240.3722
1268 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-21 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | sky lift installation work complate and inspection not done due to whether condition was not ok rain and wind is very high so further plane tomorrow | open | 0.92307 | WTG Environmental | O2-14 | 48944 | 48943.4335
1269 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-21 | O2_15 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 11:30 | 11:30 | 12:19 | 0 | 0.81667 | 0.81667 | wtg manual stop for customer audit work. | Close | 0.03141 | WTG Breakdown Maintenance | O2-10 | 50278 | 1710.8486
1270 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-21 | O2_20 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 11:26 | 11:26 | 12:22 | 0 | 0.93333 | 0.93333 | wtg manual stop for customer audit work. | Close | 0.035897 | WTG Breakdown Maintenance | O2-24 | 50597 | 1967.6611
1271 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-21 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 13:04 | 13:04 | 13:38 | 0 | 0.56667 | 0.56667 | wtg manual stop for customer audit work. | Close | 0.021795 | WTG Breakdown Maintenance | O2-11 | 47808 | 1128.8
1272 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-22 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 5:56 | 5:56 | 6:02 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-26 | 31309 | 130.4542
1273 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-22 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 7:40 | 7:40 | 7:43 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-02 | 32913 | 68.5688
1274 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-22 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | ROW issue |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | sky lift installation work complate and inspection not done due to ROW issue. | open | 0.92307 | WTG Force Majeure | O2-14 | 31473 | 31472.6357
1275 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-22 | O2_18 | TQGXIIPL | GEDA | 3.846% | 1316 | Timeout fault rotor bear. lubr. | Break down |  | 6:14 | 6:14 | 6:36 | 0 | 0.36667 | 0.36667 | check Event And Data log then apply manual DO for rotor bearing luber found is ok then reset & started wtg. | Close | 0.014103 | WTG Unscheduled Maintenance | O2-06 | 28395 | 433.8125
1276 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-22 | O2_18 | TQGXIIPL | GEDA | 3.846% | 1316 | Timeout fault rotor bear. lubr. | Break down |  | 20:34 | 20:34 | 20:43 | 0 | 0.15 | 0.15 | check Event And Data log then apply manual DO for rotor bearing luber found is ok then reset & started wtg. | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-06 | 28395 | 177.4688
1277 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-22 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 18:20 | 18:20 | 19:16 | 0 | 0.93333 | 0.93333 | WTG manual stop for blade load sensor related parameter checking work. | Close | 0.035897 | WTG Unscheduled Maintenance | O2-07 | 25670 | 998.2778
1278 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-22 | O2_22 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 18:12 | 18:12 | 18:15 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-06 | 28395 | 59.1562
1279 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-23 | O2_05 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 6:00 | 6:00 | 6:36 | 0 | 0.6 | 0.6 | check Event And Data log then apply shoft reboot then reset & started wtg. | Close | 0.023077 | WTG Unscheduled Maintenance | O2-02 | 36662 | 916.55
1280 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-23 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 16:53 | 16:53 | 16:58 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-02 | 36662 | 127.2986
1281 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-23 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 17:31 | 17:31 | 17:36 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-26 | 35736 | 124.0833
1282 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-23 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 18:31 | 18:31 | 18:44 | 0 | 0.21667 | 0.21667 | check Event And Data log then reset & started wtg. | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-26 | 35736 | 322.6167
1283 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-23 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | sky lift installation work complate and inspection not done due to whether condition was not ok rain and wind is very high so further plane tomorrow | Open | 0.92307 | WTG Environmental | O2-14 | 35000 | 34999.5949
1284 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-23 | O2_14 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 10:21 | 10:21 | 10:24 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-12 | 0 | 0
1285 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-23 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6605 | Wind.dir. diff. level 2 | Break down |  | 17:51 | 17:51 | 17:54 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-21 | 32231 | 67.1479
1286 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-23 | O2_18 | TQGXIIPL | GEDA | 3.846% | 1316 | Timeout fault rotor bear. lubr. | Break down |  | 10:42 | 10:42 | 10:47 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Unscheduled Maintenance | O2-06 | 32886 | 114.1875
1287 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-23 | O2_19 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 8:19 | 8:19 | 8:35 | 0 | 0.26667 | 0.26667 | WTG manual stop for blade load sensor related parameter checking work. | Close | 0.010256 | WTG Breakdown Maintenance | O2-07 | 30932 | 343.6889
1288 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_02 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Auto reset |  | 5:54 | 5:54 | 5:55 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-05 | 46848 | 32.5333
1289 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 1:45 | 1:45 | 1:47 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-07 | 44567 | 61.8986
1290 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 2:39 | 2:39 | 2:41 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-07 | 44567 | 61.8986
1291 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_04 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 6:03 | 6:03 | 6:06 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-07 | 44567 | 92.8479
1292 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 7:33 | 7:33 | 7:34 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-07 | 44567 | 30.9493
1293 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 3:51 | 3:51 | 4:10 | 0 | 0.31667 | 0.31667 | check Event And Data log then reset & started wtg. | Close | 0.012179 | WTG Breakdown Maintenance | O2-02 | 46613 | 615.0326
1294 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Auto reset |  | 0:03 | 0:03 | 0:06 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-26 | 45247 | 94.2646
1295 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Auto reset |  | 0:40 | 0:40 | 0:42 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-26 | 45247 | 62.8431
1296 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 1:12 | 1:12 | 1:17 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Breakdown Maintenance | O2-26 | 45247 | 157.1076
1297 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 1:39 | 1:39 | 1:45 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | WTG Breakdown Maintenance | O2-26 | 45247 | 188.5292
1298 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_08 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Break down |  | 3:04 | 3:04 | 3:13 | 0 | 0.15 | 0.15 | check Event And Data log then reset & started wtg. | Close | 0.0057692 | WTG Breakdown Maintenance | O2-26 | 45247 | 282.7938
1299 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_08 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Break down |  | 5:46 | 5:46 | 6:01 | 0 | 0.25 | 0.25 | check Event And Data log then reset & started wtg. | Close | 0.0096154 | WTG Breakdown Maintenance | O2-26 | 45247 | 471.3229
1300 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_08 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Break down |  | 8:23 | 8:23 | 8:35 | 0 | 0.2 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | WTG Breakdown Maintenance | O2-26 | 45247 | 377.0583
1301 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 6:19 | 6:19 | 6:27 | 0 | 0.13333 | 0.13333 | check Event And Data log then reset & started wtg. | Close | 0.0051282 | WTG Breakdown Maintenance | O2-22 | 40585 | 225.4722
1302 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_18 | TQGXIIPL | GEDA | 3.846% | 1316 | Timeout fault rotor bear. lubr. | Break down |  | 0:47 | 0:47 | 0:54 | 0 | 0.11667 | 0.11667 | check Event And Data log then reset & started wtg. | Close | 0.0044872 | WTG Breakdown Maintenance | O2-06 | 42185 | 205.066
1303 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_18 | TQGXIIPL | GEDA | 3.846% | 1316 | Timeout fault rotor bear. lubr. | Break down |  | 14:56 | 14:56 | 15:03 | 0 | 0.11667 | 0.11667 | check Event And Data log then reset & started wtg. | Close | 0.0044872 | WTG Breakdown Maintenance | O2-06 | 42185 | 205.066
1304 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 5:41 | 5:41 | 5:45 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-24 | 43964 | 122.1222
1305 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_22 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 0:56 | 0:56 | 1:00 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | WTG Unscheduled Maintenance | O2-06 | 42185 | 117.1806
1306 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_22 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 2:41 | 2:41 | 2:43 | 0 | 0.033333 | 0.033333 | Auto reset | Close | 0.0012821 | WTG Unscheduled Maintenance | O2-06 | 42185 | 58.5903
1307 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Environment |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | Today Blade Root TE Joint both top side and bottom side defect grinding work almost complate and tomorrow plan for first layer inspection work. | Open | 0.92307 | WTG Environmental | O2-14 | 43210 | 43209.4999
1308 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-24 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 6:45 | 6:45 | 8:15 | 0 | 1.5 | 1.5 | Check event log fast log found abnormal temperature value after trail so ok then reset and started wtg | Close | 0.057692 | WTG Breakdown Maintenance | O2-26 | 45247 | 2827.9375
1309 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-25 | O2_01 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 6:52 | 6:52 | 6:54 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-26 | 9536 | 13.2444
1310 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-25 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 22:58 | 22:58 | 24:00 | 0 | 1.0333 | 1.0333 | Attended wtg due to Blade bearing lubrication failure Warnning checked lubrication Pump motor connection found ok verified lubrication system feedback connectio work in progress (WIP). | Close | 0.039744 | WTG Breakdown Maintenance | O2-05 | 10550 | 454.2361
1311 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-25 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Environment |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | Today Blade Root TE Joint both top side and bottom side defect grinding work complate And Defect laminatin all layer removed Done tode Approx 4 mtr WIP((whether condition was not ok rain and wind is very high )) | Open | 0.92307 | WTG Environmental | O2-14 | 8612 | 8611.9003
1312 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-25 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 10:36 | 10:36 | 11:28 | 0 | 0.86667 | 0.86667 | Attend turbine and check generator earthing brush found brush worn out so replace its then reset and started wtg. | Close | 0.033333 | WTG Breakdown Maintenance | O2-11 | 10093 | 364.4694
1313 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-25 | O2_17 | TQGXIIPL | GEDA | 3.846% | 550 | Pitch current asymmetry | Break down |  | 6:07 | 6:07 | 6:20 | 0 | 0.21667 | 0.21667 | check Event And Data log then reset & started wtg. | Close | 0.0083333 | WTG Breakdown Maintenance | O2-22 | 14081 | 127.1201
1314 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-25 | O2_18 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 17:04 | 17:04 | 18:28 | 0 | 1.4 | 1.4 | Attended wtg due to inside nacell high temperature warring check all related connections and verified PT100 Sensor wiring found loose connection Tightened PT100 Sensor connection after trail so ok then reset and startted wtg. | Close | 0.053846 | WTG Breakdown Maintenance | O2-06 | 13541 | 789.8917
1315 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-26 | O2_02 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 0:00 | 0:00 | 0:37 | 0 | 0.61667 | 0.61667 | malfunction with the KF007 relay lubrication pump, but after retightening the A1 and A2 connections and verifying the feedback, the pump began working correctly during the trial and was then reset and started wtg. | Close | 0.023718 | WTG Breakdown Maintenance | O2-05 | 6206 | 159.4597
1316 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-26 | O2_07 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Auto reset |  | 7:23 | 7:23 | 7:24 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-04 | 6918 | 4.8042
1317 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-26 | O2_08 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 7:00 | 7:00 | 7:08 | 0 | 0.13333 | 0.13333 | check Event And Data log then reset & started wtg. | Close | 0.0051282 | WTG Breakdown Maintenance | O2-26 | 6401 | 35.5611
1318 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-26 | O2_08 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 11:31 | 11:31 | 11:46 | 0 | 0.25 | 0.25 | check Event And Data log then reset & started wtg. | Close | 0.0096154 | WTG Breakdown Maintenance | O2-26 | 6401 | 66.6771
1319 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-26 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Environment |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | Surface grinding Done and chemfering and Marking WIP (whether condition was not ok rain and wind is very high ) | Open | 0.92307 | WTG Environmental | O2-14 | 6657 | 6656.923
1320 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-26 | O2_16 | TQGXIIPL | GEDA | 3.846% | 6505 | Wind.sp. diff. level 2 | Break down |  | 13:54 | 14:15 | 19:06 | 0.35 | 4.85 | 5.2 | Check error related data Scada so found Ultrasonic sensor 2 value malfunction so Attend turbine and check error related circuit so found Ultrasonic sensor 2 failure so arrange material and replace it then reset and start turbine.(turbine delay start due to bad weather conditions ) | Close | 0.2 | WTG Breakdown Maintenance | O2-21 | 7106 | 1539.6333
1321 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-26 | O2_22 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 15:42 | 15:42 | 15:47 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Breakdown Maintenance | O2-06 | 7570 | 26.2847
1322 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-26 | O2_22 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 18:06 | 18:06 | 19:37 | 0 | 1.5167 | 1.5167 | WTG stopped due to a software update and an error related to the pitch measuring system 1><2 between shift . After a hard reboot and a successful trial Then reset and started wtg | Close | 0.058333 | WTG Breakdown Maintenance | O2-06 | 7570 | 478.3819
1323 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-26 | O2_23 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 17:18 | 17:18 | 17:24 | 0 | 0.1 | 0.1 | WTG manually stopping software update After reset and started wtg | Close | 0.0038462 | WTG Breakdown Maintenance | O2-11 | 6362 | 26.5083
1324 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-27 | O2_03 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 1:11 | 1:11 | 1:13 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-09 | 31282 | 43.4472
1325 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-27 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 23:47 | 23:47 | 23:50 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Breakdown Maintenance | O2-02 | 29694 | 61.8625
1326 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-27 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 21:57 | 21:57 | 22:02 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Breakdown Maintenance | O2-26 | 31562 | 109.5903
1327 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-27 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Environment |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | whether condition was not ok rain and wind is very high | Open | 0.92307 | WTG Environmental | O2-14 | 32706 | 32705.6215
1328 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-27 | O2_13 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Break down |  | 14:03 | 14:03 | 18:16 | 0 | 4.2167 | 4.2167 | manual stop on the WTG to carry out slip ring modification work, and then after completing the task After reset and started wtg | Close | 0.16218 | WTG Breakdown Maintenance | O2-11 | 32970 | 5792.6458
1329 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-27 | O2_13 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 18:50 | 18:50 | 18:54 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Breakdown Maintenance | O2-11 | 32970 | 91.5833
1330 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-27 | O2_17 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset |  | 14:15 | 14:15 | 14:22 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-22 | 37800 | 183.75
1331 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-27 | O2_20 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down |  | 5:58 | 5:58 | 6:15 | 0 | 0.28333 | 0.28333 | check Event And Data log then reset & started wtg. | Close | 0.010897 | WTG Breakdown Maintenance | O2-24 | 32878 | 388.1431
1332 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-27 | O2_21 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 6:16 | 6:16 | 6:25 | 0 | 0.15 | 0.15 | Auto reset | Close | 0.0057692 | WTG Unscheduled Maintenance | O2-06 | 35928 | 224.55
1333 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-27 | O2_23 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 15:05 | 15:05 | 15:21 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-11 | 32970 | 366.3333
1334 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_02 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 8:17 | 8:17 | 8:19 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-05 | 54703 | 75.9764
1335 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_02 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 14:07 | 14:07 | 14:14 | 0 | 0.11667 | 0.11667 | Auto reset | Close | 0.0044872 | WTG Unscheduled Maintenance | O2-05 | 54703 | 265.9174
1336 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_08 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Break down |  | 7:45 | 7:45 | 7:48 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Breakdown Maintenance | O2-26 | 55344 | 115.3
1337 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 8:13 | 8:13 | 8:19 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | WTG Breakdown Maintenance | O2-26 | 55344 | 230.6
1338 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_08 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Break down |  | 8:56 | 8:56 | 9:20 | 0 | 0.4 | 0.4 | check Event And Data log then reset & started wtg. | Close | 0.015385 | WTG Breakdown Maintenance | O2-26 | 55344 | 922.4
1339 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 9:37 | 10:56 | 13:17 | 1.3167 | 2.35 | 3.6667 | attended wtg check circuit identified a faulty motor encoder cable. After replacing it with a new one then reset and started wtg. | Close | 0.14103 | WTG Breakdown Maintenance | O2-26 | 55344 | 8455.3333
1340 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_08 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Break down |  | 19:58 | 19:58 | 20:03 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Breakdown Maintenance | O2-26 | 55344 | 192.1667
1341 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 20:35 | 20:35 | 20:36 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | WTG Breakdown Maintenance | O2-26 | 55344 | 38.4333
1342 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_10 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Auto reset |  | 14:24 | 14:24 | 14:25 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-15 | 58053 | 40.3146
1343 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_13 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset |  | 19:50 | 19:50 | 20:00 | 0 | 0.16667 | 0.16667 | Auto reset | Close | 0.0064103 | WTG Unscheduled Maintenance | O2-11 | 56457 | 392.0625
1344 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Environment |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | Weather condition was not ok rain and wind was very high | Open | 0.92307 | WTG Environmental | O2-14 | 56319 | 56318.3482
1345 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset |  | 14:07 | 14:07 | 14:13 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 56225 | 234.2708
1346 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 15:01 | 15:01 | 15:07 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-21 | 56225 | 234.2708
1347 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 13:23 | 13:23 | 13:27 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Breakdown Maintenance | O2-22 | 58011 | 161.1417
1348 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 20:14 | 20:14 | 20:16 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-22 | 58011 | 80.5708
1349 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_17 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 18:14 | 18:14 | 18:17 | 0 | 0.05 | 0.05 | Auto reset | Close | 0.0019231 | WTG Unscheduled Maintenance | O2-22 | 58011 | 120.8562
1350 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 21:50 | 21:50 | 21:54 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Breakdown Maintenance | O2-22 | 58011 | 161.1417
1351 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 22:27 | 22:27 | 22:31 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Breakdown Maintenance | O2-22 | 58011 | 161.1417
1352 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_18 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down |  | 11:38 | 11:38 | 11:44 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | WTG Breakdown Maintenance | O2-06 | 58092 | 242.05
1353 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_20 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 11:40 | 11:40 | 11:46 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-24 | 54860 | 228.5833
1354 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_21 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 9:36 | 9:36 | 9:49 | 0 | 0.21667 | 0.21667 | Auto reset | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-06 | 58092 | 524.4417
1355 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_22 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Auto reset |  | 14:36 | 14:36 | 14:37 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-06 | 58092 | 40.3417
1356 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_23 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset |  | 16:03 | 16:03 | 16:09 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-11 | 56457 | 235.2375
1357 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_23 | TQGXIIPL | GEDA | 3.846% | 2520 | Gen.speed analog<>gear.speed | Break down |  | 20:00 | 20:00 | 20:11 | 0 | 0.18333 | 0.18333 | check Event And Data log then reset & started wtg. | Close | 0.0070513 | WTG Breakdown Maintenance | O2-11 | 56457 | 431.2687
1358 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_24 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset |  | 14:05 | 14:05 | 14:13 | 0 | 0.13333 | 0.13333 | Auto reset | Close | 0.0051282 | WTG Unscheduled Maintenance | O2-20 | 52311 | 290.6167
1359 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_04 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 23:10 | 23:10 | 23:11 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-07 | 53572 | 37.2028
1360 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 23:42 | 23:42 | 23:47 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Breakdown Maintenance | O2-26 | 55344 | 192.1667
1361 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-28 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3000 | Frequency converter not ready | Break down |  | 23:42 | 23:42 | 23:48 | 0 | 0.1 | 0.1 | check Event And Data log then reset & started wtg. | Close | 0.0038462 | WTG Breakdown Maintenance | O2-22 | 58011 | 241.7125
1362 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_01 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 10:15 | 10:15 | 10:21 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2_26 | 55208 | 230.0333
1363 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_03 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down |  | 2:56 | 2:56 | 3:00 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | WTG Unscheduled Maintenance | O2_09 | 45425 | 126.1806
1364 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 0:33 | 0:33 | 0:35 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2_02 | 56261 | 78.1403
1365 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 3:11 | 3:11 | 3:13 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2_02 | 56261 | 78.1403
1366 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 4:37 | 4:37 | 4:40 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Breakdown Maintenance | O2_02 | 56261 | 117.2104
1367 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 20:00 | 20:00 | 20:08 | 0 | 0.13333 | 0.13333 | check Event And Data log then reset & started wtg. | Close | 0.0051282 | WTG Breakdown Maintenance | O2_02 | 56261 | 312.5611
1368 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 20:40 | 20:40 | 20:42 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2_02 | 56261 | 78.1403
1369 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_08 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down |  | 1:35 | 1:35 | 1:39 | 0 | 0.066667 | 0.066667 | Auto reset | Close | 0.0025641 | WTG Unscheduled Maintenance | O2_26 | 55208 | 153.3556
1370 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 1:50 | 1:50 | 1:52 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2_26 | 55208 | 76.6778
1371 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 6:50 | 6:50 | 6:55 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Breakdown Maintenance | O2_26 | 55208 | 191.6944
1372 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 7:43 | 7:43 | 7:48 | 0 | 0.083333 | 0.083333 | check Event And Data log then reset & started wtg. | Close | 0.0032051 | WTG Breakdown Maintenance | O2_26 | 55208 | 191.6944
1373 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 10:14 | 10:14 | 10:30 | 0 | 0.26667 | 0.26667 | check Event And Data log then reset & started wtg. | Close | 0.010256 | WTG Breakdown Maintenance | O2_26 | 55208 | 613.4222
1374 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 11:48 | 11:48 | 11:58 | 0 | 0.16667 | 0.16667 | check Event And Data log then reset & started wtg. | Close | 0.0064103 | WTG Breakdown Maintenance | O2_26 | 55208 | 383.3889
1375 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 14:00 | 14:00 | 14:25 | 0 | 0.41667 | 0.41667 | check Event And Data log then reset & started wtg. | Close | 0.016026 | WTG Breakdown Maintenance | O2_26 | 55208 | 958.4722
1376 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 18:56 | 18:56 | 19:15 | 0 | 0.31667 | 0.31667 | check Event And Data log then reset & started wtg. | Close | 0.012179 | WTG Breakdown Maintenance | O2_26 | 55208 | 728.4389
1377 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 19:35 | 19:35 | 19:54 | 0 | 0.31667 | 0.31667 | check Event And Data log then reset & started wtg. | Close | 0.012179 | WTG Breakdown Maintenance | O2_26 | 55208 | 728.4389
1378 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_09 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Break down |  | 12:35 | 12:35 | 12:51 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2_03 | 53336 | 592.6222
1379 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_09 | TQGXIIPL | GEDA | 3.846% | 3110 | Frequency converter error | Break down |  | 12:55 | 12:55 | 12:57 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2_03 | 53336 | 74.0778
1380 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_09 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down |  | 19:19 | 19:19 | 19:31 | 0 | 0.2 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | WTG Breakdown Maintenance | O2_03 | 53336 | 444.4667
1381 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_09 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down |  | 21:00 | 22:00 | 24:00 | 1 | 1.9997 | 2.9997 | attend and check error related ckt so found XD209 TB and TB003 field rectifier fuse failure so arrange material WIP. | Open | 0.11537 | WTG Breakdown Maintenance | O2_03 | 53336 | 6666.3827
1382 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_10 | TQGXIIPL | GEDA | 3.846% | 3271 | Converter torque monitor level 1 | Break down |  | 19:32 | 19:32 | 19:34 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2_15 | 56720 | 78.7778
1383 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Major BD |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | Weather condition was not ok rain and wind was very high so further plane tomorrow. | Open | 0.92307 | WTG Environmental | O2_14 | 58023 | 58022.3284
1384 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_16 | TQGXIIPL | GEDA | 3.846% | 175 | SLC error | Break down |  | 1:00 | 1:00 | 1:01 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | WTG Breakdown Maintenance | O2_21 | 62347 | 43.2965
1385 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 1:59 | 1:59 | 2:01 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2_22 | 63422 | 88.0861
1386 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 2:29 | 2:29 | 2:32 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Breakdown Maintenance | O2_22 | 63422 | 132.1292
1387 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 5:17 | 5:17 | 5:19 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2_22 | 63422 | 88.0861
1388 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 5:55 | 5:55 | 5:59 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Breakdown Maintenance | O2_22 | 63422 | 176.1722
1389 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 6:27 | 6:27 | 6:31 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Breakdown Maintenance | O2_22 | 63422 | 176.1722
1390 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 20:15 | 20:15 | 20:23 | 0 | 0.13333 | 0.13333 | check Event And Data log then reset & started wtg. | Close | 0.0051282 | WTG Breakdown Maintenance | O2_22 | 63422 | 352.3444
1391 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_19 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Break down |  | 12:29 | 12:29 | 12:37 | 0 | 0.13333 | 0.13333 | check Event And Data log then reset & started wtg. | Close | 0.0051282 | WTG Breakdown Maintenance | O2_07 | 57606 | 320.0333
1392 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_21 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Break down |  | 21:13 | 21:13 | 21:14 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2_06 | 62725 | 43.559
1393 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-29 | O2_23 | TQGXIIPL | GEDA | 3.846% | 1732 | Max. oil temperature gearbox input | Break down |  | 19:38 | 19:38 | 19:55 | 0 | 0.28333 | 0.28333 | check Event And Data log then found temp sensor malfunctioning so apply shoft reboot then reset & started wtg. | Close | 0.010897 | WTG Breakdown Maintenance | O2_11 | 57284 | 676.2694
1394 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 13:13 | 13:13 | 13:22 | 0 | 0.15 | 0.15 | check Event And Data log then reset & started wtg. | Close | 0.0057692 | WTG Breakdown Maintenance | O2-02 | 53878 | 336.7375
1395 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_05 | TQGXIIPL | GEDA | 3.846% | 305 | Brake control | Auto reset |  | 13:23 | 13:23 | 13:24 | 0 | 0.016667 | 0.016667 | Auto reset | Close | 0.00064103 | WTG Unscheduled Maintenance | O2-02 | 53878 | 37.4153
1396 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_05 | TQGXIIPL | GEDA | 3.846% | 6130 | Yaw speed high | Auto reset |  | 13:33 | 13:33 | 13:39 | 0 | 0.1 | 0.1 | Auto reset | Close | 0.0038462 | WTG Unscheduled Maintenance | O2-02 | 53878 | 224.4917
1397 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_05 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 15:14 | 15:14 | 15:27 | 0 | 0.21667 | 0.21667 | Manual stop of WTG as instructed by the customer for transformer tap changing work by the BOP team | Close | 0.0083333 | WTG Breakdown Maintenance | O2-02 | 53878 | 486.3986
1398 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_05 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 17:08 | 17:08 | 17:19 | 0 | 0.18333 | 0.18333 | check Event And Data log then reset & started wtg. | Close | 0.0070513 | WTG Breakdown Maintenance | O2-02 | 53878 | 411.5681
1399 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_08 | TQGXIIPL | GEDA | 3.846% | 741 | Battery drive trigger by HC | Break down |  | 1:21 | 1:21 | 1:33 | 0 | 0.2 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | WTG Breakdown Maintenance | O2-26 | 53074 | 442.2833
1400 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_08 | TQGXIIPL | GEDA | 3.846% | 641 | Sim.angle E enc. <> act.angle 1 | Break down |  | 4:41 | 4:41 | 4:42 | 0 | 0.016667 | 0.016667 | check Event And Data log then reset & started wtg. | Close | 0.00064103 | WTG Breakdown Maintenance | O2-26 | 53074 | 36.8569
1401 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 10:44 | 10:44 | 11:03 | 0 | 0.31667 | 0.31667 | check Event And Data log then reset & started wtg. | Close | 0.012179 | WTG Breakdown Maintenance | O2-26 | 53074 | 700.2819
1402 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_08 | TQGXIIPL | GEDA | 3.846% | 665 | Pitch error | Break down |  | 11:05 | 11:05 | 16:54 | 0 | 5.8167 | 5.8167 | We have attend turbine for Rep pitch error check contactor all NO NC auxiliary switch during pitching time but no any abnormalities observed so further we have check pitch motor Encoder cable from PPD side, Motor side and found cable in brown cable broken so arrange cable and replace. After taking the trail and Pitch motor temp high error occurred so check PPD side connection,cable physical condition, it's ohmic value and found Unacceptable so we further check motor side connector in all connections and found one cable in Motor Connector in lug open so fixed properly and checked ohmic value found normal after successful generation trail started turbine. | Close | 0.22372 | WTG Breakdown Maintenance | O2-26 | 53074 | 12863.0736
1403 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_08 | TQGXIIPL | GEDA | 3.846% | 152 | SLC app. not in SAFE mode | Break down |  | 17:09 | 17:09 | 17:19 | 0 | 0.16667 | 0.16667 | check Event And Data log then reset & started wtg. | Close | 0.0064103 | WTG Breakdown Maintenance | O2-26 | 53074 | 368.5694
1404 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_09 | TQGXIIPL | GEDA | 3.846% | 551 | Pitch motor current too high | Break down |  | 0:00 | 0:00 | 2:29 | 0 | 2.4833 | 2.4833 | attend and check error related ckt so found XD209 TB and TB003 field rectifier fuse failure so arrange material and replace it then reset and start turbine | Close | 0.095513 | WTG Breakdown Maintenance | O2-03 | 52369 | 5418.7368
1405 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_10 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down |  | 10:34 | 10:34 | 10:54 | 0 | 0.33333 | 0.33333 | check Event And Data log then reset & started wtg. | Close | 0.012821 | WTG Breakdown Maintenance | O2-15 | 51323 | 712.8194
1406 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_10 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down |  | 16:29 | 16:29 | 16:31 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-15 | 51323 | 71.2819
1407 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 20:12 | 20:12 | 20:28 | 0 | 0.26667 | 0.26667 | Auto reset | Close | 0.010256 | WTG Unscheduled Maintenance | O2-21 | 59418 | 660.2
1408 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_16 | TQGXIIPL | GEDA | 3.846% | 4970 | Tower oscillation XF | Auto reset |  | 20:45 | 20:45 | 20:57 | 0 | 0.2 | 0.2 | Auto reset | Close | 0.0076923 | WTG Unscheduled Maintenance | O2-21 | 59418 | 495.15
1409 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 0:57 | 0:57 | 1:00 | 0 | 0.05 | 0.05 | check Event And Data log then reset & started wtg. | Close | 0.0019231 | WTG Breakdown Maintenance | O2-22 | 58811 | 122.5229
1410 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 4:36 | 4:36 | 4:40 | 0 | 0.066667 | 0.066667 | check Event And Data log then reset & started wtg. | Close | 0.0025641 | WTG Breakdown Maintenance | O2-22 | 58811 | 163.3639
1411 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_17 | TQGXIIPL | GEDA | 3.846% | 3211 | Conv. load shedding (CAN) | Break down |  | 5:13 | 5:13 | 5:25 | 0 | 0.2 | 0.2 | check Event And Data log then reset & started wtg. | Close | 0.0076923 | WTG Breakdown Maintenance | O2-22 | 58811 | 490.0917
1412 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_17 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Customer |  | 11:52 | 11:52 | 12:06 | 0 | 0.23333 | 0.23333 | Manual stop of WTG as instructed by the customer for transformer tap changing work by the BOP team | Close | 0.0089744 | WTG Breakdown Maintenance | O2-22 | 58811 | 571.7736
1413 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_20 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down |  | 10:35 | 10:35 | 10:37 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-24 | 55787 | 77.4819
1414 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_24 | TQGXIIPL | GEDA | 3.846% | 1070 | Drive train monitor level 2 | Break down |  | 10:34 | 10:34 | 10:36 | 0 | 0.033333 | 0.033333 | check Event And Data log then reset & started wtg. | Close | 0.0012821 | WTG Breakdown Maintenance | O2-20 | 55431 | 76.9875
1415 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_24 | TQGXIIPL | GEDA | 3.846% | 4540 | Tower oscillation X level 2 | Auto reset |  | 13:48 | 13:48 | 14:01 | 0 | 0.21667 | 0.21667 | Auto reset | Close | 0.0083333 | WTG Unscheduled Maintenance | O2-20 | 55431 | 500.4188
1416 | 2026 | 2025 | Year_2 | 2025-06-01 | 2025-06-30 | O2_12 | TQGXIIPL | GEDA | 3.846% | 55 | WTG shut down | Environment |  | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | Griding complete and Chamfering Completed (Weather condition was not ok rain and wind was very high) | Open | 0.92307 | WTG Environmental | O2-14 | 53754 | 53753.3778
Formulas:
Month = Table6[[#This Row],[Date]]-DAY(Table6[[#This Row],[Date]])+1

## IGA_BD
Sr. No. | Financial Year | Calendar Year | Operating Year | Month | Date | Affected Feeder | SPV | Consumer | Plant Equivalent Weightage | Breakdown Description | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Loss of KWH | Estimated Energy Loss (kWh) | Scope | PTW No. | Job Card No.
1 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-03 | O2_10 | TQGXIIPL | GEDA | 3.846% | O2-10 Manual stop (WTG Manual stop for USS Yard transformer oil leakage arrests work) | 17:48 | 17:48 | 18:09 | 0 | 0.35 | 0.35 | WTG Manual stop for USS Yard Transformer Oil Leakage Arrests work | Close | 0.013462 | IG Breakdown Maintenance | 362 | 1140.3 | O2 Project
2 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-05 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 7:45 | 7:45 | 8:20 | 0 | 0.58333 | 0.58333 | Feeder-1 tripping Earth fault during line petrolling found for bird fault Pole no CP-103 Near O2-02. Test trail and feeder charge. | Close | 0.29167 | IG Breakdown Maintenance | 274 | 1438.5 | O2 Project
3 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-07 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in Earth fault | 7:25 | 7:25 | 7:48 | 0 | 0.38333 | 0.38333 | Feeder-1 tripping Earth fault during line petrolling found for bird fault Pole no CP-34 Near O2-01. Test trail and feeder charge. | Close | 0.19167 | IG Breakdown Maintenance | 1276 | 4402.2 | O2 Project
4 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-12 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 7:20 | 7:20 | 7:32 | 0 | 0.2 | 0.2 | Feeder#1 Trip in Over Current & earth fault/master relay trip | Close | 0.1 | IG Breakdown Maintenance | 406 | 730.8 | O2 Project
5 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-12 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 12:26 | 12:26 | 24:00 | 0 | 11.5667 | 11.5667 | Manual Shutdown taken for TR LV cable Inspection Work and conductor replacement work. | Open | 5.7833 | IG Breakdown Maintenance | 406 | 42264.6 | O2 Project
6 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-12 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 12:26 | 12:26 | 24:00 | 0 | 11.5667 | 11.5667 | Manual Shutdown taken for TR LV cable Inspection Work and conductor replacement work. | Open | 5.7833 | IG Breakdown Maintenance | 406 | 42264.6 | O2 Project
7 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-13 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 0:00 | 0:00 | 7:04 | 0 | 7.0667 | 7.0667 | Manual Shutdown taken for TR LV cable Inspection Work and conductor replacement work. | Close | 3.5333 | IG Breakdown Maintenance | 1490 | 94764 | O2 Project
8 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-13 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 0:00 | 0:00 | 7:04 | 0 | 7.0667 | 7.0667 | Manual Shutdown taken for TR LV cable Inspection Work and conductor replacement work. | Close | 3.5333 | IG Breakdown Maintenance | 1490 | 94764 | O2 Project
9 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-16 | O2_10 | TQGXIIPL | GEDA | 3.846% | Converter torque monitor level 1(grid voltage down) | 9:08 | 9:08 | 9:24 | 0 | 0.26667 | 0.26667 | Checked related error data log and found grid voltage down so check by BOP team ,grid volage is normalise then reset & started WTG. | Close | 0.010256 | IG Breakdown Maintenance | 1650.5 | 3961.2 | O2 Project
10 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-21 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 8:56 | 8:56 | 9:31 | 0 | 0.58333 | 0.58333 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.29167 | IG Breakdown Maintenance | 406 | 2131.5 | O2 Project
11 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-21 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 18:44 | 18:44 | 19:10 | 0 | 0.43333 | 0.43333 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.21667 | IG Breakdown Maintenance | 406 | 1583.4 | O2 Project
12 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-21 | O2_01 | TQGXIIPL | GEDA | 3.846% | O2_01 WTG Shutdown | 9:31 | 9:31 | 18:44 | 0 | 9.2167 | 9.2167 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.35449 | IG Breakdown Maintenance | 406 | 33677.7 | O2 Project
13 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-21 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2_02 WTG Shutdown | 9:31 | 9:31 | 18:44 | 0 | 9.2167 | 9.2167 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.35449 | IG Breakdown Maintenance | 406 | 33677.7 | O2 Project
14 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-21 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2_05 WTG Shutdown | 9:31 | 9:31 | 18:44 | 0 | 9.2167 | 9.2167 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.35449 | IG Breakdown Maintenance | 406 | 33677.7 | O2 Project
15 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-21 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2_08 WTG Shutdown | 9:31 | 9:31 | 18:44 | 0 | 9.2167 | 9.2167 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.35449 | IG Breakdown Maintenance | 406 | 33677.7 | O2 Project
16 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-21 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2_25 WTG Shutdown | 9:31 | 9:31 | 18:44 | 0 | 9.2167 | 9.2167 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.35449 | IG Breakdown Maintenance | 406 | 33677.7 | O2 Project
17 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-21 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2_26 WTG Shutdown | 9:31 | 9:31 | 18:44 | 0 | 9.2167 | 9.2167 | Feeder-1 Shutdown taking by for near O2_09 conductor repairing work & Conductor replacement work Note:- O2_01,26,08,25,02,05 jumper open | Close | 0.35449 | IG Breakdown Maintenance | 406 | 33677.7 | O2 Project
18 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-22 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 15:19 | 15:19 | 15:48 | 0 | 0.48333 | 0.48333 | Feeder-2 Shutdown taking by for near O2_04 conductor repairing work,& conductor replacement work Note:-O2_04,O2_07,O2_19 isolator closing work | Close | 0.24167 | IG Breakdown Maintenance | 469.4 | 2041.89 | O2 Project
19 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-22 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2_04 WTG Shutdown | 12:36 | 12:36 | 15:19 | 0 | 2.7167 | 2.7167 | Feeder-2 Shutdown taking by for near O2_04 conductor repairing work,& conductor replacement work Note:-O2_04,O2_07,O2_19 isolator closing work | Close | 0.10449 | IG Breakdown Maintenance | 469.4 | 11476.83 | O2 Project
20 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-22 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 WTG Shutdown | 12:36 | 12:36 | 15:19 | 0 | 2.7167 | 2.7167 | Feeder-2 Shutdown taking by for near O2_04 conductor repairing work,& conductor replacement work Note:-O2_04,O2_07,O2_19 isolator closing work | Close | 0.10449 | IG Breakdown Maintenance | 469.4 | 11476.83 | O2 Project
21 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-22 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 WTG Shutdown | 12:36 | 12:36 | 15:19 | 0 | 2.7167 | 2.7167 | Feeder-2 Shutdown taking by for near O2_04 conductor repairing work,& conductor replacement work Note:-O2_04,O2_07,O2_19 isolator closing work | Close | 0.10449 | IG Breakdown Maintenance | 469.4 | 11476.83 | O2 Project
22 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-28 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 18:12 | 18:12 | 18:23 | 0 | 0.18333 | 0.18333 | Feeder#1 Trip in Over Current & earth fault/master relay trip | Close | 0.091667 | IG Breakdown Maintenance | 990.6 | 1634.49 | O2 Project
23 | 2026 | 2025 | Year_1 | 2025-04-01 | 2025-04-28 | O2_14 | TQGXIIPL | GEDA | 3.846% | O2-14 WTG Shutdown (Grid loss) | 14:41 | 14:41 | 15:38 | 0 | 0.95 | 0.95 | WTG stop for HT Yard Inspection Work. | Close | 0.036538 | IG Breakdown Maintenance | 990.6 | 8469.63 | O2 Project
24 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-06 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in over current. | 0:14 | 0:14 | 0:46 | 0 | 0.53333 | 0.53333 | Trip in over current Due to Havy rain and lighting also gusty wind whether normalisation then line inspection test trail and feeder charge | Close | 0.26667 | IG Breakdown Maintenance | 1124.4 | 5397.12 | O2 Project
25 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-06 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in over current. | 15:32 | 15:32 | 17:50 | 0 | 2.3 | 2.3 | Trip in over current Due to Havy rain and lighting also gusty wind whether normalisation then line inspection test trail and feeder charge | Close | 1.15 | IG Breakdown Maintenance | 1124.4 | 23275.08 | O2 Project
26 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-06 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 15:55 | 15:55 | 24:00 | 0 | 8.0833 | 8.0833 | Trip in over current Due to Havy rain and lighting also gusty wind whether normalisation then line inspection WIP | Open | 4.0417 | IG Breakdown Maintenance | 1124.4 | 81800.1 | O2 Project
27 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-06 | O2_16 | TQGXIIPL | GEDA | 3.846% | O2_16 Grid Loss | 17:50 | 17:50 | 20:48 | 0 | 2.9667 | 2.9667 | After grid resume time VCB OFF after PSS Team attend and charge VCB | Close | 0.1141 | IG Breakdown Maintenance | 1124.4 | 30021.48 | O2 Project
28 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-07 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 0:00 | 0:00 | 2:10 | 0 | 2.1667 | 2.1667 | Trip in over current Due to Havy rain and lighting also gusty wind whether normalisation then line inspection found for panther line pin isulator damage replace with new reset and test trail and feeder charge | Close | 1.0833 | IG Breakdown Maintenance | 659.6 | 12862.2 | O2 Project
29 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-07 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 16:02 | 16:02 | 16:58 | 0 | 0.93333 | 0.93333 | Feeder-1 shutdown take for OFC Splicing work | Close | 0.46667 | IG Breakdown Maintenance | 659.6 | 5540.64 | O2 Project
30 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-07 | O2_13 | TQGXIIPL | GEDA | 3.846% | O2_13 Grid Loss | 2:10 | 2:10 | 2:23 | 0 | 0.21667 | 0.21667 | After grid resume time VCB OFF after PSS Team attend and charge VCB | Close | 0.0083333 | IG Breakdown Maintenance | 659.6 | 1286.22 | O2 Project
31 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-07 | O2_14 | TQGXIIPL | GEDA | 3.846% | O2_14 Grid Loss | 2:10 | 2:10 | 2:32 | 0 | 0.36667 | 0.36667 | After grid resume time VCB OFF after PSS Team attend and charge VCB | Close | 0.014103 | IG Breakdown Maintenance | 659.6 | 2176.68 | O2 Project
32 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-07 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2_25 Grid Loss | 2:10 | 2:10 | 3:10 | 0 | 1 | 1 | After grid resume time VCB OFF after PSS Team attend and charge VCB | Close | 0.038462 | IG Breakdown Maintenance | 659.6 | 5936.4 | O2 Project
33 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-08 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Tripped in over current. | 17:54 | 17:54 | 18:54 | 0 | 1 | 1 | Feeder#1 Trip in Over Current & earth fault/master relay trip | Close | 0.5 | IG Breakdown Maintenance | 208 | 1872 | O2 Project
34 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-09 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 17:17 | 17:17 | 19:03 | 0 | 1.7667 | 1.7667 | Feeder-2 Trip in Earth fault after take a trial then charge it. | Close | 0.88333 | IG Breakdown Maintenance | 230 | 3657 | O2 Project
35 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-09 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown for O2-19 line jumper Open work | 21:47 | 21:47 | 21:57 | 0 | 0.16667 | 0.16667 | Feeder-2 shutdown for O2-19 line jumper Open work | Close | 0.083333 | IG Breakdown Maintenance | 230 | 345 | O2 Project
36 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-09 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2_04 Grid Loss | 19:04 | 19:04 | 21:46 | 0 | 2.7 | 2.7 | O2-04, O2-19 & O2-07 Internal lines rectification work | Close | 0.10385 | IG Breakdown Maintenance | 230 | 5589 | O2 Project
37 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-09 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 19:04 | 19:04 | 21:46 | 0 | 2.7 | 2.7 | O2-04, O2-19 & O2-07 Internal lines rectification work | Close | 0.10385 | IG Breakdown Maintenance | 230 | 5589 | O2 Project
38 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-09 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 Grid Loss | 19:04 | 19:04 | 21:46 | 0 | 2.7 | 2.7 | O2-04, O2-19 & O2-07 Internal lines rectification work | Close | 0.10385 | IG Breakdown Maintenance | 230 | 5589 | O2 Project
39 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-09 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 Grid Loss | 21:58 | 21:58 | 24:00 | 0 | 2.0333 | 2.0333 | O2-19 Internal lines rectification work | Open | 0.078205 | IG Breakdown Maintenance | 230 | 4209 | O2 Project
40 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-09 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2_04 Grid Loss | 23:45 | 23:45 | 24:00 | 0 | 0.25 | 0.25 | O2-04 & O2-07 Internal lines rectification work | Close | 0.0096154 | IG Breakdown Maintenance | 230 | 517.5 | O2 Project
41 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-09 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 23:45 | 23:45 | 24:00 | 0 | 0.25 | 0.25 | O2-04 & O2-07 Internal lines rectification work | Close | 0.0096154 | IG Breakdown Maintenance | 230 | 517.5 | O2 Project
42 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-10 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 13:00 | 13:00 | 14:35 | 0 | 1.5833 | 1.5833 | Feeder-2 Trip in Earth fault after take a trial then charge it. | Close | 0.79167 | IG Breakdown Maintenance | 384 | 5472 | O2 Project
43 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-10 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 18:24 | 18:24 | 18:35 | 0 | 0.18333 | 0.18333 | Feeder-2 Trip in Earth fault after take a trial then charge it. | Close | 0.091667 | IG Breakdown Maintenance | 384 | 633.6 | O2 Project
44 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-10 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2_04 Grid Loss | 0:00 | 0:00 | 0:54 | 0 | 0.9 | 0.9 | O2-04 & O2-07 Internal lines rectification work | Close | 0.034615 | IG Breakdown Maintenance | 384 | 3110.4 | O2 Project
45 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-10 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 0:00 | 0:00 | 0:54 | 0 | 0.9 | 0.9 | O2-04 & O2-07 Internal lines rectification work | Close | 0.034615 | IG Breakdown Maintenance | 384 | 3110.4 | O2 Project
46 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-10 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2_17 Grid Loss | 14:36 | 14:36 | 16:38 | 0 | 2.0333 | 2.0333 | O2-17 & O2-22 Internal lines rectification work | Close | 0.078205 | IG Breakdown Maintenance | 384 | 7027.2 | O2 Project
47 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-10 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2_22 Grid Loss | 14:36 | 14:36 | 16:38 | 0 | 2.0333 | 2.0333 | O2-17 & O2-22 Internal lines rectification work | Close | 0.078205 | IG Breakdown Maintenance | 384 | 7027.2 | O2 Project
48 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-10 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 Grid Loss | 0:00 | 0:00 | 24:00 | 0 | 23.9997 | 23.9997 | O2-19 Jumper open work WIP | Open | 0.92307 | IG Breakdown Maintenance | 384 | 82943.04 | O2 Project
49 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-11 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 16:21 | 16:21 | 17:25 | 0 | 1.0667 | 1.0667 | Feeder-2 Trip in Earth fault after take a trial then charge it. | Close | 0.53333 | IG Breakdown Maintenance | 340 | 3264 | O2 Project
50 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-11 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder#1 Tripped due to Snake fault at Location no O2_13 | 17:38 | 17:38 | 18:10 | 0 | 0.53333 | 0.53333 | Feeder#1 Tripped due to snack fault at Location no O2_13 | Close | 0.26667 | IG Breakdown Maintenance | 340 | 1632 | O2 Project
51 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-11 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid loss | 17:26 | 17:26 | 19:20 | 0 | 1.9 | 1.9 | O2-19 Internal lines rectification work | Close | 0.073077 | IG Breakdown Maintenance | 340 | 5814 | O2 Project
52 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-11 | Wind_F2 | TQGXIIPL | GEDA | 50% | O2-19 Isolator closing Work | 0:00 | 0:00 | 0:06 | 0 | 0.1 | 0.1 | O2-19 Isolator closing Work | Close | 0.05 | IG Breakdown Maintenance | 340 | 306 | O2 Project
53 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-12 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 15:16 | 15:16 | 16:26 | 0 | 1.1667 | 1.1667 | Feeder-2 Trip in Earth fault after take a trial then charge it. | Close | 0.58333 | IG Breakdown Maintenance | 384 | 4032 | O2 Project
54 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-12 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2_19 Grid loss | 16:27 | 16:27 | 20:42 | 0 | 4.25 | 4.25 | O2-19 Transformer Bushing Replacement work | Close | 0.16346 | IG Breakdown Maintenance | 384 | 14688 | O2 Project
55 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-13 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 22:29 | 22:29 | 24:00 | 0 | 1.5164 | 1.5164 | VCB OFF after BOP Team attend and check VCB wip. | Close | 0.058323 | IG Breakdown Maintenance | 469.4 | 6406.1365 | O2 Project
56 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-14 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 0:00 | 0:00 | 0:06 | 0 | 0.1 | 0.1 | VCB OFF after BOP Team attend and check VCB then charge and start WTG | Close | 0.0038462 | IG Breakdown Maintenance | 437.7 | 393.93 | O2 Project
57 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-14 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 8:17 | 8:17 | 9:12 | 0 | 0.91667 | 0.91667 | VCB tripped by unknown person after BOP Team attend and check VCB then charge and start WTG | Close | 0.035256 | IG Breakdown Maintenance | 437.7 | 3611.025 | O2 Project
58 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-14 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2_07 Grid Loss | 20:52 | 20:52 | 21:32 | 0 | 0.66667 | 0.66667 | VCB tripped by unknown person after BOP Team attend and check VCB then charge and start WTG | Close | 0.025641 | IG Breakdown Maintenance | 437.7 | 2626.2 | O2 Project
59 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-15 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 17:49 | 17:49 | 18:24 | 0 | 0.58333 | 0.58333 | Feeder#2 Trip in earth Falut/over current (O2_17,O2_22 section isolator open) | Close | 0.29167 | IG Breakdown Maintenance | 296 | 1554 | O2 Project
60 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-15 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 21:26 | 21:26 | 21:33 | 0 | 0.11667 | 0.11667 | Feeder-2 shutdown for O2_17 &O2_22 section Isolator closing work | Close | 0.058333 | IG Breakdown Maintenance | 296 | 310.8 | O2 Project
61 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-15 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2_17 Grid Loss | 18:24 | 18:24 | 21:26 | 0 | 3.0333 | 3.0333 | O2_17,O2_22 section isolator open BY BOP team | Close | 0.11667 | IG Breakdown Maintenance | 296 | 8080.8 | O2 Project
62 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-15 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2_22 Grid Loss | 18:24 | 18:24 | 21:26 | 0 | 3.0333 | 3.0333 | O2_17,O2_22 section isolator open BY BOP team | Close | 0.11667 | IG Breakdown Maintenance | 296 | 8080.8 | O2 Project
63 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-16 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in earth Falut/over current | 16:40 | 16:40 | 18:19 | 0 | 1.65 | 1.65 | Feeder#2 Trip in earth Falut/over current after take a trial then charge it. | Close | 0.825 | IG Breakdown Maintenance | 564.5 | 8382.825 | O2 Project
64 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-16 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 19:04 | 19:04 | 19:11 | 0 | 0.11667 | 0.11667 | Feeder-2 shutdown for O2_07 &O2_04,O2-19 section Isolator closing work | Close | 0.058333 | IG Breakdown Maintenance | 564.5 | 592.725 | O2 Project
65 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-16 | O2_17 | TQGXIIPL | GEDA | 3.846% | O2-17 WTG Shutdown | 15:54 | 15:54 | 16:40 | 0 | 0.76667 | 0.76667 | O2_17,O2_22 section isolator open BY BOP team | Close | 0.029487 | IG Breakdown Maintenance | 564.5 | 3895.05 | O2 Project
66 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-16 | O2_22 | TQGXIIPL | GEDA | 3.846% | O2-22 WTG Shutdown | 15:54 | 15:54 | 16:40 | 0 | 0.76667 | 0.76667 | O2_17,O2_22 section isolator open BY BOP team | Close | 0.029487 | IG Breakdown Maintenance | 564.5 | 3895.05 | O2 Project
67 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-16 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid loss | 18:19 | 18:19 | 19:04 | 0 | 0.75 | 0.75 | O2_07,O2_04,O2_19 section isolator open BY BOP team | Close | 0.028846 | IG Breakdown Maintenance | 564.5 | 3810.375 | O2 Project
68 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-16 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2-04 Grid loss | 18:19 | 18:19 | 19:04 | 0 | 0.75 | 0.75 | O2_07,O2_04,O2_19 section isolator open BY BOP team | Close | 0.028846 | IG Breakdown Maintenance | 564.5 | 3810.375 | O2 Project
69 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-16 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid loss | 18:19 | 18:19 | 19:04 | 0 | 0.75 | 0.75 | O2_07,O2_04,O2_19 section isolator open BY BOP team | Close | 0.028846 | IG Breakdown Maintenance | 564.5 | 3810.375 | O2 Project
70 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-17 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in earth Falut/over current | 6:44 | 6:44 | 6:57 | 0 | 0.21667 | 0.21667 | Feeder#2 Trip in earth Falut/over current after take a trial then charge it. | Close | 0.10833 | IG Breakdown Maintenance | 469.4 | 915.33 | O2 Project
71 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-18 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 11:12 | 11:12 | 12:26 | 0 | 1.2333 | 1.2333 | Feeder#1 Shutdown taking by pin insulator fall down repairing work | Close | 0.61667 | IG Breakdown Maintenance | 437.7 | 4858.47 | O2 Project
72 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-20 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 Trip in Earth fault | 8:37 | 8:37 | 8:54 | 0 | 0.28333 | 0.28333 | Feeder#1Trip in earth Falut/over current /master reley trip after take a trial then charge it. | Close | 0.14167 | IG Breakdown Maintenance | 501.1 | 1277.805 | O2 Project
73 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-20 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 17:22 | 17:22 | 17:40 | 0 | 0.3 | 0.3 | Feeder#2 Trip in earth Falut/over current after take a trial then charge it. | Close | 0.15 | IG Breakdown Maintenance | 501.1 | 1352.97 | O2 Project
74 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-21 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder#1Trip in earth Falut/over current /master reley trip | 10:14 | 10:14 | 13:30 | 0 | 3.2667 | 3.2667 | Feeder#1Trip in earth Falut/over current /master reley trip ,Hi teck Project ROW due to payment issue. | Close | 1.6333 | IG Breakdown Maintenance | 296 | 8702.4 | O2 Project
75 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-21 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 13:30 | 13:30 | 19:16 | 0 | 5.7667 | 5.7667 | Feeder#1 Shutdown taken by project team 33kv line pending work. | Close | 2.8833 | IG Breakdown Maintenance | 296 | 15362.4 | O2 Project
76 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-21 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 shutdown | 14:35 | 14:35 | 19:10 | 0 | 4.5833 | 4.5833 | Feeder#2 Shutdown taken by project team 33kv line pending work. | Close | 2.2917 | IG Breakdown Maintenance | 296 | 12210 | O2 Project
77 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 0:19 | 0:19 | 1:11 | 0 | 0.86667 | 0.86667 | Feeder#2 Trip in earth Falut after take a trial then charge it. | Close | 0.43333 | IG Breakdown Maintenance | 154.8 | 1207.44 | O2 Project
78 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_04 | TQGXIIPL | GEDA | 3.846% | O2-04 Grid loss | 1:11 | 1:11 | 3:50 | 0 | 2.65 | 2.65 | O2-04, O2-07 and O2-19 section Isolator open by BOP team found fault and correct it then close Isotator then start WTG. | Close | 0.10192 | IG Breakdown Maintenance | 154.8 | 3691.98 | O2 Project
79 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid loss | 1:11 | 1:11 | 3:50 | 0 | 2.65 | 2.65 | O2-04, O2-07 and O2-19 section Isolator open by BOP team found fault and correct it then close Isotator then start WTG. | Close | 0.10192 | IG Breakdown Maintenance | 154.8 | 3691.98 | O2 Project
80 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_19 | TQGXIIPL | GEDA | 3.846% | O2-19 Grid loss | 1:11 | 1:11 | 3:50 | 0 | 2.65 | 2.65 | O2-04, O2-07 and O2-19 section Isolator open by BOP team found fault and correct it then close Isotator then start WTG. | Close | 0.10192 | IG Breakdown Maintenance | 154.8 | 3691.98 | O2 Project
81 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 9:11 | 9:11 | 11:23 | 0 | 2.2 | 2.2 | Feeder#1 Shutdown taken by project team for section Isolator installation work | Close | 1.1 | IG Breakdown Maintenance | 154.8 | 3065.04 | O2 Project
82 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_01 | TQGXIIPL | GEDA | 3.846% | O2-01 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 154.8 | 9102.24 | O2 Project
83 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2-02 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 154.8 | 9102.24 | O2 Project
84 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_03 | TQGXIIPL | GEDA | 3.846% | O2-03 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 154.8 | 9102.24 | O2 Project
85 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 154.8 | 9102.24 | O2 Project
86 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 154.8 | 9102.24 | O2 Project
87 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_09 | TQGXIIPL | GEDA | 3.846% | O2-09 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 154.8 | 9102.24 | O2 Project
88 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_11 | TQGXIIPL | GEDA | 3.846% | O2-11 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 154.8 | 9102.24 | O2 Project
89 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_12 | TQGXIIPL | GEDA | 3.846% | O2-12 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 154.8 | 9102.24 | O2 Project
90 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_14 | TQGXIIPL | GEDA | 3.846% | O2-14 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 154.8 | 9102.24 | O2 Project
91 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_23 | TQGXIIPL | GEDA | 3.846% | O2-23 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 154.8 | 9102.24 | O2 Project
92 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 154.8 | 9102.24 | O2 Project
93 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 WTG Shutdown (Grid loss) | 11:23 | 11:23 | 17:55 | 0 | 6.5333 | 6.5333 | jumper open by project team at O2 14 for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 154.8 | 9102.24 | O2 Project
94 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-22 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 17:55 | 17:55 | 19:01 | 0 | 1.1 | 1.1 | Feeder#1 Shutdown taken by project team for section Isolator installation work and jumper closing work at O2-14. | Close | 0.55 | IG Breakdown Maintenance | 154.8 | 1532.52 | O2 Project
95 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-23 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 20:36 | 20:36 | 20:56 | 0 | 0.33333 | 0.33333 | Feeder-2 tripped in Earth fault after take a trial then charge it. | Close | 0.16667 | IG Breakdown Maintenance | 384 | 1152 | O2 Project
96 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-24 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 9:22 | 9:22 | 10:35 | 0 | 1.2167 | 1.2167 | Feeder#1 Shutdown taken by project team for section Isolator installation work | Close | 0.60833 | IG Breakdown Maintenance | 1490 | 16315.5 | O2 Project
97 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-24 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder-1 shutdown | 17:07 | 17:07 | 18:28 | 0 | 1.35 | 1.35 | Feeder#1 Shutdown taken by project team for section Isolator installation work | Close | 0.675 | IG Breakdown Maintenance | 1490 | 18103.5 | O2 Project
98 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-24 | O2_01 | TQGXIIPL | GEDA | 3.846% | O2-01 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 1490 | 87612 | O2 Project
99 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-24 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2-02 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 1490 | 87612 | O2 Project
100 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-24 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. After grid rusume start WTG | Close | 0.25128 | IG Breakdown Maintenance | 1490 | 87612 | O2 Project
101 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-24 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. After grid rusume start WTG | Close | 0.25128 | IG Breakdown Maintenance | 1490 | 87612 | O2 Project
102 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-24 | O2_09 | TQGXIIPL | GEDA | 3.846% | O2-09 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 1490 | 87612 | O2 Project
103 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-24 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 1490 | 87612 | O2 Project
104 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-24 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 WTG Shutdown (Grid loss) | 10:35 | 10:35 | 17:07 | 0 | 6.5333 | 6.5333 | jumper open by project team for section Isolator installation work. | Close | 0.25128 | IG Breakdown Maintenance | 1490 | 87612 | O2 Project
105 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-25 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feefer-1 shutdown | 9:30 | 9:30 | 10:20 | 0 | 0.83333 | 0.83333 | Feeder#1 Shutdown taken by project team for section Isolator installation work | Close | 0.41667 | IG Breakdown Maintenance | 1543.5 | 11576.25 | O2 Project
106 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-25 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder#1 Trip in Over Current | 15:42 | 15:42 | 16:56 | 0 | 1.2333 | 1.2333 | Feeder#1 Trip in Over Current after take a trial then charge it. | Close | 0.61667 | IG Breakdown Maintenance | 1543.5 | 17132.85 | O2 Project
107 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-25 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 WTG Shutdown (Grid loss) | 10:20 | 10:20 | 15:42 | 0 | 5.3667 | 5.3667 | jumper open by project team for section Isolator installation work. | Close | 0.20641 | IG Breakdown Maintenance | 1543.5 | 74551.05 | O2 Project
108 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-25 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 WTG Shutdown (Grid loss) | 10:20 | 10:20 | 15:42 | 0 | 5.3667 | 5.3667 | jumper open by project team for section Isolator installation work. | Close | 0.20641 | IG Breakdown Maintenance | 1543.5 | 74551.05 | O2 Project
109 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-25 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2-02 WTG Shutdown (Grid loss) | 10:20 | 10:20 | 15:42 | 0 | 5.3667 | 5.3667 | jumper open by project team for section Isolator installation work. | Close | 0.20641 | IG Breakdown Maintenance | 1543.5 | 74551.05 | O2 Project
110 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-26 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder#1 Trip in Over Current | 0:37 | 0:37 | 0:51 | 0 | 0.23333 | 0.23333 | Feeder#1 Trip in Over Current after take a trial then charge it. | Close | 0.11667 | IG Breakdown Maintenance | 1222.5 | 2567.25 | O2 Project
111 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-26 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 0:02 | 0:02 | 0:52 | 0 | 0.83333 | 0.83333 | Feeder-2 tripped in Earth fault after take a trial then charge it. | Close | 0.41667 | IG Breakdown Maintenance | 1222.5 | 9168.75 | O2 Project
112 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-27 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feeder#1 Trip in Earth fault | 10:36 | 10:36 | 13:33 | 0 | 2.95 | 2.95 | Feeder#1 Trip in Over Current after take a trial then charge it. | Close | 1.475 | IG Breakdown Maintenance | 2435.5 | 64662.525 | O2 Project
113 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-28 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feefer-1 shutdown | 9:12 | 9:12 | 9:41 | 0 | 0.48333 | 0.48333 | Feeder#1 Shutdown taken by project team for section Isolator installation work | Close | 0.24167 | IG Breakdown Maintenance | 1922.8 | 8364.18 | O2 Project
114 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-28 | Wind_F1 | TQGXIIPL | GEDA | 50% | Feefer-1 shutdown | 11:35 | 11:35 | 12:39 | 0 | 1.0667 | 1.0667 | Feeder#1 Shutdown taken by project team for section Isolator installation work | Close | 0.53333 | IG Breakdown Maintenance | 1922.8 | 18458.88 | O2 Project
115 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-28 | O2_01 | TQGXIIPL | GEDA | 3.846% | O2-01 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | 1922.8 | 32879.88 | O2 Project
116 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-28 | O2_09 | TQGXIIPL | GEDA | 3.846% | O2-09 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | 1922.8 | 32879.88 | O2 Project
117 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-28 | O2_25 | TQGXIIPL | GEDA | 3.846% | O2-25 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | 1922.8 | 32879.88 | O2 Project
118 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-28 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | 1922.8 | 32879.88 | O2 Project
119 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-28 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | 1922.8 | 32879.88 | O2 Project
120 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-28 | O2_05 | TQGXIIPL | GEDA | 3.846% | O2-05 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | 1922.8 | 32879.88 | O2 Project
121 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-28 | O2_02 | TQGXIIPL | GEDA | 3.846% | O2-02 WTG Shutdown (Grid loss) | 9:41 | 9:41 | 11:35 | 0 | 1.9 | 1.9 | jumper open by project team for section Isolator installation work. | Close | 0.073077 | IG Breakdown Maintenance | 1922.8 | 32879.88 | O2 Project
122 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-28 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feefer-2 shutdown | 12:52 | 12:52 | 17:08 | 0 | 4.2667 | 4.2667 | Feeder#2 Shutdown taken by project team for section Isolator installation work | Close | 2.1333 | IG Breakdown Maintenance | 1922.8 | 73835.52 | O2 Project
123 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-28 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 WTG Shutdown (Grid loss) | 12:39 | 12:39 | 17:08 | 0 | 4.4833 | 4.4833 | jumper open by project team for section Isolator installation work. | Close | 0.17244 | IG Breakdown Maintenance | 1922.8 | 77584.98 | O2 Project
124 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-28 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 WTG Shutdown (Grid loss) | 12:39 | 12:39 | 17:08 | 0 | 4.4833 | 4.4833 | jumper open by project team for section Isolator installation work. | Close | 0.17244 | IG Breakdown Maintenance | 1922.8 | 77584.98 | O2 Project
125 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-31 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 15:15 | 15:15 | 16:01 | 0 | 0.76667 | 0.76667 | Feeder-2 Trip in Earth fault after take a trial then charge it. | Close | 0.38333 | IG Breakdown Maintenance | 2472.4 | 17059.56 | O2 Project
126 | 2026 | 2025 | Year_1 | 2025-05-01 | 2025-05-31 | O2_07 | TQGXIIPL | GEDA | 3.846% | O2-07 Grid loss | 16:01 | 16:01 | 17:09 | 0 | 1.1333 | 1.1333 | After grid resume found VCB tripped so VCB Charge after reset and start wtg | Close | 0.04359 | IG Breakdown Maintenance | 2472.4 | 25218.48 | O2 Project
127 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-03 | O2_03 | TQGXIIPL | GEDA | 3.846% | O2-03 WTG Shutdown (Grid loss) | 18:43 | 18:43 | 19:01 | 0 | 0.3 | 0.3 | USS work for BOP. | Close | 0.011538 | IG Breakdown Maintenance | 1813.4 | 4896.18 | O2 Project
128 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-14 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in earth fault/Over current | 17:37 | 17:37 | 19:13 | 0 | 1.6 | 1.6 | Feeder-2 Tripped in earth fault/Over current so check ckt reset relay and Annunciator also Inspected the 33kv line and during test trial TNC Switch didn,t operate so we check it,s connection and related ckt, also check VCB closing coils found the closing coil stuck after resolve then cherge Feeder. | Close | 0.8 | IG Breakdown Maintenance | 564.5 | 8128.8 | O2 Project
129 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-14 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Trip in Earth fault | 19:59 | 19:59 | 20:10 | 0 | 0.18333 | 0.18333 | Feeder-2 tripped in Earth fault so take trial and charge feeder.(Due to heavy lightning at site) | Close | 0.091667 | IG Breakdown Maintenance | 564.5 | 931.425 | O2 Project
130 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-16 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in earth fault/Over current | 7:55 | 7:55 | 8:09 | 0 | 0.23333 | 0.23333 | Feeder#2 Trip in earth Falut/over current.so take trial and charge feeder. | Close | 0.11667 | IG Breakdown Maintenance | 1813.4 | 3808.14 | O2 Project
131 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-16 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in earth fault/Over current | 13:35 | 13:35 | 14:24 | 0 | 0.81667 | 0.81667 | Feeder#2 Trip in earth Falut/over current.so take trial and charge feeder. | Close | 0.40833 | IG Breakdown Maintenance | 1813.4 | 13328.49 | O2 Project
132 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-16 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in earth fault/Over current | 19:07 | 19:07 | 19:39 | 0 | 0.53333 | 0.53333 | Feeder#2 Trip in earth Falut/over current.so take trial and charge feeder. | Close | 0.26667 | IG Breakdown Maintenance | 1813.4 | 8704.32 | O2 Project
133 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-16 | Wind_F2 | TQGXIIPL | GEDA | 50% | Feeder-2 Tripped in earth fault/Over current | 20:30 | 20:30 | 21:19 | 0 | 0.81667 | 0.81667 | Feeder#2 Trip in earth Falut/over current.so take trial and charge feeder.(Due to heavyrain and lightning at site) | Close | 0.40833 | IG Breakdown Maintenance | 1813.4 | 13328.49 | O2 Project
134 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-16 | O2_08 | TQGXIIPL | GEDA | 3.846% | O2-08 Grid loss | 14:24 | 14:24 | 14:52 | 0 | 0.46667 | 0.46667 | After grid resume found VCB tripped so VCB Charge by BOP team then after reset and start wtg | Close | 0.017949 | IG Breakdown Maintenance | 1813.4 | 7616.28 | O2 Project
135 | 2026 | 2025 | Year_1 | 2025-06-01 | 2025-06-16 | O2_26 | TQGXIIPL | GEDA | 3.846% | O2-26 Grid loss | 21:19 | 21:19 | 22:09 | 0 | 0.83333 | 0.83333 | After grid resume found VCB tripped so VCB Charge by BOP team then after reset and start wtg | Close | 0.032051 | IG Breakdown Maintenance | 1813.4 | 13600.5 | O2 Project
Formulas:
Month = Table10[[#This Row],[Date]]-DAY(Table10[[#This Row],[Date]])+1

## Grid_BD
Sr. No. | Financial Year | Calendar Year | Operating Year | Month | Date | Affected Feeder | SPV | Concumaer | Plant Equivalent Weightage | Breakdown Description | Breakdown Type | Fault Start TimeStamp | Work Start TimeStamp | Fault Clearance time | Response Time | Resolution Time | Breakdown Time | Action taken | Status | Plant Equivalent breakdown | Fault Category | Paired WTG for Enegy based MA | Loss of KWH | Estimated Energy Loss (kWh) | Curtailment Order imit. | EGA_Including_CurtailmentOrder | PTW No. | Job Card No.
1 | 2025 | 2025 | Year_1 | 2025-02-01 | 2025-02-28 | Line1 | TQGXIIPL | GEDA | 100% | 66Kv Line shutdown taking By GETCO team from Getco end 66KV line Strengthening work. | Manual shutdown | 8:20 | 8:20 | 18:34 | 0 | 10.2333 | 10.2333 | 66Kv Line shutdown taking By GETCO team from Getco end 66KV line Strengthening work. | Close | 10.2333 |  |  | 1222.5 | 62551.25
2 | 1905-03-14 | 1900 |  | 1899-12-31 | [10 empty] | 0 |  | 0 | [6 empty] | 0
Formulas:
Month = Table11[[#This Row],[Date]]-DAY(Table11[[#This Row],[Date]])+1
Financial Year = YEAR(Table11[[#This Row],[Date]])+IF(MONTH(Table11[[#This Row],[Date]])>=4,1,0)

## WTG-PM
Sr no | Site | Location | Turbine ID | DOC | Date of Operation | 2024 |  |  |  |  | 2025
[6 empty] | WTG 1st Month PM |  |  |  |  | WTG YPM
[6 empty] | Plan Date | Actual Date | Diff. Days | Adherence | Remark | Plan Date | 1st Day | 2nd Day | Diff. Days | Adherence | Remarks
1 | Babra | O2-11 | 5333 | 2024-03-31 | 2024-05-20 | 2024-07-08 | 2024-08-02 | 25 | 100 |  | 2025-02-27 | 2025-03-07 | 2025-03-08 | 8
2 | Babra | O2-12 | 5334 | 2024-03-31 | 2024-05-06 | 2024-06-24 | 2024-07-31 | 37 | 92.2222 | Deleyed due to other turbines restoration work | 2025-03-03 | 2025-03-11 | 2025-03-12 | 8
3 | Babra | O2-13 | 5335 | 2024-03-31 | 2024-05-02 | 2024-06-20 | 2024-07-06 | 16 | 100 |  | 2025-03-05 | 2025-03-17 | 2025-03-19 | 12
4 | Babra | O2-14 | 5336 | 2024-03-31 | 2024-05-05 | 2024-06-23 | 2024-07-16 | 23 | 100 |  | 2025-03-07 | 2025-03-20 | 2025-03-21 | 13
5 | Babra | O2-10 | 5332 | 2024-04-02 | 2024-05-05 | 2024-06-23 | 2024-07-11 | 18 | 100 |  | 2025-03-11 | 2025-04-01 | 2025-04-02 | 21
6 | Babra | O2-03 | 5341 | 2024-04-02 | 2024-05-06 | 2024-06-24 | 2024-07-19 | 25 | 100 |  | 2025-03-17 | 2025-04-05 | 2025-04-06 | 19
7 | Babra | O2-15 | 5342 | 2024-04-19 | 2024-05-02 | 2024-06-20 | 2024-07-09 | 19 | 100 |  | 2025-03-19 | 2025-04-13 | 2025-04-14 | 25
8 | Babra | O2-16 | 5337 | 2024-04-19 | 2024-05-15 | 2024-07-03 | 2024-08-19 | 47 | 81.1111 | Delayed due to turbine lift not working and lift operation delay from project team | 2025-03-21 | 2025-04-15 | 2025-04-21 | 25
9 | Babra | O2-20 | 5343 | 2024-04-19 | 2024-05-02 | 2024-06-20 | 2024-07-03 | 13 | 100 |  | 2025-03-25 | 2025-04-25 | 2025-04-26 | 31
10 | Babra | O2-09 | 5331 | 2024-05-25 | 2024-05-21 | 2024-07-09 | 2024-08-16 | 38 | 91.1111 | Delayed due to turbine access road issue | 2025-03-27 | 2025-04-07 | 2025-04-08 | 11
11 | Babra | O2-05 | 5329 | 2024-04-19 | 2024-05-21 | 2024-07-09 | 2024-08-12 | 34 | 95.5556 | Delayed due to turbine access road issue | 2025-04-01 | 2025-03-22 | 2025-03-25 | -10
12 | Babra | O2-02 | 5340 | 2024-05-25 | 2024-05-24 | 2024-07-12 | 2024-10-27 | 107 | 14.4444 | Deleyed due to turbine access road access issue | 2025-04-03 | 2025-04-17 | 2025-04-18 | 14
13 | Babra | O2-01 | 5346 | 2024-06-26 | 2024-06-14 | 2024-08-02 | 2024-08-13 | 11 | 100 |  | 2025-04-07 | 2025-04-03 | 2025-04-04 | -4
14 | Babra | O2-06 | 5347 | 2024-06-26 | 2024-06-24 | 2024-08-12 | 2024-09-04 | 23 | 100 |  | 2025-04-09 | 2025-04-28 | 2025-04-29 | 19
15 | Babra | O2-18 | 5349 | 2024-06-26 | 2024-06-25 | 2024-08-13 | 2024-08-21 | 8 | 100 |  | 2025-04-11 | 2025-04-19 | 2025-04-20 | 8
16 | Babra | O2-21 | 5344 | 2024-06-26 | 2024-06-22 | 2024-08-10 | 2024-08-23 | 13 | 100 |  | 2025-04-15 | 2025-05-02 |  | 17 |  | PM Completed -01 day
17 | Babra | O2-24 | 5352 | 2024-07-25 | 2024-07-25 | 2024-09-12 | 2024-09-09 | -3 | 100 |  | 2025-04-17 | 2025-05-03 |  | 16 |  | PM Completed -01 day
18 | Babra | O2-25 | 5353 | 2024-06-26 | 2024-07-19 | 2024-09-06 | 2024-09-06 | 0 | 100 |  | 2025-04-21 | 2025-05-04 |  | 13 |  | PM Completed -01 day
19 | Babra | O2-26 | 5345 | 2024-08-18 | 2024-08-20 | 2024-09-10 | 2024-09-13 | 3 | 100 |  | 2025-10-01
20 | Babra | O2-04 | 5328 | 2024-08-22 | 2024-08-29 | 2024-10-17 | 2024-10-18 | 1 | 100 |  | 2025-10-03
21 | Babra | O2-07 | 5330 | 2024-08-24 | 2024-09-03 | 2024-10-22 | 2024-10-21 | -1 | 100 |  | 2025-10-05
22 | Babra | O2-08 | 5348 | 2024-09-21 | 2024-09-21 | 2024-11-09 | 2024-10-25 | -15 | 100 |  | 2025-10-08
23 | Babra | O2-19 | 5339 | 2024-10-13 | 2024-10-13 | 2024-12-14 | 2024-12-15 | 1 | 100 |  | 2025-10-10
24 | Babra | O2-22 | 5351 | 2024-10-17 | 2024-10-17 | 2024-12-15 | 2024-12-16 | 1 | 100 |  | 2025-10-12
25 | Babra | O2-23 | 5350 | 2024-10-28 | 2024-10-26 | 2024-12-16 | 2024-12-17 | 1 | 100 |  | 2025-10-15
26 | Babra | O2-17 | 5338 | 4564600% | 4564600% | 4567700% | 4567700% | 0 | 100 |  | 2025-10-17
Note : New WTGs maintenacne will add based on commissioning date
Formulas:
Plan Date = [Date of Operation]+49

## Modelling New (hidden)
Sr. No. | Month Name | Month Number | Month | CY | FY | No. of Days in Month | GHI | POA | WS | Tamb | Tmod | Egrid (MWh) | Bugt_Capacity | PR | Daily POA | Days Operated | MTD POA | YTD POA | Daily Energy (MWh) | MTD Energy (MWh) | YTD Energy (MWh) | Bugt CUF (%) | Bugt CUF (%) MTD | Bugt CUF (%)YTD | Ave. Cap MTD | Ave. Cap YTD | CC Energy MTD | WS MTD | WS YTD | Bugt PA | Bugt EGA | Bugt TA | Bugt MA | Bugt IGA | Corelation | Bugt Line loss | Bugt Reactive Power | Bugt Capacity | CC*Bugt | Total Capacity | 70.4
1 | April | 4 | 2024-04-01 | 2024 | FY25 | 30 |  |  | 6.65 |  |  | 0 | 0 |  |  | 0 |  |  | 0 | 0 | 0 | [6 empty] | 6.65 | 6.65 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5% |  |  | Hourly reactive power bugt | 3.52
2 | May | 5 | 2024-05-01 | 2024 | FY25 | 31 |  |  | 7.19 |  |  | 8711.265 | 27 |  |  | 0 |  |  | 281.0085 | 0 | 0 | 43.37% | [5 empty] | 7.19 | 6.92 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5% |  |  | Day | 84.48
3 | June | 6 | 2024-06-01 | 2024 | FY25 | 30 |  |  | 7.15 |  |  | 7436.691 | 27 |  |  | 0 |  |  | 247.8897 | 0 | 0 | 38.25% | [5 empty] | 7.15 | 6.9967 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
4 | July | 7 | 2024-07-01 | 2024 | FY25 | 31 |  |  | 8.18 |  |  | 24024.425 | 70.2 |  |  | 0 |  |  | 774.9815 | 0 | 0 | 46% | [5 empty] | 8.18 | 7.2925 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
5 | August | 8 | 2024-08-01 | 2024 | FY25 | 31 |  |  | 9.01 |  |  | 22325.728 | 70.2 |  |  | 0 |  |  | 720.1848 | 0 | 0 | 42.75% | [5 empty] | 9.01 | 7.636 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
6 | September | 9 | 2024-09-01 | 2024 | FY25 | 30 |  |  | 8.16 |  |  | 15949.744 | 70.2 |  |  | 0 |  |  | 531.6581 | 0 | 0 | 31.56% | [5 empty] | 8.16 | 7.7233 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
7 | October | 10 | 2024-10-01 | 2024 | FY25 | 31 |  |  | 9.21 |  |  | 11324.645 | 70.2 |  |  | 0 |  |  | 365.3111 | 0 | 0 | 21.68% | [5 empty] | 9.21 | 7.9357 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
8 | November | 11 | 2024-11-01 | 2024 | FY25 | 30 |  |  | 8.33 |  |  | 12231.399 | 70.2 |  |  | 0 |  |  | 407.7133 | 0 | 0 | 24.2% | [5 empty] | 8.33 | 7.985 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
9 | December | 12 | 2024-12-01 | 2024 | FY25 | 31 |  |  | 6.95 |  |  | 17896.983 | 70.2 |  |  | 0 |  |  | 577.322 | 0 | 0 | 34.27% | [5 empty] | 6.95 | 7.87 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
10 | January | 1 | 2025-01-01 | 2025 | FY25 | 31 |  |  | 5.57 |  |  | 19110.338 | 70.2 |  |  | 0 |  |  | 616.4625 | 0 | 0 | 36.59% | [5 empty] | 5.57 | 7.64 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
11 | February | 2 | 2025-02-01 | 2025 | FY25 | 28 |  |  | 5.52 |  |  | 14703.772 | 70.2 |  |  | 0 |  |  | 525.1347 | 0 | 0 | 31.17% | [5 empty] | 5.52 | 7.4473 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
12 | March | 4 | 2025-03-01 | 2025 | FY25 | 31 |  |  | 6.89 |  |  | 19615.902 | 70.2 |  |  | 3 |  |  | 632.771 | 1898.3131 | 1898.3131 | 37.56% | 37.56% | 37.56% | 70.2 | 70.2 |  | 6.89 | 7.4008 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
13 | April | 5 | 2025-04-01 | 2025 | FY26 | 30 |  |  | 6.65 |  |  | 20932.8163 | 70.2 |  |  | 30 |  |  | 697.7605 | 20932.8163 | 20932.8163 | 41.42% | 41.42% | 41.42% | 70.2 | 70.2 |  | 6.65 | 6.65 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
14 | May | 6 | 2025-05-01 | 2025 | FY26 | 31 |  |  | 7.19 |  |  | 28170.0535 | 70.2 |  |  | 31 |  |  | 908.7114 | 28170.0535 | 49102.8698 | 53.94% | 53.94% | 47.78% | 70.2 | 70.2 |  | 7.19 | 6.92 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
15 | June | 7 | 2025-06-01 | 2025 | FY26 | 30 |  |  | 7.15 |  |  | 24048.3982 | 70.2 |  |  | 30 |  |  | 801.6133 | 24048.3982 | 73151.268 | 47.58% | 47.58% | 47.71% | 70.2 | 70.2 |  | 7.15 | 6.9967 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
16 | July | 8 | 2025-07-01 | 2025 | FY26 | 31 |  |  | 8.18 |  |  | 29880.3782 | 70.2 |  |  | 0 |  |  | 963.8832 | 0 | 73151.268 | 57.21% |  | 47.71% |  | 70.2 |  | 8.18 | 7.2925 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
17 | August | 9 | 2025-08-01 | 2025 | FY26 | 31 |  |  | 9.01 |  |  | 27767.6242 | 70.2 |  |  | 0 |  |  | 895.7298 | 0 | 73151.268 | 53.17% |  | 47.71% |  | 70.2 |  | 9.01 | 7.636 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
18 | September | 10 | 2025-09-01 | 2025 | FY26 | 30 |  |  | 8.16 |  |  | 15869.9956 | 70.2 |  |  | 0 |  |  | 528.9999 | 0 | 73151.268 | 31.4% |  | 47.71% |  | 70.2 |  | 8.16 | 7.7233 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
19 | October | 11 | 2025-10-01 | 2025 | FY26 | 31 |  |  | 9.21 |  |  | 11268.0214 | 70.2 |  |  | 0 |  |  | 363.4846 | 0 | 73151.268 | 21.57% |  | 47.71% |  | 70.2 |  | 9.21 | 7.9357 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
20 | November | 12 | 2025-11-01 | 2025 | FY26 | 30 |  |  | 8.33 |  |  | 12170.242 | 70.2 |  |  | 0 |  |  | 405.6747 | 0 | 73151.268 | 24.08% |  | 47.71% |  | 70.2 |  | 8.33 | 7.985 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
21 | December | 1 | 2025-12-01 | 2025 | FY26 | 31 |  |  | 6.95 |  |  | 17807.4981 | 70.2 |  |  | 0 |  |  | 574.4354 | 0 | 73151.268 | 34.1% |  | 47.71% |  | 70.2 |  | 6.95 | 7.87 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
22 | January | 2 | 2026-01-01 | 2026 | FY26 | 31 |  |  | 5.57 |  |  | 19014.7861 | 70.2 |  |  | 0 |  |  | 613.3802 | 0 | 73151.268 | 36.41% |  | 47.71% |  | 70.2 |  | 5.57 | 7.64 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
23 | February | 4 | 2026-02-01 | 2026 | FY26 | 28 |  |  | 5.52 |  |  | 14630.2536 | 70.2 |  |  | 0 |  |  | 522.5091 | 0 | 73151.268 | 31.01% |  | 47.71% |  | 70.2 |  | 5.52 | 7.4473 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
24 | March | 5 | 2026-03-01 | 2026 | FY26 | 31 |  |  | 6.89 |  |  | 19517.8228 | 70.2 |  |  | 0 |  |  | 629.6072 | 0 | 73151.268 | 37.37% |  | 47.71% |  | 70.2 |  | 6.89 | 7.4008 | 96.03% | 99.5% |  | 97% | 99% | 95% | 5% | 5%
Formulas:
No. of Days in Month = DAY(EOMONTH([Month],0))

## Modelling (hidden)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
Date | FY | Year | Month | Days | E_Grid daily MWh | E_Grid MTD MWh | E_Grid YTD MWh | WS Daily | WS MTD | WS YTD | CUF Daily | CUF MTD | CUF YTD | Day Capacity | MTD Capacity | YTD Capacity |  |  | Month | Days | Wind Speed (m/s) | Egrid Energy (KWh) | Capacity
4538300% | 2025 | 2024 | 2024-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 4 | 30 | 8.29 | 0 | 0
4538400% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 5 | 31 | 9.1 | 8711265 | 27
4538500% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 6 | 30 | 8.23 | 7436691 | 27
4538600% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 7 | 31 | 9.35 | 24024425 | 70.2
4538700% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 8 | 31 | 8.47 | 22325728 | 70.2
4538800% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 9 | 30 | 7.08 | 15949744 | 70.2
4538900% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 10 | 31 | 5.65 | 11324645 | 70.2
4539000% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 11 | 30 | 5.59 | 12231399 | 70.2
4539100% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 12 | 31 | 6.99 | 17896983 | 70.2
4539200% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 1 | 31 | 6.74 | 19110338 | 70.2
4539300% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 2 | 28 | 7.3 | 14703772 | 70.2
4539400% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [5 empty] | 3 | 31 | 7.28 | 19615902 | 70.2
4539500% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0! | [7 empty] | 7.5058 | 22937709.6
4539600% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4539700% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4539800% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4539900% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540000% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540100% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540200% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540300% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540400% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540500% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540600% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540700% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540800% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4540900% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4541000% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4541100% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4541200% | 2025 | 2024 | 2022-04-01 | 30 | 0 | 0 | 0 | 8.29 | 8.29 | 8.29 | #DIV/0! | #DIV/0! | #DIV/0!
4541300% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 281.0085 | 281.0085 | 9.1 | 9.1 | 8.3161 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 1 | 1
4541400% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 562.0171 | 562.0171 | 9.1 | 9.1 | 8.3406 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 2 | 2
4541500% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 843.0256 | 843.0256 | 9.1 | 9.1 | 8.3636 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 3 | 3
4541600% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 1124.0342 | 1124.0342 | 9.1 | 9.1 | 8.3853 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 4 | 4
4541700% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 1405.0427 | 1405.0427 | 9.1 | 9.1 | 8.4057 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 5 | 5
4541800% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 1686.0513 | 1686.0513 | 9.1 | 9.1 | 8.425 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 6 | 6
4541900% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 1967.0598 | 1967.0598 | 9.1 | 9.1 | 8.4432 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 7 | 7
4542000% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 2248.0684 | 2248.0684 | 9.1 | 9.1 | 8.4605 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 8 | 8
4542100% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 2529.0769 | 2529.0769 | 9.1 | 9.1 | 8.4769 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 9 | 9
4542200% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 2810.0855 | 2810.0855 | 9.1 | 9.1 | 8.4925 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 10 | 10
4542300% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 3091.094 | 3091.094 | 9.1 | 9.1 | 8.5073 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 11 | 11
4542400% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 3372.1026 | 3372.1026 | 9.1 | 9.1 | 8.5214 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 12 | 12
4542500% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 3653.1111 | 3653.1111 | 9.1 | 9.1 | 8.5349 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 13 | 13
4542600% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 3934.1197 | 3934.1197 | 9.1 | 9.1 | 8.5477 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 14 | 14
4542700% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 4215.1282 | 4215.1282 | 9.1 | 9.1 | 8.56 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 15 | 15
4542800% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 4496.1368 | 4496.1368 | 9.1 | 9.1 | 8.5717 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 16 | 16
4542900% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 4777.1453 | 4777.1453 | 9.1 | 9.1 | 8.583 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 17 | 17
4543000% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 5058.1539 | 5058.1539 | 9.1 | 9.1 | 8.5938 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 18 | 18
4543100% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 5339.1624 | 5339.1624 | 9.1 | 9.1 | 8.6041 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 19 | 19
4543200% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 5620.171 | 5620.171 | 9.1 | 9.1 | 8.614 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 20 | 20
4543300% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 5901.1795 | 5901.1795 | 9.1 | 9.1 | 8.6235 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 21 | 21
4543400% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 6182.1881 | 6182.1881 | 9.1 | 9.1 | 8.6327 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 22 | 22
4543500% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 6463.1966 | 6463.1966 | 9.1 | 9.1 | 8.6415 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 23 | 23
4543600% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 6744.2052 | 6744.2052 | 9.1 | 9.1 | 8.65 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 24 | 24
4543700% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 7025.2137 | 7025.2137 | 9.1 | 9.1 | 8.6582 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 25 | 25
4543800% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 7306.2223 | 7306.2223 | 9.1 | 9.1 | 8.6661 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 26 | 26
4543900% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 7587.2308 | 7587.2308 | 9.1 | 9.1 | 8.6737 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 27 | 27
4544000% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 7868.2394 | 7868.2394 | 9.1 | 9.1 | 8.681 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 28 | 28
4544100% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 8149.2479 | 8149.2479 | 9.1 | 9.1 | 8.6881 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 29 | 29
4544200% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 8430.2565 | 8430.2565 | 9.1 | 9.1 | 8.695 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 30 | 30
4544300% | 2025 | 2024 | 2022-05-01 | 31 | 281.0085 | 8711.265 | 8711.265 | 9.1 | 9.1 | 8.7016 | 43.37% | 43.37% | 43.37% | 27 | 27 | 27 | 31 | 31
4544400% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 247.8897 | 8959.1547 | 8.23 | 8.23 | 8.694 | 38.25% | 38.25% | 43.21% | 27 | 27 | 27 | 1 | 32
4544500% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 495.7794 | 9207.0444 | 8.23 | 8.23 | 8.6867 | 38.25% | 38.25% | 43.06% | 27 | 27 | 27 | 2 | 33
4544600% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 743.6691 | 9454.9341 | 8.23 | 8.23 | 8.6795 | 38.25% | 38.25% | 42.91% | 27 | 27 | 27 | 3 | 34
4544700% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 991.5588 | 9702.8238 | 8.23 | 8.23 | 8.6726 | 38.25% | 38.25% | 42.78% | 27 | 27 | 27 | 4 | 35
4544800% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 1239.4485 | 9950.7135 | 8.23 | 8.23 | 8.6659 | 38.25% | 38.25% | 42.66% | 27 | 27 | 27 | 5 | 36
4544900% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 1487.3382 | 10198.6032 | 8.23 | 8.23 | 8.6594 | 38.25% | 38.25% | 42.54% | 27 | 27 | 27 | 6 | 37
4545000% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 1735.2279 | 10446.4929 | 8.23 | 8.23 | 8.6531 | 38.25% | 38.25% | 42.42% | 27 | 27 | 27 | 7 | 38
4545100% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 1983.1176 | 10694.3826 | 8.23 | 8.23 | 8.647 | 38.25% | 38.25% | 42.32% | 27 | 27 | 27 | 8 | 39
4545200% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 2231.0073 | 10942.2723 | 8.23 | 8.23 | 8.641 | 38.25% | 38.25% | 42.22% | 27 | 27 | 27 | 9 | 40
4545300% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 2478.897 | 11190.162 | 8.23 | 8.23 | 8.6352 | 38.25% | 38.25% | 42.12% | 27 | 27 | 27 | 10 | 41
4545400% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 2726.7867 | 11438.0517 | 8.23 | 8.23 | 8.6296 | 38.25% | 38.25% | 42.03% | 27 | 27 | 27 | 11 | 42
4545500% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 2974.6764 | 11685.9414 | 8.23 | 8.23 | 8.6241 | 38.25% | 38.25% | 41.94% | 27 | 27 | 27 | 12 | 43
4545600% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 3222.5661 | 11933.8311 | 8.23 | 8.23 | 8.6188 | 38.25% | 38.25% | 41.86% | 27 | 27 | 27 | 13 | 44
4545700% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 3470.4558 | 12181.7208 | 8.23 | 8.23 | 8.6136 | 38.25% | 38.25% | 41.78% | 27 | 27 | 27 | 14 | 45
4545800% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 3718.3455 | 12429.6105 | 8.23 | 8.23 | 8.6086 | 38.25% | 38.25% | 41.7% | 27 | 27 | 27 | 15 | 46
4545900% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 3966.2352 | 12677.5002 | 8.23 | 8.23 | 8.6036 | 38.25% | 38.25% | 41.63% | 27 | 27 | 27 | 16 | 47
4546000% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 4214.1249 | 12925.3899 | 8.23 | 8.23 | 8.5988 | 38.25% | 38.25% | 41.56% | 27 | 27 | 27 | 17 | 48
4546100% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 4462.0146 | 13173.2796 | 8.23 | 8.23 | 8.5942 | 38.25% | 38.25% | 41.49% | 27 | 27 | 27 | 18 | 49
4546200% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 4709.9043 | 13421.1693 | 8.23 | 8.23 | 8.5896 | 38.25% | 38.25% | 41.42% | 27 | 27 | 27 | 19 | 50
4546300% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 4957.794 | 13669.059 | 8.23 | 8.23 | 8.5852 | 38.25% | 38.25% | 41.36% | 27 | 27 | 27 | 20 | 51
4546400% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 5205.6837 | 13916.9487 | 8.23 | 8.23 | 8.5809 | 38.25% | 38.25% | 41.3% | 27 | 27 | 27 | 21 | 52
4546500% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 5453.5734 | 14164.8384 | 8.23 | 8.23 | 8.5766 | 38.25% | 38.25% | 41.24% | 27 | 27 | 27 | 22 | 53
4546600% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 5701.4631 | 14412.7281 | 8.23 | 8.23 | 8.5725 | 38.25% | 38.25% | 41.19% | 27 | 27 | 27 | 23 | 54
4546700% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 5949.3528 | 14660.6178 | 8.23 | 8.23 | 8.5685 | 38.25% | 38.25% | 41.14% | 27 | 27 | 27 | 24 | 55
4546800% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 6197.2425 | 14908.5075 | 8.23 | 8.23 | 8.5645 | 38.25% | 38.25% | 41.08% | 27 | 27 | 27 | 25 | 56
4546900% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 6445.1322 | 15156.3972 | 8.23 | 8.23 | 8.5607 | 38.25% | 38.25% | 41.03% | 27 | 27 | 27 | 26 | 57
4547000% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 6693.0219 | 15404.2869 | 8.23 | 8.23 | 8.5569 | 38.25% | 38.25% | 40.99% | 27 | 27 | 27 | 27 | 58
4547100% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 6940.9116 | 15652.1766 | 8.23 | 8.23 | 8.5533 | 38.25% | 38.25% | 40.94% | 27 | 27 | 27 | 28 | 59
4547200% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 7188.8013 | 15900.0663 | 8.23 | 8.23 | 8.5497 | 38.25% | 38.25% | 40.9% | 27 | 27 | 27 | 29 | 60
4547300% | 2025 | 2024 | 2022-06-01 | 30 | 247.8897 | 7436.691 | 16147.956 | 8.23 | 8.23 | 8.5462 | 38.25% | 38.25% | 40.85% | 27 | 27 | 27 | 30 | 61
4547400% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 774.9815 | 16922.9375 | 9.35 | 9.35 | 8.5549 | 46% | 46% | 41.06% | 70.2 | 70.2 | 27.6968 | 1 | 62
4547500% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 1549.9629 | 17697.9189 | 9.35 | 9.35 | 8.5634 | 46% | 46% | 41.26% | 70.2 | 70.2 | 28.3714 | 2 | 63
4547600% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 2324.9444 | 18472.9004 | 9.35 | 9.35 | 8.5718 | 46% | 46% | 41.44% | 70.2 | 70.2 | 29.025 | 3 | 64
4547700% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 3099.9258 | 19247.8818 | 9.35 | 9.35 | 8.58 | 46% | 46% | 41.6% | 70.2 | 70.2 | 29.6585 | 4 | 65
4547800% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 3874.9073 | 20022.8633 | 9.35 | 9.35 | 8.588 | 46% | 46% | 41.76% | 70.2 | 70.2 | 30.2727 | 5 | 66
4547900% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 4649.8887 | 20797.8447 | 9.35 | 9.35 | 8.5959 | 46% | 46% | 41.9% | 70.2 | 70.2 | 30.8687 | 6 | 67
4548000% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 5424.8702 | 21572.8262 | 9.35 | 9.35 | 8.6036 | 46% | 46% | 42.03% | 70.2 | 70.2 | 31.4471 | 7 | 68
4548100% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 6199.8516 | 22347.8076 | 9.35 | 9.35 | 8.6111 | 46% | 46% | 42.16% | 70.2 | 70.2 | 32.0087 | 8 | 69
4548200% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 6974.8331 | 23122.7891 | 9.35 | 9.35 | 8.6185 | 46% | 46% | 42.28% | 70.2 | 70.2 | 32.5543 | 9 | 70
4548300% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 7749.8145 | 23897.7705 | 9.35 | 9.35 | 8.6257 | 46% | 46% | 42.39% | 70.2 | 70.2 | 33.0845 | 10 | 71
4548400% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 8524.796 | 24672.752 | 9.35 | 9.35 | 8.6328 | 46% | 46% | 42.49% | 70.2 | 70.2 | 33.6 | 11 | 72
4548500% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 9299.7774 | 25447.7334 | 9.35 | 9.35 | 8.6398 | 46% | 46% | 42.59% | 70.2 | 70.2 | 34.1014 | 12 | 73
4548600% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 10074.7589 | 26222.7149 | 9.35 | 9.35 | 8.6466 | 46% | 46% | 42.69% | 70.2 | 70.2 | 34.5892 | 13 | 74
4548700% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 10849.7403 | 26997.6963 | 9.35 | 9.35 | 8.6533 | 46% | 46% | 42.78% | 70.2 | 70.2 | 35.064 | 14 | 75
4548800% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 11624.7218 | 27772.6778 | 9.35 | 9.35 | 8.6599 | 46% | 46% | 42.86% | 70.2 | 70.2 | 35.5263 | 15 | 76
4548900% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 12399.7032 | 28547.6592 | 9.35 | 9.35 | 8.6664 | 46% | 46% | 42.94% | 70.2 | 70.2 | 35.9766 | 16 | 77
4549000% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 13174.6847 | 29322.6407 | 9.35 | 9.35 | 8.6727 | 46% | 46% | 43.01% | 70.2 | 70.2 | 36.4154 | 17 | 78
4549100% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 13949.6661 | 30097.6221 | 9.35 | 9.35 | 8.6789 | 46% | 46% | 43.09% | 70.2 | 70.2 | 36.843 | 18 | 79
4549200% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 14724.6476 | 30872.6036 | 9.35 | 9.35 | 8.685 | 46% | 46% | 43.15% | 70.2 | 70.2 | 37.26 | 19 | 80
4549300% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 15499.629 | 31647.585 | 9.35 | 9.35 | 8.691 | 46% | 46% | 43.22% | 70.2 | 70.2 | 37.6667 | 20 | 81
4549400% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 16274.6105 | 32422.5665 | 9.35 | 9.35 | 8.6969 | 46% | 46% | 43.28% | 70.2 | 70.2 | 38.0634 | 21 | 82
4549500% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 17049.5919 | 33197.5479 | 9.35 | 9.35 | 8.7027 | 46% | 46% | 43.34% | 70.2 | 70.2 | 38.4506 | 22 | 83
4549600% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 17824.5734 | 33972.5294 | 9.35 | 9.35 | 8.7083 | 46% | 46% | 43.4% | 70.2 | 70.2 | 38.8286 | 23 | 84
4549700% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 18599.5548 | 34747.5108 | 9.35 | 9.35 | 8.7139 | 46% | 46% | 43.45% | 70.2 | 70.2 | 39.1976 | 24 | 85
4549800% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 19374.5363 | 35522.4923 | 9.35 | 9.35 | 8.7194 | 46% | 46% | 43.51% | 70.2 | 70.2 | 39.5581 | 25 | 86
4549900% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 20149.5177 | 36297.4737 | 9.35 | 9.35 | 8.7248 | 46% | 46% | 43.56% | 70.2 | 70.2 | 39.9103 | 26 | 87
4550000% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 20924.4992 | 37072.4552 | 9.35 | 9.35 | 8.7301 | 46% | 46% | 43.61% | 70.2 | 70.2 | 40.2545 | 27 | 88
4550100% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 21699.4806 | 37847.4366 | 9.35 | 9.35 | 8.7353 | 46% | 46% | 43.65% | 70.2 | 70.2 | 40.591 | 28 | 89
4550200% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 22474.4621 | 38622.4181 | 9.35 | 9.35 | 8.7404 | 46% | 46% | 43.7% | 70.2 | 70.2 | 40.92 | 29 | 90
4550300% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 23249.4435 | 39397.3995 | 9.35 | 9.35 | 8.7455 | 46% | 46% | 43.74% | 70.2 | 70.2 | 41.2418 | 30 | 91
4550400% | 2025 | 2024 | 2022-07-01 | 31 | 774.9815 | 24024.425 | 40172.381 | 9.35 | 9.35 | 8.7504 | 46% | 46% | 43.78% | 70.2 | 70.2 | 41.5565 | 31 | 92
4550500% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 720.1848 | 40892.5658 | 8.47 | 8.47 | 8.7481 | 42.75% | 42.75% | 43.76% | 70.2 | 70.2 | 41.8645 | 1 | 93
4550600% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 1440.3695 | 41612.7505 | 8.47 | 8.47 | 8.7459 | 42.75% | 42.75% | 43.74% | 70.2 | 70.2 | 42.166 | 2 | 94
4550700% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 2160.5543 | 42332.9353 | 8.47 | 8.47 | 8.7437 | 42.75% | 42.75% | 43.73% | 70.2 | 70.2 | 42.4611 | 3 | 95
4550800% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 2880.7391 | 43053.1201 | 8.47 | 8.47 | 8.7415 | 42.75% | 42.75% | 43.71% | 70.2 | 70.2 | 42.75 | 4 | 96
4550900% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 3600.9239 | 43773.3049 | 8.47 | 8.47 | 8.7394 | 42.75% | 42.75% | 43.69% | 70.2 | 70.2 | 43.033 | 5 | 97
4551000% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 4321.1086 | 44493.4896 | 8.47 | 8.47 | 8.7373 | 42.75% | 42.75% | 43.68% | 70.2 | 70.2 | 43.3102 | 6 | 98
4551100% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 5041.2934 | 45213.6744 | 8.47 | 8.47 | 8.7352 | 42.75% | 42.75% | 43.66% | 70.2 | 70.2 | 43.5818 | 7 | 99
4551200% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 5761.4782 | 45933.8592 | 8.47 | 8.47 | 8.7332 | 42.75% | 42.75% | 43.65% | 70.2 | 70.2 | 43.848 | 8 | 100
4551300% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 6481.663 | 46654.044 | 8.47 | 8.47 | 8.7311 | 42.75% | 42.75% | 43.63% | 70.2 | 70.2 | 44.1089 | 9 | 101
4551400% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 7201.8477 | 47374.2287 | 8.47 | 8.47 | 8.7292 | 42.75% | 42.75% | 43.62% | 70.2 | 70.2 | 44.3647 | 10 | 102
4551500% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 7922.0325 | 48094.4135 | 8.47 | 8.47 | 8.7272 | 42.75% | 42.75% | 43.61% | 70.2 | 70.2 | 44.6155 | 11 | 103
4551600% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 8642.2173 | 48814.5983 | 8.47 | 8.47 | 8.7253 | 42.75% | 42.75% | 43.59% | 70.2 | 70.2 | 44.8615 | 12 | 104
4551700% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 9362.4021 | 49534.7831 | 8.47 | 8.47 | 8.7234 | 42.75% | 42.75% | 43.58% | 70.2 | 70.2 | 45.1029 | 13 | 105
4551800% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 10082.5868 | 50254.9678 | 8.47 | 8.47 | 8.7215 | 42.75% | 42.75% | 43.57% | 70.2 | 70.2 | 45.3396 | 14 | 106
4551900% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 10802.7716 | 50975.1526 | 8.47 | 8.47 | 8.7197 | 42.75% | 42.75% | 43.56% | 70.2 | 70.2 | 45.572 | 15 | 107
4552000% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 11522.9564 | 51695.3374 | 8.47 | 8.47 | 8.7179 | 42.75% | 42.75% | 43.55% | 70.2 | 70.2 | 45.8 | 16 | 108
4552100% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 12243.1412 | 52415.5222 | 8.47 | 8.47 | 8.7161 | 42.75% | 42.75% | 43.54% | 70.2 | 70.2 | 46.0239 | 17 | 109
4552200% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 12963.3259 | 53135.7069 | 8.47 | 8.47 | 8.7144 | 42.75% | 42.75% | 43.52% | 70.2 | 70.2 | 46.2436 | 18 | 110
4552300% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 13683.5107 | 53855.8917 | 8.47 | 8.47 | 8.7126 | 42.75% | 42.75% | 43.51% | 70.2 | 70.2 | 46.4595 | 19 | 111
4552400% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 14403.6955 | 54576.0765 | 8.47 | 8.47 | 8.7109 | 42.75% | 42.75% | 43.5% | 70.2 | 70.2 | 46.6714 | 20 | 112
4552500% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 15123.8803 | 55296.2613 | 8.47 | 8.47 | 8.7092 | 42.75% | 42.75% | 43.49% | 70.2 | 70.2 | 46.8796 | 21 | 113
4552600% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 15844.065 | 56016.446 | 8.47 | 8.47 | 8.7076 | 42.75% | 42.75% | 43.48% | 70.2 | 70.2 | 47.0842 | 22 | 114
4552700% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 16564.2498 | 56736.6308 | 8.47 | 8.47 | 8.7059 | 42.75% | 42.75% | 43.47% | 70.2 | 70.2 | 47.2852 | 23 | 115
4552800% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 17284.4346 | 57456.8156 | 8.47 | 8.47 | 8.7043 | 42.75% | 42.75% | 43.46% | 70.2 | 70.2 | 47.4828 | 24 | 116
4552900% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 18004.6194 | 58177.0004 | 8.47 | 8.47 | 8.7027 | 42.75% | 42.75% | 43.46% | 70.2 | 70.2 | 47.6769 | 25 | 117
4553000% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 18724.8041 | 58897.1851 | 8.47 | 8.47 | 8.7011 | 42.75% | 42.75% | 43.45% | 70.2 | 70.2 | 47.8678 | 26 | 118
4553100% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 19444.9889 | 59617.3699 | 8.47 | 8.47 | 8.6996 | 42.75% | 42.75% | 43.44% | 70.2 | 70.2 | 48.0555 | 27 | 119
4553200% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 20165.1737 | 60337.5547 | 8.47 | 8.47 | 8.6981 | 42.75% | 42.75% | 43.43% | 70.2 | 70.2 | 48.24 | 28 | 120
4553300% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 20885.3585 | 61057.7395 | 8.47 | 8.47 | 8.6966 | 42.75% | 42.75% | 43.42% | 70.2 | 70.2 | 48.4215 | 29 | 121
4553400% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 21605.5432 | 61777.9242 | 8.47 | 8.47 | 8.6951 | 42.75% | 42.75% | 43.41% | 70.2 | 70.2 | 48.6 | 30 | 122
4553500% | 2025 | 2024 | 2022-08-01 | 31 | 720.1848 | 22325.728 | 62498.109 | 8.47 | 8.47 | 8.6936 | 42.75% | 42.75% | 43.41% | 70.2 | 70.2 | 48.7756 | 31 | 123
4553600% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 531.6581 | 63029.7671 | 7.08 | 7.08 | 8.6831 | 31.56% | 31.56% | 43.27% | 70.2 | 70.2 | 48.9484 | 1 | 124
4553700% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 1063.3163 | 63561.4253 | 7.08 | 7.08 | 8.6728 | 31.56% | 31.56% | 43.13% | 70.2 | 70.2 | 49.1184 | 2 | 125
4553800% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 1594.9744 | 64093.0834 | 7.08 | 7.08 | 8.6626 | 31.56% | 31.56% | 43% | 70.2 | 70.2 | 49.2857 | 3 | 126
4553900% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 2126.6325 | 64624.7415 | 7.08 | 7.08 | 8.6525 | 31.56% | 31.56% | 42.88% | 70.2 | 70.2 | 49.4504 | 4 | 127
4554000% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 2658.2907 | 65156.3997 | 7.08 | 7.08 | 8.6425 | 31.56% | 31.56% | 42.75% | 70.2 | 70.2 | 49.6125 | 5 | 128
4554100% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 3189.9488 | 65688.0578 | 7.08 | 7.08 | 8.6327 | 31.56% | 31.56% | 42.63% | 70.2 | 70.2 | 49.7721 | 6 | 129
4554200% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 3721.6069 | 66219.7159 | 7.08 | 7.08 | 8.623 | 31.56% | 31.56% | 42.51% | 70.2 | 70.2 | 49.9292 | 7 | 130
4554300% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 4253.2651 | 66751.3741 | 7.08 | 7.08 | 8.6134 | 31.56% | 31.56% | 42.39% | 70.2 | 70.2 | 50.084 | 8 | 131
4554400% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 4784.9232 | 67283.0322 | 7.08 | 7.08 | 8.604 | 31.56% | 31.56% | 42.28% | 70.2 | 70.2 | 50.2364 | 9 | 132
4554500% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 5316.5813 | 67814.6903 | 7.08 | 7.08 | 8.5946 | 31.56% | 31.56% | 42.16% | 70.2 | 70.2 | 50.3865 | 10 | 133
4554600% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 5848.2395 | 68346.3485 | 7.08 | 7.08 | 8.5854 | 31.56% | 31.56% | 42.05% | 70.2 | 70.2 | 50.5343 | 11 | 134
4554700% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 6379.8976 | 68878.0066 | 7.08 | 7.08 | 8.5762 | 31.56% | 31.56% | 41.95% | 70.2 | 70.2 | 50.68 | 12 | 135
4554800% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 6911.5557 | 69409.6647 | 7.08 | 7.08 | 8.5672 | 31.56% | 31.56% | 41.84% | 70.2 | 70.2 | 50.8235 | 13 | 136
4554900% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 7443.2139 | 69941.3229 | 7.08 | 7.08 | 8.5583 | 31.56% | 31.56% | 41.74% | 70.2 | 70.2 | 50.965 | 14 | 137
4555000% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 7974.872 | 70472.981 | 7.08 | 7.08 | 8.5495 | 31.56% | 31.56% | 41.64% | 70.2 | 70.2 | 51.1043 | 15 | 138
4555100% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 8506.5301 | 71004.6391 | 7.08 | 7.08 | 8.5408 | 31.56% | 31.56% | 41.54% | 70.2 | 70.2 | 51.2417 | 16 | 139
4555200% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 9038.1883 | 71536.2973 | 7.08 | 7.08 | 8.5322 | 31.56% | 31.56% | 41.44% | 70.2 | 70.2 | 51.3771 | 17 | 140
4555300% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 9569.8464 | 72067.9554 | 7.08 | 7.08 | 8.5237 | 31.56% | 31.56% | 41.34% | 70.2 | 70.2 | 51.5106 | 18 | 141
4555400% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 10101.5045 | 72599.6135 | 7.08 | 7.08 | 8.5153 | 31.56% | 31.56% | 41.25% | 70.2 | 70.2 | 51.6423 | 19 | 142
4555500% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 10633.1627 | 73131.2717 | 7.08 | 7.08 | 8.5071 | 31.56% | 31.56% | 41.16% | 70.2 | 70.2 | 51.772 | 20 | 143
4555600% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 11164.8208 | 73662.9298 | 7.08 | 7.08 | 8.4989 | 31.56% | 31.56% | 41.07% | 70.2 | 70.2 | 51.9 | 21 | 144
4555700% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 11696.4789 | 74194.5879 | 7.08 | 7.08 | 8.4907 | 31.56% | 31.56% | 40.98% | 70.2 | 70.2 | 52.0262 | 22 | 145
4555800% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 12228.1371 | 74726.2461 | 7.08 | 7.08 | 8.4827 | 31.56% | 31.56% | 40.89% | 70.2 | 70.2 | 52.1507 | 23 | 146
4555900% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 12759.7952 | 75257.9042 | 7.08 | 7.08 | 8.4748 | 31.56% | 31.56% | 40.81% | 70.2 | 70.2 | 52.2735 | 24 | 147
4556000% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 13291.4533 | 75789.5623 | 7.08 | 7.08 | 8.467 | 31.56% | 31.56% | 40.72% | 70.2 | 70.2 | 52.3946 | 25 | 148
4556100% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 13823.1115 | 76321.2205 | 7.08 | 7.08 | 8.4592 | 31.56% | 31.56% | 40.64% | 70.2 | 70.2 | 52.5141 | 26 | 149
4556200% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 14354.7696 | 76852.8786 | 7.08 | 7.08 | 8.4516 | 31.56% | 31.56% | 40.56% | 70.2 | 70.2 | 52.632 | 27 | 150
4556300% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 14886.4277 | 77384.5367 | 7.08 | 7.08 | 8.444 | 31.56% | 31.56% | 40.48% | 70.2 | 70.2 | 52.7483 | 28 | 151
4556400% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 15418.0859 | 77916.1949 | 7.08 | 7.08 | 8.4365 | 31.56% | 31.56% | 40.4% | 70.2 | 70.2 | 52.8632 | 29 | 152
4556500% | 2025 | 2024 | 2022-09-01 | 30 | 531.6581 | 15949.744 | 78447.853 | 7.08 | 7.08 | 8.4291 | 31.56% | 31.56% | 40.33% | 70.2 | 70.2 | 52.9765 | 30 | 153
4556600% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 365.3111 | 78813.1641 | 5.65 | 5.65 | 8.414 | 21.68% | 21.68% | 40.17% | 70.2 | 70.2 | 53.0883 | 1 | 154
4556700% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 730.6223 | 79178.4753 | 5.65 | 5.65 | 8.399 | 21.68% | 21.68% | 40.01% | 70.2 | 70.2 | 53.1987 | 2 | 155
4556800% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 1095.9334 | 79543.7864 | 5.65 | 5.65 | 8.3842 | 21.68% | 21.68% | 39.85% | 70.2 | 70.2 | 53.3077 | 3 | 156
4556900% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 1461.2445 | 79909.0975 | 5.65 | 5.65 | 8.3696 | 21.68% | 21.68% | 39.7% | 70.2 | 70.2 | 53.4153 | 4 | 157
4557000% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 1826.5556 | 80274.4086 | 5.65 | 5.65 | 8.3552 | 21.68% | 21.68% | 39.55% | 70.2 | 70.2 | 53.5215 | 5 | 158
4557100% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 2191.8668 | 80639.7198 | 5.65 | 5.65 | 8.3408 | 21.68% | 21.68% | 39.41% | 70.2 | 70.2 | 53.6264 | 6 | 159
4557200% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 2557.1779 | 81005.0309 | 5.65 | 5.65 | 8.3267 | 21.68% | 21.68% | 39.26% | 70.2 | 70.2 | 53.73 | 7 | 160
4557300% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 2922.489 | 81370.342 | 5.65 | 5.65 | 8.3127 | 21.68% | 21.68% | 39.12% | 70.2 | 70.2 | 53.8323 | 8 | 161
4557400% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 3287.8002 | 81735.6532 | 5.65 | 5.65 | 8.2988 | 21.68% | 21.68% | 38.98% | 70.2 | 70.2 | 53.9333 | 9 | 162
4557500% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 3653.1113 | 82100.9643 | 5.65 | 5.65 | 8.2851 | 21.68% | 21.68% | 38.84% | 70.2 | 70.2 | 54.0331 | 10 | 163
4557600% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 4018.4224 | 82466.2754 | 5.65 | 5.65 | 8.2715 | 21.68% | 21.68% | 38.71% | 70.2 | 70.2 | 54.1317 | 11 | 164
4557700% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 4383.7335 | 82831.5865 | 5.65 | 5.65 | 8.2581 | 21.68% | 21.68% | 38.57% | 70.2 | 70.2 | 54.2291 | 12 | 165
4557800% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 4749.0447 | 83196.8977 | 5.65 | 5.65 | 8.2447 | 21.68% | 21.68% | 38.44% | 70.2 | 70.2 | 54.3253 | 13 | 166
4557900% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 5114.3558 | 83562.2088 | 5.65 | 5.65 | 8.2316 | 21.68% | 21.68% | 38.31% | 70.2 | 70.2 | 54.4204 | 14 | 167
4558000% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 5479.6669 | 83927.5199 | 5.65 | 5.65 | 8.2185 | 21.68% | 21.68% | 38.18% | 70.2 | 70.2 | 54.5143 | 15 | 168
4558100% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 5844.9781 | 84292.8311 | 5.65 | 5.65 | 8.2056 | 21.68% | 21.68% | 38.06% | 70.2 | 70.2 | 54.6071 | 16 | 169
4558200% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 6210.2892 | 84658.1422 | 5.65 | 5.65 | 8.1929 | 21.68% | 21.68% | 37.93% | 70.2 | 70.2 | 54.6988 | 17 | 170
4558300% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 6575.6003 | 85023.4533 | 5.65 | 5.65 | 8.1802 | 21.68% | 21.68% | 37.81% | 70.2 | 70.2 | 54.7895 | 18 | 171
4558400% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 6940.9115 | 85388.7645 | 5.65 | 5.65 | 8.1677 | 21.68% | 21.68% | 37.69% | 70.2 | 70.2 | 54.8791 | 19 | 172
4558500% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 7306.2226 | 85754.0756 | 5.65 | 5.65 | 8.1553 | 21.68% | 21.68% | 37.57% | 70.2 | 70.2 | 54.9676 | 20 | 173
4558600% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 7671.5337 | 86119.3867 | 5.65 | 5.65 | 8.143 | 21.68% | 21.68% | 37.46% | 70.2 | 70.2 | 55.0552 | 21 | 174
4558700% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 8036.8448 | 86484.6978 | 5.65 | 5.65 | 8.1308 | 21.68% | 21.68% | 37.34% | 70.2 | 70.2 | 55.1417 | 22 | 175
4558800% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 8402.156 | 86850.009 | 5.65 | 5.65 | 8.1188 | 21.68% | 21.68% | 37.23% | 70.2 | 70.2 | 55.2273 | 23 | 176
4558900% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 8767.4671 | 87215.3201 | 5.65 | 5.65 | 8.1069 | 21.68% | 21.68% | 37.12% | 70.2 | 70.2 | 55.3119 | 24 | 177
4559000% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 9132.7782 | 87580.6312 | 5.65 | 5.65 | 8.095 | 21.68% | 21.68% | 37.01% | 70.2 | 70.2 | 55.3955 | 25 | 178
4559100% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 9498.0894 | 87945.9424 | 5.65 | 5.65 | 8.0833 | 21.68% | 21.68% | 36.9% | 70.2 | 70.2 | 55.4782 | 26 | 179
4559200% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 9863.4005 | 88311.2535 | 5.65 | 5.65 | 8.0718 | 21.68% | 21.68% | 36.79% | 70.2 | 70.2 | 55.56 | 27 | 180
4559300% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 10228.7116 | 88676.5646 | 5.65 | 5.65 | 8.0603 | 21.68% | 21.68% | 36.69% | 70.2 | 70.2 | 55.6409 | 28 | 181
4559400% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 10594.0227 | 89041.8757 | 5.65 | 5.65 | 8.0489 | 21.68% | 21.68% | 36.58% | 70.2 | 70.2 | 55.7209 | 29 | 182
4559500% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 10959.3339 | 89407.1869 | 5.65 | 5.65 | 8.0377 | 21.68% | 21.68% | 36.48% | 70.2 | 70.2 | 55.8 | 30 | 183
4559600% | 2025 | 2024 | 2022-10-01 | 31 | 365.3111 | 11324.645 | 89772.498 | 5.65 | 5.65 | 8.0265 | 21.68% | 21.68% | 36.38% | 70.2 | 70.2 | 55.8783 | 31 | 184
4559700% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 407.7133 | 90180.2113 | 5.59 | 5.59 | 8.0152 | 24.2% | 24.2% | 36.3% | 70.2 | 70.2 | 55.9557 | 1 | 185
4559800% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 815.4266 | 90587.9246 | 5.59 | 5.59 | 8.0039 | 24.2% | 24.2% | 36.22% | 70.2 | 70.2 | 56.0323 | 2 | 186
4559900% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 1223.1399 | 90995.6379 | 5.59 | 5.59 | 7.9928 | 24.2% | 24.2% | 36.14% | 70.2 | 70.2 | 56.108 | 3 | 187
4560000% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 1630.8532 | 91403.3512 | 5.59 | 5.59 | 7.9818 | 24.2% | 24.2% | 36.06% | 70.2 | 70.2 | 56.183 | 4 | 188
4560100% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 2038.5665 | 91811.0645 | 5.59 | 5.59 | 7.9709 | 24.2% | 24.2% | 35.98% | 70.2 | 70.2 | 56.2571 | 5 | 189
4560200% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 2446.2798 | 92218.7778 | 5.59 | 5.59 | 7.96 | 24.2% | 24.2% | 35.9% | 70.2 | 70.2 | 56.3305 | 6 | 190
4560300% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 2853.9931 | 92626.4911 | 5.59 | 5.59 | 7.9493 | 24.2% | 24.2% | 35.83% | 70.2 | 70.2 | 56.4031 | 7 | 191
4560400% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 3261.7064 | 93034.2044 | 5.59 | 5.59 | 7.9387 | 24.2% | 24.2% | 35.75% | 70.2 | 70.2 | 56.475 | 8 | 192
4560500% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 3669.4197 | 93441.9177 | 5.59 | 5.59 | 7.9282 | 24.2% | 24.2% | 35.68% | 70.2 | 70.2 | 56.5461 | 9 | 193
4560600% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 4077.133 | 93849.631 | 5.59 | 5.59 | 7.9177 | 24.2% | 24.2% | 35.6% | 70.2 | 70.2 | 56.6165 | 10 | 194
4560700% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 4484.8463 | 94257.3443 | 5.59 | 5.59 | 7.9074 | 24.2% | 24.2% | 35.53% | 70.2 | 70.2 | 56.6862 | 11 | 195
4560800% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 4892.5596 | 94665.0576 | 5.59 | 5.59 | 7.8971 | 24.2% | 24.2% | 35.46% | 70.2 | 70.2 | 56.7551 | 12 | 196
4560900% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 5300.2729 | 95072.7709 | 5.59 | 5.59 | 7.887 | 24.2% | 24.2% | 35.39% | 70.2 | 70.2 | 56.8234 | 13 | 197
4561000% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 5707.9862 | 95480.4842 | 5.59 | 5.59 | 7.8769 | 24.2% | 24.2% | 35.32% | 70.2 | 70.2 | 56.8909 | 14 | 198
4561100% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 6115.6995 | 95888.1975 | 5.59 | 5.59 | 7.8669 | 24.2% | 24.2% | 35.25% | 70.2 | 70.2 | 56.9578 | 15 | 199
4561200% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 6523.4128 | 96295.9108 | 5.59 | 5.59 | 7.857 | 24.2% | 24.2% | 35.18% | 70.2 | 70.2 | 57.024 | 16 | 200
4561300% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 6931.1261 | 96703.6241 | 5.59 | 5.59 | 7.8472 | 24.2% | 24.2% | 35.11% | 70.2 | 70.2 | 57.0896 | 17 | 201
4561400% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 7338.8394 | 97111.3374 | 5.59 | 5.59 | 7.8375 | 24.2% | 24.2% | 35.05% | 70.2 | 70.2 | 57.1545 | 18 | 202
4561500% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 7746.5527 | 97519.0507 | 5.59 | 5.59 | 7.8278 | 24.2% | 24.2% | 34.98% | 70.2 | 70.2 | 57.2187 | 19 | 203
4561600% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 8154.266 | 97926.764 | 5.59 | 5.59 | 7.8182 | 24.2% | 24.2% | 34.92% | 70.2 | 70.2 | 57.2824 | 20 | 204
4561700% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 8561.9793 | 98334.4773 | 5.59 | 5.59 | 7.8088 | 24.2% | 24.2% | 34.85% | 70.2 | 70.2 | 57.3454 | 21 | 205
4561800% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 8969.6926 | 98742.1906 | 5.59 | 5.59 | 7.7994 | 24.2% | 24.2% | 34.79% | 70.2 | 70.2 | 57.4078 | 22 | 206
4561900% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 9377.4059 | 99149.9039 | 5.59 | 5.59 | 7.79 | 24.2% | 24.2% | 34.73% | 70.2 | 70.2 | 57.4696 | 23 | 207
4562000% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 9785.1192 | 99557.6172 | 5.59 | 5.59 | 7.7808 | 24.2% | 24.2% | 34.67% | 70.2 | 70.2 | 57.5308 | 24 | 208
4562100% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 10192.8325 | 99965.3305 | 5.59 | 5.59 | 7.7716 | 24.2% | 24.2% | 34.6% | 70.2 | 70.2 | 57.5914 | 25 | 209
4562200% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 10600.5458 | 100373.0438 | 5.59 | 5.59 | 7.7625 | 24.2% | 24.2% | 34.54% | 70.2 | 70.2 | 57.6514 | 26 | 210
4562300% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 11008.2591 | 100780.7571 | 5.59 | 5.59 | 7.7535 | 24.2% | 24.2% | 34.48% | 70.2 | 70.2 | 57.7109 | 27 | 211
4562400% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 11415.9724 | 101188.4704 | 5.59 | 5.59 | 7.7446 | 24.2% | 24.2% | 34.43% | 70.2 | 70.2 | 57.7698 | 28 | 212
4562500% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 11823.6857 | 101596.1837 | 5.59 | 5.59 | 7.7357 | 24.2% | 24.2% | 34.37% | 70.2 | 70.2 | 57.8282 | 29 | 213
4562600% | 2025 | 2024 | 2022-11-01 | 30 | 407.7133 | 12231.399 | 102003.897 | 5.59 | 5.59 | 7.7269 | 24.2% | 24.2% | 34.31% | 70.2 | 70.2 | 57.886 | 30 | 214
4562700% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 577.322 | 102581.219 | 6.99 | 6.99 | 7.7239 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 57.9433 | 1 | 215
4562800% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 1154.6441 | 103158.5411 | 6.99 | 6.99 | 7.7209 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58 | 2 | 216
4562900% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 1731.9661 | 103735.8631 | 6.99 | 6.99 | 7.718 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.0562 | 3 | 217
4563000% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 2309.2881 | 104313.1851 | 6.99 | 6.99 | 7.715 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.1119 | 4 | 218
4563100% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 2886.6102 | 104890.5072 | 6.99 | 6.99 | 7.7121 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.1671 | 5 | 219
4563200% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 3463.9322 | 105467.8292 | 6.99 | 6.99 | 7.7092 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.2218 | 6 | 220
4563300% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 4041.2542 | 106045.1512 | 6.99 | 6.99 | 7.7064 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.276 | 7 | 221
4563400% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 4618.5763 | 106622.4733 | 6.99 | 6.99 | 7.7035 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.3297 | 8 | 222
4563500% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 5195.8983 | 107199.7953 | 6.99 | 6.99 | 7.7007 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.383 | 9 | 223
4563600% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 5773.2203 | 107777.1173 | 6.99 | 6.99 | 7.6979 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.4357 | 10 | 224
4563700% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 6350.5424 | 108354.4394 | 6.99 | 6.99 | 7.6951 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.488 | 11 | 225
4563800% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 6927.8644 | 108931.7614 | 6.99 | 6.99 | 7.6924 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.5398 | 12 | 226
4563900% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 7505.1864 | 109509.0834 | 6.99 | 6.99 | 7.6896 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.5912 | 13 | 227
4564000% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 8082.5085 | 110086.4055 | 6.99 | 6.99 | 7.6869 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.6421 | 14 | 228
4564100% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 8659.8305 | 110663.7275 | 6.99 | 6.99 | 7.6842 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.6926 | 15 | 229
4564200% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 9237.1525 | 111241.0495 | 6.99 | 6.99 | 7.6816 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.7426 | 16 | 230
4564300% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 9814.4745 | 111818.3715 | 6.99 | 6.99 | 7.6789 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.7922 | 17 | 231
4564400% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 10391.7966 | 112395.6936 | 6.99 | 6.99 | 7.6763 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.8414 | 18 | 232
4564500% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 10969.1186 | 112973.0156 | 6.99 | 6.99 | 7.6737 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.8901 | 19 | 233
4564600% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 11546.4406 | 113550.3376 | 6.99 | 6.99 | 7.6711 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.9385 | 20 | 234
4564700% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 12123.7627 | 114127.6597 | 6.99 | 6.99 | 7.6685 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 58.9864 | 21 | 235
4564800% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 12701.0847 | 114704.9817 | 6.99 | 6.99 | 7.666 | 34.27% | 34.27% | 34.31% | 70.2 | 70.2 | 59.0339 | 22 | 236
4564900% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 13278.4067 | 115282.3037 | 6.99 | 6.99 | 7.6634 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.081 | 23 | 237
4565000% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 13855.7288 | 115859.6258 | 6.99 | 6.99 | 7.6609 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.1277 | 24 | 238
4565100% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 14433.0508 | 116436.9478 | 6.99 | 6.99 | 7.6584 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.1741 | 25 | 239
4565200% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 15010.3728 | 117014.2698 | 6.99 | 6.99 | 7.656 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.22 | 26 | 240
4565300% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 15587.6949 | 117591.5919 | 6.99 | 6.99 | 7.6535 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.2656 | 27 | 241
4565400% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 16165.0169 | 118168.9139 | 6.99 | 6.99 | 7.6511 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.3107 | 28 | 242
4565500% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 16742.3389 | 118746.2359 | 6.99 | 6.99 | 7.6486 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.3556 | 29 | 243
4565600% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 17319.661 | 119323.558 | 6.99 | 6.99 | 7.6462 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.4 | 30 | 244
4565700% | 2025 | 2024 | 2022-12-01 | 31 | 577.322 | 17896.983 | 119900.88 | 6.99 | 6.99 | 7.6439 | 34.27% | 34.27% | 34.3% | 70.2 | 70.2 | 59.4441 | 31 | 245
4565800% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 616.4625 | 120517.3425 | 6.74 | 6.74 | 7.6406 | 36.59% | 36.59% | 34.31% | 70.2 | 70.2 | 59.4878 | 1 | 246
4565900% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 1232.925 | 121133.805 | 6.74 | 6.74 | 7.6373 | 36.59% | 36.59% | 34.33% | 70.2 | 70.2 | 59.5312 | 2 | 247
4566000% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 1849.3875 | 121750.2675 | 6.74 | 6.74 | 7.6341 | 36.59% | 36.59% | 34.34% | 70.2 | 70.2 | 59.5742 | 3 | 248
4566100% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 2465.8501 | 122366.7301 | 6.74 | 6.74 | 7.6309 | 36.59% | 36.59% | 34.35% | 70.2 | 70.2 | 59.6169 | 4 | 249
4566200% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 3082.3126 | 122983.1926 | 6.74 | 6.74 | 7.6277 | 36.59% | 36.59% | 34.36% | 70.2 | 70.2 | 59.6592 | 5 | 250
4566300% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 3698.7751 | 123599.6551 | 6.74 | 6.74 | 7.6246 | 36.59% | 36.59% | 34.37% | 70.2 | 70.2 | 59.7012 | 6 | 251
4566400% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 4315.2376 | 124216.1176 | 6.74 | 6.74 | 7.6214 | 36.59% | 36.59% | 34.38% | 70.2 | 70.2 | 59.7429 | 7 | 252
4566500% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 4931.7001 | 124832.5801 | 6.74 | 6.74 | 7.6183 | 36.59% | 36.59% | 34.39% | 70.2 | 70.2 | 59.7842 | 8 | 253
4566600% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 5548.1626 | 125449.0426 | 6.74 | 6.74 | 7.6152 | 36.59% | 36.59% | 34.4% | 70.2 | 70.2 | 59.8252 | 9 | 254
4566700% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 6164.6252 | 126065.5052 | 6.74 | 6.74 | 7.6121 | 36.59% | 36.59% | 34.41% | 70.2 | 70.2 | 59.8659 | 10 | 255
4566800% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 6781.0877 | 126681.9677 | 6.74 | 6.74 | 7.6091 | 36.59% | 36.59% | 34.42% | 70.2 | 70.2 | 59.9063 | 11 | 256
4566900% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 7397.5502 | 127298.4302 | 6.74 | 6.74 | 7.6061 | 36.59% | 36.59% | 34.43% | 70.2 | 70.2 | 59.9463 | 12 | 257
4567000% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 8014.0127 | 127914.8927 | 6.74 | 6.74 | 7.6031 | 36.59% | 36.59% | 34.44% | 70.2 | 70.2 | 59.986 | 13 | 258
4567100% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 8630.4752 | 128531.3552 | 6.74 | 6.74 | 7.6001 | 36.59% | 36.59% | 34.45% | 70.2 | 70.2 | 60.0255 | 14 | 259
4567200% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 9246.9377 | 129147.8177 | 6.74 | 6.74 | 7.5971 | 36.59% | 36.59% | 34.46% | 70.2 | 70.2 | 60.0646 | 15 | 260
4567300% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 9863.4003 | 129764.2803 | 6.74 | 6.74 | 7.5942 | 36.59% | 36.59% | 34.47% | 70.2 | 70.2 | 60.1034 | 16 | 261
4567400% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 10479.8628 | 130380.7428 | 6.74 | 6.74 | 7.5912 | 36.59% | 36.59% | 34.48% | 70.2 | 70.2 | 60.142 | 17 | 262
4567500% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 11096.3253 | 130997.2053 | 6.74 | 6.74 | 7.5883 | 36.59% | 36.59% | 34.49% | 70.2 | 70.2 | 60.1802 | 18 | 263
4567600% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 11712.7878 | 131613.6678 | 6.74 | 6.74 | 7.5854 | 36.59% | 36.59% | 34.5% | 70.2 | 70.2 | 60.2182 | 19 | 264
4567700% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 12329.2503 | 132230.1303 | 6.74 | 6.74 | 7.5826 | 36.59% | 36.59% | 34.5% | 70.2 | 70.2 | 60.2558 | 20 | 265
4567800% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 12945.7128 | 132846.5928 | 6.74 | 6.74 | 7.5797 | 36.59% | 36.59% | 34.51% | 70.2 | 70.2 | 60.2932 | 21 | 266
4567900% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 13562.1754 | 133463.0554 | 6.74 | 6.74 | 7.5769 | 36.59% | 36.59% | 34.52% | 70.2 | 70.2 | 60.3303 | 22 | 267
4568000% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 14178.6379 | 134079.5179 | 6.74 | 6.74 | 7.5741 | 36.59% | 36.59% | 34.53% | 70.2 | 70.2 | 60.3672 | 23 | 268
4568100% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 14795.1004 | 134695.9804 | 6.74 | 6.74 | 7.5713 | 36.59% | 36.59% | 34.54% | 70.2 | 70.2 | 60.4037 | 24 | 269
4568200% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 15411.5629 | 135312.4429 | 6.74 | 6.74 | 7.5685 | 36.59% | 36.59% | 34.55% | 70.2 | 70.2 | 60.44 | 25 | 270
4568300% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 16028.0254 | 135928.9054 | 6.74 | 6.74 | 7.5658 | 36.59% | 36.59% | 34.56% | 70.2 | 70.2 | 60.476 | 26 | 271
4568400% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 16644.4879 | 136545.3679 | 6.74 | 6.74 | 7.563 | 36.59% | 36.59% | 34.57% | 70.2 | 70.2 | 60.5118 | 27 | 272
4568500% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 17260.9505 | 137161.8305 | 6.74 | 6.74 | 7.5603 | 36.59% | 36.59% | 34.58% | 70.2 | 70.2 | 60.5473 | 28 | 273
4568600% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 17877.413 | 137778.293 | 6.74 | 6.74 | 7.5576 | 36.59% | 36.59% | 34.58% | 70.2 | 70.2 | 60.5825 | 29 | 274
4568700% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 18493.8755 | 138394.7555 | 6.74 | 6.74 | 7.555 | 36.59% | 36.59% | 34.59% | 70.2 | 70.2 | 60.6175 | 30 | 275
4568800% | 2025 | 2025 | 2023-01-01 | 31 | 616.4625 | 19110.338 | 139011.218 | 6.74 | 6.74 | 7.5523 | 36.59% | 36.59% | 34.6% | 70.2 | 70.2 | 60.6522 | 31 | 276
4568900% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 525.1347 | 139536.3527 | 7.3 | 7.3 | 7.5515 | 31.17% | 31.17% | 34.59% | 70.2 | 70.2 | 60.6866 | 1 | 277
4569000% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 1050.2694 | 140061.4874 | 7.3 | 7.3 | 7.5506 | 31.17% | 31.17% | 34.57% | 70.2 | 70.2 | 60.7209 | 2 | 278
4569100% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 1575.4041 | 140586.6221 | 7.3 | 7.3 | 7.5498 | 31.17% | 31.17% | 34.56% | 70.2 | 70.2 | 60.7548 | 3 | 279
4569200% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 2100.5389 | 141111.7569 | 7.3 | 7.3 | 7.549 | 31.17% | 31.17% | 34.54% | 70.2 | 70.2 | 60.7886 | 4 | 280
4569300% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 2625.6736 | 141636.8916 | 7.3 | 7.3 | 7.5482 | 31.17% | 31.17% | 34.53% | 70.2 | 70.2 | 60.8221 | 5 | 281
4569400% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 3150.8083 | 142162.0263 | 7.3 | 7.3 | 7.5474 | 31.17% | 31.17% | 34.52% | 70.2 | 70.2 | 60.8553 | 6 | 282
4569500% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 3675.943 | 142687.161 | 7.3 | 7.3 | 7.5466 | 31.17% | 31.17% | 34.5% | 70.2 | 70.2 | 60.8883 | 7 | 283
4569600% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 4201.0777 | 143212.2957 | 7.3 | 7.3 | 7.5459 | 31.17% | 31.17% | 34.49% | 70.2 | 70.2 | 60.9211 | 8 | 284
4569700% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 4726.2124 | 143737.4304 | 7.3 | 7.3 | 7.5451 | 31.17% | 31.17% | 34.48% | 70.2 | 70.2 | 60.9537 | 9 | 285
4569800% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 5251.3471 | 144262.5651 | 7.3 | 7.3 | 7.5443 | 31.17% | 31.17% | 34.46% | 70.2 | 70.2 | 60.986 | 10 | 286
4569900% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 5776.4819 | 144787.6999 | 7.3 | 7.3 | 7.5435 | 31.17% | 31.17% | 34.45% | 70.2 | 70.2 | 61.0181 | 11 | 287
4570000% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 6301.6166 | 145312.8346 | 7.3 | 7.3 | 7.5428 | 31.17% | 31.17% | 34.44% | 70.2 | 70.2 | 61.05 | 12 | 288
4570100% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 6826.7513 | 145837.9693 | 7.3 | 7.3 | 7.542 | 31.17% | 31.17% | 34.42% | 70.2 | 70.2 | 61.0817 | 13 | 289
4570200% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 7351.886 | 146363.104 | 7.3 | 7.3 | 7.5412 | 31.17% | 31.17% | 34.41% | 70.2 | 70.2 | 61.1131 | 14 | 290
4570300% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 7877.0207 | 146888.2387 | 7.3 | 7.3 | 7.5405 | 31.17% | 31.17% | 34.4% | 70.2 | 70.2 | 61.1443 | 15 | 291
4570400% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 8402.1554 | 147413.3734 | 7.3 | 7.3 | 7.5398 | 31.17% | 31.17% | 34.38% | 70.2 | 70.2 | 61.1753 | 16 | 292
4570500% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 8927.2901 | 147938.5081 | 7.3 | 7.3 | 7.539 | 31.17% | 31.17% | 34.37% | 70.2 | 70.2 | 61.2061 | 17 | 293
4570600% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 9452.4249 | 148463.6429 | 7.3 | 7.3 | 7.5383 | 31.17% | 31.17% | 34.36% | 70.2 | 70.2 | 61.2367 | 18 | 294
4570700% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 9977.5596 | 148988.7776 | 7.3 | 7.3 | 7.5375 | 31.17% | 31.17% | 34.35% | 70.2 | 70.2 | 61.2671 | 19 | 295
4570800% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 10502.6943 | 149513.9123 | 7.3 | 7.3 | 7.5368 | 31.17% | 31.17% | 34.34% | 70.2 | 70.2 | 61.2973 | 20 | 296
4570900% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 11027.829 | 150039.047 | 7.3 | 7.3 | 7.5361 | 31.17% | 31.17% | 34.32% | 70.2 | 70.2 | 61.3273 | 21 | 297
4571000% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 11552.9637 | 150564.1817 | 7.3 | 7.3 | 7.5354 | 31.17% | 31.17% | 34.31% | 70.2 | 70.2 | 61.357 | 22 | 298
4571100% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 12078.0984 | 151089.3164 | 7.3 | 7.3 | 7.5347 | 31.17% | 31.17% | 34.3% | 70.2 | 70.2 | 61.3866 | 23 | 299
4571200% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 12603.2331 | 151614.4511 | 7.3 | 7.3 | 7.5339 | 31.17% | 31.17% | 34.29% | 70.2 | 70.2 | 61.416 | 24 | 300
4571300% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 13128.3679 | 152139.5859 | 7.3 | 7.3 | 7.5332 | 31.17% | 31.17% | 34.27% | 70.2 | 70.2 | 61.4452 | 25 | 301
4571400% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 13653.5026 | 152664.7206 | 7.3 | 7.3 | 7.5325 | 31.17% | 31.17% | 34.26% | 70.2 | 70.2 | 61.4742 | 26 | 302
4571500% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 14178.6373 | 153189.8553 | 7.3 | 7.3 | 7.5318 | 31.17% | 31.17% | 34.25% | 70.2 | 70.2 | 61.503 | 27 | 303
4571600% | 2025 | 2025 | 2023-02-01 | 28 | 525.1347 | 14703.772 | 153714.99 | 7.3 | 7.3 | 7.5311 | 31.17% | 31.17% | 34.24% | 70.2 | 70.2 | 61.5316 | 28 | 304
4571700% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 632.771 | 154347.761 | 7.28 | 7.28 | 7.5304 | 37.56% | 37.56% | 34.25% | 70.2 | 70.2 | 61.56 | 1 | 305
4571800% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 1265.5421 | 154980.5321 | 7.28 | 7.28 | 7.5296 | 37.56% | 37.56% | 34.26% | 70.2 | 70.2 | 61.5882 | 2 | 306
4571900% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 1898.3131 | 155613.3031 | 7.28 | 7.28 | 7.5289 | 37.56% | 37.56% | 34.28% | 70.2 | 70.2 | 61.6163 | 3 | 307
4572000% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 2531.0841 | 156246.0741 | 7.28 | 7.28 | 7.5282 | 37.56% | 37.56% | 34.29% | 70.2 | 70.2 | 61.6442 | 4 | 308
4572100% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 3163.8552 | 156878.8452 | 7.28 | 7.28 | 7.5274 | 37.56% | 37.56% | 34.3% | 70.2 | 70.2 | 61.6718 | 5 | 309
4572200% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 3796.6262 | 157511.6162 | 7.28 | 7.28 | 7.5267 | 37.56% | 37.56% | 34.31% | 70.2 | 70.2 | 61.6994 | 6 | 310
4572300% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 4429.3972 | 158144.3872 | 7.28 | 7.28 | 7.526 | 37.56% | 37.56% | 34.32% | 70.2 | 70.2 | 61.7267 | 7 | 311
4572400% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 5062.1683 | 158777.1583 | 7.28 | 7.28 | 7.5253 | 37.56% | 37.56% | 34.34% | 70.2 | 70.2 | 61.7538 | 8 | 312
4572500% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 5694.9393 | 159409.9293 | 7.28 | 7.28 | 7.5245 | 37.56% | 37.56% | 34.35% | 70.2 | 70.2 | 61.7808 | 9 | 313
4572600% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 6327.7103 | 160042.7003 | 7.28 | 7.28 | 7.5238 | 37.56% | 37.56% | 34.36% | 70.2 | 70.2 | 61.8076 | 10 | 314
4572700% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 6960.4814 | 160675.4714 | 7.28 | 7.28 | 7.5231 | 37.56% | 37.56% | 34.37% | 70.2 | 70.2 | 61.8343 | 11 | 315
4572800% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 7593.2524 | 161308.2424 | 7.28 | 7.28 | 7.5224 | 37.56% | 37.56% | 34.38% | 70.2 | 70.2 | 61.8608 | 12 | 316
4572900% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 8226.0234 | 161941.0134 | 7.28 | 7.28 | 7.5217 | 37.56% | 37.56% | 34.39% | 70.2 | 70.2 | 61.8871 | 13 | 317
4573000% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 8858.7945 | 162573.7845 | 7.28 | 7.28 | 7.521 | 37.56% | 37.56% | 34.41% | 70.2 | 70.2 | 61.9132 | 14 | 318
4573100% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 9491.5655 | 163206.5555 | 7.28 | 7.28 | 7.5203 | 37.56% | 37.56% | 34.42% | 70.2 | 70.2 | 61.9392 | 15 | 319
4573200% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 10124.3365 | 163839.3265 | 7.28 | 7.28 | 7.5197 | 37.56% | 37.56% | 34.43% | 70.2 | 70.2 | 61.965 | 16 | 320
4573300% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 10757.1075 | 164472.0975 | 7.28 | 7.28 | 7.519 | 37.56% | 37.56% | 34.44% | 70.2 | 70.2 | 61.9907 | 17 | 321
4573400% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 11389.8786 | 165104.8686 | 7.28 | 7.28 | 7.5183 | 37.56% | 37.56% | 34.45% | 70.2 | 70.2 | 62.0161 | 18 | 322
4573500% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 12022.6496 | 165737.6396 | 7.28 | 7.28 | 7.5176 | 37.56% | 37.56% | 34.46% | 70.2 | 70.2 | 62.0415 | 19 | 323
4573600% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 12655.4206 | 166370.4106 | 7.28 | 7.28 | 7.5169 | 37.56% | 37.56% | 34.47% | 70.2 | 70.2 | 62.0667 | 20 | 324
4573700% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 13288.1917 | 167003.1817 | 7.28 | 7.28 | 7.5163 | 37.56% | 37.56% | 34.48% | 70.2 | 70.2 | 62.0917 | 21 | 325
4573800% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 13920.9627 | 167635.9527 | 7.28 | 7.28 | 7.5156 | 37.56% | 37.56% | 34.49% | 70.2 | 70.2 | 62.1166 | 22 | 326
4573900% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 14553.7337 | 168268.7237 | 7.28 | 7.28 | 7.515 | 37.56% | 37.56% | 34.5% | 70.2 | 70.2 | 62.1413 | 23 | 327
4574000% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 15186.5048 | 168901.4948 | 7.28 | 7.28 | 7.5143 | 37.56% | 37.56% | 34.51% | 70.2 | 70.2 | 62.1659 | 24 | 328
4574100% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 15819.2758 | 169534.2658 | 7.28 | 7.28 | 7.5136 | 37.56% | 37.56% | 34.52% | 70.2 | 70.2 | 62.1903 | 25 | 329
4574200% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 16452.0468 | 170167.0368 | 7.28 | 7.28 | 7.513 | 37.56% | 37.56% | 34.53% | 70.2 | 70.2 | 62.2145 | 26 | 330
4574300% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 17084.8179 | 170799.8079 | 7.28 | 7.28 | 7.5124 | 37.56% | 37.56% | 34.55% | 70.2 | 70.2 | 62.2387 | 27 | 331
4574400% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 17717.5889 | 171432.5789 | 7.28 | 7.28 | 7.5117 | 37.56% | 37.56% | 34.56% | 70.2 | 70.2 | 62.2627 | 28 | 332
4574500% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 18350.3599 | 172065.3499 | 7.28 | 7.28 | 7.5111 | 37.56% | 37.56% | 34.57% | 70.2 | 70.2 | 62.2865 | 29 | 333
4574600% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 18983.131 | 172698.121 | 7.28 | 7.28 | 7.5104 | 37.56% | 37.56% | 34.58% | 70.2 | 70.2 | 62.3102 | 30 | 334
4574700% | 2025 | 2025 | 2023-03-01 | 31 | 632.771 | 19615.902 | 173330.892 | 7.28 | 7.28 | 7.5098 | 37.56% | 37.56% | 34.59% | 70.2 | 70.2 | 62.3337 | 31 | 335
Formulas:
Month = [Date]-DAY([Date])+1
Days = DAY(EOMONTH(Modelling[[#This Row],[Date]],0))

## Basic Data (hidden)
[16 empty] | No. | Senvion Control | No._1 | Senvion Control M | Type | Brakg. Prg. | Alarm | Auto Reset | Avail. grp. | System
| Generator | Consumer | Capacity | % Plant Equiva. Weightage | Feeder | TX | USS | MY |  |  |  | Fault Category |  |  | Breakdown description | 0 | System OK | 0 | System OK | Info | 0 |  | 20 | 32
O2_01 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_01 |  | Total Capacity | 70.2 | Open | WTG | IG | EG | Auto reset | 10 | Negative power, too little wind | 240 | Awaiting wind | Info | 50 |  | 10 | 5
O2_02 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_02 |  |  | 43 | Close | WTG Unscheduled Maintenance | IG Unscheduled Maintenance | EG Unscheduled Maintenance | Break down | 11 | Negative power, too little wind with icing | -- | -- | Info | 50 |  | 10 | 6
O2_03 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_03 |  |  |  |  | WTG Breakdown Maintenance | IG Breakdown Maintenance | EG Breakdown Maintenance | ROW issue | 16 | Timeout start for icing | -- | -- | Info | 50 |  | 20 | 6
O2_04 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_04 |  |  |  |  | WTG Scheduled Maintenance | IG Scheduled Maintenance | EG Scheduled Maintenance | Road issue | 20 | Manual stop - on site | 13 | Manual stop | Info | 60 |  | 30 | 9
O2_05 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_05 |  |  |  |  | WTG Environmental | IG Force Majeure | EG Force Majeure | Major BD | 21 | Manual stop - remote | 11 | Stop via communica. | Info | 60 |  | 0 | 30
O2_06 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_06 |  |  |  |  | WTG Force Majeure |  |  | Ladder issue | 25 | Manual stop without login | -- | -- | Info | 60 | X | 30 | 9
O2_07 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_07 | [7 empty] | Project pending work | 28 | WTG stop | -- | -- | Info | 52 |  | 20 | 9
O2_08 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_08 | [7 empty] | Schedule WTG PM | 30 | Wind sector stop | -- | -- | Info | 52 |  | 20 | 5
O2_09 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_09 | [7 empty] | WTR | 45 | Limiting wind speed exceeded | -- | -- | Info | 0 |  | 20 | 27
O2_10 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_10 | [7 empty] | Connectivity issue | 46 | Max. wind dir. deviation high wind sp. | -- | -- | Error | 52 |  | 20 | 5 | Nacelle
O2_11 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_11 | [7 empty] | Others | 47 | Max. windspeed BP50 | -- | -- | Info | 52 |  | 20 | 5
O2_12 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_12 | [7 empty] | Environment | 50 | Night operation | 1541 | Night operation | Info | 52 |  | 20 | 2
O2_13 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_13 | [7 empty] | Blade cleaning work | 53 | Wind dir.dev. level 1 | -- | -- | Error | 52 |  | 20 | 5 | Nacelle
O2_14 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_14 | [7 empty] | Load Shedding | 54 | WTG shutdown - pitch angle & stormp. Ignored | -- | -- | Info | 180 | X | 20 | 1
O2_15 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_15 | [7 empty] | Customer | 55 | WTG shut down | 1754 | WTG shutdown | Info | 52 |  | 20 | 1
O2_16 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_16 | [8 empty] | 57 | Reduced power active | -- | -- | Info | 0 |  | 20 | 32
O2_17 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_17 | [8 empty] | 58 | Wind dir.dev. level 2 | -- | -- | Error | 52 |  | 20 | 5 | Nacelle
O2_18 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_18 | [8 empty] | 59 | Max. acceleration | -- | -- | Warning | 0 | X | 20 | 28
O2_19 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_19 | [8 empty] | 60 | Wind > power | 203 | Wind > power | Error | 52 | X | 0 | 15 | Wind Sensor
O2_20 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F1 | TX1 | O2_20 | [8 empty] | 61 | Wind < power | 202 | Wind < power | Error | 52 | X | 0 | 15 | Wind Sensor
O2_21 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_21 | [8 empty] | 62 | Extreme gust | 213 | Extreme gust | Info | 20 |  | 30 | 28
O2_22 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_22 | [8 empty] | 64 | Max. wind speed | 250 | Wind > max. | Info | 52 |  | 20 | 5
O2_23 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_23 | [8 empty] | 65 | Absence of wind during run-up | 204 | Free wheel->cut in G | Info | 50 |  | 20 | 28
O2_24 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_24 | [8 empty] | 70 | Icing (nacelle ice sensor) | 206 | Ice warning | Info | 0 |  | 30 | 28
O2_25 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_25 | [8 empty] | 71 | Outdoor temperature low | 200 | Outdoor temp. low | Info | 52 |  | 30 | 6
O2_26 | TQGXIIPL | GEDA | 2.7 | 3.846% | Wind_F2 | TX1 | O2_26 | [8 empty] | 72 | Outdoor temperature high | 201 | Outdoor temp. high | Info | 52 |  | 30 | 6
[16 empty] | 75 | Reduced power gearbox | 27 | Reduced power | Warning | 0 |  | 20 | 27
[16 empty] | 76 | Reduced power generator | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 77 | Reduced power transformer | 2024 | [P] reduced trafo | Warning | 0 | X | 20 | 27
[16 empty] | 81 | Outdoor temp. extremely low | -- | -- | Warning | 0 |  | 30 | 27
[16 empty] | 85 | Outdoor temp.>working range | 246 | -- | Info | 0 |  | 20 | 27
[16 empty] | 86 | 4-20mA outside temp. nacelle 1 | -- | -- | Error | 52 | X | 20 | 21 | Nacelle
[16 empty] | 87 | 4-20mA outside temp. nacelle 2 | -- | -- | Error | 52 | X | 20 | 21 | Nacelle
[16 empty] | 88 | Outs.temp. nacelle implaus. | -- | -- | Error | 52 | X | 20 | 21 | Nacelle
[16 empty] | 89 | Nacelle outs/inside temp. comp implausible | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 110 | Emergency stop top box | 16 | Emer.stop cont.panel | Info | 190 | X | 0 | 11
[16 empty] | 111 | Emergency stop nacelle | 92 | Emer. stop nacelle | Info | 190 | X | 0 | 11
[16 empty] | 115 | Emergency stop converter | 1404 | Freq.conv. emer.stop | Info | 190 | X | 0 | 12
[16 empty] | 117 | Emergency stop base box | 2150 | Emer. stop bottombox | Info | 190 | X | 0 | 12
[16 empty] | 120 | Conv. emergency stop 2 | -- | -- | Info | 190 | X | 0 | 12
Wind_F1 | TQGXIIPL | GEDA | 35.1 | 50% | [11 empty] | 121 | Emer.stop tower base | -- | -- | Info | 190 | X | 0 | 12
Wind_F2 | TQGXIIPL | GEDA | 35.1 | 50% | [11 empty] | 151 | SLC app. not running | -- | -- | Info | 52 |  | 20 | 15
O2_01 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 152 | SLC app. not in SAFE mode | -- | -- | Error | 52 | X | 20 | 15 | Safety System
O2_02 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 153 | SLC SF max. cable winding | -- | -- | Error | 75 | X | 0 | 15 | Safety System
O2_03 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 154 | SLC SF generator temperature | -- | -- | Error | 75 | X | 0 | 15 | Safety System
O2_04 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 156 | SLC SF overspeed | -- | -- | Error | 190 | X | 0 | 15 | Safety System
O2_05 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 157 | SLC SF max. tower oscillation | -- | -- | Error | 180 | X | 0 | 15 | Safety System
O2_06 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 158 | SLC SF max. rotor brake pad temp. | -- | -- | Error | 75 | X | 0 | 15 | Safety System
O2_07 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 159 | SLC SF emergency stop | -- | -- | Error | 190 | X | 0 | 15 | Safety System
O2_08 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 170 | SLC MF brake request HC | -- | -- | Error | 170 | X | 20 | 15 | Safety System
O2_09 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 171 | SLC MF converter grid disconnection | -- | -- | Error | 75 | X | 20 | 15 | Converter system
O2_10 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 172 | SLC MF torque protection | -- | -- | Error | 75 | X | 20 | 15 | Safety System
O2_11 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 173 | SLC MF max. tower oscillation analog | -- | -- | Error | 75 | X | 20 | 15 | Safety System
O2_12 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 175 | SLC error | -- | -- | Error | 60 | X | 0 | 15 | Safety System
O2_13 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 176 | SLC warning | -- | -- | Warning | 0 | X | 0 | 27
O2_14 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 177 | SLC MF blade regulation control | -- | -- | Error | 180 | X | 0 | 15 | Safety System
O2_15 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 178 | SLC MF safe operation speed limit | -- | -- | Error | 75 | X | 20 | 15 | Safety System
O2_16 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 181 | SLC implaus. speed | -- | -- | Error | 52 | X | 0 | 15 | Safety System
O2_17 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 182 | SLC interface error | -- | -- | Error | 52 | X | 0 | 15 | Safety System
O2_18 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 183 | SLC run-time limit active | -- | -- | Info | 0 | X | 20 | 28
O2_19 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 200 | Release manual pitch | 7 | Turbine is serviced | Info | 60 |  | 20 | 9
O2_20 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 201 | Manual pitch active | -- | -- | Info | 180 |  | 20 | 9
O2_21 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 205 | Pitch service mode | -- | -- | Info | 60 |  | 20 | 9
O2_22 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 210 | Manual brake | 451 | Manual brake | Info | 60 |  | 20 | 9
O2_23 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 220 | Sound characteristic A active | 2174 | Noise reduct.1 start | Info | 0 |  | 20 | 28
O2_24 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 221 | Sound characteristic C active | -- | -- | Info | 0 |  | 20 | 28
O2_25 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 225 | Sound characteristic B active | 2176 | Noise reduct.2 start | Info | 0 |  | 20 | 28
O2_26 | TQGXIIPL | GEDA | 2.7 | 3.846% | [11 empty] | 226 | Sound characteristic D active | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 228 | Noise reduction stop | -- | -- | Info | 52 |  | 20 | 2
[16 empty] | 229 | Bat protection active | -- | -- | Info | 52 |  | 20 | 28
[16 empty] | 245 | Parameterized P red. | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 246 | Parameterized speed red. | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 248 | Red. op. soft cut out | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 249 | Soft cut out par. implausible | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 250 | Update active | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 251 | Stop for man./aut. reboot | -- | -- | Info | 60 |  | 20 | 28
[16 empty] | 252 | Update failed | -- | -- | Warning | 0 |  | 20 | 28
[16 empty] | 253 | Manual reboot | -- | -- | Info | 60 |  | 20 | 28
[16 empty] | 254 | Man. shutdown error | -- | -- | Error | 60 |  | 0 | 28
TX1 | TQGXIIPL | GEDA | 70 | 100% | [11 empty] | 305 | Brake control | 424 | Brake control | Error | 52 | X | 0 | 23
Line1 | TQGXIIPL | GEDA | 70 | 100% | [11 empty] | 308 | Max. braking time BP20 | -- | -- | Error | 75 | X | 0 | 18
[16 empty] | 310 | Max. braking time BP50 | 431 | B50 brake time > max | Error | 180 | X | 0 | 18
[16 empty] | 320 | Max. braking time BP52 | 495 | B52 brake time>max. | Error | 180 | X | 0 | 18
[16 empty] | 325 | Max. braking time BP60 | 494 | B60 brake time>max. | Error | 180 | X | 0 | 18
[16 empty] | 330 | Max. braking time BP75 | 448 | B75 brake time > max | Error | 180 | X | 0 | 18
[16 empty] | 331 | Parameter setting BP75 implausible | -- | -- | Error | 52 | X | 20 | 15
[16 empty] | 332 | Max. braking time BP170 | 1824 | B170 brake time >max. | Error | 190 | X | 0 | 18
[16 empty] | 335 | Max. braking time BP180 | 490 | B180 brake time>max. | Error | 190 | X | 0 | 18
[16 empty] | 340 | Max. braking time BP190 | 491 | B190 brake time>max. | Error | 190 | X | 0 | 18
[16 empty] | 360 | Timeout systemtest 1 | 1540 | T.out selftest no. 1 | Error | 52 | X | 0 | 21
[16 empty] | 365 | Timeout systemtest 2 | -- | -- | Error | 52 | X | 0 | 21
[16 empty] | 370 | Timeout systemtest 3 | -- | -- | Error | 52 | X | 0 | 21
[16 empty] | 400 | Manual operation | 26 | Manual operation | Info | 0 |  | 0 | 27
[16 empty] | 402 | Semi-automatic operation | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 403 | PMU active power semi-aut. op. | -- | -- | Info | 0 |  | 20 | 32
[16 empty] | 404 | PMU react. power semi-aut. op. | -- | -- | Info | 0 |  | 20 | 32
[16 empty] | 405 | Stop manual operation | -- | -- | Info | 52 |  | 20 | 9
[16 empty] | 412 | Test brake program 190 | -- | -- | Info | 190 |  | 0 | 9
[16 empty] | 414 | Test brake program 180 | -- | -- | Info | 180 |  | 0 | 9
[16 empty] | 415 | Test brake program 170 | -- | -- | Info | 170 |  | 0 | 9
[16 empty] | 416 | Test brake program 75 | -- | -- | Info | 75 |  | 0 | 9
[16 empty] | 418 | Test brake program 60 | -- | -- | Info | 60 |  | 0 | 9
[16 empty] | 420 | Test brake program 52 | -- | -- | Info | 52 |  | 0 | 9
[16 empty] | 422 | Test brake program 50 | -- | -- | Info | 50 |  | 0 | 9
[16 empty] | 424 | Test brake program 20 | -- | -- | Info | 20 |  | 30 | 27
[16 empty] | 430 | No-load rotation active | -- | -- | Info | 75 |  | 20 | 28
[16 empty] | 435 | No speed development | -- | -- | Error | 180 | X | 0 | 15
[16 empty] | 440 | Repeating error BP 0 | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 455 | Repeating error BP52 | -- | -- | Error | 52 | X | 0 | 25
[16 empty] | 460 | Repeating error BP60 | -- | -- | Error | 60 | X | 0 | 25
[16 empty] | 465 | Repeating error BP75 | -- | -- | Error | 75 | X | 0 | 25
[16 empty] | 468 | Repeating error BP170 | -- | -- | Error | 170 | X | 0 | 25
[16 empty] | 470 | Repeating error BP180 | -- | -- | Error | 180 | X | 0 | 25
[16 empty] | 475 | Repeating error BP190 | -- | -- | Error | 190 | X | 0 | 25
[16 empty] | 513 | Timeout bridging limit switches | -- | -- | Error | 52 | X | 0 | 18
[16 empty] | 515 | Pitch limit switches | 1130 | Pitch endstop switch | Error | 52 | X | 0 | 18 | Pitch system
[16 empty] | 516 | Pitch limit switch 1 | 1906 | Pitch endstop 1 | Error | 52 | X | 0 | 18 | Pitch system
[16 empty] | 517 | Pitch limit switch 2 | 1908 | Pitch endstop 2 | Error | 52 | X | 0 | 18 | Pitch system
[16 empty] | 518 | Pitch limit switch 3 | 1909 | Pitch endstop 3 | Error | 52 | X | 0 | 18 | Pitch system
[16 empty] | 520 | Overload axis 1 | 1150 | Pitch 1 current>max | Error | 52 | X | 0 | 18
[16 empty] | 525 | Overload axis 2 | 1151 | Pitch 2 current>max | Error | 52 | X | 0 | 18
[16 empty] | 530 | Overload axis 3 | 1152 | Pitch 3 current>max | Error | 52 | X | 0 | 18
[16 empty] | 550 | Pitch current asymmetry | 1156 | Pitch(M)current asym | Error | 52 | X | 0 | 18 | Pitch system
[16 empty] | 551 | Pitch motor current too high | -- | -- | Error | 52 | X | 0 | 18 | Pitch system
[16 empty] | 553 | Blade pitch deviation test | -- | -- | Error | 52 |  | 10 | 18 | Pitch system
[16 empty] | 555 | Pitch angle deviation | 1113 | Pitch angle diff. | Error | 52 |  | 10 | 18 | Pitch system
[16 empty] | 556 | Pitch deviation BP170 | -- | -- | Error | 52 | X | 0 | 18 | Pitch system
[16 empty] | 558 | Pitch deviation Pitch Back | -- | -- | Error | 52 | X | 0 | 18 | Pitch system
[16 empty] | 563 | Pitch too fast during fast pitch back | -- | -- | Error | 52 | X | 0 | 18 | Pitch system
[16 empty] | 564 | Bladeangle implausible | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[16 empty] | 565 | Max. windspeed bladeangle | 258 | Pitch angle>max.wind | Error | 52 |  | 30 | 5 | Pitch system
[16 empty] | 566 | Pitch too slow BP50 | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[16 empty] | 567 | Pitch too slow BP52 | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[16 empty] | 568 | Pitch too slow BP60 | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[16 empty] | 569 | Pitch too slow BP75 | -- | -- | Error | 170 | X | 0 | 18 | Pitch system
[16 empty] | 570 | Pitch too slow BP180 | -- | -- | Error | 190 | X | 0 | 18 | Pitch system
[16 empty] | 574 | Pitch too slow BP190 | -- | -- | Error | 190 | X | 0 | 18 | Pitch system
[16 empty] | 576 | Pitch too slow BP170 | -- | -- | Error | 190 | X | 0 | 18 | Pitch system
[16 empty] | 577 | Pitch too fast BP170 | -- | -- | Error | 52 | X | 0 | 18 | Pitch system
[16 empty] | 578 | Pitch set point slow hold time BP75 | -- | -- | Error | 75 | X | 0 | 16 | Pitch system
[16 empty] | 579 | Pitch too fast BP75 | -- | -- | Error | 75 | X | 0 | 18 | Pitch system
[16 empty] | 581 | Set point><actual value axis 1 | 1922 | Pitch setp.<>meas. 1 | Error | 180 | X | 0 | 18 | Pitch system
[16 empty] | 582 | Set point><actual value axis 2 | 1923 | Pitch setp.<>meas. 2 | Error | 180 | X | 0 | 18 | Pitch system
[16 empty] | 583 | Set point><actual value axis 3 | 1924 | Pitch setp.<>meas. 3 | Error | 180 | X | 0 | 18 | Pitch system
[16 empty] | 586 | Dev. single pitch angle targ. | -- | -- | Error | 170 |  | 20 | 16 | Pitch system
[16 empty] | 588 | Target >< act. coll. pitch angle | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[16 empty] | 589 | Targ. pitch angle coll. dev. | -- | -- | Error | 52 |  | 20 | 16 | Pitch system
[16 empty] | 592 | Great deviation blade pitches | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[16 empty] | 594 | Blade pitch check running | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 600 | Max. temp. motor axis 1 | 1147 | Pitch motor temp. 1 | Error | 52 |  | 30 | 18 | Pitch system
[16 empty] | 605 | Max. temp. motor axis 2 | 1148 | Pitch motor temp. 2 | Error | 52 |  | 30 | 18 | Pitch system
[16 empty] | 610 | Max. temp. motor axis 3 | 1149 | Pitch motor temp. 3 | Error | 52 |  | 30 | 18 | Pitch system
[16 empty] | 628 | Max. temp. pitch motor PTC | 1199 | Pitch(M) sub2 temp. | Error | 52 |  | 20 | 18 | Pitch system
[16 empty] | 630 | Overload fan pitch motor | 1173 | Th.rel.pitch(M) fan | Error | 52 | X | 20 | 18 | Pitch system
[16 empty] | 641 | Sim.angle E enc. <> act.angle 1 | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[16 empty] | 642 | Sim.angle E enc. <> act.angle 2 | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[16 empty] | 643 | Sim.angle E enc. <> act.angle 3 | -- | -- | Error | 180 | X | 0 | 18 | Pitch system
[16 empty] | 644 | Sim.angle D <> E enc. | -- | -- | Info | 0 |  | 0 | 27
[16 empty] | 650 | Pitch controller communication error | 1157 | Pitch ctrl.communic. | Error | 180 |  | 10 | 18 | Pitch Control system
[16 empty] | 652 | Pitch controller initialisation error | -- | -- | Error | 180 |  | 10 | 18 | Pitch Control system
[16 empty] | 653 | Blade load sensors comm.failure | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 654 | Blade load sensors firmware error | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 656 | Error pitch converter 1 | 1910 | Pitch ctrl. error 1 | Error | 180 | X | 20 | 18 | Pitch Control system
[16 empty] | 657 | Error pitch converter 2 | 1911 | Pitch ctrl. error 2 | Error | 180 | X | 20 | 18 | Pitch Control system
[16 empty] | 658 | Error pitch converter 3 | 1912 | Pitch ctrl. error 3 | Error | 180 | X | 20 | 18 | Pitch Control system
[16 empty] | 660 | Limit switches error 91° | 1159 | Pitch <> endstop | Error | 190 | X | 0 | 18 | Pitch Control system
[16 empty] | 664 | Pitch system temperature low | -- | -- | Info | 52 |  | 20 | 6
[16 empty] | 665 | Pitch error | 1161 | Pitch error | Error | 52 | X | 20 | 18 | Pitch Control system
[16 empty] | 666 | Pitch box temp. too low | -- | -- | Error | 52 | X | 20 | 18 | Pitch Control system
[16 empty] | 667 | Pitch box temp. implaus. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 668 | Battery boxes overtemp. | -- | -- | Error | 52 | X | 0 | 18 | Pitch Battery system
[16 empty] | 669 | Battery boxes heating sys. fault | -- | -- | Error | 52 | X | 20 | 18 | Pitch Battery system
[16 empty] | 670 | Max. pitch speed encoder A | 1163 | Pitch motor rpm high | Error | 180 | X | 0 | 18 | Pitch Control system
[16 empty] | 672 | Max. pitch speed encoder B | -- | -- | Error | 180 | X | 0 | 18 | Pitch Control system
[16 empty] | 675 | Pitch measuring system 1><2 | 1166 | Pitchmeas.sys. 1<>2 | Error | 180 | X | 0 | 21 | Pitch Control system
[16 empty] | 679 | Pitch system temperature high | -- | -- | Error | 52 | X | 20 | 18 | Pitch Control system
[16 empty] | 681 | Limit switch error 95° axis 1 | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 682 | Limit switch error 95° axis 2 | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 683 | Limit switch error 95° axis 3 | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 687 | Power failure pitch | 1931 | No grid in hub | Error | 75 | X | 20 | 24 | Pitch Battery system
[16 empty] | 691 | Targ. pitch angle implaus. | -- | -- | Error | 170 | X | 0 | 16 | Pitch Control system
[16 empty] | 693 | Coll. pitch targ.rate exceed. | -- | -- | Error | 170 | X | 0 | 16 | Pitch Control system
[16 empty] | 694 | Sel. pitch targ.rate exceed. | -- | -- | Error | 170 | X | 0 | 16 | Pitch Control system
[16 empty] | 695 | Hub temperature high | 1198 | Hub is too hot | Error | 52 |  | 30 | 22 | Pitch system
[16 empty] | 696 | Indiv. setp.pitch ang. offset incorr. | -- | -- | Error | 52 | X | 0 | 16 | Pitch system
[16 empty] | 697 | Timeout B sensor active | -- | -- | Info | 0 |  | 0 | 27
[16 empty] | 700 | Batt. undervoltage/overvoltage | 57 | Batt. voltage stop | Error | 52 | X | 0 | 18 | Pitch Battery system
[16 empty] | 707 | Stop battery test | 2408 | Battery Check | Info | 52 |  | 10 | 28
[16 empty] | 710 | Battery test | 95 | Battery test | Info | 180 |  | 10 | 28
[16 empty] | 711 | Battery monitoring axis 1 | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 712 | Battery monitoring axis 2 | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 713 | Battery monitoring axis 3 | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 714 | Battery monitoring test interval | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 715 | Charging circuit pitch | 1175 | Pitch bat. charger | Error | 52 | X | 0 | 18 | Pitch Battery system
[16 empty] | 716 | Battery charge cycle axis 1 error | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 717 | Battery charge cycle axis 2 error | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 718 | Battery charge cycle axis 3 error | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 740 | Pitch back trigger by HC | -- | -- | Error | 170 |  | 20 | 18 | Pitch Battery system
[16 empty] | 741 | Battery drive trigger by HC | -- | -- | Error | 180 |  | 20 | 18 | Pitch Battery system
[16 empty] | 775 | Pitch heating mode | -- | -- | Info | 60 |  | 20 | 6
[16 empty] | 776 | Timeout pitch heating mode | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 780 | Error bridging start-up | -- | -- | Error | 52 | X | 0 | 18 | Pitch Battery system
[16 empty] | 785 | Error brake resistor CHP | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 786 | Signal bridging start-up + CHP | -- | -- | Warning | 0 |  | 0 | 27
[16 empty] | 806 | High rotor speed hub | -- | -- | Error | 75 | X | 30 | 14
[16 empty] | 811 | Maximum rotor speed hub | -- | -- | Error | 190 | X | 0 | 14
[16 empty] | 821 | Rotor rotation direction hub | -- | -- | Info | 52 |  | 20 | 15
[16 empty] | 825 | Rotor speed hub<>gear.sp. | -- | -- | Error | 52 |  | 20 | 21
[16 empty] | 826 | Rotor speed hub<<>>gear.sp. | -- | -- | Error | 52 |  | 20 | 21
[16 empty] | 829 | Rotor speed SLC<>gear.sp. | -- | -- | Error | 52 |  | 20 | 21
[16 empty] | 830 | Calc. rotor position implausible | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 831 | Rotor position diff. | -- | -- | Error | 52 | X | 0 | 21
[16 empty] | 835 | Check determ. of rotor position | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 836 | Rotor pos. change not plausible | -- | -- | Error | 52 | X | 0 | 21
[16 empty] | 850 | Error lubrication pump pitch | 1932 | Hub lubrication | Warning | 0 |  | 20 | 27
[16 empty] | 855 | Stop after blade bear.lubr.dr. BP50 | -- | -- | Info | 50 |  | 20 | 28
[16 empty] | 856 | Stop after blade bear.lubr.dr. 90° | -- | -- | Info | 52 |  | 20 | 28
[16 empty] | 857 | Blade bear.lubr.dr. timeout | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 858 | Blade bear.lubr. failure | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 871 | Light icing (rotor bl. ice sensor) | -- | -- | Info | 0 |  | 30 | 28
[16 empty] | 872 | Icing (Rotor bl. ice sensor) | -- | -- | Info | 0 |  | 30 | 28
[16 empty] | 873 | Icing (rotor bl. ice sens. no eval.) | -- | -- | Info | 0 |  | 30 | 28
[16 empty] | 874 | Rotor blade ice sensor error | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 875 | Rot.bl. ice sens. com. err. | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 876 | Rot.bl. ice s. eval. not pos. | -- | -- | Info | 0 |  | 30 | 27
[16 empty] | 877 | Rot.bl. ice sens. not ready | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 878 | Rotor blade ice sensor bypass active | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 960 | Blade load sensors not RFO | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 961 | Blade load sensors zero offset indiv. Error | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 962 | Blade load sensors gain error | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 963 | Blade load sensors homog. error | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 964 | Blade load sensors strain diff. high | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 965 | Blade load sensors implaus.meas.val. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 967 | Blade load sensors signal check | -- | -- | Warning | 0 |  | 20 | 28
[16 empty] | 968 | Blade load sensors signal check error | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 969 | Rotor blade load sensor back-up mode | -- | -- | Warning | 0 |  | 20 | 28
[16 empty] | 970 | Alarm - cont. blade load sensors back-up mode | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 971 | Stop - blade load sensors back-up mode | -- | -- | Info | 52 |  | 20 | 15
[16 empty] | 972 | Blade load sensors no signal activity | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 973 | Check blade bend.mom. | -- | -- | Info | 75 | X | 20 | 15
[16 empty] | 974 | Blade load sensors zero offset error | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1001 | Drive train oscillation Z level 0 | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 1005 | Drive train oscillation Z level 1 | 1558 | WP4084#2 CH1 level 1 | Error | 52 | X | 20 | 15
[16 empty] | 1015 | Drive train oscillation Z level 2 | 1564 | WP4084#2 CH1 level 2 | Error | 52 | X | 0 | 15
[16 empty] | 1050 | Drivetrain oscillations | -- | -- | Warning | 0 |  | 10 | 27
[16 empty] | 1055 | Max. drivetrain oscillations | -- | -- | Error | 52 | X | 0 | 25
[16 empty] | 1065 | Drive train monitor level 1 | -- | -- | Info | 52 |  | 20 | 15
[16 empty] | 1070 | Drive train monitor level 2 | -- | -- | Info | 52 |  | 20 | 15
[16 empty] | 1125 | 4-20mA drive train acceleration Z | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 1130 | Acceleration detector drivetrain | -- | -- | Error | 52 | X | 0 | 21
[16 empty] | 1150 | CMS drive train system error | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1151 | CMS drive train meas. val. ev. | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 1160 | Comm.err. IEC client -> CMS drive tr. | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 1161 | Comm.err. IEC server <- CMS drive tr. | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 1200 | High temp. rotorbearing | 1713 | (R) bearing temp. | Warning | 0 |  | 30 | 27
[16 empty] | 1210 | Max. temp. rotorbearing | 1714 | (R) bear. temp. stop | Error | 52 | X | 0 | 22
[16 empty] | 1215 | 4-20mA rotor bear. temp. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1216 | 4-20mA rotor bear. temp. timeout | -- | -- | Error | 52 | X | 0 | 21
[16 empty] | 1311 | Rotor bearing lubrication pump 1 overload | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1312 | Rotor bearing lubrication pump 2 overload | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1313 | Rotor bear. lubr.cont. 1 empty | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1314 | Rotor bear. lubr.cont. 2 empty | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1316 | Timeout fault rotor bear. lubr. | -- | -- | Error | 52 | X | 20 | 23
[16 empty] | 1319 | Rotor bearing lubrication failure | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1320 | Rotor bearing lubric. man.op. | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 1321 | Max. time rotor bear.lubr. 1 | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1322 | Max. time rotor bear.lubr. 2 | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1405 | Rotor locked: Stop | 1585 | Rotor locked | Info | 60 | X | 0 | 9
[16 empty] | 1407 | Rotor lock - wind too strong | -- | -- | Info | 60 | X | 0 | 9
[16 empty] | 1408 | Rotor lock 1 on | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 1409 | Rotor lock 2 on | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 1410 | Rotor lock - no storm position | -- | -- | Info | 190 | X | 0 | 9
[16 empty] | 1500 | High gearbox oil pressure | 1337 | Gear oil press. high | Error | 52 | X | 0 | 23
[16 empty] | 1510 | Low gearbox oil pressure | 1306 | Gear oil press. low | Error | 52 | X | 0 | 23
[16 empty] | 1520 | 4-20mA press. gearbox pump | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 1525 | 4-20mA press. gearbox inlet | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 1530 | Error measuring pressure inlet gear | -- | -- | Warning | 0 |  | 10 | 27
[16 empty] | 1548 | Missing gear oil (low rpm) | -- | -- | Error | 52 | X | 20 | 23
[16 empty] | 1550 | Missing gear oil (high rpm) | 1355 | Missing gear oil | Error | 52 | X | 20 | 23
[16 empty] | 1552 | Gearbox warm-up stage | 2315 | -- | Info | 0 |  | 20 | 28
[16 empty] | 1555 | Gear heating enabled | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 1557 | Gearbox warmed up idling | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 1558 | Timeout gearoil heating routine Active | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 1560 | Manual operation fan gear | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 1565 | Manual operation gear heating | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 1570 | Manual operation gear oil pump | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 1600 | High gear speed | 310 | Gear overspeed | Error | 75 | X | 30 | 14
[16 empty] | 1610 | Maximum gear speed | 328 | Gear overspeed max. | Error | 190 | X | 0 | 14
[16 empty] | 1625 | Implausible gear speed leap | -- | -- | Error | 52 |  | 20 | 21
[16 empty] | 1630 | Disc filter adaption implausible | -- | -- | Error | 52 | X | 0 | 21
[16 empty] | 1680 | Gearb.sp. SLC <> gearb.sp. | -- | -- | Error | 52 |  | 20 | 21
[16 empty] | 1685 | Gear ratio param. implaus. | -- | -- | Error | 52 | X | 20 | 15
[16 empty] | 1700 | High temp. gear bearing 1 | 1323 | Gear bearing temp. 1 | Warning | 0 |  | 20 | 27
[16 empty] | 1705 | Max. temp. gear bearing 1 | 1324 | Gear bear.temp.1stop | Error | 52 | X | 0 | 22
[16 empty] | 1707 | PT100 gear bearing 1 defect | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 1708 | Error measuring temp. gear bearing 1 | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 1710 | High temp. gear bearing 2 | 1325 | Gear bearing temp. 2 | Warning | 0 |  | 20 | 27
[16 empty] | 1715 | Max. temp. gear bearing 2 | 1326 | Gear bear.temp.2stop | Error | 52 | X | 0 | 22
[16 empty] | 1717 | PT100 gear bearing 2 defect | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 1718 | Error measuring temp. gear bearing 2 | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 1720 | Max. oilsump temperature | 1327 | Gear oil temp. high | Error | 52 | X | 20 | 22
[16 empty] | 1723 | Oilsump temperature high | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1725 | Low gear oil temperature | 1328 | Gear oil temp. low | Info | 52 | X | 30 | 6
[16 empty] | 1727 | PT100 gear oil sump defect | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 1728 | Error measuring temp. gear oil sump | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 1729 | PT100 inlet gear defect | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1731 | Oil temperature gearbox input high | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 1732 | Max. oil temperature gearbox input | -- | -- | Error | 52 | X | 0 | 22
[16 empty] | 1738 | Error measuring temp. inlet gear | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1740 | High temp. gear bearing 3 | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 1745 | Max. temp. gear bearing 3 | -- | -- | Error | 52 | X | 0 | 22
[16 empty] | 1747 | PT100 gear bearing 3 defect | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 1748 | Error measuring temp. gear bearing 3 | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 1750 | High temp. gear bearing 4 | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 1755 | Max. temp. gear bearing 4 | -- | -- | Error | 52 | X | 0 | 22
[16 empty] | 1757 | PT100 gear bearing 4 defect | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 1758 | Error measuring temp. gear bearing 4 | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 1800 | Overload gear oil pump | 1332 | Gear oil(P)therm. | Error | 52 | X | 20 | 24
[16 empty] | 1810 | Overload gear heating | 920 | Gearheat.therm.relay | Warning | 0 | X | 20 | 27
[16 empty] | 1816 | Fault fan gear oil cooler 1 | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1818 | Overload fan 1 gear oil cooler | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1819 | Overload fan 2 gear oil cooler | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1822 | Fault fan gear oil cooler 2 | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1824 | Fault fan gear oil cooler 1+2 | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1860 | Oil filter gear choked | 1339 | Gear oil fil.1 chok. | Warning | 0 | X | 0 | 27
[16 empty] | 1870 | 4-20mA pressure diff. gear oil filter | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1880 | Error meas. press. diff. oil filter | -- | -- | Warning | 0 | X | 10 | 27
[16 empty] | 1920 | Particle sensor defect | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1922 | Particle Gear Alarm 10min | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 1924 | Particle Gear Alarm 24h | -- | -- | Error | 52 | X | 0 | 23
[16 empty] | 1926 | Particle Gear Alarm Total | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 2005 | Check brake | -- | -- | Error | 52 | X | 0 | 23
[16 empty] | 2007 | Brake pads warning | -- | -- | Warning | 0 | X | 30 | 27
[16 empty] | 2050 | Brake closed in operation | 1833 | Brake closed | Error | 170 | X | 0 | 23
[16 empty] | 2125 | Timeout brake closed | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 2150 | Impulse braking | -- | -- | Info | 52 | X | 20 | 28
[16 empty] | 2160 | Permanent braking | -- | -- | Info | 0 | X | 20 | 28
[16 empty] | 2170 | Additional braking | -- | -- | Info | 75 | X | 20 | 28
[16 empty] | 2200 | Max. braking energy exceeded | -- | -- | Error | 52 | X | 0 | 15
[16 empty] | 2340 | Temp. rot.br.pad implaus. | -- | -- | Error | 52 | X | 0 | 23
[16 empty] | 2350 | Disc brake cooling down | -- | -- | Info | 52 |  | 20 | 28
[16 empty] | 2355 | Temp. rot.br.pad high | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 2356 | Max rot.br.pad temp. exceed. | -- | -- | Info | 75 |  | 0 | 15
[16 empty] | 2357 | Dragging brake monitoring | -- | -- | Info | 75 |  | 20 | 15
[16 empty] | 2358 | Temp. rot.br.pad high timeout | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 2360 | Error measuring temp. rot.br.pad 1 | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2361 | PT100 rot.br.pad 1 defect | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2370 | Error measuring temp. rot.br.pad 2 | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2371 | PT100 rot.br.pad 2 defect | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2380 | 0-10V error volt.buffer rot.br. | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2390 | Brake due to sudden sys.failure | -- | -- | Error | 52 | X | 0 | 24
[16 empty] | 2515 | Implausible gen. speed leap | -- | -- | Error | 52 | X | 0 | 21
[16 empty] | 2520 | Gen.speed analog<>gear.speed | -- | -- | Error | 52 |  | 20 | 20
[16 empty] | 2521 | Gen.sp.analog <<>> gearb.sp. | -- | -- | Error | 52 |  | 20 | 21
[16 empty] | 2530 | Gen. power derating act. | -- | -- | Info | 0 |  | 20 | 32
[16 empty] | 2540 | Gen.speed pulse error | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2541 | Gen.speed voltage error | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2550 | Overload generator fan 1 | 918 | Fan(G)ext.term.relay | Warning | 0 | X | 20 | 27
[16 empty] | 2600 | High temp. gen. bearing 1 | 526 | (G) bearing 1 temp. | Warning | 0 |  | 30 | 27
[16 empty] | 2605 | Max. temp. gen. bearing 1 | 527 | (G)bear.1 temp. stop | Error | 52 | X | 0 | 22
[16 empty] | 2607 | PT100 gen. bearing 1 defect | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2608 | Error measuring temp. gen.bearing 1 | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2610 | High temp. gen. bearing 2 | 528 | (G) bearing 2 temp. | Warning | 0 |  | 30 | 27
[16 empty] | 2615 | Max. temp. gen. bearing 2 | 529 | (G)bear.2 temp. stop | Error | 52 | X | 0 | 22
[16 empty] | 2617 | PT100 gen. bearing 2 defect | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2618 | Error measuring temp. gen. bearing 2 | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2650 | Overload generator fan 2 | 936 | (G)fan 2.term. relay | Warning | 0 | X | 20 | 27
[16 empty] | 2655 | Overload generator fan 3 | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 2660 | Thermistor generator | 510 | Thermistor G1 stator | Error | 52 | X | 0 | 22
[16 empty] | 2662 | PT100 stator temp. 2 defect | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2663 | Error measuring temp. 2 stator | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2665 | High stator temperature | 513 | G1 stator temp. | Warning | 0 |  | 30 | 27
[16 empty] | 2666 | High stator temperature 2 | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 2670 | Max. temp. stator | 514 | G1 stator temp. stop | Error | 52 | X | 30 | 22
[16 empty] | 2671 | Max. temp. stator 2 | -- | -- | Error | 52 | X | 20 | 22
[16 empty] | 2672 | PT100 stator temp. defect | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2673 | Error measuring temp. stator | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2674 | Overload generator heating | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 2675 | Overload gen. heating: stop | -- | -- | Error | 52 | X | 20 | 24
[16 empty] | 2685 | Slipring cell temp. high | 2025 | (G) slipr.air temp | Warning | 0 |  | 20 | 27
[16 empty] | 2687 | Max. slip ring cell temp. | 2026 | (G) slipr.air stop | Error | 52 |  | 30 | 22
[16 empty] | 2689 | PT100 slipring temp. defect | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2691 | Error meas. slip ring temp. | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 2695 | P red. incr. gen. coolant temp. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 2696 | Gen. max. coolant temp. | -- | -- | Error | 52 | X | 20 | 22
[16 empty] | 2710 | Generator power too high | 530 | (G) power too high | Error | 52 | X | 20 | 20
[16 empty] | 2800 | Max. power peak | 550 | (G) peak power max. | Error | 52 | X | 0 | 24
[16 empty] | 2810 | Service generator brushes | 554 | (G)Brushes worn | Warning | 0 | X | 0 | 27
[16 empty] | 2811 | Fault generator brushes | -- | -- | Error | 52 | X | 0 | 20
[16 empty] | 2822 | Overload lubrication generator | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 2823 | Fault gen. bearing lubrication | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 2826 | Man. oper. gen. lubrication | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 2828 | Timeout fault gen. lubrication | -- | -- | Error | 52 | X | 20 | 23
[16 empty] | 2829 | Gen.lubr. self-protect. active | -- | -- | Info | 0 |  | 20 | 32
[16 empty] | 2831 | Max. time generator bear.lubr. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 2832 | Generator bearing lubr. Container empty | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 2900 | Manual operation generator heating | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 2910 | Manual operation generator fan 1 | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 2920 | Manual operation generator fan 2 | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 2930 | Manual operation generator fan 3 | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 2950 | Lightning protection defect | 602 | Lightning prot. def. | Warning | 0 |  | 0 | 27
[16 empty] | 3000 | Frequency converter not ready | 1401 | Freq.conv. not ready | Error | 75 |  | 10 | 20
[16 empty] | 3005 | Conv. fuse tripped | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3010 | Conv. comm.error | -- | -- | Error | 52 | X | 20 | 15
[16 empty] | 3011 | Conv. SDO transm.error | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 3020 | Chopper util. incr. | -- | -- | Warning | 0 |  | 20 | 28
[16 empty] | 3021 | Max. chopper util. | -- | -- | Error | 75 |  | 20 | 20
[16 empty] | 3030 | Conv. warning | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3040 | Conv reset after grid restoration | -- | -- | Info | 52 |  | 30 | 28
[16 empty] | 3050 | Freq. conv. speed window | 330 | Rpm <> window | Error | 52 |  | 10 | 20
[16 empty] | 3060 | Conv. emerg.off type A | -- | -- | Error | 75 | X | 20 | 20
[16 empty] | 3061 | Conv. emerg.off type B | -- | -- | Error | 75 | X | 20 | 20
[16 empty] | 3062 | Conv. emerg.off type C | -- | -- | Error | 75 | X | 20 | 20
[16 empty] | 3063 | Conv. emerg.off type D | -- | -- | Error | 75 | X | 20 | 20
[16 empty] | 3064 | Conv. emerg.off type E | -- | -- | Error | 75 | X | 20 | 20
[16 empty] | 3065 | Conv. emerg.off type F | -- | -- | Error | 75 | X | 20 | 20
[16 empty] | 3090 | Frequency converter spare protection | -- | -- | Error | 75 | X | 0 | 20
[16 empty] | 3095 | Error converter disconnection | -- | -- | Error | 75 | X | 0 | 20
[16 empty] | 3096 | Converter disconnection implausible | -- | -- | Error | 52 | X | 0 | 20
[16 empty] | 3097 | Max. negative active power | -- | -- | Error | 75 | X | 0 | 20
[16 empty] | 3110 | Frequency converter error | 1409 | Freq. conv. error | Error | 75 | X | 20 | 20
[16 empty] | 3120 | Frequency converter overspeed | 1411 | Freq.conv.overspeed | Error | 75 |  | 10 | 14
[16 empty] | 3121 | Conv. underspeed | -- | -- | Error | 75 |  | 10 | 14
[16 empty] | 3125 | Timeout ready for connection | 651 | Cut in 0_>G1 | Error | 52 |  | 10 | 24
[16 empty] | 3130 | Timeout grid synchronisation | 1415 | Freq.conv. <> sync. | Error | 52 |  | 10 | 20
[16 empty] | 3140 | Frequency converter operation range | 1416 | Freq.conv.<>workinga | Error | 52 |  | 10 | 20
[16 empty] | 3155 | Limit conv. output act.power | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 3160 | Cable overload | 1693 | Cable overload | Warning | 0 |  | 20 | 27
[16 empty] | 3161 | P reduction power cord overl. | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 3162 | Cable overload stop | 1694 | Cable overload stop | Error | 52 |  | 20 | 24
[16 empty] | 3164 | P reduction stator cable overl. | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 3200 | Frequency converter temp. low | 1602 | Freq.conv.temp.low | Info | 52 |  | 20 | 6
[16 empty] | 3201 | Bypass conv. heating mode | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 3202 | Timeout converter temp. low | -- | -- | Error | 52 | X | 0 | 6
[16 empty] | 3210 | Frequency converter load rejection | 1644 | Freq.conv.<>parallel | Error | 75 |  | 10 | 20
[16 empty] | 3211 | Conv. load shedding (CAN) | -- | -- | Error | 75 |  | 10 | 20
[16 empty] | 3220 | Reduced power converter | 1792 | [P] reduced conv. | Warning | 0 |  | 20 | 27
[16 empty] | 3222 | Timeout reduced power conv. | -- | -- | Error | 52 | X | 20 | 20
[16 empty] | 3225 | Limit reactive power converter | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3227 | Timeout Q limit converter | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 3250 | No power | 1688 | No power | Error | 52 |  | 20 | 20
[16 empty] | 3255 | Converter power too high | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3260 | Converter power too low | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3265 | Converter torque <> setpoint | 1686 | Converter<>setpoint | Warning | 0 |  | 20 | 27
[16 empty] | 3267 | Calculated torque implausible | -- | -- | Error | 52 | X | 0 | 16
[16 empty] | 3270 | Converter torque monitor level 0 | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 3271 | Converter torque monitor level 1 | -- | -- | Error | 75 |  | 20 | 15
[16 empty] | 3280 | Conv. COM mode active | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 3281 | Conv. COM mode stop | -- | -- | Info | 60 |  | 0 | 9
[16 empty] | 3350 | No pressure increase following pump start-up | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3351 | Timeout no pressure increase following pump start-up | -- | -- | Warning | 52 | X | 0 | 23
[16 empty] | 3355 | No temp. rise after heat.coolant on | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3356 | Pump cooling sys. (tower base) diff.press. Low | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3357 | Pump cooling sys. (tower base) diff.press. too low | -- | -- | Error | 52 | X | 0 | 23
[16 empty] | 3358 | Pump cooling sys. (tower base) diff.press. High | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3359 | Pump cooling sys. (tower base) diff.press. too high | -- | -- | Error | 52 | X | 0 | 23
[16 empty] | 3360 | Implaus. act. in conv.cooling system | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 3365 | Fan 1 cool.sys. error | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3366 | Fan 2 cool.sys. error | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3367 | Fan 3 cool.sys. error | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3368 | Fan 4 cool.sys. error | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3370 | Coolant press. low | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3371 | Coolant press. too low | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 3372 | Cool sys. press. switch tripped | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 3373 | Coolant press. high (with pump on) | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3374 | Coolant press. too high (with pump on) | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 3375 | Coolant press. high (with pump off) | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3376 | Coolant press. too high (with pump on) | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 3377 | 4-20mA coolant press. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 3378 | Pump coolant inlet press. 4-20mA | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 3380 | Coolant temp. high | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3381 | P red. incr. conv. coolant temp. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 3385 | Coolant temp. too high | -- | -- | Warning | 0 |  | 0 | 27
[16 empty] | 3386 | Conv. max. coolant temp. | -- | -- | Error | 52 | X | 20 | 22
[16 empty] | 3387 | 4-20mA coolant temp. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 3390 | Cool.sys. pump man.oper. | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 3391 | Heating coolant 1&2 man.oper. | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 3392 | Fans group 1&2 cool.sys.man.oper. | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 3393 | Heating fans 1-4 cool.sys.man.oper. | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 3395 | Pump cooling sys. overload | -- | -- | Error | 52 | X | 20 | 24
[16 empty] | 3396 | Coolant heating 1&2 overload | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 3397 | Heating overload fans 1- 4 cooling sys. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 3400 | UPS warning | 1762 | UPS Warning | Warning | 0 |  | 0 | 27
[16 empty] | 3410 | UPS error | -- | -- | Error | 52 | X | 0 | 24
[16 empty] | 3420 | UPS buffer time too short | -- | -- | Error | 52 | X | 0 | 24
[16 empty] | 3430 | UPS error | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3440 | UPS air conditioning faulty | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 3455 | Grid loss auxiliary power | -- | -- | Info | 75 | X | 20 | 4
[16 empty] | 3460 | Grid loss auxiliary power without grid loss net | -- | -- | Error | 52 | X | 20 | 24
[16 empty] | 3461 | Grid loss without grid loss auxiliary power | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 3500 | Grid loss | 102 | Phase drop | Info | 75 |  | 20 | 4
[16 empty] | 3501 | Grid disconnection for self-protection | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3502 | Timeout grid error | -- | -- | Error | 75 | X | 0 | 4
[16 empty] | 3503 | Zero-seq. syst. volt. high | -- | -- | Info | 52 |  | 20 | 4
[16 empty] | 3530 | High voltage - level 1 | 110 | Voltage high | Info | 75 |  | 20 | 4
[16 empty] | 3531 | High voltage - level 2 | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3532 | Min. voltage cut in | -- | -- | Info | 52 |  | 20 | 4
[16 empty] | 3533 | Max. voltage cut in | -- | -- | Info | 52 |  | 20 | 4
[16 empty] | 3534 | Repeat voltage dip | -- | -- | Info | 52 |  | 20 | 4
[16 empty] | 3535 | Low voltage - level 1 | 111 | Voltage low | Info | 75 |  | 20 | 4
[16 empty] | 3536 | Low voltage - level 2 | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3537 | Transient fault | 128 | Transient grid error | Info | 0 |  | 20 | 27
[16 empty] | 3540 | High frequency - level 1 | 120 | Frequency high | Info | 75 |  | 20 | 4
[16 empty] | 3541 | High frequency - level 2 | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3542 | Max. frequency cut in | -- | -- | Info | 52 |  | 20 | 4
[16 empty] | 3543 | High frequency - P reduction | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 3544 | Time limit high freq. - P red. | -- | -- | Info | 0 | X | 0 | 27
[16 empty] | 3545 | Low frequency - Level 1 | 121 | Frequency low | Info | 75 |  | 20 | 4
[16 empty] | 3546 | Low frequency - level 2 | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3547 | Overfrequency | 134 | Critical frequency | Info | 0 |  | 20 | 27
[16 empty] | 3550 | Phase angle | 130 | L1-L2-L3 12 | Info | 75 |  | 20 | 4
[16 empty] | 3551 | Phase angle | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3555 | Current asymmetry | 601 | Current asymmetry | Error | 52 | X | 10 | 20
[16 empty] | 3560 | Voltage asymmetry | -- | -- | Error | 52 | X | 10 | 4
[16 empty] | 3562 | Timeout max. freq. cut in | -- | -- | Info | 52 |  | 20 | 4
[16 empty] | 3570 | Grid error | 156 | Grid error | Info | 75 |  | 20 | 4
[16 empty] | 3571 | Low frequency - level 3 | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3572 | Low frequency - level 4 | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3573 | Low frequency - level 5 | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3574 | Low frequency - level 6 | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3575 | Minimum grid frequency | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3576 | Min. frequency cut in | -- | -- | Info | 52 |  | 20 | 4
[16 empty] | 3577 | Underfrequency | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 3581 | High frequency - level 3 | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3582 | High frequency - level 4 | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3583 | High frequency - level 5 | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3584 | High frequency - level 6 | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3585 | Maximum grid frequency | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 3586 | P reduction frequency prot. | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 3590 | Overvoltage | -- | -- | Info | 75 |  | 10 | 4
[16 empty] | 3591 | Transient voltage peak | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 3592 | Repeat transient voltage peak | -- | -- | Info | 52 |  | 20 | 4
[16 empty] | 3593 | Grid recovery | -- | -- | Info | 52 |  | 20 | 4
[16 empty] | 3594 | No Connection permission | -- | -- | Info | 52 |  | 20 | 4
[16 empty] | 3595 | Grid parameters implausible | -- | -- | Error | 52 |  | 20 | 16
[16 empty] | 3630 | VQ protection | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3632 | VQ protection stop | -- | -- | Error | 52 |  | 20 | 4
[16 empty] | 3640 | Dynamic frequency control | -- | -- | Info | 0 |  | 30 | 28
[16 empty] | 3642 | End additional power | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 3750 | Grid measurement error | -- | -- | Error | 52 |  | 30 | 24
[16 empty] | 3751 | Initialization grid meas. | -- | -- | Info | 52 |  | 20 | 28
[16 empty] | 3800 | Circuit breaker | 600 | Main switch off | Error | 75 | X | 30 | 20
[16 empty] | 3802 | MVS Trafo CB off | -- | -- | Info | 75 | X | 20 | 9
[16 empty] | 3803 | P reduction current limitation | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 3804 | MVS Trafo CB tripped | -- | -- | Error | 75 | X | 0 | 24
[16 empty] | 3805 | Max. transformer temp. | 2022 | Trafo temp.stop | Error | 52 | X | 20 | 22
[16 empty] | 3807 | MVS Trafo CB remote off | -- | -- | Info | 75 | X | 0 | 9
[16 empty] | 3809 | P reduction apparent power limitation | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 3810 | Medium voltage off | 2023 | Medium Voltage off | Error | 75 | X | 0 | 15
[16 empty] | 3812 | MVS Transf. Disc. off | -- | -- | Info | 75 | X | 0 | 9
[16 empty] | 3814 | MVS Transf. ES on | -- | -- | Info | 75 | X | 0 | 9
[16 empty] | 3836 | MSS Protection system error | -- | -- | Error | 52 | X | 0 | 24
[16 empty] | 3840 | SF6 boiler pressure too low | 1695 | SF6-Pressure low | Error | 52 | X | 0 | 24
[16 empty] | 3849 | Spare potection inactive | -- | -- | Error | 52 | X | 0 | 24
[16 empty] | 3866 | LV HRC fuses triggered | -- | -- | Error | 52 | X | 0 | 24
[16 empty] | 3869 | Lightning protect. transf. Defect | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 3892 | PT100 transf. int. defect. | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 3894 | Error meas. temp. transf.int. | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 3898 | Max. transformer temp. PT100 | -- | -- | Error | 52 |  | 20 | 22
[16 empty] | 3901 | Timeout max. transf. temp. | -- | -- | Error | 75 | X | 0 | 22
[16 empty] | 3904 | Max. temp. supply transformer | -- | -- | Error | 52 |  | 20 | 22
[16 empty] | 3907 | Max. temp. supply transf. grid disconn. | -- | -- | Error | 52 | X | 0 | 22
[16 empty] | 3912 | Transf. oil pressure too high | -- | -- | Error | 75 | X | 0 | 24
[16 empty] | 3914 | Transf. fill level too low | -- | -- | Error | 52 | X | 20 | 24
[16 empty] | 3942 | PT100 supply transformer def. | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 3943 | Error measuring PT100 supply transf. | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 3950 | Aux. power operation error | -- | -- | Error | 52 | X | 20 | 24
[16 empty] | 3954 | Max. overv. aux. power ctrl. | -- | -- | Error | 52 | X | 0 | 24
[16 empty] | 3960 | Max. temp. aux. transf. nacelle | -- | -- | Error | 52 |  | 20 | 22
[16 empty] | 3962 | PT100 aux. transformer nacelle def. | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 3963 | Error meas. nacelle aux. transf. | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 3970 | Transformer pump overload | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 3972 | Transf. pump thermist. tripped | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 3974 | Transf. pump man.oper. | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 4000 | High temperature nacelle | 30 | Nacelle temp. | Warning | 0 |  | 20 | 27
[16 empty] | 4020 | Max. temperature nacelle | 31 | Nacelle temp. stop | Error | 52 |  | 20 | 6
[16 empty] | 4024 | 4-20mA inside temp. nacelle | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 4061 | Rel. air hum. nacelle inside high (in operation) | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4062 | Rel. air hum. nacelle inside too high (in operation) | -- | -- | Error | 52 | X | 20 | 6
[16 empty] | 4072 | Rel. air hum. nacelle inside too high | -- | -- | Info | 52 |  | 20 | 6
[16 empty] | 4075 | 4-20mA rel. air humidity nacelle int. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 4086 | 4-20mA rel. air humidity tower base int. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 4091 | Rel. air hum. tower base inside high (in operation) | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4092 | Rel. air hum. tower base inside too high | -- | -- | Info | 52 |  | 20 | 6
[16 empty] | 4093 | Rel. air hum. tower base inside too high (in operation) | -- | -- | Error | 52 | X | 20 | 6
[16 empty] | 4100 | Vibration | 5 | Vibration | Error | 180 | X | 0 | 23
[16 empty] | 4150 | Vibration sensor error | -- | -- | Info | 52 |  | 0 | 13
[16 empty] | 4200 | Fault fire alarm system | -- | -- | Error | 52 | X | 20 | 15
[16 empty] | 4201 | Fire warning | 2231 | Smoke warning | Error | 52 | X | 0 | 15
[16 empty] | 4202 | Fire alarm | -- | -- | Error | 52 | X | 0 | 15
[16 empty] | 4203 | Fire shut down | 2232 | Smole stop | Error | 52 | X | 0 | 15
[16 empty] | 4204 | Service fire alarm system | -- | -- | Info | 0 | X | 20 | 28
[16 empty] | 4205 | Fire alarm system inactive | -- | -- | Error | 52 | X | 0 | 9
[16 empty] | 4210 | Smoke warning nacelle | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 4215 | Smoke warning nacelle stop | -- | -- | Error | 52 | X | 0 | 15
[16 empty] | 4220 | Smoke warning tower base | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 4225 | Smoke warning tow. base stop | -- | -- | Error | 52 | X | 0 | 15
[16 empty] | 4230 | Grid disc. smoke warning | -- | -- | Error | 75 | X | 0 | 15
[16 empty] | 4250 | Manual operation nacelle fan | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 4252 | Failure nacelle fan | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4253 | Overload nacelle fan | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 4255 | Dry mode nacelle | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 4260 | Manual operation rotor hub fan | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 4262 | Failure rotor hub fan | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4263 | Overload rotor hub fan | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 4270 | Manual operation cooling pump | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 4272 | Failure cooling pump | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4273 | Overload cooling pump | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 4275 | Pressure coolant nacelle high | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4276 | Pressure difference cooling pump (nacelle) low | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4277 | Coolant pump diff.press. (nacelle) too low | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 4278 | Coolant pump diff.press. (nacelle) high | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4279 | Coolant pump diff.press. (nacelle) too high | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 4280 | Error meas. pressure coolant nacelle | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4281 | Signal Pressure coolant nacelle disturbed | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4285 | Error meas. coolant press nacelle pump inlet | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4286 | Signal Pressure coolant nacelle pump inlet disturbed | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4290 | Error meas. temperature coolant nacelle cooler | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4291 | Signal Temperature coolant nacelle cooler disturbed | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4293 | Error meas. temperature coolant generator | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4294 | Signal Temperature coolant generator disturbed | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4296 | Error meas. temperature coolant gearbox | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4297 | Signal Temperature coolant gearbox disturbed | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4500 | Tower resonance | 205 | Tower resonance time | Info | 50 |  | 20 | 28
[16 empty] | 4502 | Nat. tower freq. implausible | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4503 | Nat. tower freq. calc. imp. | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 4510 | Tower oscillation Y level 1 | 1539 | WP4084#1 CH1 level 1 | Info | 52 |  | 20 | 15
[16 empty] | 4511 | Tower oscillation Y level 1 standst. | -- | -- | Info | 52 | X | 0 | 15
[16 empty] | 4520 | Tower oscillation X level 1 | 1555 | WP4084#1 CH2 level 1 | Info | 52 |  | 20 | 15
[16 empty] | 4521 | Tower oscillation X level 1 standst. | -- | -- | Info | 52 | X | 0 | 15
[16 empty] | 4530 | Tower oscillation Y level 2 | 1556 | WP4084#1 CH1 level 2 | Info | 52 |  | 20 | 15
[16 empty] | 4531 | Tower oscillation Y level 2 standst. | -- | -- | Info | 52 | X | 0 | 15
[16 empty] | 4535 | Tower oscillation Y level 3 | -- | -- | Error | 52 | X | 0 | 15
[16 empty] | 4540 | Tower oscillation X level 2 | 1557 | WP4084#1 CH2 level 2 | Info | 52 |  | 20 | 15
[16 empty] | 4541 | Tower oscillation X level 2 standst. | -- | -- | Info | 52 | X | 0 | 15
[16 empty] | 4545 | Tower oscillation X level 3 | -- | -- | Error | 52 | X | 0 | 15
[16 empty] | 4555 | Tower accel. difference | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 4565 | System fault accel. sensor 1 | -- | -- | Error | 52 | X | 0 | 21
[16 empty] | 4582 | Oscil.sensor 1: check firmware | -- | -- | Error | 52 |  | 0 | 21
[16 empty] | 4583 | Oscil.sensor 2: check firmware | -- | -- | Error | 52 |  | 0 | 21
[16 empty] | 4584 | Oscill. encoder tower (BP act.) | -- | -- | Error | 52 | X | 0 | 21
[16 empty] | 4585 | 4-20mA tower acceleration Y | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 4587 | 4-20mA tower acceleration X | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 4588 | Oscillation encoder tower | -- | -- | Error | 52 |  | 20 | 21
[16 empty] | 4589 | Oscillation encoder TwC | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 4600 | PT100 base box temp. defect | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 4603 | Base box temperature high | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4604 | Base box temperature low | -- | -- | Warning | 0 |  | 30 | 27
[16 empty] | 4605 | Error measuring temp. tower base box | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 4607 | Heating/fan base box faulty | -- | -- | Warning | 0 |  | 0 | 27
[16 empty] | 4608 | Tower distrib. cabinet def. | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4609 | Max. base box temp. | -- | -- | Error | 52 | X | 20 | 22
[16 empty] | 4611 | PT100 temp. tower base defective | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 4620 | Tower base temp. impermissible | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 4645 | 4-20mA tower accel. Y2 (TwC) | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 4647 | 4-20mA tower accel. X2 (TwC) | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 4700 | Failure tower fan | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 4710 | Manual operation tower fan | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 4720 | Tower fan overload | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 4730 | Drying mode tower base | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 4800 | Persons in the tower base | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 4810 | Tower door opened | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 4951 | Accel.sensor XF/YF comm.error | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4956 | Accel.sensor XF/YF system error | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 4960 | Tower oscillation YF | -- | -- | Info | 52 | X | 20 | 15
[16 empty] | 4970 | Tower oscillation XF | -- | -- | Info | 52 | X | 20 | 15
[16 empty] | 5000 | Breakdown obstacle light | 1561 | Flight warn.ligh.out | Warning | 0 | X | 20 | 27
[16 empty] | 5001 | Breakdown low intensity obstacle light | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 5020 | Failure visibility measuring | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 5025 | Error no. visibility meas. devices | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 5100 | Service obstacle light | 1569 | Flight warn.ligh.def | Warning | 0 | X | 0 | 27
[16 empty] | 5500 | High hydraulic pressure | 1223 | (H)sys. press. high | Error | 52 | X | 10 | 23 | Hydraulic system
[16 empty] | 5505 | High hydr. press. flush. mode | -- | -- | Warning | 0 |  | 0 | 27
[16 empty] | 5506 | Rot.br. press. high | -- | -- | Error | 52 | X | 20 | 23 | Hydraulic system
[16 empty] | 5507 | Max. rot.br. press. | -- | -- | Error | 52 | X | 20 | 23 | Hydraulic system
[16 empty] | 5510 | Low hydraulic pressure | 1224 | (H)sys. press. low | Error | 52 | X | 20 | 23 | Hydraulic system
[16 empty] | 5516 | Rot.br. press. low | -- | -- | Error | 52 | X | 20 | 23 | Hydraulic system
[16 empty] | 5517 | Drain valve (MVB) test fail | -- | -- | Error | 52 | X | 0 | 23 | Hydraulic system
[16 empty] | 5520 | 4-20mA hydraulic pressure | -- | -- | Error | 52 | X | 20 | 21 | Hydraulic system
[16 empty] | 5525 | 4-20mA rot.br. press. | -- | -- | Error | 52 | X | 20 | 21 | Hydraulic system
[16 empty] | 5550 | Low hydraulic oil level | 1201 | (H) oil level low | Error | 52 | X | 0 | 23 | Hydraulic system
[16 empty] | 5600 | Overload hydraulic pump | 1207 | (H)motor therm.relay | Error | 52 | X | 20 | 24 | Hydraulic system
[16 empty] | 5700 | Max. operation time hydraulic | 1213 | (H) oper.time > max. | Error | 52 | X | 0 | 23 | Hydraulic system
[16 empty] | 5710 | Min. operation time hydraulic | 1214 | (H) oper.time < min. | Error | 52 | X | 10 | 23 | Hydraulic system
[16 empty] | 5730 | Pressure drop hydraulic sys. | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 5750 | Manual operation hydraulic pump | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 5760 | Hydraulic oil flushing operation | -- | -- | Info | 52 |  | 20 | 28
[16 empty] | 5770 | Manual op. hydr. oil flushing | -- | -- | Info | 52 |  | 20 | 28
[16 empty] | 6000 | Overload electr. yaw brake | 747 | Yaw(B) therm. relay | Error | 52 | X | 20 | 24 | Yaw system
[16 empty] | 6007 | Overload yaw motors group 1 | -- | -- | Error | 52 | X | 20 | 24 | Yaw system
[16 empty] | 6012 | Overload yaw motors group 2 | -- | -- | Error | 52 | X | 20 | 24 | Yaw system
[16 empty] | 6039 | Max. time yaw bear.lubr. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 6040 | Overload yaw lubr. pump | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 6041 | Yaw bearing lubric. man.op. | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 6043 | Timeout fault yaw lubrication | -- | -- | Error | 52 | X | 20 | 23 | Yaw system
[16 empty] | 6046 | Error yaw lubr. pump (no ext. press. build-up) | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 6047 | Error yaw lubr. pump (no ext. press. red.) | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 6048 | Yaw lubr. container empty | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 6052 | High yaw motor current | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 6054 | Easy yaw | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 6056 | High yaw load | -- | -- | Error | 52 |  | 20 | 6 | Yaw system
[16 empty] | 6100 | Rotating direction yaw | 742 | Yaw sensor A/B | Error | 52 |  | 10 | 21 | Yaw system
[16 empty] | 6111 | Yaw velocity too low | -- | -- | Error | 52 | X | 10 | 21 | Yaw system
[16 empty] | 6115 | Yaw sensor A defect | -- | -- | Error | 52 | X | 0 | 21 | Yaw system
[16 empty] | 6116 | Yaw sensor B defect | -- | -- | Error | 52 | X | 0 | 21 | Yaw system
[16 empty] | 6120 | Uncontrolled yaw movement | -- | -- | Error | 52 | X | 20 | 23 | Yaw system
[16 empty] | 6130 | Yaw speed high | -- | -- | Error | 52 | X | 20 | 23 | Yaw system
[16 empty] | 6200 | Cable autounwind | 715 | Cable autounwind | Info | 52 |  | 20 | 28
[16 empty] | 6210 | Max. cable twistangle | 722 | Cable twisted | Error | 52 | X | 0 | 21 | Yaw system
[16 empty] | 6300 | Yaw error | 700 | Error by yawing | Error | 52 | X | 0 | 21 | Yaw system
[16 empty] | 6350 | Check nacelle position! | 777 | Check nacelle pos. | Warning | 0 |  | 0 | 27
[16 empty] | 6355 | Error nacelle pos. Load Man. | -- | -- | Warning | 0 | X | 0 | 27
[16 empty] | 6356 | Untwisting sensor test | -- | -- | Info | 52 |  | 20 | 28
[16 empty] | 6357 | Nacelle position sensor fault | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 6400 | Manual yaw brake | -- | -- | Info | 52 |  | 20 | 9
[16 empty] | 6410 | Manual yaw | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 6411 | Manual yaw via pushbutton | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 6412 | Tower referencing act. | -- | -- | Info | 52 |  | 20 | 28
[16 empty] | 6430 | Yaw current par. implausible | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 6432 | 4-20mA yaw current sensor | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 6460 | Yaw park pos. in case of icing | -- | -- | Info | 52 | X | 20 | 6
[16 empty] | 6501 | Wind.sp. diff. level 1 | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 6505 | Wind.sp. diff. level 2 | -- | -- | Error | 52 | X | 0 | 21 | Wind Sensor
[16 empty] | 6506 | Dev. wind meas./est. | -- | -- | Warning | 0 |  | 0 | 27
[16 empty] | 6510 | Anemometer 1 defect | 224 | Wind gauge R out | Warning | 0 | X | 20 | 27
[16 empty] | 6512 | Reboot anemometer 1 | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 6721 | Comm.err. IEC server -> Shadow Mgmt. Unit | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 6750 | Man. oper. meteorology heating | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 7001 | Task runtime failure 1ms | -- | -- | Error | 180 | X | 0 | 16 | PLC system
[16 empty] | 7002 | Task runtime failure 5ms | -- | -- | Error | 180 | X | 0 | 16 | PLC system
[16 empty] | 7003 | Task runtime failure 10 ms | -- | -- | Error | 180 | X | 0 | 16 | PLC system
[16 empty] | 7004 | Task runtime failure grid measuring | -- | -- | Error | 180 | X | 0 | 16 | PLC system
[16 empty] | 7005 | Division by zero | 39 | Division by zero | Error | 180 | X | 0 | 16 | PLC system
[16 empty] | 7008 | Reboot necessary after update | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 7009 | Unexpected reboot | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 7010 | Parameter unreadable | 40 | Parameter crash | Error | 170 | X | 20 | 16 | PLC system
[16 empty] | 7011 | Loading parameters | -- | -- | Info | 60 |  | 20 | 9
[16 empty] | 7012 | Manual snapshot | -- | -- | Info | 0 |  | 20 | 32
[16 empty] | 7013 | Alarm call test | 38 | Alarm call test | Info | 0 | X | 20 | 32
[16 empty] | 7014 | Cond. snapshot | -- | -- | Info | 0 |  | 20 | 32
[16 empty] | 7016 | Parameter outside limits | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 7017 | Parameter outside limits stop | -- | -- | Error | 52 | X | 20 | 15 | PLC system
[16 empty] | 7018 | Parameter update active | -- | -- | Info | 0 | X | 20 | 28
[16 empty] | 7019 | Unsafe parametrization | -- | -- | Error | 52 | X | 0 | 15 | PLC system
[16 empty] | 7025 | Configuration error | -- | -- | Error | 52 | X | 0 | 15 | PLC system
[16 empty] | 7026 | License error | -- | -- | Info | 0 |  | 0 | 27
[16 empty] | 7027 | Runtime error | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 7028 | Software exception error | -- | -- | Info | 0 |  | 0 | 28
[16 empty] | 7029 | File transfer error | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 7030 | Controller flags implausible | -- | -- | Error | 170 | X | 0 | 16 | PLC system
[16 empty] | 7031 | Controller parameter setting implausible | -- | -- | Error | 75 |  | 0 | 16 | PLC system
[16 empty] | 7035 | Controller feed forward function reduced 50% | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 7036 | Controller feed forward function deactivated | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 7040 | Set point above rated speed | -- | -- | Error | 170 | X | 0 | 15
[16 empty] | 7050 | PT100 top box defect | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 7052 | P red. incr. top box temp. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 7053 | Top box temperature high | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 7054 | Top box temperature low | -- | -- | Warning | 0 |  | 30 | 27
[16 empty] | 7055 | Error meas. top box temp. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 7057 | Heating/fan top box faulty | -- | -- | Warning | 0 |  | 0 | 27
[16 empty] | 7058 | Fuses overload | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 7059 | Max. top box temp | -- | -- | Error | 52 | X | 20 | 22
[16 empty] | 7085 | Comm. error switch top box | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 7090 | Comm. error base box switch | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 7092 | IEC interface read requests | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 7160 | Manual stop on site - maint. Required | -- | -- | Error | 52 | X | 0 | 15
[16 empty] | 7250 | HC/WTC comm. version conflict | -- | -- | Error | 52 | X | 0 | 16
[16 empty] | 7324 | Check time synchronization | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 7325 | Time sync. failed (SNTP error) | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 7335 | mconfig.ini check failed | -- | -- | Error | 60 | X | 20 | 16 | PLC system
[16 empty] | 7340 | TwC algorithm implausible | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 7350 | New initialization rotor pos. | -- | -- | Info | 52 |  | 10 | 28
[16 empty] | 7400 | High CPU temperature | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 7401 | Max. temperature CPU | 43 | Internal temp. high | Error | 52 | X | 20 | 16 | PLC system
[16 empty] | 7402 | CPU Failure RTC | 2122 | Time adjust. error | Warning | 0 | X | 0 | 27
[16 empty] | 7403 | CPU NVRAM battery | 42 | Internal battery low | Warning | 0 | X | 0 | 27
[16 empty] | 7404 | CPU memory error | 1725 | WP3100 Watchdog | Error | 180 | X | 0 | 16 | PLC system
[16 empty] | 7415 | PLC hardware error | -- | -- | Error | 52 | X | 20 | 16
[16 empty] | 7421 | CAN bus module firmware | -- | -- | Error | 52 | X | 20 | 16
[16 empty] | 7425 | Profinet communication (nacelle cool.sys.) disrupted | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 7610 | Firmware update required | -- | -- | Info | 0 |  | 0 | 28
[16 empty] | 7611 | Firmware update failed | -- | -- | Warning | 0 |  | 0 | 27
[16 empty] | 8000 | Park master stop | 99 | Parkmasterstop | Info | 52 |  | 20 | 30
[16 empty] | 8001 | Slave tripping | -- | -- | Info | 75 |  | 20 | 4
[16 empty] | 8002 | Emer. power op. active | -- | -- | Info | 52 |  | 20 | 4
[16 empty] | 8100 | Comm. failure FDM all clients | 1007 | No park communica. | Warning | 0 |  | 20 | 27
[16 empty] | 8105 | Parkmaster operation failed | -- | -- | Info | 0 |  | 0 | 27
[16 empty] | 8200 | PMU snapshot | -- | -- | Info | 0 |  | 20 | 32
[16 empty] | 8300 | Icing (farm) | -- | -- | Info | 0 | X | 20 | 28
[16 empty] | 8400 | Comm. failure FPM | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 8401 | Comm. failure FPM: stop | -- | -- | Error | 52 |  | 20 | 16
[16 empty] | 8402 | No assignment to a PMU | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 8405 | Fallback setpoints active | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 8410 | IP duplicate in WF network | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 8420 | BCP master with same seg.no. | -- | -- | Warning | 0 | X | 20 | 27
[16 empty] | 9000 | P output externally reduced | 1793 | [P] reduced EU | Info | 0 |  | 20 | 27
[16 empty] | 9001 | P limit. extern. IEC | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 9006 | dU limit. extern. IEC | -- | -- | Info | 0 |  | 20 | 27
[16 empty] | 9022 | Stop ext. prot.dev. | -- | -- | Info | 52 |  | 20 | 2
[16 empty] | 9085 | Fallback P limit. failure IEC | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 9086 | IEC failure: stop | -- | -- | Error | 52 | X | 20 | 16
[16 empty] | 9087 | Fallback dU limit. failure IEC | -- | -- | Info | 0 |  | 20 | 28
[16 empty] | 9090 | Client failure | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 9210 | Externally stopped | 135 | EU-stop | Info | 52 |  | 20 | 4
[16 empty] | 9211 | External stop IEC | -- | -- | Info | 52 |  | 20 | 4
[16 empty] | 9801 | MVS grid disconn. off | -- | -- | Info | 75 | X | 0 | 9
[16 empty] | 9802 | MVS grid ES on | -- | -- | Info | 75 | X | 0 | 9
[16 empty] | 9811 | MVS cable outlet 1 disconn. off | -- | -- | Info | 0 | X | 0 | 27
[16 empty] | 9812 | MVS cable outlet 1 ES on | -- | -- | Info | 0 | X | 0 | 27
[16 empty] | 9821 | MVS cable outlet 2 disconn. off | -- | -- | Info | 0 | X | 0 | 27
[16 empty] | 9822 | MVS cable outlet 2 ES on | -- | -- | Info | 0 | X | 0 | 27
[16 empty] | 15000 | Hot air de-icing positioning | -- | -- | Info | 52 |  | 20 | 6
[16 empty] | 15001 | Ending hot air de-icing | -- | -- | Info | 52 |  | 20 | 6
[16 empty] | 15003 | HAD man. ice prevention | -- | -- | Info | 0 |  | 20 | 32
[16 empty] | 15004 | HAD ice prevention | -- | -- | Info | 0 |  | 20 | 32
[16 empty] | 15005 | Hot air de-icing active | -- | -- | Info | 60 |  | 20 | 6
[16 empty] | 15010 | HAD semi-aut. op. | -- | -- | Info | 60 |  | 20 | 9
[16 empty] | 15015 | HAD motor prot. fan OFF | -- | -- | Warning | 0 |  | 0 | 27
[16 empty] | 15016 | HAD motor prot. heat.reg. OFF | -- | -- | Warning | 0 |  | 0 | 27
[16 empty] | 15021 | HAD motor prot. heat.reg. A1 | -- | -- | Warning | 0 |  | 0 | 27
[16 empty] | 15022 | HAD motor prot. heat.reg. A2 | -- | -- | Warning | 0 |  | 0 | 27
[16 empty] | 15023 | HAD motor prot. heat.reg. A3 | -- | -- | Warning | 0 |  | 0 | 27
[16 empty] | 15040 | HAD outside temp. de-icing too High | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 15041 | HAD outside temp. de-icing too Low | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 15042 | HAD outside temp. ice prev. too High | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 15043 | HAD outside temp. ice prev. too low | -- | --
[16 empty] | 15050 | HAD overtemp. relay | -- | -- | Warning | 0 |  | 0 | 27
[16 empty] | 15055 | HAD overtemp. flow | -- -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15056 | HAD overtemp. control box | -- -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15060 | HAD overtemp. heating | -- -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15062 | HAD temp. sensor drift A1 | -- -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15065 | temp. sensor error | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15068 | rotor pos. sensor error | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15071 | error HFU contact. A1 | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15072 | error HFU contact. A2 | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15073 | error HFU contact. A3 | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15078 | error overtemp. Relay | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15081 | motor prot. fan A1 | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15082 | motor prot. fan A2 | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15083 | motor prot. fan A3 | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15085 | de-icing implausible | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15090 | communication error | -- |  | Warning | 0 |  | 10 | 27
[16 empty] | 15091 | comm.version error | -- |  | Warning | 0 |  | 20 | 27
[16 empty] | 15094 | rotor pos. implausible | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15095 | timeout positioning | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15096 | timeout de-icing A1 | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15097 | timeout de-icing A2 | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15098 | timeout de-icing A3 | -- |  | Warning | 0 |  | 0 | 27
[16 empty] | 15101 | max. CPU temp. | -- |  | Warning | 0 | X | 20 | 27
[16 empty] | 15102 | CPU error RTC | -- |  | Warning | 0 | X | 0 | 27
[16 empty] | 15103 | CPU NVRAM battery | -- |  | Warning | 0 | X | 0 | 27
[16 empty] | 15104 | CPU memory error | -- |  | Warning | 0 | X | 0 | 27
[16 empty] | 15105 | division by zero | -- |  | Warning | 0 | X | 0 | 27
[16 empty] | 15106 | prog.runtime error 10ms | -- |  | Warning | 0 | X | 0 | 27
[16 empty] | 15107 | mconfig.ini check failed | -- |  | Warning | 0 | X | 20 | 27
[16 empty] | 15115 | PLC hardware error | -- |  | Warning | 0 | X | 20 | 27
[16 empty] | CE100001 | Manual Stop | [7 empty] | Control Panel
[16 empty] | CE100002 | Major BD - Blade | [7 empty] | Blade
[16 empty] | CE100003 | Major BD - Transformer | [7 empty] | Transformer
[16 empty] | CE100004 | Major BD - Generator | [7 empty] | Generator
[16 empty] | CE100005 | Major BD - Gearbox | [7 empty] | Gearbox
[16 empty] | CE100006 | Major BD - Main Bearing | [7 empty] | Main Bearing
[16 empty] | CE100007 | Transmission Line Related work | [7 empty] | Transmission System
[16 empty] | CE100008 | General Work Stoppage | [7 empty] | General Work
[16 empty] | CE100009 | Major BD - Power Cable | [7 empty] | Power Cable
[16 empty] | CE100011 | Major BD - DFIG | [7 empty] | DFIG
[16 empty] | CE100012 | Major BD - Foundation | [7 empty] | Foundation
[16 empty] | CE100013 | Theft | [7 empty] | Theft
[16 empty] | CE100010 | Manual Stop - Preventive Maintenance Activity | [7 empty] | Preventive Maintenance
[16 empty] | CE100014 | Manual Stop - Audit | [7 empty] | Audit
[16 empty] | CE100015 | Manual Stop - Safety Related | [7 empty] | Safety
[16 empty] | CE100016 | Manual Stop - Blade Cleaning | [7 empty] | Blade
[16 empty] | CE100017 | UPS breakdown | [7 empty] | Control Panel
[16 empty] | 3355 | No temp. rise after heat.coolant on | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 3356 | Pump cooling sys. (tower base) diff.press low | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 6515 | 4-20mA anemometer 1 | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[16 empty] | 6520 | Anemometer 2 defect | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[16 empty] | 6522 | Reboot anemometer 2 | -- | -- | Warning | 0 |  | 20 | 27 | Wind Sensor
[16 empty] | 6525 | 4-20mA anemometer 2 | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[16 empty] | 6526 | Anemometer 3 defect | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[16 empty] | 6527 | 4-20mA anemometer 3 | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[16 empty] | 6530 | Anemometer defect | -- | -- | Error | 52 | X | 20 | 21 | Wind Sensor
[16 empty] | 6540 | Icing (anemometer) | -- | -- | Information | 0 |  | 30 | 28 | Wind Sensor
[16 empty] | 6541 | No ice detection available | -- | -- | Error | 52 | X | 20 | 21 | Wind Sensor
[16 empty] | 6542 | Reset of icing st. cd. possible | -- | -- | Information | 0 | X | 20 | 32 | Wind Sensor
[16 empty] | 6571 | Ice anemometer de-icing | -- | -- | Information | 0 |  | 30 | 28 | Wind Sensor
[16 empty] | 6601 | Wind.dir. diff. level 1 | -- | -- | Warning | 0 |  | 20 | 27 | Wind Sensor
[16 empty] | 6605 | Wind.dir. diff. level 2 | -- | -- | Error | 52 | X | 0 | 21 | Wind Sensor
[16 empty] | 6620 | Vane defect | -- | -- | Error | 52 | X | 20 | 21 | Wind Sensor
[16 empty] | 6621 | Vane 1 defect | -- | -- | Warning | 0 |  | 20 | 27 | Wind Sensor
[16 empty] | 6622 | Vane 2 defect | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[16 empty] | 6625 | Check vane! | -- | -- | Error | 52 | X | 0 | 21 | Wind Sensor
[16 empty] | 6630 | 4-20 mA vane 1 | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[16 empty] | 6635 | 4-20 mA vane 2 | -- | -- | Warning | 0 | X | 20 | 27 | Wind Sensor
[16 empty] | 6670 | Light icing (red. operation) | -- | -- | Information | 0 | X | 20 | 28 | Wind Sensor
[16 empty] | 6680 | Icing (red. operation) | -- | -- | Information | 0 | X | 20 | 28 | Wind Sensor
[16 empty] | 6681 | Light icing (dev. electr. power) | -- | -- | Information | 0 |  | 30 | 28 | Wind Sensor
[16 empty] | 6682 | Icing (dev. electr. power) | -- | -- | Information | 0 |  | 30 | 28 | Wind Sensor
[16 empty] | 6686 | Extreme icing (wind > power) | -- | -- | Information | 0 | X | 30 | 27 | Wind Sensor
[16 empty] | 6690 | Icing (stop) | -- | -- | Information | 52 | X | 20 | 6 | Wind Sensor
[16 empty] | 6694 | Timed red. icing operation act. | -- | -- | Information | 0 |  | 20 | 28 | Wind Sensor
[16 empty] | 6695 | Stop in case of ice det. act. | -- | -- | Information | 0 | X | 20 | 28 | Wind Sensor
[16 empty] | 6696 | Test start during potential icing | -- | -- | Information | 0 |  | 30 | 28 | Wind Sensor
[16 empty] | 6697 | Max. starts during icing | -- | -- | Information | 52 | X | 30 | 6 | Wind Sensor
[16 empty] | 6700 | Shadow casting | -- | -- | Information | 52 |  | 20 | 2
[16 empty] | 6710 | Shadow Management Unit defect | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 6711 | Shadow Management Unit out of service | -- | -- | Error | 52 | X | 20 | 21
[16 empty] | 6712 | Shadow Management Unit warning | -- | -- | Warning | 0 |  | 20 | 27
[16 empty] | 6720 | Comm.err. IEC client -> Shadow Mgmt. Unit | -- | -- | Warning | 0 |  | 20 | 27